## Summary
Summary:- ATR Against Chronic Overloaded DTs May 2019
ATR Done
[6 empty] | Executed |  |  |  |  | Execution Planned
SDO | Division | Chronic Overloaded DTs May2019 | Action Taken | Action Planned | No Action | Additional DT Installed | DT Augmented | Load Shifted to another DT | New Substation Scheme Completed | Space constraint substation(Cooling Fan Installed) | Additional DT Scheme Approved | DT Augmentation Scheme Approved | Load shifting In Planning | LT Feeder Scheme Approved | New Substation Scheme Approved | Space Constrain(ATR Not done)
1110 | CCK
1120 | DRG
1130 | PHG
1140 | SRD
1141 | PNR | 6 | 3 | 3 |  |  |  | 3 | [5 empty] | 3
Cenrtal |  | 6 | 3 | 3 |  |  |  | 3 | [5 empty] | 3
1210 | KKD
1220 | KNR | 2 | 2 |  |  | 1 |  |  |  | 1
1230 | LNR | 3 |  | 3 | [7 empty] | 1 | 2
1240 | MVR I&II | 1 | 1 |  |  | 1
1241 | MVR I&III
South East |  | 6 | 3 | 3 |  | 2 |  |  |  | 1 |  | 1 | 2
1211 | GTR | 45 | 3 | 42 |  |  |  |  | 3 |  | 12 | 27 |  | 3
1250 | YVR | 3 | 1 | 2 |  |  | 1 | [7 empty] | 2
1251 | KWN | 10 |  | 5 | 5 | [5 empty] | 2 | 3 |  |  |  | 5
1260 | NNG
North East |  | 58 | 4 | 49 | 5 |  | 1 |  | 3 |  | 14 | 30 |  | 3 | 2 | 5
BYPL |  | 70 | 10 | 55 | 5 | 2 | 1 | 3 | 3 | 1 | 14 | 31 | 2 | 6 | 2 | 5

## Chronic Overloaded DTs >6 Month
Chronic Overloaded DTs (>70% Overloaded From Last 6 Months ) -Dec2018 To May2019
[10 empty] | Month Wise Total Overloaded Hrs. | [8 empty] | Scheme Status with scheme no. if any
Sr.No. | SDO | DIVISION | ZONE | SSTN SAP CODE | DT CODE | SSTN NAME | NO OF DTs | DT KVA | DT Meter No. | 2018-12-01 | 2019-01-01 | 2019-02-01 | 2019-03-01 | 2019-04-01 | 2019-05-01 | ATR | Final Remarks | Remarks2 | LT SCHEME | HT SCHEME | Remarks | USER STATUS OF HT
1 | 1141 | PNR | SARAI ROHILLA | PNR101 | TG-PNR101A-2 | S/STN NO.15 GALI NO.8 KALA PAHAR | 2 | 990 | 19505749 | 262 | 242.5 | 168 | 430 | 152.5 | 78 |  | LT Scheme Approved | LT Feeder Scheme Approved | PN13AT4068 |  |  | CES
2 | 1141 | PNR | SARAI ROHILLA | PNR106 | TG-PNR106A-2 | TIN MKT. K. PAHAR:PL | 2 | 630 | 19505104 | 171 | 181 | 143.5 | 129 | 274.5 | 303.5 |  | LT Scheme Approved | LT Feeder Scheme Approved | PN18UT4004 |  |  | CSE
3 | 1141 | PNR | SARAI ROHILLA | PNR120 | TG-PNR120A-1 | SOHAN SINGH K.PAHAR:PL | 3 | 630 | 19506568 | 71 | 112.5 | 122 | 261 | 199 | 223.5 | Load Shifted to another DT | Load Shifted to another DT | Load Shifted to another DT
4 | 1141 | PNR | SARAI ROHILLA | PNR137 | TG-PNR137A-1 | RUBYWALA GALI NO-10 | 2 | 630 | 19505321 | 65.5 | 72 | 64 | 92 | 67.5 | 27 | Load Shifted to another DT | Load Shifted to another DT | Load Shifted to another DT
5 | 1141 | PNR | SARAI ROHILLA | PNR138 | TG-PNR138A-1 | RIWA GALI NO-4 | 1 | 990 | 19502594 | 55.5 | 65 | 69.5 | 46 | 91.5 | 137 |  | LT Scheme Approved | LT Feeder Scheme Approved | PN17AT4008 |  |  | CES
6 | 1141 | PNR | SARAI ROHILLA | PNR149 | TG-PNR149A-1 | HR. ROAD ANAND PARVAT | 2 | 630 | 19504684 | 131.5 | 178 | 231 | 236 | 205 | 249 | Load Shifted to another DT | Load Shifted to another DT | Load Shifted to another DT
7 | 1211 | GTR | E&F DILSHAD GARDEN | DGN069 | TG-DGN069A-1 | A-BLOCK JHILMIL INDILSHAD AREA:ID | 4 | 990 | 19505452 | 118 | 207 | 182.5 | 188.5 | 212 | 175.5 | SCHEME ALREADY PREPARED | DT Scheme Approved | Additional DT Scheme Approved | DL18LT4128,DL19LT4005 | DL18AT4119 |  | INIT
8 | 1211 | GTR | E&F DILSHAD GARDEN | DGN069 | TG-DGN069A-2 | A-BLOCK JHILMIL INDILSHAD AREA:ID | 4 | 990 | 19501371 | 253.5 | 283.5 | 265 | 279.5 | 247.5 | 190.5 | SCHEME ALREADY PREPARED | DT Scheme Approved | Additional DT Scheme Approved | DL18LT4128,DL19LT4005 | DL18AT4119 |  | INIT
9 | 1211 | GTR | E&F DILSHAD GARDEN | DGN071 | TG-DGN071A-1 | B-BLK COMPLAINT CENTER JLM IND AREA:ID | 3 | 990 | 19506356 | 73.5 | 101 | 141 | 218 | 175 | 152.5 | SCHEME ALREADY PREPARED ,LT SCHEME TO BE PREPARED | DT Scheme Approved | Additional DT Scheme Approved |  | DL18AT4034 |  | INIT
10 | 1211 | GTR | E&F DILSHAD GARDEN | DGN071 | TG-DGN071A-2 | B-BLK COMPLAINT CENTER JLM IND AREA:ID | 3 | 990 | 19501446 | 139 | 215.5 | 218 | 182.5 | 102 | 32.5 | SCHEME ALREADY PREPARED ,LT SCHEME TO BE PREPARED | DT Scheme Approved | Additional DT Scheme Approved |  | DL18AT4034 |  | INIT
11 | 1211 | GTR | E&F DILSHAD GARDEN | DGN073 | TG-DGN073A-1 | SARDAR ALUMINIUM:ID | 1 | 990 | 19501448 | 69.5 | 89.5 | 69 | 64.5 | 121.5 | 165.5 | ADDITIONAL 1.6 MVA DT SCHEME TO BE PREPARED | DT Scheme Prepared | LT Feeder Scheme Approved | DL18LT4166
12 | 1211 | GTR | E&F DILSHAD GARDEN | DGN077 | TG-DGN077A-1 | SANSAR:K | 3 | 990 | 19500679 | 96.5 | 88 | 88.5 | 64.5 | 39.5 | 37 | SCHEME ALREADY PREPARED | DT Scheme Approved | Additional DT Scheme Approved | DL18LT4158 | DL18AT4072 |  | INIT
13 | 1211 | GTR | E&F DILSHAD GARDEN | DGN077 | TG-DGN077A-2 | SANSAR:K | 3 | 990 | 19505904 | 149 | 138 | 102.5 | 128 | 87.5 | 60.5 | SCHEME ALREADY PREPARED | DT Scheme Approved | Additional DT Scheme Approved | DL18LT4158 | DL18AT4072 |  | INIT
14 | 1211 | GTR | E&F DILSHAD GARDEN | DGN077 | TG-DGN077A-3 | SANSAR:K | 3 | 990 | 19506621 | 92 | 102.5 | 175.5 | 386 | 243.5 | 254 | SCHEME ALREADY PREPARED | DT Scheme Approved | Additional DT Scheme Approved | DL18LT4158 | DL18AT4072 |  | INIT
15 | 1211 | GTR | E&F DILSHAD GARDEN | DGN081 | TG-DGN081A-3 | DILSHAD GDN S/STN-4:ID | 4 | 630 | 19504435 | 235 | 231 | 97.5 | 165 | 213 | 348.5 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL18LT4148 | DL18UT4037 |  | INIT
16 | 1211 | GTR | E&F DILSHAD GARDEN | DGN101 | TG-DGN101A-2 | B-BLK DSIDC SHED JLM IA NO-3:ID | 2 | 630 | 19501353 | 188.5 | 192.5 | 218 | 209.5 | 225 | 196 | SCHEME ALREADY PREPARED | DT Scheme Approved | Additional DT Scheme Approved | DL18LT4164 | DL18AT4074 |  | INIT
17 | 1211 | GTR | E&F DILSHAD GARDEN | DGN103 | TG-DGN103A-2 | A BLK TAHIRPUR(JLM IND AREA) S/STN-1:ID | 3 | 630 | 19501356 | 93 | 133 | 107 | 82.5 | 123.5 | 143.5 | DL18UT4039 | DT Scheme Approved | DT Augmentation Scheme Approved |  | DL18UT4039 |  | INIT
18 | 1211 | GTR | E&F DILSHAD GARDEN | DGN104 | TG-DGN104A-1 | A BLK TAHIRPUR(JLM IND AREA) S/STN-3:ID | 4 | 630 | 19505489 | 135 | 164 | 188 | 350 | 147.5 | 119.5 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL17LT4049 | DL18UT4039 |  | INIT
19 | 1211 | GTR | E&F DILSHAD GARDEN | DGN107 | TG-DGN107A-2 | B BLK OPP SWAHNEY IND.:PL | 3 | 630 | 19505690 | 216 | 154 | 147 | 149 | 130.5 | 218 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL18LT4106 | DL18UT4040 |  | INIT
20 | 1211 | GTR | E&F DILSHAD GARDEN | DGN109 | TG-DGN109A-1 | B-34 JLM INDUSTRIAL AREA | 1 | 990 | 19501836 | 182.5 | 206 | 210.5 | 167.5 | 136 | 217.5 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL18LT4165 | DL18UT4041 |  | APP1
21 | 1211 | GTR | E&F DILSHAD GARDEN | DGN112 | TG-DGN112A-1 | DAMODAR PARK,DILSHAD GARDEN:PL | 4 | 990 | 19506505 | 293 | 350.5 | 306.5 | 604 | 285 | 270 | LOAD TO BE RATIONALIZED & LT FEEDER SCHEME TO BE PREPARED | Scheme In Completed | New Substation Scheme Completed |  | DL18SS4007 |  | ACRF
22 | 1211 | GTR | E&F DILSHAD GARDEN | DGN112 | TG-DGN112A-2 | DAMODAR PARK,DILSHAD GARDEN:PL | 4 | 990 | 19502279 | 295 | 426.5 | 359.5 | 352.5 | 194 | 193 | LOAD TO BE RATIONALIZED & LT FEEDER SCHEME TO BE PREPARED | Scheme In Completed | New Substation Scheme Completed |  | DL18SS4007 |  | ACRF
23 | 1211 | GTR | E&F DILSHAD GARDEN | DGN112 | TG-DGN112A-3 | DAMODAR PARK,DILSHAD GARDEN:PL | 4 | 990 | 19505439 | 249 | 259.5 | 196.5 | 92.5 | 355 | 338.5 | LOAD TO BE RATIONALIZED & LT FEEDER SCHEME TO BE PREPARED | Scheme In Completed | New Substation Scheme Completed |  | DL18SS4007 |  | ACRF
24 | 1211 | GTR | E&F DILSHAD GARDEN | DGN114 | TG-DGN114A-1 | JHULFE BENGAL S/S NO. 2:PL | 3 | 630 | 19506419 | 243 | 184.5 | 174.5 | 343 | 264.5 | 290 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL18LT4130 | DL18UT4042 |  | APP3
25 | 1211 | GTR | E&F DILSHAD GARDEN | DGN114 | TG-DGN114A-3 | JHULFE BENGAL S/S NO. 2:PL | 3 | 990 | 19500063 | 180.5 | 131 | 145.5 | 73.5 | 157 | 224 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL18LT4130 | DL18UT4042 |  | APP3
26 | 1211 | GTR | E&F DILSHAD GARDEN | DGN128 | TG-DGN128A-1 | JULFE BENGAL S/S NO.I | 3 | 990 | 19505545 | 395 | 302.5 | 277 | 542 | 230 | 165.5 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL18LT4103 | DL18UT4043 |  | INIT
27 | 1211 | GTR | E&F DILSHAD GARDEN | DGN128 | TG-DGN128A-3 | JULFE BENGAL S/S NO.I | 3 | 630 | 19506329 | 114.5 | 173 | 263.5 | 420 | 300.5 | 149 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL18LT4103 | DL18UT4043 |  | INIT
28 | 1211 | GTR | E&F DILSHAD GARDEN | DGN147 | TG-DGN147A-1 | SATISH STEEL ROLLING MILL:ID | 2 | 630 | 19506363 | 84.5 | 142 | 108 | 226 | 92.5 | 61.5 | AUGMENTED 990 MVA DT SCHEME TO BE PREPARED | DT Scheme Approved | LT Feeder Scheme Approved | DL18LT4160
29 | 1211 | GTR | E&F DILSHAD GARDEN | DGN232 | TG-DGN232A-2 | DSIDC SUBSTATION NO-2 | 4 | 990 | 19501354 | 103.5 | 163 | 161 | 157 | 172 | 182.5 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL18LT4163 | DL18UT4055 |  | INIT
30 | 1211 | GTR | E&F DILSHAD GARDEN | DGN232 | TG-DGN232A-3 | DSIDC SUBSTATION NO-2 | 4 | 990 | 19505129 | 389 | 389 | 346.5 | 354.5 | 367.5 | 346 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL18LT4163 | DL18UT4055 |  | INIT
31 | 1211 | GTR | E&F DILSHAD GARDEN | DGN237 | TG-DGN237A-2 | B-42 JHILMIL IND AREA NEARRAILWAY LINE | 2 | 990 | 19505961 | 150 | 118.5 | 55.5 | 55 | 43 | 75 | LOAD TO BE RATIONALIZED | DT Scheme Approved | Additional DT Scheme Approved |  | DL18AT4076 |  | INIT
32 | 1211 | GTR | E&F DILSHAD GARDEN | DGN252 | TG-DGN252A-1 | RAILWAY LINE IN FRONT OF B-43 JHILMIL | 1 | 990 | 19506619 | 107 | 117.5 | 138 | 254 | 167 | 188.5 | LOAD TO BE RATIONALIZED,LT FEEDER TO PREPARED | DT Scheme Approved | Additional DT Scheme Approved |  | DL18AT4076 |  | INIT
33 | 1211 | GTR | GT ROAD SHAHDRA | DGN074 | TG-DGN074A-1 | RAJ ENGG.COMPOUND | 2 | 990 | 19501787 | 113 | 163.5 | 173 | 150 | 197.5 | 191.5 | AUGMENTED 1.6 MVA DT SCHEME TO BE PREPARED | DT Scheme Approved | LT Feeder Scheme Approved | DL18LT4090 |  | LOAD RATIONALISED ON DT.18.06.2019
34 | 1211 | GTR | GT ROAD SHAHDRA | DGN075 | TG-DGN075A-1 | PAPER PRODUCT | 2 | 990 | 19505761 | 54.5 | 70 | 66 | 150 | 81.5 | 90.5 | SCHEME TO BE PREPARED | DT Scheme Approved | Additional DT Scheme Approved |  | DL18AT4062 |  | INIT
35 | 1211 | GTR | GT ROAD SHAHDRA | DGN075 | TG-DGN075A-2 | PAPER PRODUCT | 2 | 630 | 19505760 | 166.5 | 156.5 | 106 | 104 | 78.5 | 32.5 | SCHEME TO BE PREPARED | DT Scheme Approved | Additional DT Scheme Approved |  | DL18AT4062 |  | INIT
36 | 1211 | GTR | GT ROAD SHAHDRA | DGN105 | TG-DGN105A-1 | SHAMBU NATH COMP.(F.COL):ID | 5 | 990 | 19505392 | 314.5 | 266.5 | 276 | 270 | 274 | 299 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL17LT4045,DL18LT4091 | DL18UT4065 |  | INIT
37 | 1211 | GTR | GT ROAD SHAHDRA | DGN105 | TG-DGN105A-3 | SHAMBU NATH COMP.(F.COL):ID | 5 | 990 | 19505434 | 232.5 | 139.5 | 122 | 88.5 | 53 | 40.5 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL17LT4045,DL18LT4091 | DL18UT4065 |  | INIT
38 | 1211 | GTR | GT ROAD SHAHDRA | DGN105 | TG-DGN105A-4 | SHAMBU NATH COMP.(F.COL):ID | 5 | 990 | 19505076 | 151.5 | 240.5 | 191.5 | 145.5 | 185 | 145 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL17LT4045,DL18LT4091 | DL18UT4065 |  | INIT
39 | 1211 | GTR | GT ROAD SHAHDRA | DGN110 | TG-DGN110A-1 | VERMA CASTLE:PL | 5 | 990 | 19503035 | 191 | 237.5 | 188 | 162.5 | 225.5 | 172 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL17LT4031 | DL18UT4123 |  | APP3
40 | 1211 | GTR | GT ROAD SHAHDRA | DGN110 | TG-DGN110A-3 | VERMA CASTLE:PL | 5 | 630 | 19505004 | 118 | 140.5 | 75 | 94.5 | 67 | 140.5 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL17LT4031 | DL18UT4123 |  | APP3
41 | 1211 | GTR | GT ROAD SHAHDRA | DGN110 | TG-DGN110A-4 | VERMA CASTLE:PL | 5 | 630 | 19506339 | 247.5 | 212.5 | 196.5 | 422 | 214.5 | 216 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL17LT4031 | DL18UT4123 |  | APP3
42 | 1211 | GTR | GT ROAD SHAHDRA | DGN110 | TG-DGN110A-5 | VERMA CASTLE:PL | 5 | 990 | 19506053 | 138 | 42.5 | 106.5 | 213 | 149.5 | 144 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL17LT4031 | DL18UT4123 |  | APP3
43 | 1211 | GTR | GT ROAD SHAHDRA | DGN111 | TG-DGN111A-1 | FRIENDS COLONY GALI NO.1 | 3 | 990 | 19500654 | 229.5 | 139 | 97 | 106 | 150 | 116 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL18LT4218 | DL18UT4070 |  | INIT
44 | 1211 | GTR | GT ROAD SHAHDRA | DGN127 | TG-DGN127A-2 | GALI NO.1B FRIENDS COLONY:PL | 4 | 990 | 19504119 | 141.5 | 181.5 | 154.5 | 152.5 | 147 | 77 | SCHEME TO BE PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved |  | DL18UT4067 |  | INIT
45 | 1211 | GTR | GT ROAD SHAHDRA | DGN129 | TG-DGN129A-2 | FRIENDS COLONY GALI NO-5-6 NEAR RLY.LINE:PM | 6 | 990 | 19506017 | 138 | 210.5 | 206 | 279 | 104 | 175.5 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved |  | DL18UT4068 |  | APP1
46 | 1211 | GTR | GT ROAD SHAHDRA | DGN129 | TG-DGN129A-4 | FRIENDS COLONY GALI NO-5-6 NEAR RLY.LINE:PM | 6 | 990 | 19505079 | 97 | 78 | 71 | 184.5 | 186 | 228 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved |  | DL18UT4068 |  | APP1
47 | 1211 | GTR | GT ROAD SHAHDRA | DGN178 | TG-DGN178A-1 | HANSRAJ COMPOUND S/STN | 4 | 990 | 19505895 | 77.5 | 176.5 | 180.5 | 312 | 142 | 196 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL18LT4089 | DL18UT4049 |  | INIT
48 | 1211 | GTR | GT ROAD SHAHDRA | DGN198 | TG-DGN198A-1 | GALI NO-1 METRO PARKING SS-2 | 3 | 990 | 19506421 | 149 | 163 | 197 | 606 | 294 | 291.5 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL18LT4087 | DL18UT4052 |  | INIT
49 | 1211 | GTR | GT ROAD SHAHDRA | DGN231 | TG-DGN231A-1 | GALI NO-1 RAILWAY LINE FRIENDS COLONY | 2 | 990 | 19504996 | 109 | 185.5 | 75 | 128.5 | 217 | 205.5 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL18LT4088 | DL18UT4070 |  | INIT
50 | 1211 | GTR | GT ROAD SHAHDRA | DGN231 | TG-DGN231A-2 | GALI NO-1 RAILWAY LINE FRIENDS COLONY | 2 | 630 | 19506054 | 192.5 | 195 | 218 | 430 | 227.5 | 185 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL18LT4088 | DL18UT4070 |  | INIT
51 | 1211 | GTR | GT ROAD SHAHDRA | DGN236 | TG-DGN236A-1 | 1B Friends colony near railway line. | 1 | 990 | 19505054 | 143 | 254.5 | 48 | 96 | 141 | 99 | SCHEME ALREADY PREPARED | DT Scheme Approved | DT Augmentation Scheme Approved | DL18LT4086 | DL18UT4057 |  | INIT
52 | 1220 | KNR | GANDHI NAGAR | GAN029 | TG-GAN029A-1 | SEELAMPUR PHATAK:PL | 1 | 990 | 19506480 | 201 | 311 | 321.5 | 521 | 474 | 335.5 | Additional 630 KVA DT has been installed to share the load of existing 990 KVA overloaded DT | Additional 630 KVA DT Installed | Additional DT Installed |  |  | KN14AT4109 | Completed
53 | 1220 | KNR | KRISHNA NAGAR | KRI035 | TG-KRI035A-1 | PANDIT PARK:PM | 1 | 990 | 19500865 | 30 | 27.5 | 103 | 85.5 | 178.5 | 258 | Cooling fans provided at S/stn. Pandit park. Due to space constraint the additional transformer could not be installed | Space constraint substation(Cooling Fan Installed) | Space constraint substation(Cooling Fan Installed) |  |  | KN18MS4211 | Completed
54 | 1230 | LNR | ANAND VIHAR ISBT | PVR034 | TG-PVR034A-1 | S/STN. NO.8 F.I.E., PPG:ID | 3 | 630 | 19505921 | 68 | 64.5 | 38.5 | 170 | 161 | 119.5 | FOR LOAD SHARING TO OTHER DTs INSTALLED IN SAME SSTNs,PSD HAVE BEEN ENTERED AND LOAD WILL BE SHARED WITHIN 15 DAYS | Load shifting planned | Load shifting In Planning
55 | 1230 | LNR | ANAND VIHAR ISBT | PVR040 | TG-PVR040A-2 | S/STN. NO.15 F.I.E., PPG:ID | 2 | 400 | 19504783 | 41.5 | 108 | 81 | 74.5 | 160.5 | 202.5 | FOR LOAD SHARING TO OTHER DT INSTALLED IN SAME SSTNs,PSD HAVE BEEN ENTERED AND LOAD WILL BE SHARED WITHIN 15 DAYS | Load shifting planned | Load shifting In Planning
56 | 1230 | LNR | MANDAWALI | MAN026 | TG-MAN026A-2 | WESTVINOD NAGAR NEAR MANGLAM:PL | 3 | 990 | 19506134 | 112.5 | 146.5 | 121.5 | 177 | 244.5 | 512.5 | LN18UT4138 | DT Scheme Prepared | DT Augmentation Scheme Approved |  |  | 2*1600 DTs ALLOCATION PENDING
57 | 1240 | MVR | S/STN 8 POCKET C | MV2010 | TG-MV2010A-2 | E BLOCK V. NAGAR:PL | 2 | 990 | 19502553 | 76 | 104 | 82 | 41.5 | 86.5 | 81.5 | Addl 630 KVA DT installed on temporary basis at E blk V. NGR and load has been rationalized on this DT | Additional 630 KVA DT Installed on temporary basis | Additional DT Installed | MV18AT4012 |  | 630 KVA DT installed on temporary basis at E Blk East Vinod Ngr as proposed 990 KVA DT under scheme MV18AT4012 is not available in store. So 990 KVA DT will be installed once DT will be available by removing temporary DT with prior approval of PSD
58 | 1250 | YVR | GHONDA | GHO019 | TG-GHO019A-1 | KHADDEY WALI MASJID:PM | 1 | 630 | 19506336 | 62.5 | 119 | 84.5 | 66 | 333.5 | 710 | YV18SS4044 | DT Scheme Approved | New Substation Scheme Approved |  |  |  | SCHEME YET TO START
59 | 1250 | YVR | GHONDA | GHO028 | TG-GHO028A-1 | AMBEDKAR BASTI GHONDA:PL | 2 | 990 | 19505171 | 329.5 | 341.5 | 333 | 189.5 | 94.5 | 348 | Load rationalize with 1.6 MVA DTR | DT Augmented(990 to 1600 KVA) | DT Augmented |  |  |  | Load rationalize with 1.6 MVA DTR
60 | 1250 | YVR | GHONDA | GHO040 | TG-GHO040A-1 | MAIN BRAHMPURI RD GALI NO.19:PM | 1 | 630 | 19506050 | 42.5 | 87.5 | 28.5 | 47 | 249.5 | 425 | YV18UT4160 | Scheme In Planning | New Substation Scheme Approved |  |  | SCHEME YET TO START | MLA to provide the elevated platform at Brahmpuri Road.
61 | 1251 | KWR | GOKUL PURI | KWL053 | TG-KWL053A-2 | JAWHAR NAGAR NO.-1:PL | 2 | 990 | 19504953 | 151.5 | 137 | 126.5 | 151.5 | 181 | 173 | Scheme Framed | DT Scheme Approved | DT Augmentation Scheme Approved | KW18UT4031--Yet to start |  | 1.6MVA DT required
62 | 1251 | KWR | GOKUL PURI | KWL237 | TG-KWL237A-1 | SHANI BAZAR ROAD JOHRI PUR :PM | 1 | 630 | 19505924 | 147.5 | 144.5 | 175.5 | 388 | 213.5 | 174 | Space Constraint | Space Constraint(Not ATR) | Space Constraint(Not ATR)
63 | 1251 | KWR | GOKUL PURI | KWL257 | TG-KWL257A-1 | Opposite Durga Factory (BARELIA) :PM | 1 | 400 | 19502935 | 188 | 198.5 | 209.5 | 193 | 207 | 173.5 | Space Constraint | Space Constraint(Not ATR) | Space Constraint(Not ATR)
64 | 1251 | KWR | GOKUL PURI | KWL331 | TG-KWL331A-1 | GALI NO.5 JAWAHAR NAGAR P/M | 1 | 990 | 19504775 | 113 | 138 | 65.5 | 29 | 133 | 124.5 | Scheme Framed | DT Scheme Approved | DT Augmentation Scheme Approved | KW18UT4024--Yet to start |  | 1.6MVA DT required
65 | 1251 | KWR | KARAWAL NAGAR | KWL056 | TG-KWL056A-2 | KARWAL NAGAR NO.-1 DAL MILL:PL | 2 | 990 | 19506728 | 97 | 189.5 | 188 | 319 | 213 | 235.5 | Space Constraint | Space Constraint(Not ATR) | Space Constraint(Not ATR)
66 | 1251 | KWR | KARAWAL NAGAR | KWL058 | TG-KWL058A-2 | KARWAL NAGAR NO.-4:PL | 2 | 990 | 19503507 | 175 | 130.5 | 36 | 47 | 86.5 | 125.5 | Scheme Framed | Space Constraint(Not ATR) | Space Constraint(Not ATR)
67 | 1251 | KWR | KARAWAL NAGAR | KWL059 | TG-KWL059A-1 | KARWAL NAGAR NO.-5 SBI KWR:PL | 3 | 990 | 19500596 | 150 | 161.5 | 183.5 | 177 | 193 | 186 | Scheme Framed | DT Scheme Approved | Additional DT Scheme Approved | KW17AT4040--WIP |  | 630KVA to 990KVA completed, additional 630KVA to be installed
68 | 1251 | KWR | KARAWAL NAGAR | KWL059 | TG-KWL059A-2 | KARWAL NAGAR NO.-5 SBI KWR:PL | 3 | 990 | 19502963 | 70.5 | 160 | 96 | 162.5 | 198 | 35 | Scheme Framed | Scheme Completed | Additional DT Scheme Approved | KW17AT4040--WIP |  | 630KVA to 990KVA completed, additional 630KVA to be installed
69 | 1251 | KWR | KARAWAL NAGAR | KWL264 | TG-KWL264A-1 | WEST KAMAL VIHAR (HVDS) INDUT. AREA:PM | 1 | 400 | 19505888 | 58.5 | 89 | 72.5 | 79 | 60 | 58 | Space Constraint | Space Constraint(Not ATR) | Space Constraint(Not ATR) |  |  | 400KVA DT installed at DP, which is at turning radius of road
70 | 1251 | KWR | SONIA VIHAR | KWL064 | TG-KWL064A-2 | SHERPUR CHOWK:PL | 2 | 630 | 19506395 | 124 | 98.5 | 136.5 | 195 | 146 | 171 | Scheme Framed | DT Scheme Approved | DT Augmentation Scheme Approved | KW18UT4014--Yet to start