## Complete Report
MIS Report of Distribution Transformer - Jun19
Jun19 ALL (Complete Report)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | KIKARWALAN | 1141 | PNR015 | 1S-DL-YP-CTC-DPNR-1451-PNR015 | KRISHNA TIRATH DEV NAGAR | TG-PNR015A-2 | 19506094 | 1600 | 500 | 246.7814 | 0.97967 | 1463.8372 | 475.3528 | 2045.8479 | 504.0647 | 2166.8088 | 484.4198 | 2092.7971 | 105.6255 | 2019-06-01 15:00 | [15 empty] | 445 |  |  |  | 37 |  |  |  | 180.5 |  |  |  | 53 |  |  |  | 0 | 715.5 |  | 0.34353 | 0.9149
2 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN105 | 1S-DL-YP-ETC-DDGN-2251-DGN105 | SHAMBU NATH COMP.(F.COL):ID | TG-DGN105A-5 | 19506742 | 1600 | 500 | 248 | 0.91 | 1203 | 392 | 1651 | 409 | 1726 | 402 | 1704 | 67 | 2019-06-22 11:30 | 321.5 | -236.5 | 1726 | Y | 97 | 101 | 102 | 5 |  | 0.1 | 7.7 | 92.2 | 272.51 | 261.51 | 226.21 | 255.51 | 156.22 | 156.52 | 156.52 | 166.52 | 267.05 | 277.35 | 275.05 | 273.35 | [8 empty] | 696.18 | 23.42 | 0.45 | 0.75
3 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN023 | 1S-DL-YP-ETC-DDGN-2251-DGN023 | SHIVAJI PARK ARYA SAMAJ MANDIR | TG-DGN023A-1 | 19501792 | 1600 | 500 | 250 | 0.96 | 1612 | 534 | 2155 | 471 | 1903 | 606 | 2441 | 466 | 2019-06-11 00:30 | 378.4 | 70.2 | 2441 | B | 99 | 91 | 110 | 19 |  |  | 0.5 | 99.5 | 0.3 | 0.3 |  | 0.3 | 109.52 | 196.02 | 196.02 | 109.02 | 573.54 | 514.42 | 551.43 | 573.31 | 27.28 | 1 | 91.09 | 28.41 | 0.3 |  | 3.41 | 0.3 | 712.14 | 7.46 | 0.53 | 1.01
4 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG002 | 1S-DL-YP-ETC-DKRN-2104-JAG002 | BEDI MKT:ID | TG-JAG002A-2 | 19506104 | 1600 | 500 | 243 | 0.97 | 2307 | 457 | 1978 | 874 | 4198 | 976 | 4330 | 2289 | 2019-06-08 23:00 | 710.5 | 44.5 | 4330 | B | 105 | 92 | 103 | 13 | 0.8 | 0.3 | 56.4 | 42.5 | 0.57 | 0.57 | 0.05 | 0.05 | 111.24 | 220.13 | 220.13 | 146.46 | 470.54 | 423 | 464.44 | 457.47 | 101.35 | 49.47 | 88.01 | 86.1 | 11.01 | 1.54 | 15.35 | 5.03 | 695.51 | 24.09 | 0.38 | 1.44
5 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG006 | 1S-DL-YP-ETC-DKRN-2104-JAG006 | CHANDER NAGAR:ID | TG-JAG006A-1 | 19500790 | 1600 | 500 | 242 | 0.97 | 895 | 265 | 1112 | 350 | 1488 | 280 | 1199 | 341 | 2019-06-01 00:30 | 170.2 | 65.6 | 1555 | Y | 85 | 111 | 104 | 26 |  | 0.8 | 92.2 | 7.1 | 31.49 | 1 | 3 | 4.22 | 614.05 | 428.17 | 428.17 | 528.51 | 72.45 | 289.22 | 214.49 | 185.26 | [8 empty] | 718.39 | 1.21 | 0.63 | 0.56
6 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG019 | 1S-DL-YP-ETC-DKRN-2104-JAG019 | JAGAT PURI B BLK:ID | TG-JAG019A-1 | 19506860 | 1600 | 500 | 244 | 0.97 | 1211 | 399 | 1699 | 353 | 1489 | 460 | 1974 | 420 | 2019-06-29 23:00 | 306.5 | 94 | 1974 | B | 100 | 93 | 107 | 14 | 0.4 |  | 12.8 | 86.8 |  |  |  |  | 165.57 | 204.27 | 204.27 | 170.57 | 254.19 | 215.49 | 266.19 | 249.19 |  |  | 8 | [5 empty] | 704.38 | 15.22 | 0.59 | 0.76
7 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG028 | 1S-DL-YP-ETC-DKRN-2104-JAG028 | RAM NAGAR EXT:K | TG-JAG028A-2 | 19506788 | 1600 | 500 | 243 | 0.97 | 882 | 257 | 1075 | 244 | 1025 | 381 | 1619 | 571 | 2019-06-12 00:30 | 286 | 51 | 2014 | B | 90 | 88 | 121 | 33 | 0.3 | 0.2 | 79.7 | 19.8 | 20.3 | 36.31 | 5.3 | 14 | 630.58 | 649.57 | 649.57 | 569.58 | 55.14 | 20.14 | 275.08 | 122.44 |  |  | 0.3 | [5 empty] | 706.42 | 13.18 | 0.59 | 0.55
8 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN008 | 1S-DL-YP-ETC-DKRN-2102-GAN008 | GALI GURDWARA NO. 2:ID | TG-GAN008A-2 | 19506796 | 1600 | 500 | 244 | 0.97 | 1217 | 406 | 1692 | 388 | 1619 | 423 | 1753 | 116 | 2019-06-02 16:00 | 276.5 | 81 | 1789 | R | 104 | 96 | 100 | 8 | 0.1 |  | 6.3 | 93.6 |  |  |  |  | 59.3 | 150.3 | 150.3 | 105.3 | 643.52 | 552.52 | 577.52 | 597.52 | [8 empty] | 703.22 | 16.38 | 0.69 | 0.76
9 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN022 | 1S-DL-YP-ETC-DKRN-2102-GAN022 | NEHRU GALI:PL | TG-GAN022A-1 | 19504382 | 2000 | 640 | 245 | 0.99 | 1400 | 504 | 2114 | 432 | 1790 | 463 | 1912 | 283 | 2019-06-30 14:30 | 191.4 | -4.4 | 2114 | R | 109 | 93 | 98 | 16 |  | 0.1 | 51 | 48.9 | 451.04 | 455.52 | 449.22 | 452.22 | 34.48 | 43 | 43 | 40.3 | 231.27 | 218.27 | 214.57 | 224.27 | [8 empty] | 717.19 | 2.41 | 0.29 | 0.7
10 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI005 | 1S-DL-YP-ETC-DKRN-2101-KRI005 | B - BLOCK MEERA MANDAL | TG-KRI005A-1 | 19504858 | 1600 | 500 | 244 | 0.97 | 1085 | 328 | 1421 | 437 | 1869 | 320 | 1391 | 463 | 2019-06-30 00:30 | 259.9 | 84 | 1951 | Y | 94 | 123 | 83 | 40 |  | 10.6 | 89.3 | 0.1 |  |  | 2.3 |  | 382.24 | 72.3 | 72.3 | 318.24 | 335.52 | 638.04 | 201.37 | 399.52 |  | 7.42 | [6 empty] | 718.16 | 1.44 | 0.63 | 0.68
11 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI019 | 1S-DL-YP-ETC-DKRN-2101-KRI019 | J-BLOCK KRN:PL | TG-KRI019A-1 | 19506883 | 1600 | 500 | 244 | 0.97 | 1299 | 382 | 1663 | 360 | 1564 | 556 | 2455 | 846 | 2019-06-03 | 449 | 83 | 2455 | B | 100 | 99 | 100 | 1 | 0.3 |  | 8.2 | 91.5 |  |  |  |  | 285.38 | 302.25 | 302.25 | 311.3 | 421.15 | 390.28 | 354.11 | 394.54 |  | 14 | 23.05 | 0.29 |  |  | 0.29 |  | 706.53 | 13.07 | 0.55 | 0.81
12 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI041 | 1S-DL-YP-ETC-DKRN-2101-KRI041 | RAM NAGAR L.N.MANDIR:PL | TG-KRI041A-1 | 19506779 | 1600 | 500 | 251 | 0.96 | 1465 | 776 | 3572 | 313 | 1264 | 375 | 1596 | 2161 | 2019-06-11 01:00 | 551 | 90.5 | 3572 | R | 107 | 96 | 97 | 11 | 0.4 | 0.1 | 61.4 | 38.2 |  | 3.3 | 0.3 |  | 224.3 | 339.28 | 339.28 | 290.58 | 453.42 | 364.14 | 409.44 | 413.44 | 28.3 | 0.3 |  | 3 | 1 |  |  |  | 707.42 | 12.18 | 0.51 | 0.92
13 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR019 | 1S-DL-YP-ETC-DLNR-2501-LGR019 | RAMESH PARK J & K BLOCK:PL | TG-LGR019A-1 | 19502336 | 1600 | 500 | 242 | 0.97 | 1286 | 421 | 1847 | 471 | 2103 | 393 | 1728 | 332 | 2019-06-01 | 203.6 | 88.6 | 2103 | Y | 95 | 114 | 91 | 23 |  | 0.9 | 93.3 | 5.8 |  |  | 1 |  | 269.27 | 83 | 83 | 202.57 | 450.09 | 604.17 | 391.09 | 516.09 |  | 32.19 |  | 0.3 |  |  |  |  | 719.36 | 0.24 | 0.6 | 0.8
14 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR033 | 1S-DL-YP-ETC-DLNR-2501-LGR033 | U BLOCK SHAKARPUR:PM | TG-LGR033A-1 | 19502818 | 1600 | 500 | 242 | 0.98 | 1181 | 405 | 1727 | 363 | 1563 | 413 | 1766 | 187 | 2019-06-12 14:30 | 245 | 79.4 | 1766 | B | 102 | 96 | 102 | 6 |  |  | 8 | 92 |  |  |  |  | 45 | 109.01 | 109.01 | 57.33 | 671.35 | 607.34 | 665.32 | 659.02 | [8 empty] | 716.35 | 3.25 | 0.69 | 0.74
15 | 2019-06-01 | 2019-06-30 21:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR043 | 1S-DL-YP-ETC-DLNR-2501-LGR043 | SUNDER BLOCK, SHAKARPUR:PL | TG-LGR043A-1 | 19502815 | 1600 | 500 | 243.3516 | 0.98012 | 1768.3862 | 380.2798 | 1630.5626 | 397.481 | 1707.686 | 990.6254 | 4230.9105 | 2562.6567 | 2019-06-30 01:30 | [15 empty] | 0 |  |  |  | 67.5 |  |  |  | 500.5 |  |  |  | 82.5 |  |  |  | 16.5 | 667 |  | 0.53799 | 1.1052
16 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN011 | 1S-DL-YP-ETC-DLNR-2503-MAN011 | GANESH NAGAR COM. C BLCK.:PL | TG-MAN011A-1 | 19500759 | 1600 | 500 | 236.1626 | 0.98463 | 1503.0792 | 476.6178 | 2165.3617 | 576.61 | 2608.7411 | 449.8514 | 2026.8143 | 526.5071 | 2019-06-30 23:30 | [15 empty] | 0 |  |  |  | 51.5 |  |  |  | 601.5 |  |  |  | 66.5 |  |  |  | 0 | 719.5 |  | 0.61074 | 0.93942
17 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN015 | 1S-DL-YP-ETC-DLNR-2503-MAN015 | MANDAWALI ( POST OFFICE):PL | TG-MAN015A-1 | 19505934 | 2000 | 640 | 245 | 0.97 | 1440 | 458 | 1959 | 494 | 2107 | 488 | 2096 | 142 | 2019-06-30 | 429.4 | 119 | 2136 | Y | 99 | 103 | 98 | 5 | 0.1 |  | 1.2 | 98.7 |  |  |  |  | 239.1 | 232.4 | 232.4 | 250.1 | 466.19 | 472.49 | 418.52 | 455.19 | [8 empty] | 705.29 | 14.31 | 0.63 | 0.72
18 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM017 | 1S-DL-YP-ETC-DYVR-2402-YAM017 | C-BLOCK GALI NO7 BHAJAN PURA:PL | TG-YAM017A-1 | 19502144 | 1600 | 500 | 241 | 0.97 | 1608 | 495 | 2096 | 452 | 1919 | 661 | 2819 | 826 | 2019-06-01 00:30 | 323.2 | 92 | 2819 | B | 103 | 89 | 108 | 19 |  |  | 5.7 | 94.3 |  | 0.3 |  |  | 124.48 | 232.37 | 232.37 | 148.05 | 540.14 | 466.05 | 482.36 | 525.18 | 36.54 | 2.44 | 89.43 | 28.05 |  |  | 6.06 | 0.28 | 701.56 | 18.04 | 0.53 | 1
19 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM028 | 1S-DL-YP-ETC-DYVR-2402-YAM028 | SUBJI MANDI-1 MAUJ PUR | TG-YAM028A-1 | 19506745 | 1600 | 500 | 239 | 0.97 | 1717 | 582 | 2515 | 607 | 2592 | 528 | 2265 | 296 | 2019-06-30 01:30 | 466.5 | 124.5 | 2800 | Y | 96 | 109 | 94 | 15 | 0.3 | 0.1 | 20.3 | 79.2 |  |  |  |  | 38.5 | 16.2 | 16.2 | 27.5 | 586.48 | 510.35 | 593.53 | 563.04 | 58.43 | 114.03 | 53.34 | 94.51 | 4.43 | 48.06 |  | 3.19 | 689.04 | 30.56 | 0.57 | 1.07
20 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM040 | 1S-DL-YP-ETC-DYVR-2402-YAM040 | VIJAY PARK ADARSH MOHALLA;PL | TG-YAM040A-1 | 19505645 | 1600 | 500 | 243 | 0.96 | 1023 | 383 | 1655 | 273 | 1153 | 367 | 1593 | 474 | 2019-06-11 23:30 | 300 | 84 | 1716 | B | 99 | 83 | 118 | 35 | 0.2 | 1.7 | 62.6 | 35.5 | 11.54 | 87.24 | 1.24 | 8.54 | 519.24 | 536.44 | 536.44 | 518.19 | 179.58 | 87.08 | 290.35 | 184.03 | [8 empty] | 711.16 | 8.44 | 0.54 | 0.64
21 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO008 | 1S-DL-YP-ETC-DYVR-2404-GHO008 | GAMRI KIOSK:K | TG-GHO008A-1 | 19506830 | 1600 | 500 | 243 | 0.97 | 1217 | 362 | 1489 | 394 | 1645 | 462 | 1918 | 376 | 2019-06-11 23:30 | 360.5 | 45.5 | 2132 | B | 94 | 103 | 103 | 9 | 0.1 | 2.2 | 75.2 | 22.5 | 0.3 | 0.3 | 0.3 | 0.3 | 28.2 | 14.3 | 14.3 | 19 | 672.02 | 685.22 | 640.27 | 681.22 |  | 0.3 | 26.28 | [5 empty] | 700.52 | 19.08 | 0.72 | 0.76
22 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM074 | 1S-DL-YP-ETC-DYVR-2401-SLM074 | BANARASHI CLINIC RISHI KARDAM | TG-SLM074A-1 | 19504177 | 1600 | 500 | 237 | 0.97 | 689 | 261 | 1088 | 228 | 952 | 200 | 825 | 228 | 2019-06-29 23:30 | 165.6 | 57.5 | 1088 | R | 108 | 105 | 87 | 21 |  |  | 33.2 | 66.8 | 1.3 | 2.3 | 40 | 6.3 | 657.28 | 678.21 | 678.21 | 694.08 | 57.2 | 35.27 | 0.2 | 15.4 | [8 empty] | 716.18 | 3.42 | 0.71 | 0.43
23 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL013 | 1S-DL-YP-ETC-DKWL-2451-KWL013 | C BLK MUKUND VIHAR GALI NO. 9:ID | TG-KWL013A-1 | 19505641 | 1600 | 500 | 244 | 0.97 | 1944 | 665 | 2676 | 591 | 2390 | 689 | 2810 | 371 | 2019-06-02 05:30 | 761 | 102.5 | 2810 | B | 104 | 96 | 100 | 8 | 0.1 |  | 12.6 | 87.3 |  |  |  |  | 54.36 | 126 | 126 | 81.3 | 527.59 | 488.25 | 469.25 | 512 | 109.59 | 84.52 | 124.17 | 104.17 | 6.54 | 0.11 | 3.11 | 1.41 | 699.28 | 20.32 | 0.48 | 1.22
24 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL025 | 1S-DL-YP-ETC-DKWL-2451-KWL025 | E-2, NEHRU VIHAR:ID | TG-KWL025A-1 | 19506446 | 1600 | 500 | 241 | 0.97 | 1347 | 449 | 1976 | 473 | 2085 | 425 | 1850 | 204 | 2019-06-26 10:00 | 452 | 115 | 2085 | Y | 94 | 104 | 101 | 10 | 0.1 | 0.1 | 5.7 | 94.1 |  |  |  |  | 38.3 | 16.3 | 16.3 | 25 | 668.58 | 688.58 | 686.33 | 681.58 | 0.41 | 2.41 |  | 1.11 |  |  |  |  | 708.09 | 11.51 | 0.63 | 0.84