## Complete Report
MIS Report of Distribution Transformer - Jun19
Jun19 1110 CHANDNI CHOWK (Complete Report)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM001 | 1S-DL-YP-CTC-DCCK-0105-HAM001 | NEW KASHMIRI GATE:ID | TG-HAM001A-1 | 19500261 | 990 | 320 | 234 | 0.97 | 327 | 116 | 490 | 88 | 374 | 123 | 523 | 136 | 2019-06-12 19:00 | 73.6 | 0.7 | 537 | R | 93 | 113 | 95 | 20 |  |  | 76.6 | 23.4 | 529.21 | 537.21 | 533.51 | 531.21 | 189.02 | 181.02 | 181.02 | 187.02 | [12 empty] | 718.23 | 1.37 | 0.39 | 0.33
2 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM001 | 1S-DL-YP-CTC-DCCK-0105-HAM001 | NEW KASHMIRI GATE:ID | TG-HAM001A-2 | 19500266 | 990 | 320 | 237 | 0.97 | 615 | 222 | 929 | 211 | 881 | 182 | 756 | 154 | 2019-06-15 16:30 | 145 | 14 | 1040 | R | 108 | 91 | 102 | 17 |  |  | 32.5 | 67.5 | 456.45 | 474.14 | 426.02 | 470.44 | 83.21 | 71.17 | 71.17 | 75.17 | 177.05 | 171.4 | 152.1 | 171.1 | [8 empty] | 717.11 | 2.49 | 0.39 | 0.62
3 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM002 | 1S-DL-YP-CTC-DCCK-0105-HAM002 | MORI GATE:K | TG-HAM002A-1 | 19504175 | 990 | 320 | 237 | 0.97 | 682 | 244 | 1033 | 241 | 1031 | 197 | 827 | 205 | 2019-06-08 16:30 | 157.5 | 55.9 | 1120 | Y | 105 | 101 | 94 | 11 | 0.1 | 11.8 | 57 | 31.1 | 1.3 | 12 | 4.3 | 3 | 333.36 | 356.06 | 356.06 | 359.36 | 381.25 | 348.25 | 326.3 | 353.55 | [8 empty] | 716.31 | 3.29 | 0.59 | 0.69
4 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM002 | 1S-DL-YP-CTC-DCCK-0105-HAM002 | MORI GATE:K | TG-HAM002A-2 | 19500255 | 990 | 320 | 244 | 0.97 | 460 | 145 | 602 | 198 | 817 | 117 | 480 | 296 | 2019-06-12 16:00 | 103.8 | 25.8 | 885 | Y | 96 | 117 | 87 | 30 | 0.1 | 2.4 | 40.2 | 57.4 | 336.57 | 271.27 | 375.57 | 315.27 | 365.03 | 287.03 | 287.03 | 345.33 | 17 | 160.3 |  | 58 | [8 empty] | 719 | 1 | 0.51 | 0.46
5 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM003 | 1S-DL-YP-CTC-DCCK-0105-HAM003 | HAMILTON ROAD STN:ID | TG-HAM003A-1 | 19500270 | 990 | 320 | 234 | 0.97 | 467 | 166 | 729 | 139 | 607 | 162 | 703 | 111 | 2019-06-15 15:00 | 101.6 | -1.5 | 800 | R | 109 | 88 | 103 | 21 |  | 0.3 | 69.7 | 30 | 503.25 | 525.55 | 510.55 | 511.25 | 87.3 | 182 | 182 | 117 | 128.3 | 11.3 | 112.3 | 91 | [8 empty] | 719.25 | 0.35 | 0.31 | 0.47
6 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM003 | 1S-DL-YP-CTC-DCCK-0105-HAM003 | HAMILTON ROAD STN:ID | TG-HAM003A-2 | 19500269 | 990 | 320 | 236 | 0.96 | 809 | 297 | 1288 | 271 | 1177 | 242 | 1028 | 226 | 2019-06-13 15:30 | 201.7 | 36.1 | 1396 | R | 117 | 97 | 86 | 31 | 1.4 | 30.9 | 66.1 | 1.6 | 12 | 84 | 108.26 | 37 | 398.59 | 423.26 | 423.26 | 472.29 | 238.3 | 207.03 | 194 | 207 | 69 | 4 |  | 2 |  |  |  |  | 718.29 | 1.31 | 0.46 | 0.82
7 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM004 | 1S-DL-YP-CTC-DCCK-0105-HAM004 | GANDA NALA:K | TG-HAM004A-1 | 19504134 | 990 | 320 | 232 | 0.97 | 690 | 199 | 915 | 258 | 1186 | 233 | 1054 | 234 | 2019-06-29 15:30 | 142 | 25.8 | 1186 | Y | 87 | 117 | 96 | 30 |  | 25.8 | 74.2 |  | 291.58 | 25.3 | 212 | 146.3 | 255.3 | 471.28 | 471.28 | 370.58 | 170.32 | 221.02 | 200.02 | 200.32 | [8 empty] | 718 | 2 | 0.46 | 0.7
8 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM005 | 1S-DL-YP-CTC-DCCK-0105-HAM005 | GURU NANAK MKT:ID | TG-HAM005A-1 | 19506182 | 990 | 320 | 238 | 0.97 | 717 | 172 | 773 | 303 | 1385 | 243 | 1085 | 530 | 2019-06-29 16:00 | 198.4 | 2.6 | 1514 | Y | 87 | 121 | 92 | 34 | 0.2 | 2.7 | 39.4 | 57.7 | 475.42 | 458.12 | 490.21 | 470.12 | 86 | 36.3 | 36.3 | 45.3 | 117.23 | 147.23 | 153.44 | 163.23 |  | 37 | [6 empty] | 679.05 | 40.55 | 0.27 | 0.72
9 | 2019-06-02 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM006 | 1S-DL-YP-CTC-DCCK-0105-HAM006 | DOI:ID | TG-HAM006A-1 | 19500262 | 990 | 320 | 233 | 0.97 | 483 | 130 | 582 | 178 | 801 | 175 | 776 | 207 | 2019-06-26 15:30 | 85.4 | 11 | 855 | Y | 79 | 118 | 103 | 39 | 0.1 | 1 | 52.7 | 46.2 | 481.58 | 294.58 | 316.58 | 351.28 | 209.42 | 277.46 | 277.46 | 270.12 | 3 | 121.56 | 73.3 | 73 | [8 empty] | 694.4 | 1.2 | 0.46 | 0.49
10 | 2019-06-03 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM007 | 1S-DL-YP-CTC-DCCK-0105-HAM007 | PRIYADARSHANI:PG | TG-HAM007A-1 | 19504800 | 990 | 320 | 240 | 0.98 | 171 | 48 | 200 | 60 | 253 | 62 | 262 | 58 | 2019-06-14 01:00 | 30.2 | 9.6 | 293 | B | 77 | 116 | 107 | 39 |  |  | 78.2 | 21.8 | 671.45 | 671.15 | 670.15 | 671.45 |  | 0.3 | 0.3 | [13 empty] | 671.45 | 0.15 | 0.66 | 0.17
11 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM008 | 1S-DL-YP-CTC-DCCK-0105-HAM008 | NICHOLSON ROAD:PL | TG-HAM008A-1 | 19500265 | 990 | 320 | 239 | 0.96 | 350 | 135 | 571 | 106 | 444 | 108 | 458 | 120 | 2019-06-08 16:30 | 99.4 | 19.1 | 581 | R | 116 | 100 | 84 | 32 |  |  | 0.3 | 99.7 | 503.57 | 530.27 | 554.27 | 524.57 | 211.3 | 189.3 | 189.3 | 195 | 4.3 | [11 empty] | 719.57 | 0.03 | 0.47 | 0.35
12 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM009 | 1S-DL-YP-CTC-DCCK-0105-HAM009 | CHABBI GANJ:PL | TG-HAM009A-1 | 19503476 | 990 | 320 | 251 | 0.97 | 970 | 333 | 1326 | 335 | 1393 | 302 | 1238 | 134 | 2019-06-13 15:00 | 158.2 | 17.7 | 1455 | Y | 115 | 109 | 76 | 39 | 96 | 3.5 | 0.5 |  | 400.33 | 458.26 | 488.56 | 470.26 | 107.29 | 52.36 | 52.36 | 51.06 | 133.06 | 189.09 | 169.08 | 188.08 | 72.51 | 14.48 | 3.19 | 6.49 | 2.3 | 1.3 |  |  | 716.29 | 3.31 | 0.29 | 0.98
13 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM012 | 1S-DL-YP-CTC-DCCK-0105-HAM012 | VALLO DRUM | TG-HAM012A-1 | 19504799 | 100 | 40 | 238 | 0.73 | 61 | 20 | 82 | 25 | 107 | 16 | 66 | 35 | 2019-06-16 05:30 | 47.9 | -0.1 | 114 | Y | 85 | 139 | 76 | 63 | 0.3 | 17.5 | 32.2 | 50.1 | 360.41 | 353.41 | 358.11 | 356.11 | 212.21 | 4.3 | 4.3 | 79.21 | 145.58 | 360.49 | 83.3 | 283.28 | [8 empty] | 719 | 1 | 0.4 | 0.61
14 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM013 | 1S-DL-YP-CTC-DCCK-0105-HAM013 | MONKEY BRIDGE:PKG | TG-HAM013A-1 | 19506393 | 990 | 320 | 239 | 0.96 | 161 | 39 | 163 | 39 | 165 | 82 | 328 | 164 | 2019-06-16 06:00 | 57 | 12.2 | 328 | B | 102 | 110 | 89 | 21 | 93.6 | 3.7 | 2.7 |  | 718.58 | 718.58 | 718.28 | 718.58 | [16 empty] | 718.58 | 1.02 | 0.65 | 0.16
15 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM014 | 1S-DL-YP-CTC-DCCK-0105-HAM014 | PUNJA SHAREEF:PKG | TG-HAM014A-1 | 19506401 | 990 | 320 | 242 | 0.97 | 800 | 425 | 1804 | 143 | 674 | 232 | 1016 | 1004 | 2019-06-29 17:00 | 248 | 3.8 | 1804 | R | 99 | 97 | 104 | 7 | 100 |  |  |  | 486.27 | 488.27 | 488.27 | 486.27 | 38.3 | 54 | 54 | 44 | 170 | 154 | 160 | 165.3 | 1 |  |  | 0.3 | 0.3 |  |  |  | 696.27 | 23.33 | 0.25 | 0.81
16 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM015 | 1S-DL-YP-CTC-DCCK-0105-HAM015 | DELHI POLYTECHNIC:ID | TG-HAM015A-1 | 19500250 | 630 | 200 | 233 | 0.98 | 332 | 108 | 471 | 116 | 507 | 108 | 474 | 35 | 2019-06-15 16:00 | 69.5 | 0.5 | 570 | Y | 98 | 114 | 88 | 26 |  |  | 13.1 | 86.9 | 502.58 | 485.28 | 501.58 | 494.28 | 82.3 | 81 | 81 | 81.3 | 134.3 | 153.3 | 112.3 | 144 | [8 empty] | 719.58 | 0.02 | 0.31 | 0.53
17 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM015 | 1S-DL-YP-CTC-DCCK-0105-HAM015 | DELHI POLYTECHNIC:ID | TG-HAM015A-2 | 19500249 | 630 | 200 | 231 | 0.97 | 346 | 108 | 476 | 100 | 435 | 138 | 604 | 153 | 2019-06-26 22:30 | 76.4 | 11 | 604 | B | 98 | 98 | 103 | 5 |  |  | 23.1 | 76.9 |  |  |  |  | 349 | 335 | 335 | 302 | 370.58 | 384.58 | 442.28 | 417.58 | [8 empty] | 719.58 | 0.02 | 0.76 | 0.55
18 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM016 | 1S-DL-YP-CTC-DCCK-0105-HAM016 | BUBUNA MARKET:PKG | TG-HAM016A-1 | 19501218 | 990 | 320 | 244 | 0.97 | 594 | 193 | 798 | 170 | 696 | 231 | 963 | 234 | 2019-06-29 16:30 | 144.3 | 14.7 | 1025 | B | 92 | 80 | 128 | 48 |  | 0.9 | 90.7 | 8.4 | 480.22 | 486.11 | 312.23 | 474.52 | 73.19 | 104.18 | 104.18 | 69.19 | 161.48 | 125 | 191.37 | 171.18 | [8 empty] | 715.29 | 4.31 | 0.38 | 0.6
19 | 2019-06-02 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM017 | 1S-DL-YP-CTC-DCCK-0105-HAM017 | KASHMERE GATE POLICE THANA:PL | TG-HAM017A-1 | 19500234 | 990 | 320 | 243 | 0.97 | 763 | 213 | 871 | 269 | 1110 | 281 | 1145 | 258 | 2019-06-15 16:00 | 160.4 | 8.8 | 1257 | Y | 81 | 107 | 112 | 31 | 0.1 | 5.2 | 67.5 | 27.2 | 457.3 | 445 | 429.3 | 446 | 52.3 | 43 | 43 | 51 | 186 | 189 | 172 | 199 |  | 19 | 32.3 | [5 empty] | 696 | 0 | 0.37 | 0.77
20 | 2019-06-02 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM018 | 1S-DL-YP-CTC-DCCK-0105-HAM018 | ELECTRIC CREMATION:ID | TG-HAM018A-1 | 19505070 | 400 | 120 | 234 | 0.96 | 88 | 32 | 138 | 26 | 111 | 30 | 130 | 25 | 2019-06-26 13:00 | 32 | 0.3 | 154 | R | 94 | 86 | 120 | 34 | 1.9 | 9.6 | 38.5 | 50.1 | 620.58 | 695.58 | 618.58 | 686.58 | 75 |  |  | 9 | [12 empty] | 695.58 | 0.02 | 0.6 | 0.22
21 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM019 | 1S-DL-YP-CTC-DCCK-0105-HAM019 | KASHMERE GATE TAXI STAND:PL | TG-HAM019A-1 | 19503468 | 990 | 320 | 245 | 0.97 | 557 | 168 | 731 | 166 | 718 | 223 | 966 | 242 | 2019-06-28 15:00 | 122.9 | 7.4 | 966 | B | 93 | 98 | 109 | 16 |  |  | 3.8 | 96.3 | 504 | 481.3 | 477 | 485 | 126 | 135 | 135 | 117 | 90 | 103.3 | 157 | 118 | [8 empty] | 720 | 0 | 0.31 | 0.56
22 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM032 | 1S-DL-YP-CTC-DCCK-0105-HAM032 | GEETA COLONY FLY OVER | TG-HAM032A-1 | 19506298 | 400 | 120 | 238 | 0.88 | 347 | 120 | 521 | 129 | 555 | 98 | 415 | 127 | 2019-06-16 16:00 | 134.5 | 2.6 | 555 | Y | 100 | 104 | 96 | 8 |  | 1.9 | 70.5 | 27.6 | 245.07 | 298.48 | 273.18 | 315.48 | 144.43 | 87.32 | 87.32 | 73.02 | 303.3 | 307 | 298.31 | 304.3 | 0.01 | 0.01 |  | 0.01 |  |  |  |  | 693.21 | 26.39 | 0.39 | 0.87
23 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM034 | 1S-DL-YP-CTC-DCCK-0105-HAM034 | YAMUNA BAZAR GHAT DELHI 6 | TG-HAM034A-1 | 19505145 | 630 | 200 | 237.8669 | 0.97481 | 928.7217 | 326.9159 | 1458.3392 | 334.054 | 1525.2215 | 267.7518 | 1168.0488 | 328.8724 | 2019-06-15 13:00 | [15 empty] | 0 |  |  |  | 47.5 |  |  |  | 671.5 |  |  |  | 0 |  |  |  | 0.5 | 719.5 |  | 0.3637 | 1.4742
24 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR001 | 1S-DL-YP-CTC-DCCK-0104-LHR001 | MOHALLA NIHARIYAN:K | TG-LHR001A-1 | 19505697 | 990 | 320 | 242 | 0.93 | 996 | 333 | 1383 | 328 | 1371 | 335 | 1408 | 32 | 2019-06-11 01:30 | 389.4 | 149.4 | 1493 | Y | 99 | 106 | 96 | 10 | 0.1 |  | 16.2 | 83.7 | [8 empty] | 536.46 | 438.5 | 637.46 | 535.17 | 172.3 | 272.56 | 79 | 181.29 | 8 | 5.3 | 0.3 | 0.3 | 717.16 | 2.44 | 0.72 | 1.01
25 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR001 | 1S-DL-YP-CTC-DCCK-0104-LHR001 | MOHALLA NIHARIYAN:K | TG-LHR001A-2 | 19501527 | 990 | 320 | 237 | 0.96 | 527 | 156 | 642 | 192 | 783 | 179 | 730 | 124 | 2019-06-29 17:00 | 156 | 42 | 828 | Y | 95 | 106 | 99 | 11 |  | 5.6 | 42.3 | 52.2 | 6.3 | 3 | 1 | 2.3 | 634.15 | 514.2 | 514.2 | 592.55 | 76.3 | 199.55 | 101.5 | 121.5 | [8 empty] | 717.15 | 2.45 | 0.65 | 0.53
26 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR002 | 1S-DL-YP-CTC-DCCK-0104-LHR002 | FARASH KHANNA:PL | TG-LHR002A-1 | 19501532 | 990 | 320 | 245 | 0.94 | 741 | 275 | 1148 | 223 | 937 | 243 | 977 | 195 | 2019-06-01 16:30 | 223 | 83.9 | 1166 | R | 96 | 104 | 100 | 8 | 96.3 | 3.7 | [6 empty] | 323.58 | 211.16 | 211.16 | 237.45 | 391.03 | 506.15 | 469.43 | 479.46 | 2.3 | [7 empty] | 717.31 | 2.29 | 0.6 | 0.75
27 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR003 | 1S-DL-YP-CTC-DCCK-0104-LHR003 | MOHALLA SHAHGANJ:K | TG-LHR003A-1 | 19505363 | 990 | 320 | 238 | 0.95 | 878 | 377 | 1612 | 172 | 713 | 329 | 1478 | 840 | 2019-06-17 23:00 | 389.8 | 79 | 1612 | R | 102 | 100 | 98 | 4 | 1.3 | 64.3 | 33.8 | 0.6 |  |  | 0.3 |  | 10.3 | 13.46 | 13.46 | 6.3 | 665.53 | 667.37 | 679.53 | 681.23 | 13.3 | 9 | 1 | 2.3 | 0.3 |  |  |  | 690.23 | 29.37 | 0.68 | 0.89
28 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR003 | 1S-DL-YP-CTC-DCCK-0104-LHR003 | MOHALLA SHAHGANJ:K | TG-LHR003A-2 | 19501626 | 990 | 200 | 237 | 0.96 | 761 | 260 | 1101 | 253 | 1074 | 249 | 1055 | 40 | 2019-06-28 17:00 | 215.3 | 39.6 | 1161 | R | 99 | 102 | 99 | 3 |  |  | 0.5 | 99.5 |  | 0.24 |  | 0.24 | 71.25 | 39.25 | 39.25 | 41.31 | 641.23 | 673.29 | 662.53 | 671.23 | 0.3 | [7 empty] | 713.18 | 6.42 | 0.68 | 0.77
29 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR005 | 1S-DL-YP-CTC-DCCK-0104-LHR005 | GALI SAMOSA:PL | TG-LHR005A-1 | 19501558 | 990 | 320 | 234 | 0.96 | 403 | 105 | 436 | 152 | 634 | 146 | 613 | 188 | 2019-06-02 04:00 | 103.8 | 45.6 | 654 | Y | 79 | 110 | 110 | 31 |  |  | 5.2 | 94.8 | 81 | 3.3 |  | 4 | 638.57 | 643.57 | 643.57 | 715.27 |  | 72.3 | 63 | 0.3 | [8 empty] | 719.57 | 0.03 | 0.74 | 0.41
30 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR006 | 1S-DL-YP-CTC-DCCK-0104-LHR006 | GANESH ICE FACTORY:ID | TG-LHR006A-1 | 19505065 | 990 | 320 | 241 | 0.97 | 661 | 202 | 851 | 191 | 808 | 267 | 1133 | 306 | 2019-06-26 15:30 | 160.4 | 19.9 | 1166 | B | 92 | 93 | 114 | 22 |  |  | 0.1 | 99.9 | 446.17 | 312.17 | 416.47 | 392.47 | 94.28 | 246.3 | 246.3 | 127.3 | 176.54 | 158.52 | 210.22 | 197.22 |  |  | 7.3 | [5 empty] | 717.39 | 2.21 | 0.42 | 0.67
31 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR007 | 1S-DL-YP-CTC-DCCK-0104-LHR007 | LAHORI GATE DISPENSARY:ID | TG-LHR007A-1 | 19501165 | 990 | 320 | 235 | 0.97 | 713 | 219 | 952 | 256 | 1113 | 239 | 1046 | 140 | 2019-06-14 15:00 | 135.4 | 30.2 | 1191 | R | 105 | 86 | 109 | 23 |  |  | 25.4 | 74.6 | 21.3 | 233.57 | 1 | 16 | 490.57 | 288.3 | 288.3 | 502.27 | 205.29 | 196.29 | 224.29 | 200.59 | 1.3 | 0.3 | [6 empty] | 719.26 | 0.34 | 0.49 | 0.72
32 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR007 | 1S-DL-YP-CTC-DCCK-0104-LHR007 | LAHORI GATE DISPENSARY:ID | TG-LHR007A-2 | 19506366 | 990 | 320 | 248 | 0.97 | 392 | 146 | 625 | 119 | 513 | 127 | 548 | 99 | 2019-06-29 15:00 | 80.3 | 16.3 | 625 | R | 105 | 93 | 101 | 12 | 0.1 |  | 7 | 92.8 | 465.27 | 487.27 | 466.27 | 475.27 | 226.3 | 206.3 | 206.3 | 221 | 4.3 | 2.3 | 2 | [9 empty] | 696.27 | 23.33 | 0.48 | 0.4
33 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR008 | 1S-DL-YP-CTC-DCCK-0104-LHR008 | LAHORI GATE DIESEL:ID | TG-LHR008A-1 | 19501161 | 990 | 320 | 248 | 0.97 | 750 | 221 | 929 | 270 | 1159 | 260 | 1117 | 212 | 2019-06-06 14:30 | 184.7 | 33.9 | 1169 | Y | 83 | 114 | 103 | 31 |  | 6.2 | 90.4 | 3.4 | 68.58 |  | 19 | 11.3 | 472.54 | 468.03 | 468.03 | 491.07 | 174.26 | 243.45 | 205.41 | 213.41 |  | 4.3 | 3.3 | [5 empty] | 716.18 | 3.42 | 0.48 | 0.76
34 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR009 | 1S-DL-YP-CTC-DCCK-0104-LHR009 | LAHORI GATE CHOWK:PL | TG-LHR009A-1 | 19506641 | 990 | 320 | 243 | 0.96 | 469 | 113 | 468 | 185 | 776 | 171 | 715 | 282 | 2019-06-26 16:00 | 144.3 | 9.6 | 776 | Y | 68 | 125 | 107 | 57 | 0.1 |  | 35.6 | 64.3 | 500.56 | 455.26 | 458.56 | 465.26 | 195.3 | 107.3 | 107.3 | 174 |  | 133.3 | 123 | 57 | [8 empty] | 696.26 | 23.34 | 0.38 | 0.47
35 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR010 | 1S-DL-YP-CTC-DCCK-0104-LHR010 | NAYA BAZAR BOOSTER:ID | TG-LHR010A-1 | 19500228 | 990 | 320 | 239 | 0.98 | 727 | 210 | 961 | 273 | 1278 | 245 | 1138 | 275 | 2019-06-10 14:30 | 139.1 | 14 | 1278 | Y | 81 | 115 | 104 | 34 |  | 2 | 48.3 | 49.8 | 214.39 | 16.3 | 43.3 | 54 | 339.44 | 474.53 | 474.53 | 466.23 | 161.07 | 201.37 | 211.32 | 195.07 |  | 22.3 | [6 empty] | 715.3 | 4.3 | 0.49 | 0.73
36 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR011 | 1S-DL-YP-CTC-DCCK-0104-LHR011 | OPP NOVELTY CINEMA:PL | TG-LHR011A-1 | 19503759 | 990 | 320 | 239 | 0.97 | 351 | 90 | 378 | 133 | 551 | 128 | 535 | 166 | 2019-06-12 16:30 | 81.7 | 1.5 | 698 | B | 69 | 120 | 111 | 51 |  | 0.1 | 5 | 94.9 | 574.44 | 53.18 | 94.48 | 154.18 | 143.3 | 643.26 | 643.26 | 563.56 |  | 21.3 | 18 | [9 empty] | 718.14 | 1.46 | 0.67 | 0.35
37 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR012 | 1S-DL-YP-CTC-DCCK-0104-LHR012 | GHEE MANDI:ID | TG-LHR012A-1 | 19502979 | 990 | 320 | 239 | 0.96 | 585 | 162 | 665 | 173 | 714 | 250 | 1027 | 340 | 2019-06-30 | 151.6 | 42.7 | 1027 | B | 97 | 103 | 100 | 6 |  | 0.1 | 43.9 | 55.9 | 3.51 | 3.51 | 0.48 | 1.33 | 349.19 | 266.34 | 266.34 | 307.09 | 356.58 | 439.43 | 392.51 | 401.26 | [8 empty] | 710.08 | 9.52 | 0.7 | 0.59
38 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR012 | 1S-DL-YP-CTC-DCCK-0104-LHR012 | GHEE MANDI:ID | TG-LHR012A-2 | 19506623 | 990 | 320 | 239 | 0.96 | 677 | 378 | 1704 | 143 | 619 | 155 | 659 | 1066 | 2019-06-11 05:00 | 242.6 | 42.2 | 1704 | R | 114 | 92 | 94 | 22 | 0.3 | 0.1 | 64 | 35.6 | 2.01 | 2.17 | 2.01 | 2.01 | 101.04 | 272.53 | 272.53 | 184.2 | 589.02 | 417.57 | 437.1 | 506.46 | 0.3 |  | 0.24 |  | 0.3 |  |  |  | 693.07 | 26.53 | 0.67 | 0.68
39 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR013 | 1S-DL-YP-CTC-DCCK-0104-LHR013 | S.N.MKT:K | TG-LHR013A-1 | 19506592 | 990 | 320 | 235 | 0.96 | 574 | 179 | 765 | 195 | 841 | 200 | 857 | 85 | 2019-06-03 16:30 | 221.1 | 58.2 | 1019 | B | 104 | 93 | 103 | 11 | 0.1 | 0.1 | 16.9 | 82.9 |  | 0.3 |  |  | 378.57 | 534.57 | 534.57 | 463.29 | 317.3 | 161 | 277.28 | 232.58 | [8 empty] | 696.27 | 23.33 | 0.65 | 0.58
40 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR013 | 1S-DL-YP-CTC-DCCK-0104-LHR013 | S.N.MKT:K | TG-LHR013A-2 | 19501164 | 990 | 320 | 235 | 0.97 | 592 | 246 | 1088 | 181 | 805 | 165 | 724 | 332 | 2019-06-29 17:00 | 155.3 | 35.3 | 1164 | R | 129 | 90 | 81 | 48 |  |  | 41 | 59 | 4.3 | 199.27 | 206.27 | 65 | 464.57 | 358.3 | 358.3 | 471.27 | 250.3 | 162 | 57.3 | 183.3 | [8 empty] | 719.57 | 0.03 | 0.53 | 0.6
41 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR014 | 1S-DL-YP-CTC-DCCK-0104-LHR014 | S.P.MUKERJI MARG:PM | TG-LHR014A-1 | 19501578 | 990 | 320 | 245 | 0.99 | 401 | 140 | 587 | 146 | 616 | 114 | 480 | 124 | 2019-06-15 14:30 | 60.4 | -7.4 | 661 | Y | 108 | 113 | 79 | 34 |  |  | 5.6 | 94.4 | 436.28 | 444.56 | 497.28 | 475.26 | 271.51 | 200.53 | 200.53 | 241.23 | 9 | 71.3 |  | 0.3 | [8 empty] | 717.19 | 2.41 | 0.49 | 0.41
42 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR015 | 1S-DL-YP-CTC-DCCK-0104-LHR015 | ZEENAT MAHAL:K | TG-LHR015A-1 | 19501530 | 990 | 320 | 238 | 0.94 | 879 | 304 | 1254 | 280 | 1148 | 295 | 1212 | 93 | 2019-06-03 04:00 | 268.6 | 116.3 | 1254 | R | 98 | 97 | 105 | 8 |  |  | 7.5 | 92.5 |  |  |  |  | 28.3 | 19 | 19 | 11.3 | 679.45 | 694.45 | 666.15 | 695.45 | 10.3 | 5 | 46.3 | 11.3 |  |  |  |  | 718.45 | 1.15 | 0.67 | 0.89
43 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR015 | 1S-DL-YP-CTC-DCCK-0104-LHR015 | ZEENAT MAHAL:K | TG-LHR015A-2 | 19505377 | 630 | 200 | 241 | 0.95 | 204 | 73 | 299 | 35 | 143 | 95 | 387 | 213 | 2019-06-02 01:30 | 73.4 | 26.6 | 465 | R | 117 | 63 | 120 | 57 | 0.1 |  | 14.9 | 85 | 21.3 | 666.57 | 39 | 96 | 673.59 | 29.3 | 29.3 | 600.27 | 0.58 |  | 13.3 | [9 empty] | 696.27 | 23.33 | 0.72 | 0.32
44 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR016 | 1S-DL-YP-CTC-DCCK-0104-LHR016 | KHARI BAOLI:PG | TG-LHR016A-1 | 19505364 | 990 | 320 | 247 | 0.97 | 667 | 181 | 762 | 245 | 1039 | 241 | 1012 | 265 | 2019-06-13 16:00 | 156.8 | 32 | 1076 | Y | 82 | 113 | 105 | 31 | 0.2 |  | 26.4 | 73.4 | 474.22 | 253.22 | 316.52 | 425.22 | 86.29 | 259.3 | 259.3 | 104 | 158.24 | 206.23 | 188.52 | 189.53 | [8 empty] | 719.15 | 0.45 | 0.42 | 0.67
45 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR017 | 1S-DL-YP-CTC-DCCK-0104-LHR017 | LAL QUAN:PL | TG-LHR017A-1 | 19506435 | 990 | 320 | 237 | 0.95 | 1085 | 324 | 1380 | 244 | 1043 | 517 | 2313 | 1140 | 2019-06-05 02:30 | 407 | 120.3 | 2568 | Y | 87 | 113 | 100 | 26 | 0.4 | 2.2 | 73 | 24.5 |  |  |  |  | 24.31 | 0.01 | 0.01 | 3.01 | 669.17 | 637.19 | 679.47 | 688.19 | 1 | 56.3 | 6.3 | 2.58 |  | 0.58 | 1 | 0.3 | 694.48 | 25.12 | 0.55 | 1.1
46 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR018 | 1S-DL-YP-CTC-DCCK-0104-LHR018 | BARSHABULLA:ID | TG-LHR018A-1 | 19501501 | 990 | 320 | 231 | 0.96 | 842 | 245 | 1096 | 286 | 1296 | 311 | 1422 | 285 | 2019-06-12 16:30 | 208.3 | 28.7 | 1499 | B | 84 | 95 | 120 | 36 | 0.1 | 14.8 | 80.7 | 4.4 | 244.3 | 123 | 18.3 | 91.3 | 259.44 | 381.14 | 381.14 | 407.14 | 215 | 206 | 175.52 | 202.3 |  | 9 | 107 | 18 |  |  |  |  | 719.14 | 0.46 | 0.45 | 0.85
47 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR018 | 1S-DL-YP-CTC-DCCK-0104-LHR018 | BARSHABULLA:ID | TG-LHR018A-2 | 19505696 | 990 | 320 | 237 | 0.96 | 1156 | 408 | 1794 | 396 | 1739 | 352 | 1518 | 253 | 2019-06-26 17:30 | 256.3 | 13.1 | 1794 | R | 100 | 108 | 91 | 17 | 0.5 | 2.4 | 74.4 | 22.7 | 458.01 | 443.01 | 455.31 | 452.01 | 36 | 36.3 | 36.3 | 36.3 | 102 | 92.3 | 133.57 | 104.3 | 120.27 | 130.27 | 97.3 | 125.27 | 2.3 | 16.3 | 0.3 | 0.3 | 718.58 | 1.02 | 0.29 | 1.17
48 | 2019-06-02 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR019 | 1S-DL-YP-CTC-DCCK-0104-LHR019 | CHARKHE WALAN:PL | TG-LHR019A-1 | 19501607 | 630 | 200 | 231 | 0.98 | 439 | 140 | 624 | 137 | 619 | 161 | 729 | 108 | 2019-06-29 17:30 | 86.5 | 7.4 | 797 | B | 109 | 89 | 102 | 20 |  |  | 40.9 | 59.1 | 30.3 | 109.03 | 73 | 58.3 | 437.53 | 415.48 | 415.48 | 435.51 | 225.55 | 169.27 | 204.12 | 199.57 |  |  | 0.3 | [5 empty] | 694.18 | 1.42 | 0.51 | 0.7
49 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR019 | 1S-DL-YP-CTC-DCCK-0104-LHR019 | CHARKHE WALAN:PL | TG-LHR019A-2 | 19504961 | 990 | 320 | 240 | 0.95 | 817 | 269 | 1147 | 265 | 1116 | 283 | 1208 | 81 | 2019-06-11 01:30 | 244.4 | 102.3 | 1325 | R | 99 | 99 | 102 | 3 | 0.1 | 0.5 | 81.9 | 17.5 |  |  |  |  | 3 | 11 | 11 | 7.3 | 709.13 | 695.11 | 664.21 | 704.43 | 3 | 9.02 | 39.22 | 3 |  |  |  |  | 715.13 | 4.47 | 0.74 | 0.83
50 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR020 | 1S-DL-YP-CTC-DCCK-0104-LHR020 | CHAMELI:ID | TG-LHR020A-1 | 19501606 | 990 | 200 | 224 | 0.96 | 710 | 246 | 1096 | 268 | 1213 | 195 | 897 | 277 | 2019-06-12 01:00 | 184 | 42.8 | 1213 | Y | 103 | 103 | 94 | 9 | 99.2 | 0.7 | 0.1 |  | 0.06 | 0.06 | 1.14 | 0.06 | 79.1 | 124.51 | 124.51 | 118.35 | 629.25 | 583.14 | 513.13 | 590 |  | 0.3 | [6 empty] | 708.41 | 11.19 | 0.7 | 0.72
51 | 2019-06-04 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR023 | 1S-DL-YP-CTC-DCCK-0104-LHR023 | JOGIWARA:ID | TG-LHR023A-1 | 19501520 | 990 | 320 | 242 | 0.96 | 990 | 340 | 1468 | 343 | 1478 | 306 | 1323 | 150 | 2019-06-11 17:00 | 231.8 | 49.3 | 1540 | Y | 108 | 102 | 89 | 19 |  |  | 5.2 | 94.8 | 0.3 | 0.3 | 6 | 0.3 | 76.27 | 185.25 | 185.25 | 182.31 | 420.27 | 299.36 | 264.23 | 325.23 | 141.42 | 145.29 | 66.36 | 137.36 | 6.54 | 15 |  |  | 646 | 2 | 0.54 | 1
52 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR023 | 1S-DL-YP-CTC-DCCK-0104-LHR023 | JOGIWARA:ID | TG-LHR023A-2 | 19505551 | 990 | 320 | 238 | 0.96 | 904 | 324 | 1439 | 293 | 1294 | 287 | 1277 | 154 | 2019-06-01 13:00 | 294.4 | -90.2 | 1607 | Y | 139 | 82 | 79 | 60 | 0.1 |  | 16.3 | 83.6 | 393.36 | 532.54 | 564.18 | 438.06 | 95.55 | 94.19 | 94.19 | 186.07 | 158.29 | 63.13 | 65.21 | 39.47 | 65.49 | 24.53 | 22.15 | 52.19 | 2.3 | 1 |  |  | 716.19 | 3.41 | 0.23 | 0.91
53 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR023 | 1S-DL-YP-CTC-DCCK-0104-LHR023 | JOGIWARA:ID | TG-LHR023A-3 | 19506567 | 630 | 200 | 237 | 0.95 | 442 | 138 | 621 | 146 | 650 | 158 | 708 | 76 | 2019-06-05 12:00 | 173.4 | 55 | 933 | B | 94 | 95 | 111 | 17 | 0.3 |  | 41.1 | 58.7 | 0.09 | 0.09 | 0.09 | 0.09 | 120.2 | 111.57 | 111.57 | 66.27 | 573.12 | 581.59 | 646.59 | 627.29 | 0.24 |  | 1.3 |  |  |  | 0.3 |  | 694.05 | 25.55 | 0.71 | 0.7
54 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR024 | 1S-DL-YP-CTC-DCCK-0104-LHR024 | PANDIT BROS:K | TG-LHR024A-1 | 19503227 | 990 | 320 | 244 | 0.98 | 814 | 255 | 1022 | 304 | 1223 | 255 | 1028 | 198 | 2019-06-15 17:00 | 179.6 | 2.9 | 1271 | Y | 97 | 111 | 93 | 18 |  | 0.1 | 38.6 | 61.2 | 465.43 | 458.13 | 468.13 | 465.43 | 28 | 24.3 | 24.3 | 23 | 222.38 | 169.42 | 223.38 | 224.38 | 0.3 | 64.26 |  | 3.3 |  |  |  |  | 716.51 | 3.09 | 0.31 | 0.82
55 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR024 | 1S-DL-YP-CTC-DCCK-0104-LHR024 | PANDIT BROS:K | TG-LHR024A-2 | 19503236 | 990 | 320 | 244 | 0.97 | 871 | 260 | 1162 | 339 | 1505 | 272 | 1222 | 317 | 2019-06-01 14:30 | 186.2 | 1.5 | 1525 | Y | 82 | 124 | 93 | 42 |  |  | 29.7 | 70.3 | 479.34 | 443.46 | 475.48 | 465.34 | 58.1 | 50.32 | 50.32 | 44.4 | 174.28 | 155.57 | 190.58 | 172.58 | 2 | 56.57 | 8 | 31 |  | 7 |  |  | 714.12 | 5.48 | 0.27 | 0.88
56 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR025 | 1S-DL-YP-CTC-DCCK-0104-LHR025 | CYCLE STAND:ID | TG-LHR025A-1 | 19501167 | 990 | 320 | 236 | 0.98 | 735 | 257 | 1161 | 246 | 1098 | 232 | 1046 | 100 | 2019-06-03 14:00 | 146.5 | 1.5 | 1185 | R | 100 | 99 | 101 | 2 |  |  | 9 | 91 | 464.33 | 469.03 | 468.33 | 465.33 | 41.04 | 45.34 | 45.34 | 47.04 | 212 | 203.3 | 204.3 | 205.3 | 0.3 | [7 empty] | 718.07 | 1.53 | 0.31 | 0.74
57 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR025 | 1S-DL-YP-CTC-DCCK-0104-LHR025 | CYCLE STAND:ID | TG-LHR025A-2 | 19501166 | 990 | 320 | 235 | 0.96 | 911 | 302 | 1302 | 332 | 1459 | 277 | 1207 | 221 | 2019-06-29 18:00 | 265 | 35.3 | 1482 | Y | 96 | 106 | 98 | 10 |  | 10.4 | 72.8 | 16.7 | 1 |  |  | 0.3 | 7.17 | 6.17 | 6.17 | 3.3 | 672.08 | 568.27 | 650.05 | 665.25 | 30.3 | 135.41 | 53.5 | 41.3 |  | 0.3 |  |  | 710.55 | 9.05 | 0.71 | 0.92
58 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR026 | 1S-DL-YP-CTC-DCCK-0104-LHR026 | OLD KRISHNA MARKET:ID | TG-LHR026A-1 | 19501852 | 990 | 320 | 246 | 0.97 | 815 | 284 | 1202 | 221 | 922 | 310 | 1316 | 352 | 2019-06-03 17:00 | 197.2 | -4.4 | 1440 | B | 92 | 88 | 120 | 32 |  | 13.2 | 37.6 | 49.2 | 467.44 | 469.14 | 459.44 | 466.44 | 28.31 | 33.16 | 33.16 | 28.35 | 214.02 | 215.33 | 63.49 | 206.28 | 7.46 |  | 158.4 | 16.16 |  |  | 4 |  | 718.03 | 1.57 | 0.33 | 0.82
59 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR027 | 1S-DL-YP-CTC-DCCK-0104-LHR027 | NEW KRISHNA MKT:ID | TG-LHR027A-1 | 19504835 | 990 | 320 | 238 | 0.98 | 939 | 292 | 1316 | 315 | 1429 | 332 | 1483 | 148 | 2019-06-07 15:00 | 153.1 | -4.4 | 1551 | B | 92 | 100 | 108 | 16 |  |  | 40.2 | 59.8 | 461.19 | 460.19 | 456.49 | 459.19 | 32 | 33.3 | 33.3 | 34.3 | 180.05 | 93.25 | 66.42 | 93.55 | 45.02 | 131.12 | 151.25 | 130.42 |  |  | 9.3 |  | 718.26 | 1.34 | 0.32 | 0.95
60 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR028 | 1S-DL-YP-CTC-DCCK-0104-LHR028 | KATRA NEEL:PKG | TG-LHR028A-1 | 19501559 | 990 | 320 | 243 | 0.95 | 526 | 192 | 824 | 213 | 916 | 122 | 509 | 370 | 2019-06-29 17:00 | 140.6 | 2.2 | 943 | Y | 121 | 101 | 79 | 42 | 68.2 | 31.3 | 0.5 |  | 6 | 219.54 | 182.57 | 60.57 | 501.31 | 314.37 | 314.37 | 510.48 | 210.52 | 183.52 | 1 | 146.38 | [8 empty] | 718.23 | 1.37 | 0.56 | 0.53
61 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR028 | 1S-DL-YP-CTC-DCCK-0104-LHR028 | KATRA NEEL:PKG | TG-LHR028A-2 | 19506179 | 630 | 200 | 238 | 0.97 | 543 | 241 | 1063 | 171 | 746 | 131 | 572 | 431 | 2019-06-14 16:00 | 183.2 | 0.6 | 1063 | R | 99 | 94 | 107 | 13 | 0.1 |  | 37 | 62.8 | 483.49 | 490.19 | 482.19 | 482.19 | 33 | 34 | 34 | 33 | 200.35 | 193.35 | 208.05 | 202.35 | 0.3 | 0.3 |  | 0.3 | 0.3 |  |  |  | 718.24 | 1.36 | 0.23 | 0.86
62 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR029 | 1S-DL-YP-CTC-DCCK-0104-LHR029 | PNB:ID | TG-LHR029A-1 | 19505441 | 990 | 320 | 245 | 0.97 | 720 | 274 | 1254 | 172 | 761 | 273 | 1346 | 545 | 2019-06-01 19:00 | 249.6 | 18.6 | 1346 | B | 101 | 99 | 100 | 2 | 0.1 | 0.4 | 42.4 | 57 | 308.3 | 247.3 | 358.3 | 329.3 | 178 | 247 | 247 | 160 | 233 | 225.3 | 230.3 | 230.3 | 0.3 |  | 1 | [5 empty] | 720 | 0 | 0.44 | 0.73
63 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR029 | 1S-DL-YP-CTC-DCCK-0104-LHR029 | PNB:ID | TG-LHR029A-2 | 19503561 | 990 | 320 | 238 | 0.95 | 453 | 117 | 494 | 186 | 781 | 150 | 624 | 250 | 2019-06-12 16:00 | 128.1 | 42.7 | 881 | Y | 87 | 108 | 105 | 21 | 0.1 | 3.7 | 79.4 | 16.7 | 271 | 138.3 | 55 | 102 | 440.3 | 483 | 483 | 573 | 8.3 | 98.3 | 77 | 45 | [8 empty] | 720 | 0 | 0.59 | 0.46
64 | 2019-06-02 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR030 | 1S-DL-YP-CTC-DCCK-0104-LHR030 | KUTCHA GHASI RAM:PL | TG-LHR030A-1 | 19500241 | 990 | 320 | 238 | 0.97 | 674 | 190 | 822 | 258 | 1117 | 226 | 964 | 255 | 2019-06-03 15:30 | 175.9 | 23.6 | 1117 | Y | 93 | 108 | 98 | 15 |  |  | 25.5 | 74.5 | 37.3 | 6.3 | 23 | 12.3 | 457.57 | 446.57 | 446.57 | 463.27 | 200.3 | 242.3 | 217 | 220 | [8 empty] | 695.57 | 0.03 | 0.53 | 0.68
65 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR031 | 1S-DL-YP-CTC-DCCK-0104-LHR031 | BATA:PL | TG-LHR031A-1 | 19500240 | 990 | 320 | 244 | 0.97 | 538 | 174 | 709 | 204 | 836 | 160 | 661 | 157 | 2019-06-15 16:30 | 140.6 | 2.9 | 887 | Y | 93 | 117 | 90 | 27 | 0.6 | 3.3 | 74.3 | 21.9 | 460.5 | 436.5 | 463.5 | 454.5 | 123.33 | 76.56 | 76.56 | 110.44 | 134.08 | 204.45 | 84 | 152.57 | [8 empty] | 718.31 | 1.29 | 0.36 | 0.54
66 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR032 | 1S-DL-YP-CTC-DCCK-0104-LHR032 | HAVELI HYDERQULI:PM | TG-LHR032A-1 | 19506524 | 630 | 200 | 230.4152 | 0.97886 | 524.6712 | 264.1057 | 1178.6225 | 136.5367 | 595.684 | 124.0287 | 540.8779 | 612.1843 | 2019-06-13 14:00 | [15 empty] | 0 |  |  |  | 136 |  |  |  | 580.5 |  |  |  | 2 |  |  |  | 0 | 718.5 |  | 0.64435 | 0.83281
67 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR033 | 1S-DL-YP-CTC-DCCK-0104-LHR033 | KATRA BARYIAN I/D:ID | TG-LHR033A-1 | 19504637 | 990 | 320 | 237 | 0.97 | 586 | 217 | 924 | 214 | 907 | 155 | 679 | 237 | 2019-06-29 16:00 | 155.3 | 43.4 | 968 | Y | 98 | 117 | 86 | 31 | 19.6 | 80.4 |  |  | 3 |  | 12 | 1.3 | 506.27 | 238.29 | 238.29 | 479.57 | 210.3 | 481.28 | 92 | 238.3 | [8 empty] | 719.57 | 0.03 | 0.64 | 0.59
68 | 2019-06-12 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR034 | 1S-DL-YP-CTC-DCCK-0104-LHR034 | KATRA BARYIAN PLINTH:PL | TG-LHR034A-1 | 19501572 | 630 | 200 | 242 | 0.98 | 599 | 218 | 900 | 210 | 873 | 171 | 718 | 170 | 2019-06-12 16:00 | 126 | 19.3 | 965 | Y | 111 | 97 | 92 | 19 |  | 1.4 | 78.2 | 20.5 |  |  |  |  | 14 | 135.59 | 135.59 | 72.59 | 337.03 | 235.04 | 309.27 | 310.34 | 86.51 | 68.21 | 9 | 58.21 | 4 | 2.3 |  |  | 441.54 | 14.06 | 0.58 | 0.95
69 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR035 | 1S-DL-YP-CTC-DCCK-0104-LHR035 | BAGH DIVAR:PM | TG-LHR035A-1 | 19501498 | 990 | 320 | 239 | 0.97 | 689 | 218 | 973 | 246 | 1096 | 226 | 1002 | 111 | 2019-06-12 13:30 | 142 | 11.8 | 1108 | Y | 89 | 106 | 106 | 17 |  | 0.2 | 75.7 | 24 | 482.23 | 477.23 | 466.23 | 474.23 | 45 | 43 | 43 | 48 | 192 | 199 | 201.3 | 197 | [8 empty] | 719.23 | 0.37 | 0.35 | 0.7
70 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR036 | 1S-DL-YP-CTC-DCCK-0104-LHR036 | TOWN HALL:ID | TG-LHR036A-1 | 19501451 | 990 | 320 | 238 | 0.98 | 383 | 97 | 438 | 118 | 532 | 169 | 764 | 290 | 2019-06-03 12:30 | 79.5 | -39 | 786 | B | 76 | 86 | 138 | 62 |  |  | 7.9 | 92.1 | 490.3 | 476.3 | 448 | 460.3 | 229.3 | 243.3 | 243.3 | 259.3 |  |  | 157.3 | [9 empty] | 720 | 0 | 0.36 | 0.39
71 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR036 | 1S-DL-YP-CTC-DCCK-0104-LHR036 | TOWN HALL:ID | TG-LHR036A-2 | 19501170 | 990 | 320 | 240 | 0.98 | 465 | 153 | 646 | 208 | 889 | 104 | 443 | 387 | 2019-06-12 16:00 | 109.7 | 4.4 | 889 | Y | 96 | 119 | 85 | 34 |  |  | 21.2 | 78.8 | 480.22 | 465.52 | 492.22 | 474.22 | 101 | 69.3 | 69.3 | 150 | 138.3 | 184.3 |  | 95.3 | [8 empty] | 719.52 | 0.08 | 0.44 | 0.47
72 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR036 | 1S-DL-YP-CTC-DCCK-0104-LHR036 | TOWN HALL:ID | TG-LHR036A-3 | 19501169 | 990 | 320 | 247 | 0.97 | 705 | 241 | 995 | 222 | 908 | 242 | 978 | 80 | 2019-06-26 13:30 | 153.1 | 19.1 | 1163 | Y | 105 | 95 | 100 | 10 |  | 3.9 | 95.3 | 0.8 | 441.52 | 459.52 | 450.52 | 453.22 | 64.3 | 59.3 | 59.3 | 60.3 | 213.3 | 200 | 174 | 206 |  | 0.3 | [6 empty] | 719.52 | 0.08 | 0.38 | 0.71
73 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR037 | 1S-DL-YP-CTC-DCCK-0104-LHR037 | CHURCH MISSION:K | TG-LHR037A-1 | 19504833 | 990 | 320 | 238 | 0.99 | 418 | 129 | 578 | 138 | 618 | 151 | 668 | 79 | 2019-06-06 14:30 | 63.3 | 8.8 | 693 | B | 96 | 96 | 108 | 12 |  |  | 10.7 | 89.3 | 116.42 | 162.13 | 56.58 | 97.15 | 598.16 | 541.45 | 541.45 | 614.43 | 2 | 13 | 42.3 | 5 | [8 empty] | 716.58 | 3.02 | 0.63 | 0.42
74 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR037 | 1S-DL-YP-CTC-DCCK-0104-LHR037 | CHURCH MISSION:K | TG-LHR037A-2 | 19503541 | 990 | 320 | 237 | 0.97 | 645 | 237 | 1029 | 205 | 882 | 203 | 864 | 157 | 2019-06-15 15:30 | 128.8 | 47.1 | 1158 | R | 113 | 100 | 88 | 25 |  | 19.4 | 77.1 | 3.5 |  | 1 | 1.3 |  | 309.42 | 413.07 | 413.07 | 437.04 | 407.15 | 302.5 | 199.5 | 279.53 | [8 empty] | 716.57 | 3.03 | 0.62 | 0.65
75 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR038 | 1S-DL-YP-CTC-DCCK-0104-LHR038 | CLOTH MKT:K | TG-LHR038A-1 | 19505344 | 990 | 320 | 246 | 0.97 | 602 | 198 | 870 | 216 | 939 | 189 | 824 | 101 | 2019-06-29 13:30 | 138.2 | 3.8 | 939 | Y | 99 | 105 | 96 | 9 | 0.1 | 0.1 | 38.8 | 61 | 464.41 | 464.41 | 467.11 | 464.41 | 34.5 | 35.29 | 35.29 | 36.2 | 189.42 | 189.03 | 179.42 | 188.12 | [8 empty] | 689.13 | 30.47 | 0.31 | 0.61
76 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR039 | 1S-DL-YP-CTC-DCCK-0104-LHR039 | JAI PURIA BUILDING:K | TG-LHR039A-1 | 19504640 | 990 | 320 | 237 | 0.97 | 664 | 231 | 1025 | 175 | 768 | 259 | 1134 | 325 | 2019-06-12 16:00 | 134.7 | 28.7 | 1138 | B | 99 | 88 | 114 | 26 |  |  | 11.4 | 88.6 | 241.41 | 256.41 | 132.19 | 201.11 | 282.3 | 311.42 | 311.42 | 321.3 | 193.39 | 149.27 | 217.39 | 195.09 | [8 empty] | 717.5 | 2.1 | 0.46 | 0.67
77 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR040 | 1S-DL-YP-CTC-DCCK-0104-LHR040 | TILAK BAZAR:PKG | TG-LHR040A-1 | 19506178 | 990 | 320 | 246 | 0.96 | 728 | 194 | 805 | 251 | 1045 | 282 | 1175 | 324 | 2019-06-26 13:30 | 204.2 | 43.2 | 1175 | B | 108 | 79 | 113 | 34 | 0.2 | 0.1 | 18.5 | 81.2 | 2 | 387.22 | 1.3 | 13 | 480.28 | 127 | 127 | 476.52 | 213.05 | 181.11 | 221.11 | 205.41 |  |  | 3 | [5 empty] | 695.33 | 24.27 | 0.48 | 0.74
78 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR041 | 1S-DL-YP-CTC-DCCK-0104-LHR041 | NAYA BANSH:PL | TG-LHR041A-1 | 19501519 | 990 | 320 | 248 | 0.96 | 271 | 75 | 301 | 101 | 410 | 95 | 384 | 99 | 2019-06-12 15:30 | 89.1 | 22.8 | 431 | Y | 86 | 107 | 107 | 21 |  |  | 37.6 | 62.4 | 626.19 | 315.59 | 327.27 | 405.49 | 93.14 | 403.34 | 403.34 | 313.44 | [12 empty] | 719.33 | 0.27 | 0.7 | 0.27
79 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR042 | 1S-DL-YP-CTC-DCCK-0104-LHR042 | GADODIA I/D:ID | TG-LHR042A-1 | 19501497 | 630 | 200 | 242 | 0.97 | 331 | 86 | 349 | 135 | 553 | 110 | 449 | 177 | 2019-06-03 15:30 | 77.3 | 13.3 | 575 | Y | 80 | 119 | 100 | 39 |  | 0.2 | 63.6 | 36.2 | 508.57 | 462.27 | 472.27 | 486.57 | 146.3 | 81.3 | 81.3 | 89 | 64.3 | 176 | 122.3 | 144 | [8 empty] | 719.57 | 0.03 | 0.43 | 0.53
80 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR043 | 1S-DL-YP-CTC-DCCK-0104-LHR043 | GADODIA KIOSK:K | TG-LHR043A-1 | 19506662 | 990 | 320 | 234.3152 | 0.96926 | 947.8727 | 347.9285 | 1554.2928 | 285.6446 | 1246.5942 | 314.2996 | 1399.7489 | 266.4758 | 2019-06-06 16:00 | [15 empty] | 480.5 |  |  |  | 37 |  |  |  | 133 |  |  |  | 63 |  |  |  | 0 | 713.5 |  | 0.29798 | 0.95745
81 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR044 | 1S-DL-YP-CTC-DCCK-0104-LHR044 | GADODIA PLINTH:PL | TG-LHR044A-1 | 19500238 | 990 | 320 | 249 | 0.96 | 619 | 176 | 734 | 235 | 984 | 209 | 869 | 217 | 2019-06-29 15:30 | 146.5 | 27.2 | 984 | Y | 96 | 101 | 103 | 7 |  | 0.1 | 6.9 | 92.9 | 426.57 | 411.27 | 403.57 | 421.57 | 121 | 98.3 | 98.3 | 98.3 | 172 | 210 | 205.3 | 199.3 | [8 empty] | 719.57 | 0.03 | 0.43 | 0.63
82 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR045 | 1S-DL-YP-CTC-DCCK-0104-LHR045 | LAL QUAN DMS:PL | TG-LHR045A-1 | 19506180 | 990 | 320 | 237 | 0.94 | 741 | 186 | 787 | 194 | 830 | 360 | 1601 | 794 | 2019-06-13 22:00 | 245.4 | 86.4 | 1601 | B | 97 | 104 | 99 | 7 | 0.3 | 0.1 | 22.2 | 77.4 |  |  |  |  | 57.22 | 20 | 20 | 28.51 | 638.23 | 676.09 | 651.48 | 667.18 | 0.24 | [5 empty] | 0.3 |  | 696.09 | 23.51 | 0.69 | 0.75
83 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR046 | 1S-DL-YP-CTC-DCCK-0104-LHR046 | LAL DARWAZA:PM | TG-LHR046A-1 | 19506181 | 400 | 120 | 244.0093 | 0.92864 | 333.0715 | 188.3708 | 758.3976 | 82.5021 | 323.3727 | 62.1987 | 243.6202 | 479.8973 | 2019-06-02 10:00 | [15 empty] | 0.5 |  |  |  | 21.5 |  |  |  | 694.5 |  |  |  | 3 |  |  |  | 0 | 719.5 |  | 0.68443 | 0.83268
84 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR046 | 1S-DL-YP-CTC-DCCK-0104-LHR046 | LAL DARWAZA:PM | TG-LHR046A-2 | 19504892 | 400 | 120 | 239 | 0.94 | 260 | 67 | 271 | 67 | 276 | 126 | 523 | 249 | 2019-06-12 00:30 | 86.7 | 42.2 | 523 | B | 79 | 95 | 125 | 46 |  |  | 26.9 | 73.1 | 2.3 | 0.3 | 0.3 | 0.3 | 492.57 | 184.3 | 184.3 | 125.3 | 224.3 | 534.57 | 680.57 | 593.57 |  |  | 21 | [5 empty] | 719.57 | 0.03 | 0.72 | 0.65
85 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR047 | 1S-DL-YP-CTC-DCCK-0104-LHR047 | LAMBI GALI:PL | TG-LHR047A-1 | 19501516 | 990 | 320 | 236 | 0.93 | 884 | 287 | 1183 | 317 | 1314 | 280 | 1148 | 152 | 2019-06-03 04:30 | 290 | 145 | 1405 | Y | 103 | 108 | 88 | 20 |  | 0.3 | 75.7 | 24 |  |  |  |  | 3.13 |  |  | 1.3 | 613.32 | 610.3 | 677.21 | 658.42 | 100.04 | 107.19 | 16.28 | 57.37 | 1 |  |  |  | 717.49 | 2.11 | 0.73 | 0.89
86 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR048 | 1S-DL-YP-CTC-DCCK-0104-LHR048 | P.S HAUZ QUAZI:PL | TG-LHR048A-1 | 19501649 | 990 | 320 | 239 | 0.96 | 535 | 181 | 753 | 211 | 883 | 143 | 592 | 252 | 2019-06-29 17:00 | 127.3 | 16.9 | 883 | Y | 133 | 64 | 103 | 69 |  |  | 0.3 | 99.7 | 270.23 | 624.21 | 501.53 | 510.53 | 312.3 | 63.58 | 63.58 | 173.26 | 135.56 | 30.3 | 58.51 | 34.3 | [8 empty] | 718.49 | 1.11 | 0.36 | 0.54
87 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR048 | 1S-DL-YP-CTC-DCCK-0104-LHR048 | P.S HAUZ QUAZI:PL | TG-LHR048A-2 | 19501648 | 990 | 320 | 230 | 0.94 | 892 | 357 | 1590 | 262 | 1168 | 273 | 1211 | 402 | 2019-06-02 04:00 | 284.1 | 117.8 | 1598 | R | 108 | 90 | 101 | 18 |  | 0 | 1.9 | 98.1 |  |  |  |  | 4.3 | 18 | 18 | 5.3 | 557.54 | 699.17 | 664.48 | 670.47 | 143.53 | 0.3 | 46.59 | 41.3 | 11.3 |  |  |  | 717.47 | 2.13 | 0.71 | 0.9
88 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR048 | 1S-DL-YP-CTC-DCCK-0104-LHR048 | P.S HAUZ QUAZI:PL | TG-LHR048A-3 | 19506502 | 990 | 320 | 258 | 0.93 | 746 | 192 | 829 | 216 | 966 | 338 | 1512 | 625 | 2019-06-28 14:30 | 294.7 | 57.6 | 1512 | B | 101 | 95 | 104 | 9 | 0.1 |  | 13 | 87 | 4 | 7.3 | 0.3 | 2 | 498.39 | 504.36 | 504.36 | 500.06 | 190.24 | 180.57 | 198.54 | 190.57 | [6 empty] | 0.3 |  | 693.03 | 26.57 | 0.47 | 0.75
89 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR050 | 1S-DL-YP-CTC-DCCK-0104-LHR050 | ZAKIR HUSSAIN:PL | TG-LHR050A-1 | 19501628 | 630 | 200 | 240.225 | 0.96147 | 221.3307 | 95.3577 | 405.6738 | 42.9675 | 182.0813 | 83.0055 | 350.3819 | 201.7125 | 2019-06-14 13:30 | [15 empty] | 496.5 |  |  |  | 222.5 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 719 |  | 0.49917 | 0.35132
90 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR050 | 1S-DL-YP-CTC-DCCK-0104-LHR050 | ZAKIR HUSSAIN:PL | TG-LHR050A-2 | 19506144 | 990 | 320 | 261 | 0.94 | 284 | 124 | 556 | 111 | 486 | 49 | 208 | 319 | 2019-06-28 14:30 | 111.4 | 4.8 | 556 | R | 99 | 124 | 77 | 47 | 0.1 |  | 0.1 | 99.9 | 604.52 | 547.43 | 660.5 | 601.52 | 88.53 | 146.02 | 146.02 | 91.53 | [12 empty] | 693.45 | 26.15 | 0.31 | 0.29
91 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR051 | 1S-DL-YP-CTC-DCCK-0104-LHR051 | NEW HAUZ QUAZI:ID | TG-LHR051A-1 | 19501494 | 990 | 320 | 265 | 0.96 | 460 | 145 | 570 | 167 | 655 | 148 | 580 | 81 | 2019-06-29 16:00 | 129.5 | 3.7 | 655 | Y | 95 | 104 | 101 | 9 |  |  | 1.9 | 98.1 | 504.08 | 506.38 | 503.11 | 506.38 | 133.28 | 85.45 | 85.45 | 107.28 | 79.37 | 124.5 | 103.37 | 103.07 | [8 empty] | 717.13 | 2.47 | 0.32 | 0.46
92 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR051 | 1S-DL-YP-CTC-DCCK-0104-LHR051 | NEW HAUZ QUAZI:ID | TG-LHR051A-2 | 19501627 | 990 | 320 | 245 | 0.96 | 626 | 207 | 891 | 206 | 891 | 214 | 927 | 36 | 2019-06-05 14:30 | 147.2 | 5.9 | 1004 | Y | 95 | 99 | 105 | 10 |  |  | 16.4 | 83.6 | 231.55 | 316.25 | 165.55 | 219.55 | 333.54 | 218.15 | 218.15 | 321.45 | 150.44 | 181.53 | 179.53 | 174.53 | [8 empty] | 716.33 | 3.27 | 0.46 | 0.63
93 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR051 | 1S-DL-YP-CTC-DCCK-0104-LHR051 | NEW HAUZ QUAZI:ID | TG-LHR051A-3 | 19505507 | 630 | 200 | 242 | 0.95 | 693 | 223 | 1044 | 218 | 1040 | 252 | 1236 | 194 | 2019-06-28 15:00 | 265.6 | 48 | 1236 | B | 95 | 99 | 107 | 12 | 0.1 | 0.1 | 4.6 | 95.1 | 1 |  |  |  | 35 | 13.3 | 13.3 | 13.3 | 654.42 | 666.12 | 576.23 | 655.27 | 27 | 38 | 131.04 | 48.45 | 0.3 | 0.3 | 4.45 | 0.3 | 718.12 | 1.48 | 0.58 | 1.1
94 | 2019-06-02 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR052 | 1S-DL-YP-CTC-DCCK-0104-LHR052 | OLD HAUZ QUAZI:ID | TG-LHR052A-1 | 19501647 | 990 | 320 | 239 | 0.97 | 622 | 216 | 923 | 200 | 858 | 207 | 885 | 57 | 2019-06-29 15:30 | 143.5 | 8.8 | 934 | R | 97 | 99 | 104 | 7 |  | 0.1 | 2.3 | 97.6 | 477.56 | 464.26 | 462.56 | 467.56 | 39.3 | 48 | 48 | 44.3 | 177.44 | 182.44 | 186.44 | 182.44 | [8 empty] | 695.1 | 0.5 | 0.35 | 0.63
95 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR052 | 1S-DL-YP-CTC-DCCK-0104-LHR052 | OLD HAUZ QUAZI:ID | TG-LHR052A-2 | 19501646 | 990 | 320 | 239 | 0.97 | 674 | 238 | 1014 | 207 | 876 | 229 | 975 | 123 | 2019-06-29 16:00 | 162.7 | 8.8 | 1062 | R | 108 | 89 | 103 | 19 |  | 0.1 | 0.4 | 99.4 | 482.26 | 489.26 | 482.26 | 485.26 | 40.3 | 50.28 | 50.28 | 46 | 196.14 | 179.16 | 190.44 | 187.44 | [8 empty] | 719.1 | 0.5 | 0.36 | 0.68
96 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR052 | 1S-DL-YP-CTC-DCCK-0104-LHR052 | OLD HAUZ QUAZI:ID | TG-LHR052A-3 | 19506145 | 630 | 200 | 246 | 0.96 | 416 | 151 | 745 | 150 | 666 | 115 | 547 | 173 | 2019-06-28 14:30 | 163.2 | 16.4 | 804 | Y | 106 | 109 | 85 | 24 | 100 |  |  |  | 298 | 218 | 461.58 | 301 | 265.5 | 317.52 | 317.52 | 270.04 | 131.46 | 159.14 | 43.27 | 124.32 |  | 0.3 | [6 empty] | 695.36 | 24.24 | 0.38 | 0.66
97 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR053 | 1S-DL-YP-CTC-DCCK-0104-LHR053 | RODH GRAM:K | TG-LHR053A-1 | 19501608 | 990 | 320 | 235 | 0.95 | 744 | 302 | 1266 | 201 | 841 | 242 | 1021 | 369 | 2019-06-03 04:00 | 215.6 | 105.2 | 1335 | R | 121 | 88 | 91 | 33 |  |  | 7.5 | 92.5 |  |  |  |  | 6.29 | 135.17 | 135.17 | 29.47 | 632.22 | 583.53 | 634.23 | 689.23 | 80.19 | [7 empty] | 719.1 | 0.5 | 0.72 | 0.75
98 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR053 | 1S-DL-YP-CTC-DCCK-0104-LHR053 | RODH GRAM:K | TG-LHR053A-2 | 19501609 | 990 | 320 | 237 | 0.95 | 530 | 167 | 686 | 126 | 514 | 237 | 965 | 394 | 2019-06-13 21:00 | 165.6 | 65.5 | 965 | B | 93 | 86 | 120 | 34 |  | 0.1 | 19.7 | 80.2 | 3.3 | 3 | 1.3 | 1.3 | 483.02 | 609.32 | 609.32 | 314.08 | 232.5 | 106.5 | 635.12 | 403.44 | [8 empty] | 719.22 | 0.38 | 0.76 | 0.54
99 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR054 | 1S-DL-YP-CTC-DCCK-0104-LHR054 | HAMDARD:ID | TG-LHR054A-1 | 19501504 | 400 | 120 | 247 | 0.94 | 337 | 178 | 782 | 78 | 319 | 80 | 337 | 454 | 2019-06-11 05:00 | 132.2 | 35.1 | 782 | R | 107 | 97 | 95 | 12 | 0.1 |  | 50 | 50 |  |  |  |  | 53.25 | 76.25 | 76.25 | 43.32 | 628.52 | 640.52 | 645.1 | 674.15 | 35.3 | 1 | 1.3 | 0.3 | 0.3 |  |  |  | 718.17 | 1.43 | 0.65 | 0.84
100 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR055 | 1S-DL-YP-CTC-DCCK-0104-LHR055 | GALI KASIM JAAN:ID | TG-LHR055A-1 | 19501574 | 990 | 320 | 238.5275 | 0.9506 | 966.7434 | 345.9584 | 1528.6248 | 308.2865 | 1358.0305 | 312.4985 | 1369.6464 | 165.0931 | 2019-06-02 04:30 | [15 empty] | 0 |  |  |  | 14.5 |  |  |  | 551.5 |  |  |  | 74 |  |  |  | 0 | 640 |  | 0.62588 | 0.97651
101 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR055 | 1S-DL-YP-CTC-DCCK-0104-LHR055 | GALI KASIM JAAN:ID | TG-LHR055A-2 | 19501573 | 990 | 320 | 230 | 0.95 | 934 | 308 | 1387 | 336 | 1522 | 290 | 1285 | 206 | 2019-06-02 04:00 | 255.4 | 120.7 | 1569 | Y | 105 | 107 | 88 | 19 | 0.3 | 66.1 | 33.7 | [5 empty] | 0.3 |  |  | 1 | 562.02 | 532.26 | 691.27 | 620.56 | 153.54 | 182 | 16 | 95 | 0.3 | 2.3 |  |  | 716.56 | 3.04 | 0.71 | 0.94
102 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR056 | 1S-DL-YP-CTC-DCCK-0104-LHR056 | GALI HASHMUDDIN:PKG | TG-LHR056A-1 | 19500694 | 990 | 320 | 241.1914 | 0.9491 | 1138.5187 | 395.903 | 1664.7171 | 413.7793 | 1782.9935 | 328.8364 | 1333.6971 | 403.3799 | 2019-06-30 01:00 | [15 empty] | 0 |  |  |  | 0 |  |  |  | 415.5 |  |  |  | 202.5 |  |  |  | 99 | 717 |  | 0.67461 | 1.15
103 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR057 | 1S-DL-YP-CTC-DCCK-0104-LHR057 | MOTHER DAIRY:K | TG-LHR057A-1 | 19506540 | 990 | 320 | 242 | 0.95 | 552 | 202 | 837 | 160 | 657 | 190 | 789 | 161 | 2019-06-29 17:30 | 170.2 | 59.5 | 931 | R | 93 | 102 | 106 | 13 | 0.1 | 0.1 | 26.9 | 72.8 | 15 | 7 | 5 | 5 | 548.55 | 513.25 | 513.25 | 549.27 | 132 | 175.3 | 195.56 | 141.28 | [8 empty] | 695.55 | 24.05 | 0.61 | 0.56
104 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR057 | 1S-DL-YP-CTC-DCCK-0104-LHR057 | MOTHER DAIRY:K | TG-LHR057A-2 | 19506586 | 990 | 320 | 237.2716 | 0.95149 | 660.145 | 157.2395 | 697.4166 | 242.044 | 1088.7189 | 260.8614 | 1160.7255 | 431.8319 | 2019-06-27 16:30 | [15 empty] | 0.5 |  |  |  | 144 |  |  |  | 574 |  |  |  | 0 |  |  |  | 0 | 718.5 |  | 0.68421 | 0.66681
105 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR057 | 1S-DL-YP-CTC-DCCK-0104-LHR057 | MOTHER DAIRY:K | TG-LHR057A-3 | 19505786 | 990 | 320 | 238 | 0.94 | 787 | 227 | 986 | 305 | 1347 | 254 | 1117 | 316 | 2019-06-05 16:30 | 345.3 | 104.3 | 1347 | Y | 98 | 110 | 93 | 17 | 0.1 |  | 5 | 94.9 |  |  |  |  | 55.28 | 10.3 | 10.3 | 33 | 660.32 | 704.3 | 619 | 683 |  | 1 | [6 empty] | 716 | 4 | 0.67 | 0.79
106 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR059 | 1S-DL-YP-CTC-DCCK-0104-LHR059 | GALI SHATARA:PL | TG-LHR059A-1 | 19505553 | 990 | 320 | 238 | 0.93 | 769 | 270 | 1150 | 251 | 1062 | 247 | 1063 | 87 | 2019-06-11 19:00 | 305.9 | 51.5 | 1150 | R | 108 | 99 | 94 | 14 | 0.1 |  | 1.8 | 98.1 | 2.2 | 1.33 | 1.33 | 1.33 | 17.33 | 83.38 | 83.38 | 33.53 | 690.22 | 626.34 | 627.52 | 676.19 | 1.3 | [7 empty] | 711.45 | 8.15 | 0.66 | 0.78
107 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | LHR021 | 1S-DL-YP-CTC-DCCK-0104-LHR021 | ROSHAN PURA:PM | TG-LHR021A-1 | 19500242 | 990 | 300 | 238 | 0.96 | 564 | 174 | 759 | 207 | 901 | 183 | 795 | 128 | 2019-06-29 17:00 | 153.9 | 40 | 905 | Y | 91 | 104 | 105 | 14 |  | 0.1 | 5.5 | 94.4 | 167.3 | 129.3 | 60 | 119 | 419.49 | 394.19 | 394.19 | 424.19 | 132.3 | 196 | 178 | 176.3 | [8 empty] | 719.49 | 0.11 | 0.54 | 0.57
108 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | LHR022 | 1S-DL-YP-CTC-DCCK-0104-LHR022 | NAI SARAK PIAO:PM | TG-LHR022A-1 | 19505408 | 990 | 300 | 244 | 0.98 | 747 | 282 | 1215 | 242 | 1045 | 223 | 959 | 226 | 2019-06-15 14:00 | 145.5 | 7.5 | 1216 | R | 112 | 93 | 95 | 19 | 0.1 | 0.1 | 8.4 | 91.5 | 395.05 | 399.35 | 405.05 | 398.05 | 66 | 89 | 89 | 86.3 | 223.53 | 207.23 | 198.53 | 211.23 | 11 | [7 empty] | 695.58 | 24.02 | 0.35 | 0.75
109 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | LHR049 | 1S-DL-YP-CTC-DCCK-0104-LHR049 | MORE SARAI KHATTA NO-1:PM | TG-LHR049A-1 | 19500251 | 630 | 200 | 239 | 0.96 | 241 | 99 | 424 | 76 | 325 | 66 | 287 | 123 | 2019-06-11 17:30 | 52.9 | -0.5 | 434 | R | 123 | 95 | 82 | 41 |  |  | 4.8 | 95.2 | 109.58 | 479.19 | 536.44 | 450.19 | 579.34 | 239.43 | 239.43 | 268.43 | 29.3 | [11 empty] | 719.02 | 0.58 | 0.55 | 0.38
110 | 2019-06-03 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL001 | 1S-DL-YP-CTC-DCCK-0103-THL001 | FOUNTAIN:ID | TG-THL001A-1 | 19501099 | 990 | 320 | 240 | 0.97 | 672 | 228 | 965 | 240 | 1025 | 203 | 866 | 139 | 2019-06-15 16:30 | 134.7 | 5.2 | 1066 | R | 103 | 106 | 91 | 15 |  |  | 15.6 | 84.4 | 423.51 | 390.21 | 420.21 | 412.51 | 47.3 | 72.3 | 72.3 | 56.3 | 200.2 | 208.5 | 192.3 | 202.2 | [8 empty] | 671.41 | 0.19 | 0.36 | 0.68
111 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL001 | 1S-DL-YP-CTC-DCCK-0103-THL001 | FOUNTAIN:ID | TG-THL001A-2 | 19506394 | 990 | 320 | 240 | 0.97 | 633 | 226 | 1003 | 180 | 799 | 227 | 1016 | 211 | 2019-06-29 15:30 | 150.4 | 7.7 | 1049 | R | 105 | 96 | 99 | 9 | 0.1 | 0.1 | 22.7 | 77 | 450.23 | 458.23 | 446.53 | 450.53 | 53.3 | 62 | 62 | 59.3 | 197.38 | 181.08 | 188.38 | 191.08 | [8 empty] | 701.31 | 18.29 | 0.34 | 0.64
112 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL001 | 1S-DL-YP-CTC-DCCK-0103-THL001 | FOUNTAIN:ID | TG-THL001A-3 | 19503418 | 990 | 320 | 246 | 0.98 | 224 | 87 | 358 | 58 | 241 | 79 | 326 | 105 | 2019-06-22 14:30 | 44.9 | -7.4 | 417 | R | 121 | 73 | 106 | 48 |  |  | 7.6 | 92.4 | 543.49 | 719.49 | 662.19 | 676.49 | 176 |  |  | 43 | [12 empty] | 719.49 | 0.11 | 0.41 | 0.23
113 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL001 | 1S-DL-YP-CTC-DCCK-0103-THL001 | FOUNTAIN:ID | TG-THL001A-4 | 19501761 | 990 | 320 | 239 | 0.98 | 544 | 178 | 774 | 189 | 825 | 177 | 762 | 58 | 2019-06-06 16:00 | 179.6 | -5.2 | 938 | Y | 93 | 115 | 92 | 23 |  | 0.8 | 7 | 92.2 | 340.49 | 286.58 | 383.49 | 332.49 | 258 | 229.51 | 229.51 | 222.3 | 121 | 203 | 144 | 164.3 | [8 empty] | 719.49 | 0.11 | 0.45 | 0.55
114 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL002 | 1S-DL-YP-CTC-DCCK-0103-THL002 | GALI GULIYAN:PKG | TG-THL002A-1 | 19504567 | 990 | 320 | 232 | 0.98 | 707 | 185 | 820 | 266 | 1206 | 256 | 1130 | 354 | 2019-06-29 16:30 | 163.4 | 23.6 | 1308 | Y | 82 | 126 | 92 | 44 | 20.7 | 35.1 | 35.1 | 9.1 | 25.3 | 1 | 4.3 | 1 | 436.28 | 103.3 | 103.3 | 290.3 | 234 | 582.58 | 300.58 | 404.28 |  | 8.3 | [6 empty] | 719.44 | 0.16 | 0.6 | 0.71
115 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL002 | 1S-DL-YP-CTC-DCCK-0103-THL002 | GALI GULIYAN:PKG | TG-THL002A-2 | 19501098 | 990 | 320 | 238 | 0.97 | 577 | 174 | 770 | 170 | 768 | 232 | 1005 | 236 | 2019-06-29 16:00 | 117 | 39 | 1005 | B | 104 | 83 | 113 | 30 | 42.8 | 18.8 | 23.5 | 14.9 | 1.3 | 40 | 1 | 1.3 | 308.19 | 474.19 | 474.19 | 313.58 | 332.3 | 128 | 452.49 | 326.51 | [8 empty] | 642.19 | 0.11 | 0.68 | 0.58
116 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL003 | 1S-DL-YP-CTC-DCCK-0103-THL003 | OLD LAJPAT RAI MKT:ID | TG-THL003A-1 | 19506891 | 990 | 320 | 244 | 0.98 | 648 | 235 | 1022 | 222 | 950 | 191 | 825 | 173 | 2019-06-26 16:00 | 211.5 | 1.6 | 1256 | Y | 103 | 101 | 97 | 6 | 0.1 |  | 61.9 | 38 | 467.48 | 467.22 | 472.22 | 471.52 | 42.04 | 46 | 46 | 39.3 | 192.02 | 188.02 | 184.02 | 190.32 |  | 0.3 | [6 empty] | 701.54 | 18.06 | 0.33 | 0.65
117 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL003 | 1S-DL-YP-CTC-DCCK-0103-THL003 | OLD LAJPAT RAI MKT:ID | TG-THL003A-2 | 19501230 | 990 | 320 | 244 | 0.98 | 646 | 236 | 1020 | 207 | 887 | 204 | 867 | 144 | 2019-06-12 16:30 | 124.4 | 0.7 | 1061 | R | 105 | 97 | 98 | 8 |  | 1.2 | 57.7 | 41.1 | 479.49 | 482.49 | 482.49 | 481.49 | 42 | 46 | 46 | 44 | 194.32 | 187.32 | 195.32 | 190.32 | [8 empty] | 716.21 | 3.39 | 0.29 | 0.65
118 | 2019-06-02 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL003 | 1S-DL-YP-CTC-DCCK-0103-THL003 | OLD LAJPAT RAI MKT:ID | TG-THL003A-3 | 19501177 | 990 | 320 | 245 | 0.97 | 583 | 186 | 804 | 230 | 1014 | 167 | 727 | 257 | 2019-06-13 16:00 | 122.2 | 0.7 | 1022 | Y | 97 | 115 | 89 | 26 |  | 3.8 | 57.6 | 38.6 | 479.49 | 473.19 | 478.19 | 478.49 | 57.46 | 36 | 36 | 45.16 | 156.56 | 185.12 | 147.56 | 170.26 | [8 empty] | 694.31 | 1.29 | 0.28 | 0.59
119 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL004 | 1S-DL-YP-CTC-DCCK-0103-THL004 | KATRA KUSHAL RAI:ID | TG-THL004A-1 | 19500224 | 990 | 320 | 237 | 0.96 | 728 | 234 | 1028 | 303 | 1347 | 192 | 840 | 444 | 2019-06-02 23:30 | 206.1 | 62.6 | 1347 | Y | 106 | 112 | 81 | 31 |  |  | 5.6 | 94.4 | 0.3 | 0.3 | 0.3 | 0.3 | 109.59 | 108.3 | 108.3 | 159.29 | 607.02 | 588.31 | 419.34 | 557.32 |  | 20 | [6 empty] | 717.31 | 2.29 | 0.69 | 0.74
120 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL004 | 1S-DL-YP-CTC-DCCK-0103-THL004 | KATRA KUSHAL RAI:ID | TG-THL004A-2 | 19500225 | 990 | 320 | 238 | 0.97 | 877 | 287 | 1242 | 310 | 1355 | 280 | 1223 | 123 | 2019-06-08 17:00 | 217.9 | 32.4 | 1401 | Y | 94 | 111 | 95 | 17 |  |  | 30.5 | 69.5 | 102.22 | 14 | 110 | 60.3 | 389.11 | 455.25 | 455.25 | 424.03 | 203.29 | 183.07 | 203.29 | 204.29 | 12 | 54.3 | 11.39 | 18 |  |  |  |  | 707.02 | 12.58 | 0.44 | 0.89
121 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL004 | 1S-DL-YP-CTC-DCCK-0103-THL004 | KATRA KUSHAL RAI:ID | TG-THL004A-3 | 19503562 | 990 | 320 | 233 | 0.97 | 699 | 270 | 1204 | 226 | 1009 | 204 | 912 | 257 | 2019-06-12 15:30 | 150.1 | 33.1 | 1208 | R | 109 | 103 | 88 | 21 |  |  | 9.5 | 90.5 | 55 | 38.3 | 136 | 62 | 425.18 | 451.18 | 451.18 | 432.48 | 236 | 227.3 | 193 | 222.3 | 1 | [7 empty] | 717.18 | 2.42 | 0.51 | 0.71
122 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL005 | 1S-DL-YP-CTC-DCCK-0103-THL005 | PAIWALLAN :ID | TG-THL005A-1 | 19501181 | 990 | 320 | 249 | 0.96 | 750 | 278 | 1159 | 257 | 1050 | 216 | 892 | 232 | 2019-06-26 16:30 | 188.4 | 19.1 | 1161 | R | 106 | 90 | 105 | 16 |  | 0.8 | 97.6 | 1.5 | 80 | 186 | 20.3 | 60.3 | 424.17 | 353.47 | 353.47 | 484.17 | 210.14 | 178.44 | 192.44 | 173.44 | 4 | [7 empty] | 718.31 | 1.29 | 0.45 | 0.76
123 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL005 | 1S-DL-YP-CTC-DCCK-0103-THL005 | PAIWALLAN :ID | TG-THL005A-2 | 19506371 | 990 | 320 | 237 | 0.96 | 619 | 203 | 900 | 222 | 995 | 194 | 870 | 113 | 2019-06-13 14:30 | 161 | 18.9 | 1025 | Y | 93 | 99 | 108 | 15 | 0.2 | 1 | 89.8 | 9 | 232.37 | 215.3 | 111 | 181 | 338.07 | 339.44 | 339.44 | 379.14 | 124.57 | 140.27 | 161.18 | 135.27 | [8 empty] | 695.41 | 24.19 | 0.48 | 0.63
124 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL005 | 1S-DL-YP-CTC-DCCK-0103-THL005 | PAIWALLAN :ID | TG-THL005A-3 | 19506372 | 990 | 320 | 246 | 0.97 | 658 | 338 | 1542 | 143 | 628 | 176 | 781 | 848 | 2019-06-07 13:30 | 204.2 | 7 | 1542 | R | 107 | 91 | 103 | 16 | 0.3 |  | 6.8 | 92.9 | 465.34 | 475.04 | 469.34 | 470.34 | 47.35 | 71.02 | 71.02 | 44.33 | 200.15 | 167.48 | 205.17 | 198.47 |  |  |  |  | 0.3 |  |  |  | 713.54 | 6.06 | 0.32 | 0.66
125 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL006 | 1S-DL-YP-CTC-DCCK-0103-THL006 | NEW LAJPAT RAI MKT:ID | TG-THL006A-1 | 19500223 | 990 | 320 | 239 | 0.99 | 866 | 395 | 1692 | 200 | 843 | 271 | 1161 | 744 | 2019-06-03 16:00 | 131.7 | -8.8 | 1701 | R | 124 | 83 | 93 | 41 |  | 0.3 | 53 | 46.6 | 429.29 | 423.45 | 434.13 | 429.43 | 44.58 | 97.41 | 97.41 | 59.14 | 97.56 | 194.03 | 216.37 | 205.52 | 105.56 |  | 2.1 | 20.4 | 37.1 |  |  |  | 715.29 | 4.31 | 0.31 | 0.87
126 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL007 | 1S-DL-YP-CTC-DCCK-0103-THL007 | MALIWARA : PKG | TG-THL007A-1 | 19505462 | 990 | 320 | 244 | 0.97 | 819 | 294 | 1256 | 266 | 1143 | 259 | 1108 | 134 | 2019-06-29 17:00 | 193.9 | 12.2 | 1295 | R | 99 | 109 | 92 | 17 | 0.1 | 0.1 | 40 | 59.8 | 468.34 | 452.45 | 467.04 | 466.34 | 28.3 | 45.49 | 45.49 | 33 | 202.23 | 195.53 | 216.23 | 216.53 | 20 | 25 |  | 3 |  |  |  |  | 719.27 | 0.33 | 0.35 | 0.83
127 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL008 | 1S-DL-YP-CTC-DCCK-0103-THL008 | PARADE GROUND:PL | TG-THL008A-1 | 19501051 | 630 | 200 | 238 | 0.98 | 209 | 84 | 393 | 79 | 370 | 45 | 207 | 176 | 2019-06-07 15:30 | 39.1 | 0.5 | 445 | Y | 118 | 98 | 84 | 34 |  | 17.8 | 41.7 | 40.6 | 506.18 | 539.48 | 694.48 | 559.18 | 212.3 | 176.3 | 176.3 | 160.3 | 1 | 3.3 | [10 empty] | 719.48 | 0.12 | 0.39 | 0.33
128 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL008 | 1S-DL-YP-CTC-DCCK-0103-THL008 | PARADE GROUND:PL | TG-THL008A-2 | 19504779 | 630 | 200 | 239 | 0.99 | 217 | 86 | 370 | 72 | 310 | 60 | 256 | 99 | 2019-06-14 14:30 | 30.4 | -6.9 | 381 | R | 120 | 96 | 84 | 36 |  | 0.2 | 80.6 | 19.2 | 498.58 | 507.55 | 572.25 | 517.55 | 218.27 | 212 | 212 | 202 | 2.3 | [11 empty] | 719.55 | 0.05 | 0.41 | 0.35
129 | 2019-06-02 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL009 | 1S-DL-YP-CTC-DCCK-0103-THL009 | ANGURI BAGH:PL | TG-THL009A-1 | 19500246 | 990 | 320 | 238 | 0.96 | 416 | 145 | 629 | 139 | 603 | 133 | 574 | 48 | 2019-06-03 16:30 | 125.1 | 36.8 | 642 | R | 101 | 98 | 101 | 3 |  |  | 6.9 | 93.1 | 137.3 | 147.3 | 112 | 126 | 506.58 | 542.28 | 542.28 | 561.58 | 51.3 | 6 | 7 | 8 | [8 empty] | 695.58 | 0.02 | 0.62 | 0.42
130 | 2019-06-12 12:00 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL010 | 1S-DL-YP-CTC-DCCK-0103-THL010 | KUCHHA NALWA:PKG | TG-THL010A-1 | 19506919 | 990 | 320 | 242.2021 | 0.98798 | 941.4822 | 381.6131 | 1681.3372 | 286.9879 | 1267.5585 | 272.8812 | 1200.8502 | 450.8496 | 2019-06-27 14:30 | [15 empty] | 284 |  |  |  | 19.5 |  |  |  | 67 |  |  |  | 69 |  |  |  | 0 | 439.5 |  | 0.31478 | 0.95099
131 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL011 | 1S-DL-YP-CTC-DCCK-0103-THL011 | THANA TOWN HALL:PKG | TG-THL011A-1 | 19501517 | 990 | 320 | 243 | 0.97 | 671 | 257 | 1076 | 203 | 837 | 211 | 882 | 220 | 2019-06-04 18:00 | 157.5 | 4.4 | 1173 | R | 110 | 89 | 101 | 21 |  | 0.1 | 48.9 | 51 | 472 | 488 | 478 | 479 | 36.3 | 43 | 43 | 39 | 209.47 | 187.17 | 197.17 | 200.17 | [8 empty] | 718.17 | 1.43 | 0.32 | 0.68
132 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL012 | 1S-DL-YP-CTC-DCCK-0103-THL012 | KACHHA BAGH:PL | TG-THL012A-1 | 19501851 | 990 | 320 | 245 | 0.97 | 564 | 198 | 858 | 202 | 858 | 164 | 675 | 183 | 2019-06-28 14:30 | 117.8 | 2.9 | 987 | R | 105 | 103 | 92 | 13 | 31.8 | 9 | 29.5 | 29.7 | 484.48 | 478.48 | 488.48 | 483.48 | 51 | 52 | 52 | 52.3 | 183.41 | 188.41 | 124.11 | 183.11 | [8 empty] | 719.29 | 0.31 | 0.32 | 0.57
133 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL012 | 1S-DL-YP-CTC-DCCK-0103-THL012 | KACHHA BAGH:PL | TG-THL012A-2 | 19505691 | 630 | 200 | 240 | 0.98 | 496 | 222 | 1113 | 215 | 1006 | 59 | 264 | 801 | 2019-06-01 19:00 | 190.2 | -0.4 | 1113 | R | 117 | 104 | 79 | 38 | 0.1 | 0.1 | 83 | 16.8 | 474.19 | 473.49 | 489.19 | 477.19 | 32.3 | 44 | 44 | 44.3 | 197 | 200 | 135 | 197 | 14.3 | 0.3 |  |  | 0.3 | 0.3 |  |  | 718.49 | 1.11 | 0.25 | 0.79
134 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL013 | 1S-DL-YP-CTC-DCCK-0103-THL013 | MEENA BAZAR:PKG | TG-THL013A-1 | 19504137 | 400 | 250 | 238 | 0.98 | 49 | 7 | 32 | 20 | 87 | 21 | 89 | 56 | 2019-06-13 15:30 | 8.1 | 0.6 | 109 | B | 59 | 115 | 125 | 66 |  | 0.1 | 9.9 | 89.9 | 720 | 720 | 720 | 720 | [16 empty] | 720 | 0 | 0.29 | 0.12
135 | 2019-06-02 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL014 | 1S-DL-YP-CTC-DCCK-0103-THL014 | KUMAR CINEMA:PKG | TG-THL014A-1 | 19500231 | 990 | 320 | 243 | 0.98 | 840 | 285 | 1226 | 265 | 1150 | 290 | 1240 | 84 | 2019-06-25 16:00 | 161.2 | -17.7 | 1275 | B | 97 | 99 | 103 | 6 |  | 0.9 | 66.5 | 32.6 | 430.41 | 417.41 | 407.11 | 420.11 | 46 | 62.3 | 62.3 | 56.3 | 192.06 | 193.23 | 187.44 | 195.36 | 23.47 | 19 | 31.09 | 20.17 |  |  |  |  | 692.34 | 3.26 | 0.34 | 0.85
136 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL015 | 1S-DL-YP-CTC-DCCK-0103-THL015 | MAHARASHTRA BANK:PKG | TG-THL015A-1 | 19500561 | 990 | 320 | 239.1336 | 0.97583 | 887.9624 | 292.7948 | 1245.6174 | 303.7032 | 1306.082 | 291.4644 | 1220.8443 | 75.9445 | 2019-06-12 16:00 | [15 empty] | 79 |  |  |  | 395.5 |  |  |  | 207 |  |  |  | 36.5 |  |  |  | 0 | 718 |  | 0.44186 | 0.89693
137 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL016 | 1S-DL-YP-CTC-DCCK-0103-THL016 | SUBHASH MARG:PKG | TG-THL016A-1 | 19504810 | 990 | 320 | 245 | 0.97 | 366 | 117 | 489 | 167 | 704 | 81 | 336 | 320 | 2019-06-13 14:00 | 96.4 | -0.7 | 704 | Y | 101 | 124 | 76 | 48 |  | 4.5 | 45.5 | 50 | 517.3 | 508 | 611 | 520 | 201 | 93 | 93 | 200 | 1.3 | 119 | [10 empty] | 720 | 0 | 0.29 | 0.37
138 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL016 | 1S-DL-YP-CTC-DCCK-0103-THL016 | SUBHASH MARG:PKG | TG-THL016A-2 | 19506857 | 990 | 320 | 246 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [7 empty] | 40.9 | 59.1 | 706 | 706 | 706 | 706 | [16 empty] | 706 | 14 |  | 0
139 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL018 | 1S-DL-YP-CTC-DCCK-0103-THL018 | MORE SARAI KHATTA NO-2:PKG | TG-THL018A-1 | 19506169 | 990 | 320 | 240 | 0.98 | 545 | 192 | 822 | 202 | 872 | 150 | 646 | 206 | 2019-06-29 17:00 | 108.8 | 0.3 | 898 | Y | 106 | 111 | 83 | 28 |  |  | 27.4 | 72.6 | 475.49 | 469.49 | 490.49 | 480.19 | 81 | 76.51 | 76.51 | 89.21 | 137.02 | 147.11 | 56.52 | 124.11 | [8 empty] | 693.51 | 26.09 | 0.26 | 0.55
140 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL018 | 1S-DL-YP-CTC-DCCK-0103-THL018 | MORE SARAI KHATTA NO-2:PKG | TG-THL018A-2 | 19505779 | 990 | 320 | 245 | 0.96 | 523 | 194 | 819 | 209 | 824 | 120 | 507 | 315 | 2019-06-12 15:30 | 146.2 | 0.3 | 948 | R | 118 | 118 | 64 | 54 | 99.9 |  | 0.1 |  | 494.39 | 495.09 | 547.27 | 503.39 | 61.18 | 55.48 | 55.48 | 90.07 | 161.42 | 166.42 |  | 123.53 | [8 empty] | 717.39 | 2.21 | 0.27 | 0.53
141 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL019 | 1S-DL-YP-CTC-DCCK-0103-THL019 | KINARI BAZAR:PM | TG-THL019A-1 | 19503057 | 400 | 120 | 236 | 0.97 | 384 | 118 | 520 | 118 | 518 | 148 | 664 | 145 | 2019-06-21 17:00 | 80.3 | 3.3 | 675 | B | 95 | 103 | 101 | 8 |  | 7.1 | 66.4 | 26.5 | 235.1 | 196.1 | 235.1 | 204.4 | 215.04 | 181.3 | 181.3 | 240.04 | 243.26 | 254.3 | 172.04 | 203.34 | 24.3 | 82.3 | 78.22 | 69.52 |  | 3.3 | 4 |  | 718.1 | 1.5 | 0.4 | 0.96
142 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL019 | 1S-DL-YP-CTC-DCCK-0103-THL019 | KINARI BAZAR:PM | TG-THL019A-2 | 19503058 | 400 | 120 | 237 | 0.97 | 371 | 116 | 511 | 149 | 662 | 106 | 463 | 180 | 2019-06-14 15:30 | 89.1 | 1.7 | 719 | Y | 94 | 120 | 86 | 34 | 2 | 20.9 | 73.5 | 3.6 | 460.05 | 380.05 | 464.05 | 458.35 | 23 | 98 | 98 | 24.3 | 162.07 | 53.4 | 233.07 | 142.07 | 73 | 103.27 |  | 93 |  | 83 |  |  | 718.12 | 1.48 | 0.36 | 0.93
143 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL020 | 1S-DL-YP-CTC-DCCK-0103-THL020 | DIWAN HALL:PM | TG-THL020A-1 | 19501226 | 400 | 120 | 239 | 0.98 | 344 | 121 | 536 | 94 | 417 | 129 | 576 | 143 | 2019-06-29 16:00 | 71.5 | -0.3 | 578 | B | 106 | 85 | 109 | 24 | 0.1 | 0.1 | 31.9 | 67.9 | 463.29 | 477.54 | 461.59 | 471.29 | 38.34 | 31.39 | 31.39 | 32.34 | 145.3 | 200.04 | 122 | 188.04 | 62.04 |  | 91.34 | 17.3 |  |  |  |  | 709.37 | 10.23 | 0.3 | 0.86
144 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL020 | 1S-DL-YP-CTC-DCCK-0103-THL020 | DIWAN HALL:PM | TG-THL020A-2 | 19503325 | 400 | 120 | 241 | 0.97 | 138 | 46 | 210 | 49 | 225 | 42 | 192 | 28 | 2019-06-03 14:30 | 25.4 | -1.1 | 277 | B | 45 | 35 | 220 | 185 |  |  | 2.4 | 97.6 | 652.29 | 651.29 | 549.47 | 651.29 | 14 | 15 | 15 | 15 |  |  | 57.23 | [9 empty] | 666.29 | 29.31 | 0.1 | 0.34
145 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL020 | 1S-DL-YP-CTC-DCCK-0103-THL020 | DIWAN HALL:PM | TG-THL020A-3 | 19505844 | 400 | 120 | 241 | 0.98 | 372 | 105 | 468 | 121 | 539 | 146 | 653 | 161 | 2019-06-12 15:00 | 86.6 | -1.1 | 780 | R | 105 | 81 | 113 | 32 | 0.2 | 2.6 | 21.9 | 75.3 | 306.56 | 308.07 | 299.37 | 302.37 | 40.3 | 65.36 | 65.36 | 49.06 | 83.45 | 76.14 | 109.46 | 99.44 | 32.16 | 15 | 17.58 | 13.3 | 1.3 |  | 10 |  | 707.1 | 12.5 | 0.23 | 0.93
146 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL021 | 1S-DL-YP-CTC-DCCK-0103-THL021 | TIKONA PARK:PL | TG-THL021A-1 | 19501180 | 990 | 200 | 239 | 0.98 | 702 | 197 | 859 | 228 | 986 | 278 | 1215 | 312 | 2019-06-29 17:00 | 141.2 | -0.9 | 1278 | B | 100 | 110 | 91 | 19 |  |  | 21.6 | 78.4 | 488.14 | 481.14 | 481.44 | 480.44 | 35 | 30.38 | 30.38 | 37.36 | 186.34 | 197.56 | 158.55 | 191.28 |  |  | 13.04 | [5 empty] | 709.48 | 10.12 | 0.28 | 0.71
147 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL021 | 1S-DL-YP-CTC-DCCK-0103-THL021 | TIKONA PARK:PL | TG-THL021A-2 | 19501176 | 630 | 200 | 239 | 0.98 | 497 | 136 | 595 | 150 | 653 | 211 | 931 | 311 | 2019-06-14 15:30 | 87.9 | -0.5 | 936 | B | 82 | 95 | 123 | 41 |  |  | 32.8 | 67.2 | 486.17 | 476.47 | 468.47 | 476.47 | 36.02 | 38.02 | 38.02 | 29.38 | 187.29 | 194.59 | 75.5 | 203.23 |  |  | 137.16 |  |  |  | 1 |  | 709.48 | 10.12 | 0.29 | 0.79
148 | 2019-06-02 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL022 | 1S-DL-YP-CTC-DCCK-0103-THL022 | BATTERY BUS:ID | TG-THL022A-1 | 19501178 | 990 | 320 | 240 | 0.98 | 447 | 149 | 635 | 174 | 740 | 124 | 519 | 191 | 2019-06-25 14:30 | 84.6 | -2.2 | 755 | Y | 99 | 107 | 94 | 13 |  |  | 69.3 | 30.7 | 477.19 | 475.19 | 479.19 | 474.49 | 141.3 | 102 | 102 | 150.3 | 77 | 118.3 | 3 | 70.3 | [8 empty] | 695.49 | 0.11 | 0.31 | 0.45
149 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL023 | 1S-DL-YP-CTC-DCCK-0103-THL023 | DTC:PACKAGE S/STN | TG-THL023A-1 | 19501055 | 990 | 320 | 228 | 0.97 | 395 | 129 | 601 | 119 | 550 | 148 | 674 | 108 | 2019-06-29 16:30 | 69.2 | 0.7 | 679 | B | 98 | 101 | 101 | 3 | 9.8 | 90.2 |  |  | 500.19 | 506.49 | 501.19 | 498.19 | 214 | 213 | 213 | 221.3 | 5.3 |  | 30.3 | [9 empty] | 719.49 | 0.11 | 0.33 | 0.4
150 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL023 | 1S-DL-YP-CTC-DCCK-0103-THL023 | DTC:PACKAGE S/STN | TG-THL023A-2 | 19506856 | 990 | 320 | 242 | 0.96 | 4 | 4 | 15 | 0 | 0 | 0 | 0 | 15 | 2019-06-02 19:30 | 1.6 | 0.3 | 15 | R | 299 | 0 | 1 | 299 |  |  | 18.8 | 81.2 | 705.48 | 705.48 | 705.48 | 705.48 | [16 empty] | 705.48 | 14.12 | 0.09 | 0
151 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL024 | 1S-DL-YP-CTC-DCCK-0103-THL024 | JUBILEE CINEMA:PKG | TG-THL024A-1 | 19501654 | 990 | 320 | 238 | 0.97 | 719 | 281 | 1227 | 221 | 990 | 217 | 969 | 248 | 2019-06-12 14:30 | 134 | 30.9 | 1249 | R | 115 | 95 | 90 | 25 | 7.2 | 92.8 |  |  | 29.3 | 154.28 | 199.28 | 112 | 469.19 | 368.51 | 368.51 | 405.19 | 201 | 196 | 188.16 | 202 | 19.3 | [7 empty] | 719.19 | 0.41 | 0.46 | 0.73
152 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL024 | 1S-DL-YP-CTC-DCCK-0103-THL024 | JUBILEE CINEMA:PKG | TG-THL024A-2 | 19506851 | 990 | 320 | 241 | 0.97 | 382 | 150 | 648 | 131 | 564 | 100 | 426 | 194 | 2019-06-29 17:00 | 81.9 | 8.3 | 654 | R | 107 | 94 | 99 | 13 | 0.3 |  | 31.2 | 68.6 | 504.49 | 524.19 | 535.19 | 512.49 | 169.21 | 181.21 | 181.21 | 192.51 | 31.3 | [11 empty] | 705.4 | 14.2 | 0.4 | 0.39
153 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL025 | 1S-DL-YP-CTC-DCCK-0103-THL025 | SHRI RAM:PL | TG-THL025A-1 | 19501100 | 990 | 320 | 244 | 0.97 | 843 | 243 | 1071 | 321 | 1435 | 278 | 1244 | 315 | 2019-06-29 13:30 | 206.1 | 1.5 | 1435 | Y | 92 | 106 | 102 | 14 | 0.4 | 0.1 | 56 | 43.6 | 359.11 | 361.41 | 366.11 | 362.11 | 38 | 32 | 32 | 34.3 | 168.33 | 146.34 | 165.23 | 163.59 |  | 25.29 | 2.4 | 5.04 |  |  |  |  | 714.04 | 5.56 | 0.26 | 0.85
154 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL026 | 1S-DL-YP-CTC-DCCK-0103-THL026 | KATRA ASHARFEE:PKG | TG-THL026A-1 | 19501216 | 990 | 320 | 245 | 0.98 | 603 | 201 | 821 | 198 | 804 | 204 | 833 | 25 | 2019-06-15 15:00 | 138.4 | -0.7 | 907 | B | 110 | 95 | 94 | 16 |  |  | 31.1 | 68.9 | 450.21 | 472.21 | 473.51 | 465.21 | 90.38 | 83.45 | 83.45 | 84.46 | 173.38 | 158.31 | 160.3 | 164.3 | [8 empty] | 714.37 | 5.23 | 0.3 | 0.61
155 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL026 | 1S-DL-YP-CTC-DCCK-0103-THL026 | KATRA ASHARFEE:PKG | TG-THL026A-2 | 19505692 | 990 | 300 | 246 | 0.94 | 125 | 24 | 100 | 41 | 171 | 60 | 253 | 133 | 2019-06-28 14:00 | 26.4 | 0.3 | 253 | B | 106 | 57 | 137 | 80 | 0.1 |  | 45 | 55 | 718.44 | 718.44 | 718.44 | 718.44 | [16 empty] | 718.44 | 1.16 | 0.24 | 0.13
156 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL027 | 1S-DL-YP-CTC-DCCK-0103-THL027 | KATRA PYARE LAL:PKG | TG-THL027A-1 | 19505469 | 990 | 320 | 240 | 0.97 | 610 | 283 | 1203 | 73 | 310 | 254 | 1073 | 835 | 2019-06-15 17:30 | 103.4 | -10.2 | 1288 | R | 142 | 33 | 125 | 109 |  | 0.1 | 22.3 | 77.6 | 467.08 | 677.57 | 475.08 | 481.08 | 20.3 | 20.18 | 20.18 | 34.3 | 162.27 |  | 204.37 | 182.37 | 48.1 |  | 0.3 | [5 empty] | 698.15 | 21.45 | 0.29 | 0.62
157 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL028 | 1S-DL-YP-CTC-DCCK-0103-THL028 | MOTI BAZAR:PKG | TG-THL028A-1 | 19506477 | 990 | 320 | 246 | 0.97 | 772 | 247 | 1063 | 257 | 1107 | 268 | 1162 | 86 | 2019-06-29 16:00 | 257.9 | 6.7 | 1465 | Y | 93 | 111 | 97 | 18 | 0.1 |  | 14.1 | 85.7 | 474.03 | 456.33 | 465.33 | 466.33 | 25 | 34.3 | 34.3 | 26 | 201.3 | 195 | 207.3 | 208.3 | 0.3 | 15 | 3 | [5 empty] | 701.03 | 18.57 | 0.33 | 0.78
158 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL029 | 1S-DL-YP-CTC-DCCK-0103-THL029 | GALI PARATHE:PKG | TG-THL029A-1 | 19501182 | 990 | 320 | 233 | 0.98 | 769 | 288 | 1302 | 258 | 1175 | 223 | 1017 | 247 | 2019-06-06 15:30 | 150.9 | 10.3 | 1302 | R | 114 | 98 | 88 | 26 | 0.3 | 0.2 | 62 | 37.4 | 344.34 | 372.13 | 380.29 | 365.13 | 70.25 | 51.46 | 51.46 | 57.16 | 197.46 | 200.25 | 199.25 | 202.25 | 12.09 | 0.3 | [6 empty] | 714.17 | 5.43 | 0.37 | 0.78
159 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL030 | 1S-DL-YP-CTC-DCCK-0103-THL030 | ESPLANADE ROAD:PL | TG-THL030A-1 | 19501054 | 630 | 200 | 246 | 0.95 | 194 | 69 | 294 | 68 | 290 | 57 | 243 | 49 | 2019-06-29 16:30 | 57 | 17 | 312 | Y | 109 | 87 | 104 | 22 |  |  | 24.6 | 75.4 | 254.51 | 497.49 | 293.3 | 346.49 | 464.58 | 222 | 222 | 373 | [12 empty] | 719.49 | 0.11 | 0.65 | 0.31
160 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL035 | 1S-DL-YP-CTC-DCCK-0103-THL035 | CHARHAT:PKG | TG-THL035A-1 | 19501855 | 990 | 320 | 236.277 | 0.96705 | 875.7033 | 281.4418 | 1193.8147 | 289.1169 | 1223.9824 | 305.1446 | 1304.5384 | 99.144 | 2019-06-11 23:30 | [15 empty] | 0 |  |  |  | 62 |  |  |  | 626.5 |  |  |  | 31 |  |  |  | 0 | 719.5 |  | 0.6625 | 0.88455