## Loading Condition > 80%
MIS Report of Distribution Transformer - Jun19
Jun19 1110 CHANDNI CHOWK (Loading Condition > 80% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM003 | 1S-DL-YP-CTC-DCCK-0105-HAM003 | HAMILTON ROAD STN:ID | TG-HAM003A-2 | 19500269 | 990 | 320 | 236 | 0.96 | 809 | 297 | 1288 | 271 | 1177 | 242 | 1028 | 226 | 2019-06-13 15:30 | 201.7 | 36.1 | 1396 | R | 117 | 97 | 86 | 31 | 1.4 | 30.9 | 66.1 | 1.6 | 12 | 84 | 108.26 | 37 | 398.59 | 423.26 | 423.26 | 472.29 | 238.3 | 207.03 | 194 | 207 | 69 | 4 |  | 2 |  |  |  |  | 718.29 | 1.31 | 0.46 | 0.82
2 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM005 | 1S-DL-YP-CTC-DCCK-0105-HAM005 | GURU NANAK MKT:ID | TG-HAM005A-1 | 19506182 | 990 | 320 | 238 | 0.97 | 717 | 172 | 773 | 303 | 1385 | 243 | 1085 | 530 | 2019-06-29 16:00 | 198.4 | 2.6 | 1514 | Y | 87 | 121 | 92 | 34 | 0.2 | 2.7 | 39.4 | 57.7 | 475.42 | 458.12 | 490.21 | 470.12 | 86 | 36.3 | 36.3 | 45.3 | 117.23 | 147.23 | 153.44 | 163.23 |  | 37 | [6 empty] | 679.05 | 40.55 | 0.27 | 0.72
3 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM009 | 1S-DL-YP-CTC-DCCK-0105-HAM009 | CHABBI GANJ:PL | TG-HAM009A-1 | 19503476 | 990 | 320 | 251 | 0.97 | 970 | 333 | 1326 | 335 | 1393 | 302 | 1238 | 134 | 2019-06-13 15:00 | 158.2 | 17.7 | 1455 | Y | 115 | 109 | 76 | 39 | 96 | 3.5 | 0.5 |  | 400.33 | 458.26 | 488.56 | 470.26 | 107.29 | 52.36 | 52.36 | 51.06 | 133.06 | 189.09 | 169.08 | 188.08 | 72.51 | 14.48 | 3.19 | 6.49 | 2.3 | 1.3 |  |  | 716.29 | 3.31 | 0.29 | 0.98
4 | 2019-06-02 | 2019-06-30 23:30 | CHANDNI CHOWK | HAMILTON ROAD | 1110 | HAM017 | 1S-DL-YP-CTC-DCCK-0105-HAM017 | KASHMERE GATE POLICE THANA:PL | TG-HAM017A-1 | 19500234 | 990 | 320 | 243 | 0.97 | 763 | 213 | 871 | 269 | 1110 | 281 | 1145 | 258 | 2019-06-15 16:00 | 160.4 | 8.8 | 1257 | Y | 81 | 107 | 112 | 31 | 0.1 | 5.2 | 67.5 | 27.2 | 457.3 | 445 | 429.3 | 446 | 52.3 | 43 | 43 | 51 | 186 | 189 | 172 | 199 |  | 19 | 32.3 | [5 empty] | 696 | 0 | 0.37 | 0.77
5 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR001 | 1S-DL-YP-CTC-DCCK-0104-LHR001 | MOHALLA NIHARIYAN:K | TG-LHR001A-1 | 19505697 | 990 | 320 | 242 | 0.93 | 996 | 333 | 1383 | 328 | 1371 | 335 | 1408 | 32 | 2019-06-11 01:30 | 389.4 | 149.4 | 1493 | Y | 99 | 106 | 96 | 10 | 0.1 |  | 16.2 | 83.7 | [8 empty] | 536.46 | 438.5 | 637.46 | 535.17 | 172.3 | 272.56 | 79 | 181.29 | 8 | 5.3 | 0.3 | 0.3 | 717.16 | 2.44 | 0.72 | 1.01
6 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR015 | 1S-DL-YP-CTC-DCCK-0104-LHR015 | ZEENAT MAHAL:K | TG-LHR015A-1 | 19501530 | 990 | 320 | 238 | 0.94 | 879 | 304 | 1254 | 280 | 1148 | 295 | 1212 | 93 | 2019-06-03 04:00 | 268.6 | 116.3 | 1254 | R | 98 | 97 | 105 | 8 |  |  | 7.5 | 92.5 |  |  |  |  | 28.3 | 19 | 19 | 11.3 | 679.45 | 694.45 | 666.15 | 695.45 | 10.3 | 5 | 46.3 | 11.3 |  |  |  |  | 718.45 | 1.15 | 0.67 | 0.89
7 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR017 | 1S-DL-YP-CTC-DCCK-0104-LHR017 | LAL QUAN:PL | TG-LHR017A-1 | 19506435 | 990 | 320 | 237 | 0.95 | 1085 | 324 | 1380 | 244 | 1043 | 517 | 2313 | 1140 | 2019-06-05 02:30 | 407 | 120.3 | 2568 | Y | 87 | 113 | 100 | 26 | 0.4 | 2.2 | 73 | 24.5 |  |  |  |  | 24.31 | 0.01 | 0.01 | 3.01 | 669.17 | 637.19 | 679.47 | 688.19 | 1 | 56.3 | 6.3 | 2.58 |  | 0.58 | 1 | 0.3 | 694.48 | 25.12 | 0.55 | 1.1
8 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR018 | 1S-DL-YP-CTC-DCCK-0104-LHR018 | BARSHABULLA:ID | TG-LHR018A-1 | 19501501 | 990 | 320 | 231 | 0.96 | 842 | 245 | 1096 | 286 | 1296 | 311 | 1422 | 285 | 2019-06-12 16:30 | 208.3 | 28.7 | 1499 | B | 84 | 95 | 120 | 36 | 0.1 | 14.8 | 80.7 | 4.4 | 244.3 | 123 | 18.3 | 91.3 | 259.44 | 381.14 | 381.14 | 407.14 | 215 | 206 | 175.52 | 202.3 |  | 9 | 107 | 18 |  |  |  |  | 719.14 | 0.46 | 0.45 | 0.85
9 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR018 | 1S-DL-YP-CTC-DCCK-0104-LHR018 | BARSHABULLA:ID | TG-LHR018A-2 | 19505696 | 990 | 320 | 237 | 0.96 | 1156 | 408 | 1794 | 396 | 1739 | 352 | 1518 | 253 | 2019-06-26 17:30 | 256.3 | 13.1 | 1794 | R | 100 | 108 | 91 | 17 | 0.5 | 2.4 | 74.4 | 22.7 | 458.01 | 443.01 | 455.31 | 452.01 | 36 | 36.3 | 36.3 | 36.3 | 102 | 92.3 | 133.57 | 104.3 | 120.27 | 130.27 | 97.3 | 125.27 | 2.3 | 16.3 | 0.3 | 0.3 | 718.58 | 1.02 | 0.29 | 1.17
10 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR019 | 1S-DL-YP-CTC-DCCK-0104-LHR019 | CHARKHE WALAN:PL | TG-LHR019A-2 | 19504961 | 990 | 320 | 240 | 0.95 | 817 | 269 | 1147 | 265 | 1116 | 283 | 1208 | 81 | 2019-06-11 01:30 | 244.4 | 102.3 | 1325 | R | 99 | 99 | 102 | 3 | 0.1 | 0.5 | 81.9 | 17.5 |  |  |  |  | 3 | 11 | 11 | 7.3 | 709.13 | 695.11 | 664.21 | 704.43 | 3 | 9.02 | 39.22 | 3 |  |  |  |  | 715.13 | 4.47 | 0.74 | 0.83
11 | 2019-06-04 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR023 | 1S-DL-YP-CTC-DCCK-0104-LHR023 | JOGIWARA:ID | TG-LHR023A-1 | 19501520 | 990 | 320 | 242 | 0.96 | 990 | 340 | 1468 | 343 | 1478 | 306 | 1323 | 150 | 2019-06-11 17:00 | 231.8 | 49.3 | 1540 | Y | 108 | 102 | 89 | 19 |  |  | 5.2 | 94.8 | 0.3 | 0.3 | 6 | 0.3 | 76.27 | 185.25 | 185.25 | 182.31 | 420.27 | 299.36 | 264.23 | 325.23 | 141.42 | 145.29 | 66.36 | 137.36 | 6.54 | 15 |  |  | 646 | 2 | 0.54 | 1
12 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR023 | 1S-DL-YP-CTC-DCCK-0104-LHR023 | JOGIWARA:ID | TG-LHR023A-2 | 19505551 | 990 | 320 | 238 | 0.96 | 904 | 324 | 1439 | 293 | 1294 | 287 | 1277 | 154 | 2019-06-01 13:00 | 294.4 | -90.2 | 1607 | Y | 139 | 82 | 79 | 60 | 0.1 |  | 16.3 | 83.6 | 393.36 | 532.54 | 564.18 | 438.06 | 95.55 | 94.19 | 94.19 | 186.07 | 158.29 | 63.13 | 65.21 | 39.47 | 65.49 | 24.53 | 22.15 | 52.19 | 2.3 | 1 |  |  | 716.19 | 3.41 | 0.23 | 0.91
13 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR024 | 1S-DL-YP-CTC-DCCK-0104-LHR024 | PANDIT BROS:K | TG-LHR024A-1 | 19503227 | 990 | 320 | 244 | 0.98 | 814 | 255 | 1022 | 304 | 1223 | 255 | 1028 | 198 | 2019-06-15 17:00 | 179.6 | 2.9 | 1271 | Y | 97 | 111 | 93 | 18 |  | 0.1 | 38.6 | 61.2 | 465.43 | 458.13 | 468.13 | 465.43 | 28 | 24.3 | 24.3 | 23 | 222.38 | 169.42 | 223.38 | 224.38 | 0.3 | 64.26 |  | 3.3 |  |  |  |  | 716.51 | 3.09 | 0.31 | 0.82
14 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR024 | 1S-DL-YP-CTC-DCCK-0104-LHR024 | PANDIT BROS:K | TG-LHR024A-2 | 19503236 | 990 | 320 | 244 | 0.97 | 871 | 260 | 1162 | 339 | 1505 | 272 | 1222 | 317 | 2019-06-01 14:30 | 186.2 | 1.5 | 1525 | Y | 82 | 124 | 93 | 42 |  |  | 29.7 | 70.3 | 479.34 | 443.46 | 475.48 | 465.34 | 58.1 | 50.32 | 50.32 | 44.4 | 174.28 | 155.57 | 190.58 | 172.58 | 2 | 56.57 | 8 | 31 |  | 7 |  |  | 714.12 | 5.48 | 0.27 | 0.88
15 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR025 | 1S-DL-YP-CTC-DCCK-0104-LHR025 | CYCLE STAND:ID | TG-LHR025A-2 | 19501166 | 990 | 320 | 235 | 0.96 | 911 | 302 | 1302 | 332 | 1459 | 277 | 1207 | 221 | 2019-06-29 18:00 | 265 | 35.3 | 1482 | Y | 96 | 106 | 98 | 10 |  | 10.4 | 72.8 | 16.7 | 1 |  |  | 0.3 | 7.17 | 6.17 | 6.17 | 3.3 | 672.08 | 568.27 | 650.05 | 665.25 | 30.3 | 135.41 | 53.5 | 41.3 |  | 0.3 |  |  | 710.55 | 9.05 | 0.71 | 0.92
16 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR026 | 1S-DL-YP-CTC-DCCK-0104-LHR026 | OLD KRISHNA MARKET:ID | TG-LHR026A-1 | 19501852 | 990 | 320 | 246 | 0.97 | 815 | 284 | 1202 | 221 | 922 | 310 | 1316 | 352 | 2019-06-03 17:00 | 197.2 | -4.4 | 1440 | B | 92 | 88 | 120 | 32 |  | 13.2 | 37.6 | 49.2 | 467.44 | 469.14 | 459.44 | 466.44 | 28.31 | 33.16 | 33.16 | 28.35 | 214.02 | 215.33 | 63.49 | 206.28 | 7.46 |  | 158.4 | 16.16 |  |  | 4 |  | 718.03 | 1.57 | 0.33 | 0.82
17 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR027 | 1S-DL-YP-CTC-DCCK-0104-LHR027 | NEW KRISHNA MKT:ID | TG-LHR027A-1 | 19504835 | 990 | 320 | 238 | 0.98 | 939 | 292 | 1316 | 315 | 1429 | 332 | 1483 | 148 | 2019-06-07 15:00 | 153.1 | -4.4 | 1551 | B | 92 | 100 | 108 | 16 |  |  | 40.2 | 59.8 | 461.19 | 460.19 | 456.49 | 459.19 | 32 | 33.3 | 33.3 | 34.3 | 180.05 | 93.25 | 66.42 | 93.55 | 45.02 | 131.12 | 151.25 | 130.42 |  |  | 9.3 |  | 718.26 | 1.34 | 0.32 | 0.95
18 | 2019-06-12 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR034 | 1S-DL-YP-CTC-DCCK-0104-LHR034 | KATRA BARYIAN PLINTH:PL | TG-LHR034A-1 | 19501572 | 630 | 200 | 242 | 0.98 | 599 | 218 | 900 | 210 | 873 | 171 | 718 | 170 | 2019-06-12 16:00 | 126 | 19.3 | 965 | Y | 111 | 97 | 92 | 19 |  | 1.4 | 78.2 | 20.5 |  |  |  |  | 14 | 135.59 | 135.59 | 72.59 | 337.03 | 235.04 | 309.27 | 310.34 | 86.51 | 68.21 | 9 | 58.21 | 4 | 2.3 |  |  | 441.54 | 14.06 | 0.58 | 0.95
19 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR047 | 1S-DL-YP-CTC-DCCK-0104-LHR047 | LAMBI GALI:PL | TG-LHR047A-1 | 19501516 | 990 | 320 | 236 | 0.93 | 884 | 287 | 1183 | 317 | 1314 | 280 | 1148 | 152 | 2019-06-03 04:30 | 290 | 145 | 1405 | Y | 103 | 108 | 88 | 20 |  | 0.3 | 75.7 | 24 |  |  |  |  | 3.13 |  |  | 1.3 | 613.32 | 610.3 | 677.21 | 658.42 | 100.04 | 107.19 | 16.28 | 57.37 | 1 |  |  |  | 717.49 | 2.11 | 0.73 | 0.89
20 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR048 | 1S-DL-YP-CTC-DCCK-0104-LHR048 | P.S HAUZ QUAZI:PL | TG-LHR048A-2 | 19501648 | 990 | 320 | 230 | 0.94 | 892 | 357 | 1590 | 262 | 1168 | 273 | 1211 | 402 | 2019-06-02 04:00 | 284.1 | 117.8 | 1598 | R | 108 | 90 | 101 | 18 |  | 0 | 1.9 | 98.1 |  |  |  |  | 4.3 | 18 | 18 | 5.3 | 557.54 | 699.17 | 664.48 | 670.47 | 143.53 | 0.3 | 46.59 | 41.3 | 11.3 |  |  |  | 717.47 | 2.13 | 0.71 | 0.9
21 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR051 | 1S-DL-YP-CTC-DCCK-0104-LHR051 | NEW HAUZ QUAZI:ID | TG-LHR051A-3 | 19505507 | 630 | 200 | 242 | 0.95 | 693 | 223 | 1044 | 218 | 1040 | 252 | 1236 | 194 | 2019-06-28 15:00 | 265.6 | 48 | 1236 | B | 95 | 99 | 107 | 12 | 0.1 | 0.1 | 4.6 | 95.1 | 1 |  |  |  | 35 | 13.3 | 13.3 | 13.3 | 654.42 | 666.12 | 576.23 | 655.27 | 27 | 38 | 131.04 | 48.45 | 0.3 | 0.3 | 4.45 | 0.3 | 718.12 | 1.48 | 0.58 | 1.1
22 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR053 | 1S-DL-YP-CTC-DCCK-0104-LHR053 | RODH GRAM:K | TG-LHR053A-1 | 19501608 | 990 | 320 | 235 | 0.95 | 744 | 302 | 1266 | 201 | 841 | 242 | 1021 | 369 | 2019-06-03 04:00 | 215.6 | 105.2 | 1335 | R | 121 | 88 | 91 | 33 |  |  | 7.5 | 92.5 |  |  |  |  | 6.29 | 135.17 | 135.17 | 29.47 | 632.22 | 583.53 | 634.23 | 689.23 | 80.19 | [7 empty] | 719.1 | 0.5 | 0.72 | 0.75
23 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR054 | 1S-DL-YP-CTC-DCCK-0104-LHR054 | HAMDARD:ID | TG-LHR054A-1 | 19501504 | 400 | 120 | 247 | 0.94 | 337 | 178 | 782 | 78 | 319 | 80 | 337 | 454 | 2019-06-11 05:00 | 132.2 | 35.1 | 782 | R | 107 | 97 | 95 | 12 | 0.1 |  | 50 | 50 |  |  |  |  | 53.25 | 76.25 | 76.25 | 43.32 | 628.52 | 640.52 | 645.1 | 674.15 | 35.3 | 1 | 1.3 | 0.3 | 0.3 |  |  |  | 718.17 | 1.43 | 0.65 | 0.84
24 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | LAHORI GATE | 1110 | LHR055 | 1S-DL-YP-CTC-DCCK-0104-LHR055 | GALI KASIM JAAN:ID | TG-LHR055A-2 | 19501573 | 990 | 320 | 230 | 0.95 | 934 | 308 | 1387 | 336 | 1522 | 290 | 1285 | 206 | 2019-06-02 04:00 | 255.4 | 120.7 | 1569 | Y | 105 | 107 | 88 | 19 | 0.3 | 66.1 | 33.7 | [5 empty] | 0.3 |  |  | 1 | 562.02 | 532.26 | 691.27 | 620.56 | 153.54 | 182 | 16 | 95 | 0.3 | 2.3 |  |  | 716.56 | 3.04 | 0.71 | 0.94
25 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL004 | 1S-DL-YP-CTC-DCCK-0103-THL004 | KATRA KUSHAL RAI:ID | TG-THL004A-2 | 19500225 | 990 | 320 | 238 | 0.97 | 877 | 287 | 1242 | 310 | 1355 | 280 | 1223 | 123 | 2019-06-08 17:00 | 217.9 | 32.4 | 1401 | Y | 94 | 111 | 95 | 17 |  |  | 30.5 | 69.5 | 102.22 | 14 | 110 | 60.3 | 389.11 | 455.25 | 455.25 | 424.03 | 203.29 | 183.07 | 203.29 | 204.29 | 12 | 54.3 | 11.39 | 18 |  |  |  |  | 707.02 | 12.58 | 0.44 | 0.89
26 | 2019-06-02 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL014 | 1S-DL-YP-CTC-DCCK-0103-THL014 | KUMAR CINEMA:PKG | TG-THL014A-1 | 19500231 | 990 | 320 | 243 | 0.98 | 840 | 285 | 1226 | 265 | 1150 | 290 | 1240 | 84 | 2019-06-25 16:00 | 161.2 | -17.7 | 1275 | B | 97 | 99 | 103 | 6 |  | 0.9 | 66.5 | 32.6 | 430.41 | 417.41 | 407.11 | 420.11 | 46 | 62.3 | 62.3 | 56.3 | 192.06 | 193.23 | 187.44 | 195.36 | 23.47 | 19 | 31.09 | 20.17 |  |  |  |  | 692.34 | 3.26 | 0.34 | 0.85
27 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL019 | 1S-DL-YP-CTC-DCCK-0103-THL019 | KINARI BAZAR:PM | TG-THL019A-1 | 19503057 | 400 | 120 | 236 | 0.97 | 384 | 118 | 520 | 118 | 518 | 148 | 664 | 145 | 2019-06-21 17:00 | 80.3 | 3.3 | 675 | B | 95 | 103 | 101 | 8 |  | 7.1 | 66.4 | 26.5 | 235.1 | 196.1 | 235.1 | 204.4 | 215.04 | 181.3 | 181.3 | 240.04 | 243.26 | 254.3 | 172.04 | 203.34 | 24.3 | 82.3 | 78.22 | 69.52 |  | 3.3 | 4 |  | 718.1 | 1.5 | 0.4 | 0.96
28 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL020 | 1S-DL-YP-CTC-DCCK-0103-THL020 | DIWAN HALL:PM | TG-THL020A-1 | 19501226 | 400 | 120 | 239 | 0.98 | 344 | 121 | 536 | 94 | 417 | 129 | 576 | 143 | 2019-06-29 16:00 | 71.5 | -0.3 | 578 | B | 106 | 85 | 109 | 24 | 0.1 | 0.1 | 31.9 | 67.9 | 463.29 | 477.54 | 461.59 | 471.29 | 38.34 | 31.39 | 31.39 | 32.34 | 145.3 | 200.04 | 122 | 188.04 | 62.04 |  | 91.34 | 17.3 |  |  |  |  | 709.37 | 10.23 | 0.3 | 0.86
29 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL020 | 1S-DL-YP-CTC-DCCK-0103-THL020 | DIWAN HALL:PM | TG-THL020A-3 | 19505844 | 400 | 120 | 241 | 0.98 | 372 | 105 | 468 | 121 | 539 | 146 | 653 | 161 | 2019-06-12 15:00 | 86.6 | -1.1 | 780 | R | 105 | 81 | 113 | 32 | 0.2 | 2.6 | 21.9 | 75.3 | 306.56 | 308.07 | 299.37 | 302.37 | 40.3 | 65.36 | 65.36 | 49.06 | 83.45 | 76.14 | 109.46 | 99.44 | 32.16 | 15 | 17.58 | 13.3 | 1.3 |  | 10 |  | 707.1 | 12.5 | 0.23 | 0.93
30 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL021 | 1S-DL-YP-CTC-DCCK-0103-THL021 | TIKONA PARK:PL | TG-THL021A-2 | 19501176 | 630 | 200 | 239 | 0.98 | 497 | 136 | 595 | 150 | 653 | 211 | 931 | 311 | 2019-06-14 15:30 | 87.9 | -0.5 | 936 | B | 82 | 95 | 123 | 41 |  |  | 32.8 | 67.2 | 486.17 | 476.47 | 468.47 | 476.47 | 36.02 | 38.02 | 38.02 | 29.38 | 187.29 | 194.59 | 75.5 | 203.23 |  |  | 137.16 |  |  |  | 1 |  | 709.48 | 10.12 | 0.29 | 0.79
31 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL027 | 1S-DL-YP-CTC-DCCK-0103-THL027 | KATRA PYARE LAL:PKG | TG-THL027A-1 | 19505469 | 990 | 320 | 240 | 0.97 | 610 | 283 | 1203 | 73 | 310 | 254 | 1073 | 835 | 2019-06-15 17:30 | 103.4 | -10.2 | 1288 | R | 142 | 33 | 125 | 109 |  | 0.1 | 22.3 | 77.6 | 467.08 | 677.57 | 475.08 | 481.08 | 20.3 | 20.18 | 20.18 | 34.3 | 162.27 |  | 204.37 | 182.37 | 48.1 |  | 0.3 | [5 empty] | 698.15 | 21.45 | 0.29 | 0.62

## Loading Condition > 100%
MIS Report of Distribution Transformer - Jun19
Jun19 1110 CHANDNI CHOWK (Loading Condition > 100% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL006 | 1S-DL-YP-CTC-DCCK-0103-THL006 | NEW LAJPAT RAI MKT:ID | TG-THL006A-1 | 19500223 | 990 | 320 | 239 | 0.99 | 866 | 395 | 1692 | 200 | 843 | 271 | 1161 | 744 | 2019-06-03 16:00 | 131.7 | -8.8 | 1701 | R | 124 | 83 | 93 | 41 |  | 0.3 | 53 | 46.6 | 429.29 | 423.45 | 434.13 | 429.43 | 44.58 | 97.41 | 97.41 | 59.14 | 97.56 | 194.03 | 216.37 | 205.52 | 105.56 |  | 2.1 | 20.4 | 37.1 |  |  |  | 715.29 | 4.31 | 0.31 | 0.87
2 | 2019-06-01 | 2019-06-30 23:30 | CHANDNI CHOWK | TOWN HALL | 1110 | THL019 | 1S-DL-YP-CTC-DCCK-0103-THL019 | KINARI BAZAR:PM | TG-THL019A-2 | 19503058 | 400 | 120 | 237 | 0.97 | 371 | 116 | 511 | 149 | 662 | 106 | 463 | 180 | 2019-06-14 15:30 | 89.1 | 1.7 | 719 | Y | 94 | 120 | 86 | 34 | 2 | 20.9 | 73.5 | 3.6 | 460.05 | 380.05 | 464.05 | 458.35 | 23 | 98 | 98 | 24.3 | 162.07 | 53.4 | 233.07 | 142.07 | 73 | 103.27 |  | 93 |  | 83 |  |  | 718.12 | 1.48 | 0.36 | 0.93