## Complete Report
MIS Report of Distribution Transformer - Jun19
Jun19 1120 DARYA GANJ (Complete Report)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY001 | 1S-DL-YP-CTC-DDRG-0102-DRY001 | AMBEDKAR STADIUM:ID | TG-DRY001A-1 | 19503368 | 400 | 120 | 244 | 0.98 | 239 | 88 | 368 | 75 | 314 | 76 | 319 | 51 | 2019-06-01 16:30 | 73.1 | -17.9 | 368 | R | 112 | 95 | 93 | 19 |  |  | 0.8 | 99.2 | 16.3 | 18.48 | 18.18 | 17.48 | 327.56 | 625.58 | 625.58 | 608.28 | 373.2 | 73 | 66 | 91.3 | [8 empty] | 717.46 | 2.14 | 0.59 | 0.6
2 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY002 | 1S-DL-YP-CTC-DDRG-0102-DRY002 | ANGLO SANSKRIT:PKG | TG-DRY002A-1 | 19504433 | 990 | 320 | 246 | 0.96 | 375 | 138 | 585 | 111 | 468 | 126 | 527 | 102 | 2019-06-10 13:00 | 86.8 | -5.2 | 595 | R | 98 | 90 | 111 | 21 |  |  | 3.8 | 96.2 | 474.28 | 495.58 | 435.28 | 471.28 | 239.3 | 224 | 224 | 248.3 | 6 | [11 empty] | 719.58 | 0.02 | 0.48 | 0.38
3 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY003 | 1S-DL-YP-CTC-DDRG-0102-DRY003 | ANSARI RD:PKG | TG-DRY003A-1 | 19501698 | 990 | 320 | 245 | 0.95 | 454 | 141 | 589 | 135 | 558 | 179 | 748 | 176 | 2019-06-04 15:30 | 131 | 28 | 748 | B | 89 | 95 | 116 | 27 |  |  | 7.4 | 92.6 | 481.08 | 459.26 | 274.59 | 458.56 | 197.27 | 224.09 | 224.09 | 189.12 | 41 | 36 | 114.27 | 71.27 | [8 empty] | 719.35 | 0.25 | 0.49 | 0.46
4 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY003 | 1S-DL-YP-CTC-DDRG-0102-DRY003 | ANSARI RD:PKG | TG-DRY003A-2 | 19501696 | 990 | 320 | 246 | 0.96 | 402 | 137 | 582 | 130 | 548 | 135 | 564 | 30 | 2019-06-11 16:00 | 101.6 | 19.9 | 638 | Y | 106 | 106 | 88 | 18 |  | 0.3 | 99.6 | 0.1 | 464.59 | 457.53 | 488.53 | 476.53 | 234.36 | 241.12 | 241.12 | 241.12 | 20 | 20.3 | 2 | 1.3 | [8 empty] | 719.35 | 0.25 | 0.5 | 0.41
5 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY003 | 1S-DL-YP-CTC-DDRG-0102-DRY003 | ANSARI RD:PKG | TG-DRY003A-3 | 19503208 | 990 | 320 | 244 | 0.96 | 711 | 266 | 1138 | 221 | 942 | 225 | 961 | 187 | 2019-06-10 14:00 | 205.3 | 12.5 | 1138 | R | 114 | 93 | 94 | 21 |  |  | 0.4 | 99.6 | 425.59 | 459.59 | 464.59 | 455.29 | 75.14 | 58.09 | 58.09 | 53.44 | 216.52 | 201.27 | 208.22 | 210.22 | 1.3 | [7 empty] | 719.35 | 0.25 | 0.38 | 0.72
6 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY006 | 1S-DL-YP-CTC-DDRG-0102-DRY006 | AZAD BHAWAN I/D:ID | TG-DRY006A-1 | 19506819 | 990 | 320 | 248 | 0.96 | 391 | 138 | 598 | 124 | 536 | 129 | 555 | 55 | 2019-06-04 15:30 | 136 | -17.6 | 706 | B | 103 | 103 | 94 | 9 |  |  | 1.2 | 98.8 | 546.08 | 548.38 | 555.08 | 549.08 | 164.06 | 162.06 | 162.06 | 162.06 | 1 | 0.3 | [10 empty] | 711.14 | 8.46 | 0.26 | 0.4
7 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY007 | 1S-DL-YP-CTC-DDRG-0102-DRY007 | BACHHO KA GHAR:PKG | TG-DRY007A-1 | 19500132 | 990 | 320 | 239 | 0.96 | 457 | 150 | 639 | 143 | 617 | 165 | 704 | 79 | 2019-06-10 16:00 | 132.5 | 7.4 | 722 | B | 98 | 102 | 99 | 4 |  |  | 8.5 | 91.5 | 477.58 | 489.28 | 473.28 | 477.58 | 154.31 | 195.01 | 195.01 | 167.31 | 85.55 | 33.55 | 106.25 | 72.55 | [8 empty] | 718.24 | 1.36 | 0.4 | 0.46
8 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY007 | 1S-DL-YP-CTC-DDRG-0102-DRY007 | BACHHO KA GHAR:PKG | TG-DRY007A-2 | 19504372 | 630 | 200 | 240 | 0.98 | 582 | 219 | 943 | 191 | 822 | 171 | 740 | 177 | 2019-06-10 15:00 | 122.4 | -1.8 | 984 | R | 108 | 104 | 88 | 20 |  |  | 26.8 | 73.2 | 376.29 | 291.29 | 417.59 | 375.59 | 92 | 181 | 181 | 100.3 | 105 | 174.33 | 224.03 | 152.34 | 125.33 | 72.3 | 13 | 90.29 | 20.3 |  |  |  | 719.32 | 0.28 | 0.39 | 0.92
9 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY008 | 1S-DL-YP-CTC-DDRG-0102-DRY008 | BHARAT GENERAL | TG-DRY008A-1 | 19500211 | 990 | 300 | 245 | 0.94 | 545 | 170 | 728 | 171 | 733 | 204 | 877 | 146 | 2019-06-10 15:00 | 175.3 | 17.9 | 877 | B | 95 | 92 | 112 | 20 |  |  | 6.3 | 93.7 | 487.58 | 490.58 | 363.28 | 488.28 | 73.3 | 90 | 90 | 75 | 158.3 | 139 | 170 | 156.3 | [8 empty] | 719.58 | 0.02 | 0.42 | 0.55
10 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY009 | 1S-DL-YP-CTC-DDRG-0102-DRY009 | CNG:PM | TG-DRY009A-1 | 19500329 | 400 | 120 | 241 | 0.99 | 70 | 25 | 105 | 25 | 103 | 20 | 82 | 22 | 2019-06-07 19:30 | 9.9 | -6.3 | 131 | Y | 91 | 96 | 114 | 23 |  | 0.1 | 0.1 | 99.8 | 717.51 | 708.21 | 717.51 | 717.51 |  | 9.3 | 9.3 | [13 empty] | 717.51 | 2.09 | 0.62 | 0.18
11 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY010 | 1S-DL-YP-CTC-DDRG-0102-DRY010 | COMMERCIAL SCHOOL:PKG | TG-DRY010A-1 | 19505274 | 990 | 320 | 241 | 0.98 | 937 | 223 | 929 | 485 | 2087 | 229 | 953 | 1146 | 2019-06-28 16:30 | 224.6 | 11.5 | 2087 | Y | 98 | 101 | 101 | 3 | 0.1 |  | 0.7 | 99.2 | 407.15 | 320.3 | 364.59 | 378.3 | 81.13 | 169.36 | 169.36 | 111.58 | 219.33 | 217.25 | 215.24 | 217.03 |  |  |  | 0.3 |  | 0.3 |  |  | 708.01 | 11.59 | 0.33 | 0.95
12 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY010 | 1S-DL-YP-CTC-DDRG-0102-DRY010 | COMMERCIAL SCHOOL:PKG | TG-DRY010A-2 | 19504271 | 990 | 200 | 240 | 0.96 | 508 | 171 | 726 | 185 | 786 | 152 | 644 | 123 | 2019-06-14 15:00 | 144.9 | 16.6 | 836 | Y | 105 | 99 | 96 | 9 |  |  |  | 100 | 308 | 454.29 | 427.02 | 429.3 | 289.28 | 107.59 | 107.59 | 169.26 | 120.31 | 155.31 | 64.57 | 119.03 | [8 empty] | 717.59 | 2.01 | 0.47 | 0.51
13 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY011 | 1S-DL-YP-CTC-DDRG-0102-DRY011 | DARYA GANJ KOTWALI:PL | TG-DRY011A-1 | 19501677 | 630 | 200 | 244 | 0.97 | 581 | 187 | 780 | 210 | 916 | 184 | 801 | 127 | 2019-06-12 15:00 | 126.5 | 23 | 964 | Y | 98 | 100 | 102 | 4 | 100 |  |  |  | 2 | 12 |  |  | 403.28 | 421.58 | 421.58 | 420.58 | 236.3 | 172.3 | 361 | 218.3 | 78 | 107 | 33.3 | 80.3 |  | 6.3 |  |  | 719.58 | 0.02 | 0.52 | 0.92
14 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY012 | 1S-DL-YP-CTC-DDRG-0102-DRY012 | DARYA GANJ NO 8:PG | TG-DRY012A-1 | 19500131 | 990 | 320 | 245 | 0.96 | 473 | 198 | 815 | 131 | 542 | 144 | 591 | 252 | 2019-06-13 14:30 | 120.7 | 25 | 860 | R | 123 | 85 | 92 | 38 |  |  | 0.8 | 99.2 | 104.2 | 375.28 | 274.58 | 237.19 | 417.37 | 338.02 | 338.02 | 388.03 | 195 | 3.27 | 36.46 | 91.35 | [8 empty] | 716.57 | 3.03 | 0.54 | 0.48
15 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY013 | 1S-DL-YP-CTC-DDRG-0102-DRY013 | DARYA GANJ:ID | TG-DRY013A-1 | 19500215 | 990 | 300 | 245 | 0.96 | 521 | 171 | 737 | 171 | 734 | 179 | 763 | 27 | 2019-06-29 15:00 | 141.5 | 33.8 | 829 | R | 106 | 96 | 98 | 10 |  |  | 26.8 | 73.2 | 119 | 207.3 | 132.3 | 149.3 | 448.58 | 384.58 | 384.58 | 437.58 | 152 | 127.3 | 93 | 132.3 | [8 empty] | 719.58 | 0.02 | 0.53 | 0.53
16 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY013 | 1S-DL-YP-CTC-DDRG-0102-DRY013 | DARYA GANJ:ID | TG-DRY013A-2 | 19506482 | 990 | 300 | 247 | 0.97 | 498 | 158 | 1010 | 202 | 1313 | 137 | 872 | 391 | 2019-06-11 15:00 | 206.1 | 9.9 | 1313 | Y | 101 | 112 | 87 | 25 | 0.1 | 0 | 4 | 95.9 | 422.58 | 433.28 | 472.28 | 458.58 | 225.37 | 110.39 | 110.39 | 147.39 | 69.38 | 174.06 | 15.1 | 111.36 | [8 empty] | 718.13 | 1.47 | 0.44 | 0.5
17 | 2019-06-02 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY013 | 1S-DL-YP-CTC-DDRG-0102-DRY013 | DARYA GANJ:ID | TG-DRY013A-3 | 19500212 | 990 | 300 | 245 | 0.95 | 655 | 188 | 789 | 211 | 885 | 257 | 1094 | 270 | 2019-06-12 15:00 | 178 | 31.7 | 1153 | B | 81 | 99 | 120 | 39 |  |  | 13.3 | 86.7 | 450.58 | 177.29 | 103.29 | 203.29 | 85.18 | 333.37 | 333.37 | 297.37 | 156.43 | 181.53 | 205.25 | 191.53 |  |  | 4 | [5 empty] | 692.59 | 3.01 | 0.45 | 0.66
18 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY013 | 1S-DL-YP-CTC-DDRG-0102-DRY013 | DARYA GANJ:ID | TG-DRY013A-4 | 19505293 | 990 | 200 | 246 | 0.96 | 533 | 171 | 1107 | 201 | 1322 | 161 | 1030 | 262 | 2019-06-11 15:00 | 237.6 | 24 | 1322 | Y | 92 | 118 | 90 | 28 | 0.1 | 0.1 | 4.7 | 95.2 | 451.27 | 363.59 | 464.57 | 455.57 | 135.09 | 195.07 | 195.07 | 142.39 | 108.05 | 135.35 | 46.07 | 96.05 | [8 empty] | 694.41 | 25.19 | 0.4 | 0.54
19 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY014 | 1S-DL-YP-CTC-DDRG-0102-DRY014 | DELHI GATE [K]:K | TG-DRY014A-1 | 19506756 | 990 | 320 | 248 | 0.97 | 630 | 227 | 968 | 174 | 735 | 230 | 989 | 244 | 2019-06-22 15:30 | 270.1 | 14.4 | 1029 | B | 100 | 101 | 99 | 2 | 0.1 |  | 1.3 | 98.6 | 254.29 | 262.59 | 345 | 279.59 | 341.02 | 326.02 | 326.02 | 294.32 | 123.57 | 130.27 | 173.2 | 144.57 | [8 empty] | 719.28 | 0.32 | 0.41 | 0.64
20 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY014 | 1S-DL-YP-CTC-DDRG-0102-DRY014 | DELHI GATE [K]:K | TG-DRY014A-2 | 19501651 | 990 | 320 | 244 | 0.96 | 417 | 144 | 572 | 149 | 591 | 124 | 489 | 94 | 2019-06-03 15:30 | 106 | 14.7 | 643 | Y | 96 | 110 | 94 | 16 |  |  | 4.4 | 95.6 | 484.59 | 455.59 | 497.29 | 482.29 | 231.38 | 233.38 | 233.38 | 234.08 | 3 | 30 | 0.3 | 3 | [8 empty] | 719.37 | 0.23 | 0.45 | 0.42
21 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY015 | 1S-DL-YP-CTC-DDRG-0102-DRY015 | EMCA HOUSE:PG | TG-DRY015A-1 | 19500142 | 990 | 320 | 245 | 0.96 | 760 | 238 | 1005 | 252 | 1100 | 270 | 1133 | 115 | 2019-06-10 15:00 | 175.2 | 37.5 | 1212 | B | 93 | 89 | 118 | 29 | 99.5 |  | 0.1 | 0.4 | 85.59 | 153.59 | 0.3 | 26.59 | 409.47 | 342.47 | 342.47 | 462.47 | 221.14 | 220.14 | 348.49 | 227.14 |  |  | 10.25 | [5 empty] | 717 | 3 | 0.5 | 0.77
22 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY017 | 1S-DL-YP-CTC-DDRG-0102-DRY017 | GANDHI NIDHI | TG-DRY017A-1 | 19500351 | 630 | 200 | 238 | 0.97 | 456 | 169 | 737 | 108 | 467 | 180 | 787 | 298 | 2019-06-06 14:00 | 86.5 | 26.2 | 842 | B | 114 | 67 | 119 | 52 |  | 0.1 | 14.5 | 85.4 |  | 108.58 |  | 0.3 | 184.35 | 532.09 | 532.09 | 266.24 | 530.46 | 75.44 | 539.57 | 449.57 | 1.3 |  | 10.3 | [5 empty] | 716.51 | 3.09 | 0.61 | 0.72
23 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY018 | 1S-DL-YP-CTC-DDRG-0102-DRY018 | GULAB BHAWAN:ID | TG-DRY018A-1 | 19501653 | 990 | 320 | 238 | 0.95 | 147 | 58 | 246 | 43 | 184 | 46 | 193 | 59 | 2019-06-10 13:30 | 39 | -20.6 | 251 | R | 116 | 93 | 91 | 25 | 0.1 |  | 0.2 | 99.7 | 719.25 | 719.25 | 719.25 | 719.25 | [16 empty] | 719.25 | 0.35 | 0.29 | 0.15
24 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY018 | 1S-DL-YP-CTC-DDRG-0102-DRY018 | GULAB BHAWAN:ID | TG-DRY018A-2 | 19504086 | 990 | 320 | 237 | 0.97 | 325 | 112 | 482 | 106 | 454 | 107 | 458 | 26 | 2019-06-28 15:30 | 77.3 | 0.7 | 497 | R | 103 | 89 | 108 | 19 |  | 4.2 | 59.6 | 36.2 | 187.06 | 191.06 | 183.36 | 188.06 | 84.54 | 80.54 | 80.54 | 83.54 | [12 empty] | 719.22 | 0.38 | 0.46 | 0.33
25 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY019 | 1S-DL-YP-CTC-DDRG-0102-DRY019 | HANS BHAWAN:ID | TG-DRY019A-1 | 19506278 | 990 | 300 | 247 | 0.98 | 368 | 110 | 459 | 148 | 618 | 110 | 461 | 158 | 2019-06-10 11:30 | 81.9 | 2.7 | 618 | Y | 97 | 103 | 100 | 6 |  | 0.1 | 0.4 | 99.6 | 538.03 | 555.03 | 540.03 | 541.33 | 172.36 | 152.36 | 152.36 | 169.06 |  | 3 | 0.3 | [9 empty] | 710.39 | 9.21 | 0.3 | 0.37
26 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY019 | 1S-DL-YP-CTC-DDRG-0102-DRY019 | HANS BHAWAN:ID | TG-DRY019A-2 | 19506277 | 630 | 200 | 240 | 0.96 | 472 | 153 | 940 | 156 | 979 | 163 | 1047 | 93 | 2019-06-11 15:00 | 175.6 | 2.2 | 1047 | B | 94 | 98 | 107 | 13 | 0.2 |  | 1.7 | 98.1 | 440.59 | 450.59 | 442.29 | 445.29 | 66.09 | 57.39 | 57.39 | 58.39 | 203.3 | 202 | 215.09 | 206.3 | [8 empty] | 710.38 | 9.22 | 0.3 | 0.75
27 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY020 | 1S-DL-YP-CTC-DDRG-0102-DRY020 | HINDI PARK:ID | TG-DRY020A-1 | 19506622 | 990 | 320 | 248 | 0.97 | 530 | 162 | 678 | 236 | 973 | 132 | 533 | 388 | 2019-06-24 15:00 | 200.6 | 3.5 | 973 | Y | 95 | 106 | 99 | 11 | 0.1 | 0.1 | 0.9 | 98.9 | 359 | 290.3 | 332 | 321.3 | 228.15 | 274.09 | 274.09 | 264.15 | 121.5 | 144.26 | 98.5 | 123.2 | [8 empty] | 709.05 | 10.55 | 0.46 | 0.54
28 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY020 | 1S-DL-YP-CTC-DDRG-0102-DRY020 | HINDI PARK:ID | TG-DRY020A-2 | 19501697 | 990 | 320 | 246 | 0.96 | 644 | 203 | 828 | 218 | 886 | 223 | 914 | 76 | 2019-06-11 15:00 | 171.5 | 28 | 937 | B | 102 | 94 | 104 | 10 |  |  | 4.2 | 95.8 | 191 | 390.29 | 159.3 | 256.3 | 308.08 | 107.58 | 107.58 | 242.38 | 218.26 | 219.07 | 212.56 | 218.26 | [8 empty] | 717.34 | 2.26 | 0.47 | 0.65
29 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY020 | 1S-DL-YP-CTC-DDRG-0102-DRY020 | HINDI PARK:ID | TG-DRY020A-3 | 19501676 | 990 | 320 | 252 | 0.95 | 716 | 251 | 995 | 237 | 942 | 227 | 903 | 79 | 2019-06-06 15:30 | 235.5 | 50.8 | 1065 | B | 111 | 86 | 104 | 25 |  |  | 0.2 | 99.8 | 2.3 | 280 | 1.3 | 12 | 443.29 | 212.58 | 212.58 | 460.28 | 270.44 | 223.45 | 258.14 | 244.15 |  |  | 0.3 | [5 empty] | 716.43 | 3.17 | 0.51 | 0.72
30 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY020 | 1S-DL-YP-CTC-DDRG-0102-DRY020 | HINDI PARK:ID | TG-DRY020A-4 | 19505513 | 990 | 320 | 248 | 0.96 | 475 | 142 | 591 | 145 | 586 | 188 | 768 | 180 | 2019-06-24 15:30 | 199 | 9 | 864 | B | 110 | 97 | 93 | 17 | 0.1 |  | 0.8 | 99.2 | 492.27 | 501.56 | 493.28 | 499.26 | 206.07 | 176.08 | 176.08 | 198.08 | 10.3 | 31 | 18 | 11.3 | [8 empty] | 709.04 | 10.56 | 0.33 | 0.48
31 | 2019-06-02 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY021 | 1S-DL-YP-CTC-DDRG-0102-DRY021 | IP GRID:K | TG-DRY021A-1 | 19501684 | 990 | 320 | 246 | 0.95 | 483 | 182 | 763 | 156 | 649 | 145 | 610 | 137 | 2019-06-11 15:00 | 172.2 | 12.5 | 775 | R | 110 | 96 | 93 | 17 |  |  | 5 | 95 | 354.3 | 433.22 | 435.22 | 417.22 | 210.09 | 207.17 | 207.17 | 190.17 | 130.41 | 54.41 | 48.11 | 87.41 | [8 empty] | 695.2 | 0.4 | 0.45 | 0.49
32 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY023 | 1S-DL-YP-CTC-DDRG-0102-DRY023 | MADINA LIBRARY:ID | TG-DRY023A-1 | 19500354 | 400 | 120 | 244 | 0.99 | 100 | 39 | 168 | 29 | 127 | 33 | 140 | 36 | 2019-06-27 14:30 | 17.7 | -0.8 | 168 | R | 108 | 113 | 79 | 34 |  | 0.1 | 32.2 | 67.8 | 705.01 | 703.01 | 710.31 | 706.01 | 14.3 | 16.3 | 16.3 | 13.3 | [12 empty] | 719.31 | 0.29 | 0.3 | 0.25
33 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY023 | 1S-DL-YP-CTC-DDRG-0102-DRY023 | MADINA LIBRARY:ID | TG-DRY023A-2 | 19504276 | 630 | 200 | 244 | 0.92 | 251 | 90 | 358 | 77 | 306 | 83 | 332 | 45 | 2019-06-29 19:30 | 116.4 | -0.5 | 368 | R | 108 | 98 | 94 | 14 |  |  |  | 100 | 492.53 | 495.53 | 513.53 | 496.53 | 198.3 | 200 | 200 | 199 | 4.3 | [11 empty] | 719.21 | 0.39 | 0.26 | 0.4
34 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY024 | 1S-DL-YP-CTC-DDRG-0102-DRY024 | MAHAVIR VATIKA:K | TG-DRY024A-1 | 19501678 | 990 | 320 | 246 | 0.95 | 223 | 64 | 264 | 66 | 270 | 93 | 381 | 114 | 2019-06-30 | 78.8 | 14 | 390 | B | 32 | 123 | 145 | 113 |  |  | 0.2 | 99.8 | 686.04 | 673.08 | 508.11 | 698.47 | 31.3 | 44.26 | 44.26 | 18.47 | [12 empty] | 717.34 | 2.26 | 0.54 | 0.23
35 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY024 | 1S-DL-YP-CTC-DDRG-0102-DRY024 | MAHAVIR VATIKA:K | TG-DRY024A-2 | 19505537 | 990 | 320 | 247 | 0.97 | 347 | 132 | 559 | 89 | 361 | 127 | 522 | 183 | 2019-06-24 15:00 | 123.2 | 12.5 | 593 | Y | 86 | 120 | 94 | 34 | 0.1 | 0.1 | 3.8 | 96.1 | 643.27 | 478.54 | 524.33 | 519.33 | 73.37 | 238.4 | 238.4 | 198.01 | 0.3 |  | 0.3 | [9 empty] | 717.34 | 2.26 | 0.43 | 0.35
36 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY025 | 1S-DL-YP-CTC-DDRG-0102-DRY025 | MILAP:ID | TG-DRY025A-1 | 19501657 | 990 | 320 | 246 | 0.96 | 409 | 138 | 553 | 145 | 576 | 126 | 504 | 64 | 2019-06-28 17:30 | 124.4 | 0.7 | 623 | Y | 102 | 102 | 97 | 5 |  |  | 6.4 | 93.6 | 462.3 | 459 | 470.3 | 468.3 | 246.44 | 250.14 | 250.14 | 243.44 | 9.3 | 9.3 | 3.3 | 6.3 | [8 empty] | 718.44 | 1.16 | 0.43 | 0.41
37 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY026 | 1S-DL-YP-CTC-DDRG-0102-DRY026 | MWK CLY | TG-DRY026A-1 | 19505273 | 400 | 120 | 242 | 0.95 | 44 | 17 | 68 | 26 | 104 | 0 | 0 | 91 | 2019-06-13 19:00 | 36.8 | -0.5 | 104 | Y | 139 | 161 | 1 | 160 | 35.2 | 30.9 | 18.7 | 15.3 | 711.05 | 711.05 | 711.05 | 711.05 | [16 empty] | 711.05 | 8.55 | 0.26 | 0.11
38 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY027 | 1S-DL-YP-CTC-DDRG-0102-DRY027 | NEHRU HOUSE:ID | TG-DRY027A-1 | 19506305 | 990 | 300 | 243 | 0.96 | 680 | 209 | 865 | 233 | 960 | 238 | 983 | 108 | 2019-06-10 11:00 | 297 | -43.5 | 1046 | B | 96 | 97 | 106 | 10 | 0.1 |  | 0.4 | 99.5 | 379.57 | 385.27 | 359.59 | 372.59 | 138.07 | 130.07 | 130.07 | 139.05 | 188.47 | 191.17 | 209.17 | 194.47 | [8 empty] | 706.51 | 13.09 | 0.39 | 0.69
39 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY028 | 1S-DL-YP-CTC-DDRG-0102-DRY028 | PRATAP PRESS:PKG | TG-DRY028A-1 | 19501656 | 630 | 200 | 248 | 0.99 | 194 | 67 | 275 | 67 | 277 | 61 | 251 | 25 | 2019-06-10 10:30 | 17 | -20.2 | 285 | R | 111 | 97 | 92 | 19 |  |  |  | 100 | 520 | 564.19 | 602.09 | 545.39 | 199.2 | 155.01 | 155.01 | 173.41 | [12 empty] | 719.2 | 0.4 | 0.33 | 0.31
40 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY028 | 1S-DL-YP-CTC-DDRG-0102-DRY028 | PRATAP PRESS:ID | TG-DRY028A-2 | 19501652 | 400 | 120 | 247 | 0.96 | 173 | 55 | 228 | 73 | 304 | 45 | 187 | 102 | 2019-06-06 14:30 | 60.7 | 5.5 | 304 | Y | 111 | 104 | 85 | 26 |  |  | 2.6 | 97.4 | 335 | 361 | 464 | 395 | 326.19 | 276.09 | 276.09 | 303.49 | 58 | 82.1 |  | 20.3 | [8 empty] | 719.19 | 0.41 | 0.49 | 0.43
41 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY031 | 1S-DL-YP-CTC-DDRG-0102-DRY031 | ROSE GARDEN:PM | TG-DRY031A-1 | 19500377 | 100 | 40 | 245 | 0.89 | 58 | 15 | 61 | 6 | 26 | 37 | 158 | 119 | 2019-06-09 19:30 | 37.5 | -0.9 | 182 | R | 144 | 52 | 104 | 92 | 38.9 | 4.6 | 0.2 | 56.3 | 472.35 | 719.14 | 457.14 | 408.14 | 54.39 |  |  | 192 | 53.3 |  | 32 | 119 | 114 |  | 86 |  | 24.3 |  | 4.3 |  | 719.14 | 0.46 | 0.37 | 0.58
42 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY032 | 1S-DL-YP-CTC-DDRG-0102-DRY032 | RPH STORE KANCHAN PURI:PACKAGE S/STN | TG-DRY032A-1 | 19501683 | 990 | 320 | 236 | 0.96 | 262 | 86 | 366 | 89 | 384 | 86 | 369 | 17 | 2019-06-10 12:30 | 42.7 | 0.7 | 402 | Y | 94 | 126 | 80 | 46 |  |  | 0.1 | 99.9 | 628.38 | 603.08 | 654.05 | 630.08 | 90.57 | 116.27 | 116.27 | 89.27 | [12 empty] | 719.35 | 0.25 | 0.33 | 0.26
43 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY033 | 1S-DL-YP-CTC-DDRG-0102-DRY033 | SARASWATI SCHOOL:PG | TG-DRY033A-1 | 19506523 | 990 | 320 | 247 | 0.93 | 100 | 36 | 153 | 36 | 150 | 28 | 118 | 34 | 2019-06-29 13:00 | 34.2 | 8 | 194 | R | 104 | 100 | 96 | 8 |  | 0.3 | 0.5 | 99.2 | 694.03 | 694.03 | 694.03 | 694.03 | [16 empty] | 694.03 | 25.57 | 0.62 | 0.1
44 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY035 | 1S-DL-YP-CTC-DDRG-0102-DRY035 | VIKRAM NAGAR:PACKAGE S/STN | TG-DRY035A-1 | 19506404 | 990 | 320 | 238 | 0.97 | 510 | 125 | 521 | 208 | 881 | 177 | 744 | 315 | 2019-06-12 | 117.1 | 22.4 | 922 | Y | 82 | 113 | 104 | 31 |  | 0.2 | 28.1 | 71.7 | 254.08 | 124.09 | 82.39 | 134.39 | 448.29 | 387.28 | 387.28 | 471.58 | 6.3 | 197.3 | 110.3 | 102.3 | [8 empty] | 709.07 | 10.53 | 0.56 | 0.52
45 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY035 | 1S-DL-YP-CTC-DDRG-0102-DRY035 | VIKRAM NAGAR:PACKAGE S/STN | TG-DRY035A-2 | 19505152 | 990 | 320 | 238 | 0.97 | 806 | 199 | 834 | 219 | 929 | 388 | 1670 | 793 | 2019-06-12 00:30 | 183.7 | 49.6 | 1732 | B | 86 | 92 | 122 | 36 | 0.6 | 1.8 | 44.2 | 53.3 | 1.24 | 3.3 |  | 0.3 | 414.45 | 350.41 | 350.41 | 294.41 | 292.3 | 354.28 | 414.58 | 412.28 |  |  | 92.3 | 1 |  |  | 10.3 |  | 708.39 | 11.21 | 0.56 | 0.81
46 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY072 | 1S-DL-YP-CTC-DDRG-0102-DRY072 | ANNA NAGAR DRG | TG-DRY072A-1 | 19505442 | 990 | 320 | 234 | 0.97 | 682 | 234 | 1011 | 207 | 885 | 241 | 1037 | 141 | 2019-06-11 | 263.4 | 47.7 | 1037 | B | 115 | 85 | 100 | 30 |  | 0.1 | 5 | 94.9 |  | 1 |  |  | 207.53 | 571.25 | 571.25 | 358.53 | 508.21 | 143.49 | 382.35 | 357.21 | [8 empty] | 716.14 | 3.46 | 0.58 | 0.69
47 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY075 | 1S-DL-YP-CTC-DDRG-0102-DRY075 | DELHI SACHIVALYA | TG-DRY075A-1 | 19504587 | 100 | 40 | 234 | 0.85 | 41 | 2 | 10 | 28 | 121 | 11 | 44 | 99 | 2019-06-15 19:00 | 33.1 | -0.1 | 121 | Y | 29 | 190 | 81 | 161 | 2.4 | 41.5 | 1.9 | 54.2 | 718 | 401.33 | 582 | 403 |  | 1.27 | 1.27 | 314 |  | 311.3 |  | 1 |  | 3.3 | [6 empty] | 718 | 2 | 0.38 | 0.41
48 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY076 | 1S-DL-YP-CTC-DDRG-0102-DRY076 | LOK NAYAK SETU | TG-DRY076A-1 | 19504557 | 400 | 120 | 247 | 0.95 | 111 | 33 | 133 | 39 | 157 | 39 | 160 | 25 | 2019-06-10 13:00 | 36.4 | -0.3 | 211 | R | 101 | 113 | 86 | 27 |  |  | 0.9 | 99.1 | 545.48 | 581.15 | 662.15 | 583.3 | 172.12 | 136.45 | 136.45 | 134.3 | [12 empty] | 718 | 2 | 0.43 | 0.28
49 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY077 | 1S-DL-YP-CTC-DDRG-0102-DRY077 | S/STN NO-1 VELODROME ROAD | TG-DRY077A-1 | 19506628 | 100 | 40 | 249 | 0.71 | 16 | 0 | 0 | 7 | 30 | 8 | 32 | 31 | 2019-06-01 19:00 | 7.4 | -6 | 32 | Y | 5 | 121 | 174 | 169 |  |  | 2.5 | 97.5 | 704.33 | 695.33 | 671.03 | 704.33 |  | 9 | 9 | [13 empty] | 704.33 | 15.27 | 0.19 | 0.16
50 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY078 | 1S-DL-YP-CTC-DDRG-0102-DRY078 | S/STN NO-2 VELODROME ROAD | TG-DRY078A-1 | 19506859 | 100 | 40 | 247 | 0.73 | 56 | 28 | 113 | 27 | 109 | 0 | 0 | 111 | 2019-06-24 19:00 | 50.4 | 0 | 116 | Y | 142 | 158 | 0 | 158 |  | 0.2 | 43.5 | 56.2 | 396.14 | 390.14 | 706.14 | 390.14 | 0.3 |  |  | 240.3 | 308 | 313.3 |  | 75.3 | 1.3 | 2.3 | [6 empty] | 706.14 | 13.46 | 0.31 | 0.56
51 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY079 | 1S-DL-YP-CTC-DDRG-0102-DRY079 | S/STN NO-3 VELODROME ROAD | TG-DRY079A-1 | 19504561 | 100 | 40 | 230 | 0.86 | 77 | 14 | 53 | 38 | 153 | 25 | 100 | 86 | 2019-06-04 03:30 | 56.2 | -0.1 | 153 | Y | 53 | 153 | 93 | 100 | 47.1 | 11.6 | 24.1 | 17.2 | 401.56 | 157.39 | 401.56 | 401.26 | 256.3 | 239.55 | 239.55 | 1 | 56.3 | 83.22 | 298 | 312.3 |  | 233 | 2.3 |  |  | 1 |  |  | 716.56 | 3.04 | 0.4 | 0.77
52 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY082 | 1S-DL-YP-CTC-DDRG-0102-DRY082 | CNG SHANTI VAN | TG-DRY082A-1 | 19504590 | 100 | 40 | 233 | 0.97 | 50 | 11 | 43 | 25 | 101 | 15 | 60 | 51 | 2019-06-14 | 20.1 | -4.3 | 107 | Y | 78 | 112 | 110 | 34 |  |  | 37 | 63 | 387.5 | 292 | 112.24 | 240.3 | 315 | 119.53 | 119.53 | 410.5 | 16.3 | 307.27 | 41.3 | 68 | [8 empty] | 719.2 | 0.4 | 0.51 | 0.5
53 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY083 | 1S-DL-YP-CTC-DDRG-0102-DRY083 | ROSE BIRD-II | TG-DRY083A-1 | 19504690 | 100 | 40 | 245 | 0.71 | 83 | 28 | 115 | 29 | 118 | 25 | 102 | 15 | 2019-06-06 19:00 | 74.6 | -0.1 | 124 | Y | 100 | 116 | 84 | 32 |  |  | 2.1 | 97.9 | 401.11 | 401.11 | 402.11 | 401.11 | 1 | 1 | 1 | 1 | 311.56 | 304.56 | 286.56 | 314.26 | 4 | 11 |  | 1.3 |  |  |  |  | 718.07 | 1.53 | 0.28 | 0.83
54 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY089 | 1S-DL-YP-CTC-DDRG-0102-DRY089 | GHATA MASJID:PG | TG-DRY089A-1 | 19500136 | 990 | 320 | 243 | 0.96 | 948 | 331 | 1418 | 308 | 1316 | 308 | 1320 | 100 | 2019-06-03 15:30 | 217.9 | 42.7 | 1418 | R | 103 | 100 | 96 | 7 |  |  | 5.2 | 94.8 | 1.3 |  | 6 |  | 302.51 | 381.22 | 381.22 | 370.28 | 303.1 | 244.34 | 234.22 | 252.04 | 109.32 | 92.07 | 85.18 | 95.31 | 1 |  |  |  | 718.03 | 1.57 | 0.51 | 0.96
55 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY092 | 1S-DL-YP-CTC-DDRG-0102-DRY092 | PWD OFFICE,UNDER F/O NEAR IG STADIUM:LTC | TG-DRY092A-1 | 19505147 | 400 | 120 | 248 | 0.98 | 71 | 30 | 124 | 20 | 82 | 21 | 85 | 41 | 2019-06-25 16:00 | 15.7 | -0.6 | 128 | Y | 100 | 92 | 108 | 16 |  |  | 0.5 | 99.5 | 707.33 | 707.03 | 702.35 | 708.03 | 0.3 | 1 | 1 | [13 empty] | 708.03 | 11.57 | 0.32 | 0.18
56 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU001 | 1S-DL-YP-CTC-DDRG-0106-HAU001 | 84 GHANTA:K | TG-HAU001A-1 | 19500381 | 990 | 320 | 236 | 0.98 | 1063 | 322 | 1486 | 452 | 1919 | 289 | 1202 | 625 | 2019-06-11 01:00 | 92 | -57.4 | 1919 | Y | 76 | 123 | 101 | 47 | 54.6 |  | 1.9 | 43.6 | 286.03 |  |  |  | 40.34 | 2.3 | 2.3 | 54.35 | 314.09 | 427.33 | 598.3 | 566.41 | 73.16 | 198.34 | 96.01 | 88.19 | 0.59 | 86.24 | 4.3 | 5.26 | 715.01 | 4.59 | 0.57 | 1.07
57 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU001 | 1S-DL-YP-CTC-DDRG-0106-HAU001 | 84 GHANTA:K | TG-HAU001A-2 | 19501686 | 990 | 320 | 232 | 0.96 | 1036 | 297 | 1348 | 342 | 1556 | 398 | 1833 | 421 | 2019-06-15 00:30 | 242.9 | 102.3 | 1908 | B | 85 | 102 | 113 | 28 |  | 0.2 | 34.4 | 65.4 |  |  |  |  | 10.31 | 1 | 1 | 1 | 652.14 | 457.44 | 348.21 | 484.34 | 52.46 | 219.14 | 249.35 | 214.41 |  | 37.33 | 117.35 | 15.16 | 715.31 | 4.29 | 0.7 | 1.05
58 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU001 | 1S-DL-YP-CTC-DDRG-0106-HAU001 | 84 GHANTA:K | TG-HAU001A-3 | 19503790 | 990 | 320 | 238 | 0.96 | 981 | 394 | 1632 | 250 | 1018 | 337 | 1393 | 536 | 2019-06-12 02:30 | 248 | 115.6 | 1750 | R | 113 | 80 | 107 | 33 |  | 0.7 | 60.3 | 39 |  |  |  |  | 1.3 | 30.18 | 30.18 | 1 | 366.13 | 681.34 | 447.51 | 525.01 | 221.18 | 3 | 264.43 | 188.51 | 125.51 |  | 2.18 |  | 714.52 | 5.08 | 0.71 | 0.99
59 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU002 | 1S-DL-YP-CTC-DDRG-0106-HAU002 | BASTI NARNAUL:PL | TG-HAU002A-1 | 19500207 | 990 | 320 | 238 | 0.96 | 573 | 191 | 780 | 211 | 866 | 171 | 700 | 144 | 2019-06-29 17:00 | 159.7 | 38.3 | 981 | Y | 92 | 120 | 88 | 32 |  |  | 1.5 | 98.5 | 26.3 | 2 | 42.3 | 5.3 | 554.21 | 312.53 | 312.53 | 503.29 | 135.36 | 401.34 | 94.06 | 207.28 | [8 empty] | 716.27 | 3.33 | 0.61 | 0.58
60 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU003 | 1S-DL-YP-CTC-DDRG-0106-HAU003 | DDA HOUSING COMP.TURKMAN GATE:ID | TG-HAU003A-1 | 19501668 | 990 | 320 | 233 | 0.95 | 722 | 260 | 1096 | 238 | 1008 | 224 | 943 | 133 | 2019-06-12 01:30 | 214.2 | 96.4 | 1192 | R | 107 | 97 | 96 | 11 |  |  | 0.2 | 99.8 |  |  |  |  | 12 | 41 | 41 | 24.3 | 700.41 | 673.41 | 669.11 | 690.11 | 2 | [7 empty] | 714.41 | 5.19 | 0.75 | 0.73
61 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU003 | 1S-DL-YP-CTC-DDRG-0106-HAU003 | DDA HOUSING COMP.TURKMAN GATE:ID | TG-HAU003A-2 | 19501667 | 990 | 320 | 231 | 0.95 | 793 | 209 | 916 | 257 | 1138 | 327 | 1455 | 470 | 2019-06-02 04:30 | 214.9 | 96.4 | 1540 | B | 75 | 96 | 129 | 54 |  | 1.1 | 52.5 | 46.4 |  |  |  |  | 253.41 | 59 | 59 | 29.25 | 437.19 | 630.3 | 435.49 | 660.35 |  | 1.3 | 242.41 | 1 |  |  | 10 |  | 714.37 | 5.23 | 0.72 | 0.8
62 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU003 | 1S-DL-YP-CTC-DDRG-0106-HAU003 | DDA HOUSING COMP.TURKMAN GATE:ID | TG-HAU003A-3 | 19505526 | 990 | 320 | 234 | 0.96 | 722 | 254 | 1111 | 288 | 1274 | 180 | 782 | 434 | 2019-06-05 15:00 | 352 | 53.4 | 1274 | Y | 120 | 92 | 89 | 31 | 0.1 | 0.1 | 13.5 | 86.4 |  | 2.3 | 2.3 |  | 116.42 | 338.03 | 338.03 | 255.41 | 595.55 | 373.34 | 305.42 | 458.56 | 2 | 0.3 | [6 empty] | 714.37 | 5.23 | 0.6 | 0.73
63 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU003 | 1S-DL-YP-CTC-DDRG-0106-HAU003 | DDA HOUSING COMP.TURKMAN GATE:ID | TG-HAU003A-4 | 19505108 | 630 | 200 | 229 | 0.96 | 368 | 79 | 354 | 150 | 684 | 139 | 640 | 310 | 2019-06-02 08:30 | 184.4 | 32.6 | 709 | Y | 76 | 120 | 104 | 44 | 0.1 | 0.1 | 8.5 | 91.4 | 90.08 | 1 | 20.55 | 10.3 | 598.58 | 355 | 355 | 586.26 | 2 | 335.06 | 190.1 | 94.1 | [8 empty] | 691.06 | 28.54 | 0.57 | 0.58
64 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU004 | 1S-DL-YP-CTC-DDRG-0106-HAU004 | FHATAK KIRORE:ID | TG-HAU004A-1 | 19500365 | 630 | 200 | 241 | 0.96 | 204 | 65 | 278 | 68 | 287 | 71 | 302 | 21 | 2019-06-11 17:00 | 48.3 | 9.7 | 356 | B | 105 | 71 | 125 | 54 |  |  | 24.1 | 75.9 | 550.21 | 553.51 | 510.51 | 539.21 | 167.57 | 164.27 | 164.27 | 178.57 |  |  | 0.3 | [9 empty] | 718.18 | 1.42 | 0.46 | 0.32
65 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU005 | 1S-DL-YP-CTC-DDRG-0106-HAU005 | GALI BAJRANG BALI:PL | TG-HAU005A-1 | 19500323 | 990 | 200 | 233 | 0.97 | 669 | 206 | 910 | 230 | 1027 | 233 | 1037 | 123 | 2019-06-29 17:00 | 164.7 | 24.4 | 1057 | B | 91 | 106 | 103 | 15 |  | 0.2 | 5.9 | 93.9 | 414.45 | 266.31 | 362.23 | 348.23 | 116.28 | 254.42 | 254.42 | 173.2 | 185.27 | 195.27 | 201.27 | 194.57 | [8 empty] | 716.4 | 3.2 | 0.43 | 0.68
66 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU006 | 1S-DL-YP-CTC-DDRG-0106-HAU006 | GALI DAKOTAN:PM | TG-HAU006A-1 | 19500348 | 990 | 320 | 243 | 0.96 | 901 | 304 | 1245 | 286 | 1169 | 311 | 1277 | 96 | 2019-06-06 | 207.6 | 6.6 | 1316 | B | 105 | 89 | 105 | 16 |  |  | 0.5 | 99.5 | 1 | 1 | 1 | 1 | 78.22 | 220.5 | 220.5 | 115.55 | 585.14 | 485.35 | 582.3 | 571.3 | 49.22 | 6.33 | 56.03 | 25.33 |  |  |  |  | 713.58 | 6.02 | 0.6 | 0.91
67 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU007 | 1S-DL-YP-CTC-DDRG-0106-HAU007 | GALI KUNDEWALAN:PL | TG-HAU007A-1 | 19500325 | 990 | 320 | 245 | 0.95 | 268 | 101 | 420 | 75 | 311 | 92 | 381 | 96 | 2019-06-30 | 71.4 | 7.4 | 436 | R | 125 | 79 | 96 | 46 |  |  | 0.8 | 99.2 | 342.48 | 692.12 | 598.54 | 576.5 | 375.24 | 26 | 26 | 141.22 | [12 empty] | 718.12 | 1.48 | 0.6 | 0.27
68 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU008 | 1S-DL-YP-CTC-DDRG-0106-HAU008 | GALI SHANKAR:ID | TG-HAU008A-1 | 19506161 | 990 | 320 | 232 | 0.96 | 965 | 252 | 1194 | 323 | 1522 | 389 | 1739 | 476 | 2019-06-03 13:00 | 413.4 | 117.4 | 1739 | B | 101 | 105 | 93 | 12 | 100 | [7 empty] | 7.3 | 1.3 | 1.3 | 5.3 | 598.5 | 575.51 | 642.28 | 601.5 | 111.33 | 135.32 | 68.55 | 111.03 | 0.3 | 5.3 | 1 |  | 718.23 | 1.37 | 0.67 | 0.97
69 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU008 | 1S-DL-YP-CTC-DDRG-0106-HAU008 | GALI SHANKAR:ID | TG-HAU008A-2 | 19505535 | 990 | 320 | 239 | 0.95 | 1096 | 334 | 1516 | 387 | 1782 | 375 | 1722 | 242 | 2019-06-03 13:30 | 499.5 | 88 | 1782 | Y | 92 | 110 | 98 | 18 | 0.1 |  | 7.4 | 92.4 |  |  |  |  | 68 | 13.3 | 13.3 | 27.3 | 649.02 | 672.24 | 670.36 | 689.32 |  | 31.08 | 2.3 |  | 0.14 | 0.14 | 0.14 | 0.14 | 717.16 | 2.44 | 0.5 | 1.11
70 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU009 | 1S-DL-YP-CTC-DDRG-0106-HAU009 | HAMDARD:K | TG-HAU009A-1 | 19505506 | 990 | 320 | 239 | 0.97 | 690 | 225 | 1105 | 220 | 1037 | 245 | 1186 | 129 | 2019-06-28 15:00 | 281.6 | -2.6 | 1186 | B | 99 | 99 | 101 | 2 | 0.1 | 0.1 | 1.1 | 98.8 | 22 | 20.3 | 15 | 12.3 | 558.54 | 538.05 | 538.05 | 557.05 | 120.56 | 143.15 | 142.45 | 132.15 | [8 empty] | 701.5 | 18.1 | 0.47 | 0.7
71 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU009 | 1S-DL-YP-CTC-DDRG-0106-HAU009 | HAMDARD:K | TG-HAU009A-2 | 19505725 | 630 | 200 | 242 | 0.96 | 303 | 92 | 386 | 80 | 335 | 131 | 551 | 196 | 2019-06-11 23:00 | 98.8 | 30.6 | 599 | B | 94 | 83 | 123 | 40 | 0.2 |  | 17.9 | 81.9 | 115.53 | 174.23 | 9 | 55 | 534.12 | 527.42 | 527.42 | 560.35 | 52.3 | 0.3 | 243.06 | 87 | [8 empty] | 702.35 | 17.25 | 0.63 | 0.48
72 | 2019-06-02 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU010 | 1S-DL-YP-CTC-DDRG-0106-HAU010 | HAMMATGARH:K | TG-HAU010A-1 | 19500364 | 990 | 320 | 245 | 0.95 | 497 | 160 | 646 | 145 | 588 | 192 | 777 | 168 | 2019-06-11 14:00 | 148.7 | 26.5 | 853 | B | 97 | 83 | 119 | 36 |  |  | 0.8 | 99.2 | 464.4 | 492.1 | 430.26 | 464.4 | 92.58 | 183.51 | 183.51 | 94.28 | 134.23 | 16 | 154.53 | 132.53 | [8 empty] | 692.01 | 3.59 | 0.42 | 0.5
73 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU010 | 1S-DL-YP-CTC-DDRG-0106-HAU010 | HAMMATGARH:K | TG-HAU010A-2 | 19500332 | 990 | 320 | 235 | 0.95 | 779 | 197 | 846 | 300 | 1298 | 281 | 1219 | 418 | 2019-06-10 23:30 | 237 | 106.7 | 1343 | Y | 79 | 110 | 111 | 32 | 25.8 | 0.1 | 5.8 | 68.2 |  |  |  |  | 234.15 | 29.3 | 29.3 | 36.3 | 481.2 | 641.35 | 652.05 | 679.05 |  | 44.3 | 56 | [5 empty] | 715.35 | 4.25 | 0.71 | 0.79
74 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU011 | 1S-DL-YP-CTC-DDRG-0106-HAU011 | RAJ ENGINEERING:ID | TG-HAU011A-1 | 19500218 | 990 | 320 | 238 | 0.96 | 808 | 266 | 1188 | 254 | 1131 | 288 | 1281 | 131 | 2019-06-05 15:00 | 206.8 | 64.8 | 1281 | B | 104 | 94 | 102 | 10 |  |  | 0.7 | 99.3 |  | 3.3 | 0.3 |  | 156.25 | 220.22 | 220.22 | 187.52 | 539.17 | 494.2 | 507.5 | 529.2 | 22.3 |  | 15 | 1 |  |  |  |  | 718.12 | 1.48 | 0.61 | 0.82
75 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU011 | 1S-DL-YP-CTC-DDRG-0106-HAU011 | RAJ ENGINEERING:ID | TG-HAU011A-2 | 19504377 | 990 | 320 | 237 | 0.96 | 767 | 215 | 965 | 321 | 1458 | 230 | 1034 | 462 | 2019-06-05 15:00 | 198.7 | 67 | 1476 | Y | 91 | 122 | 86 | 36 |  |  | 2 | 98 | 0.3 |  | 0.3 |  | 186.25 | 63.25 | 63.25 | 141.25 | 531.19 | 522.18 | 497.19 | 576.49 |  | 132.31 | [6 empty] | 718.14 | 1.46 | 0.68 | 0.77
76 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU012 | 1S-DL-YP-CTC-DDRG-0106-HAU012 | SARAK PREM NARAIN:PL | TG-HAU012A-1 | 19501687 | 990 | 320 | 242 | 0.94 | 1042 | 296 | 1219 | 384 | 1543 | 362 | 1504 | 306 | 2019-06-27 05:30 | 349.6 | 87.6 | 1774 | Y | 80 | 119 | 102 | 39 | 90.4 | 9.4 | 0.2 |  | 4 | 0.3 | 0.3 | 0.3 | 27.17 | 4.3 | 4.3 | 5.3 | 679 | 236.53 | 508.31 | 507.12 | 6.25 | 316.04 | 193.46 | 200.05 |  | 158.45 | 7.55 | 3.25 | 716.42 | 3.18 | 0.69 | 1.05
77 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU013 | 1S-DL-YP-CTC-DDRG-0106-HAU013 | SEEMA LODGE:PL | TG-HAU013A-1 | 19500385 | 990 | 320 | 236 | 0.94 | 660 | 250 | 1077 | 219 | 957 | 190 | 819 | 224 | 2019-06-11 01:00 | 200.9 | 106 | 1091 | R | 108 | 100 | 92 | 16 |  | 0.1 | 39.4 | 60.6 |  |  |  |  | 68.3 | 178 | 178 | 140.3 | 651.25 | 541.55 | 486.25 | 579.25 | [8 empty] | 719.55 | 0.05 | 0.71 | 0.67
78 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU014 | 1S-DL-YP-CTC-DDRG-0106-HAU014 | BARSHABULLA:ID DRG | TG-HAU014A-1 | 19503477 | 990 | 320 | 230 | 0.96 | 968 | 316 | 1432 | 317 | 1428 | 335 | 1529 | 99 | 2019-06-13 17:00 | 235.5 | 77.3 | 1636 | R | 103 | 95 | 101 | 8 |  | 1.3 | 61.9 | 36.9 |  |  |  |  | 134.3 | 188 | 188 | 134.3 | 453.23 | 438.53 | 520.53 | 482.53 | 123.27 | 91.57 | 79.57 | 101.27 | 7.3 |  | 2 |  | 718.5 | 1.1 | 0.57 | 0.98
79 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU015 | 1S-DL-YP-CTC-DDRG-0106-HAU015 | NEW HAUZ QUAZI:ID DRG | TG-HAU015A-1 | 19502903 | 990 | 320 | 238 | 0.96 | 945 | 360 | 1575 | 329 | 1438 | 255 | 1114 | 410 | 2019-06-01 15:00 | 238.5 | 75.1 | 1575 | R | 107 | 101 | 92 | 15 |  |  | 0.4 | 99.6 |  |  |  |  | 23.3 | 49.3 | 49.3 | 40.3 | 533 | 554.52 | 618.39 | 591.2 | 155.34 | 113.42 | 14.26 | 86.14 | 6 |  |  |  | 718.04 | 1.56 | 0.65 | 0.95
80 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | HAU016 | 1S-DL-YP-CTC-DDRG-0106-HAU016 | NEW AMAR:PM | TG-HAU016A-1 | 19500324 | 400 | 120 | 236 | 0.97 | 178 | 55 | 241 | 41 | 177 | 81 | 355 | 156 | 2019-06-11 16:00 | 41.4 | 0.8 | 377 | B | 90 | 78 | 132 | 54 |  |  | 15 | 85 | 523.18 | 548.16 | 484.51 | 508.21 | 190 | 170.02 | 170.02 | 157.57 | 5 |  | 187.3 | 52 | [8 empty] | 718.18 | 1.42 | 0.31 | 0.44
81 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS001 | 1S-DL-YP-CTC-DDRG-0101-JMS001 | BULIBULI KHANA:ID | TG-JMS001A-1 | 19505784 | 990 | 320 | 255 | 0.91 | 879 | 483 | 2022 | 12 | 50 | 384 | 1608 | 1801 | 2019-06-03 13:30 | 421.1 | 114.9 | 2022 | R | 158 | 3 | 139 | 155 | 0.1 | 0.1 | 28.8 | 71 |  | 706.56 |  |  | 0.3 |  |  | 26.2 | 220.27 |  | 404.52 | 680.06 | 292.39 |  | 266.17 | 0.3 | 193.2 |  | 34.57 |  | 706.56 | 13.04 | 0.63 | 0.89
82 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS001 | 1S-DL-YP-CTC-DDRG-0101-JMS001 | BULIBULI KHANA:ID | TG-JMS001A-2 | 19501700 | 990 | 320 | 229 | 0.94 | 984 | 351 | 1500 | 327 | 1393 | 306 | 1308 | 167 | 2019-06-04 04:30 | 334.1 | 152.4 | 1513 | R | 102 | 99 | 99 | 3 |  |  | 5.3 | 94.7 | [8 empty] | 443.48 | 499.48 | 508.18 | 483.18 | 270 | 217.21 | 209.51 | 234.51 | 4.21 | 1 |  |  | 718.09 | 1.51 | 0.74 | 0.99
83 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS002 | 1S-DL-YP-CTC-DDRG-0101-JMS002 | CHANDNI MAHAL:ID | TG-JMS002A-1 | 19501664 | 990 | 320 | 231 | 0.96 | 632 | 192 | 834 | 227 | 977 | 213 | 920 | 125 | 2019-06-03 | 150.9 | 63.3 | 1079 | Y | 86 | 118 | 95 | 32 |  | 1.5 | 60.3 | 38.2 | 4 |  |  |  | 538.3 | 72.3 | 72.3 | 239.3 | 175.52 | 645.52 | 351.52 | 478.52 | [8 empty] | 718.22 | 1.38 | 0.67 | 0.64
84 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS002 | 1S-DL-YP-CTC-DDRG-0101-JMS002 | CHANDNI MAHAL:ID | TG-JMS002A-2 | 19505094 | 990 | 200 | 235 | 0.95 | 1253 | 374 | 1718 | 447 | 2153 | 431 | 2127 | 422 | 2019-06-02 18:00 | 424.8 | 43.6 | 2153 | Y | 116 | 81 | 103 | 35 | 10.7 | 69.8 | 19.5 | 0.1 | 1.32 | 5.3 | 3.02 | 3 | 10.47 | 269.25 | 269.25 | 52.25 | 639.03 | 431.55 | 590.01 | 650.25 | 52.28 | 0.3 | 23.3 | 1.3 | 4 | 0.3 | 2 | 0.3 | 707.5 | 12.1 | 0.43 | 1.27
85 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS002 | 1S-DL-YP-CTC-DDRG-0101-JMS002 | CHANDNI MAHAL:ID | TG-JMS002A-3 | 19503569 | 990 | 320 | 228 | 0.96 | 288 | 93 | 429 | 114 | 525 | 80 | 369 | 137 | 2019-06-02 20:00 | 83.9 | 23.6 | 525 | Y | 95 | 120 | 85 | 35 |  | 0.1 | 20.8 | 79.1 | 437.07 | 128.23 | 588.37 | 356.37 | 281.58 | 590.42 | 590.42 | 362.28 | [12 empty] | 719.05 | 0.55 | 0.68 | 0.29
86 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS002 | 1S-DL-YP-CTC-DDRG-0101-JMS002 | CHANDNI MAHAL:ID | TG-JMS002A-4 | 19505203 | 630 | 200 | 224 | 0.95 | 805 | 395 | 1790 | 216 | 938 | 193 | 839 | 905 | 2019-06-29 02:30 | 291 | 69.4 | 2084 | R | 118 | 94 | 88 | 30 | 0.6 | 0.6 | 21.3 | 77.4 | [5 empty] | 1.3 | 1.3 | 1.3 | 160 | 396 | 513 | 302 | 216.3 | 275.45 | 177.02 | 316.3 | 319.32 | 22.47 | 2 | 76.02 | 696.02 | 23.58 | 0.64 | 1.28
87 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS003 | 1S-DL-YP-CTC-DDRG-0101-JMS003 | CHANDNI MAHAL [K]:K | TG-JMS003A-1 | 19504749 | 990 | 320 | 236 | 0.94 | 1090 | 374 | 1564 | 381 | 1596 | 336 | 1391 | 191 | 2019-06-03 04:00 | 355.5 | 140.6 | 1744 | Y | 101 | 100 | 99 | 2 |  | 0.8 | 59.9 | 39.2 | [5 empty] | 2.3 | 2.3 |  | 425 | 401 | 443.3 | 420.3 | 254 | 223.3 | 235.58 | 251.3 | 40.58 | 92.58 | 40.3 | 47.58 | 719.58 | 0.02 | 0.69 | 1.1
88 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS004 | 1S-DL-YP-CTC-DDRG-0101-JMS004 | DELHI GATE TELEPHONE EXCHANGE PM:K | TG-JMS004A-1 | 19505683 | 990 | 320 | 238 | 0.96 | 1090 | 345 | 1448 | 363 | 1506 | 383 | 1617 | 148 | 2019-06-17 03:00 | 320.6 | 67.2 | 2129 | B | 101 | 93 | 107 | 14 | 0.4 |  | 83.7 | 15.9 |  |  |  |  | 5.55 | 5.55 | 5.55 | 5.55 | 587.47 | 639.56 | 526.38 | 597.44 | 106.12 | 55.47 | 159.59 | 96.53 | 7.16 | 5.32 | 14.38 | 6.38 | 707.1 | 12.5 | 0.62 | 1.1
89 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS004 | 1S-DL-YP-CTC-DDRG-0101-JMS004 | DELHI GATE TELEPHONE EXCHANGE PM:K | TG-JMS004A-2 | 19505473 | 990 | 300 | 245 | 0.95 | 1451 | 401 | 1653 | 524 | 2207 | 526 | 2150 | 528 | 2019-06-16 04:30 | 541.2 | 41.7 | 2659 | R | 102 | 95 | 102 | 7 | 47.3 | 22 | 21.1 | 9.5 | 27 | 50 | 21.33 | 28 | 109.21 | 94.28 | 94.28 | 85.58 | 575.13 | 569.18 | 602.53 | 598.23 | 1.3 |  | 1.06 | 1.25 | 0.49 | 0.07 | 1.26 | 0.07 | 713.53 | 6.07 | 0.33 | 1.47
90 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS005 | 1S-DL-YP-CTC-DDRG-0101-JMS005 | FOOTOVER BRIDGE:K | TG-JMS005A-1 | 19500210 | 990 | 300 | 239 | 0.96 | 441 | 187 | 788 | 125 | 529 | 129 | 543 | 252 | 2019-06-11 17:00 | 138.7 | 26.2 | 805 | R | 118 | 93 | 89 | 29 |  |  | 0.8 | 99.2 | 80.37 | 238.35 | 298.26 | 143.07 | 499.5 | 471.27 | 471.27 | 528.2 | 137 | 7.25 | 9 | 46 | [8 empty] | 717.27 | 2.33 | 0.59 | 0.45
91 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS005 | 1S-DL-YP-CTC-DDRG-0101-JMS005 | FOOTOVER BRIDGE:K | TG-JMS005A-2 | 19500208 | 990 | 300 | 237 | 0.95 | 590 | 166 | 683 | 246 | 1016 | 178 | 729 | 313 | 2019-06-02 04:00 | 179.4 | 83.5 | 1053 | Y | 90 | 120 | 90 | 30 |  |  | 37.9 | 62.1 |  |  |  |  | 406.52 | 40.22 | 40.22 | 179.52 | 312.53 | 679.23 | 344.55 | 539.53 | [8 empty] | 719.45 | 0.15 | 0.73 | 0.6
92 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS005 | 1S-DL-YP-CTC-DDRG-0101-JMS005 | FOOTOVER BRIDGE:K | TG-JMS005A-3 | 19502105 | 990 | 300 | 239 | 0.95 | 460 | 166 | 679 | 177 | 729 | 117 | 473 | 235 | 2019-06-16 | 135.2 | 54.5 | 752 | Y | 101 | 110 | 89 | 21 |  | 0.1 | 67.1 | 32.8 | 15 | 7.3 | 17.59 | 2 | 619 | 517 | 517 | 674.29 | 85.59 | 195.29 | 4.3 | 43.3 | [8 empty] | 719.59 | 0.01 | 0.69 | 0.46
93 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS006 | 1S-DL-YP-CTC-DDRG-0101-JMS006 | GANJ MEER KHAN:PM | TG-JMS006A-1 | 19505263 | 990 | 320 | 258 | 0.91 | 1234 | 425 | 1527 | 468 | 1763 | 341 | 1290 | 409 | 2019-06-12 02:00 | 543 | 196.5 | 1962 | Y | 98 | 117 | 85 | 32 | 100 | [11 empty] | 159.08 | 82.38 | 416.58 | 178.34 | 313.19 | 191.49 | 254.58 | 293.53 | 222.59 | 420.59 | 20.3 | 222.59 | 695.26 | 24.34 | 0.73 | 1.25
94 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS007 | 1S-DL-YP-CTC-DDRG-0101-JMS007 | GANJ MEER KHAN-2:PL | TG-JMS007A-1 | 19500134 | 990 | 320 | 238 | 0.94 | 700 | 258 | 1122 | 216 | 940 | 227 | 987 | 164 | 2019-06-30 00:30 | 236.3 | 101.6 | 1158 | R | 107 | 92 | 102 | 15 |  |  | 0.3 | 99.7 |  |  |  |  | 103.43 | 195.43 | 195.43 | 98.55 | 608.31 | 518.01 | 640.22 | 614.49 | 1.3 | [7 empty] | 713.44 | 6.16 | 0.72 | 0.71
95 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS008 | 1S-DL-YP-CTC-DDRG-0101-JMS008 | GIRDHAR PANNA:ID | TG-JMS008A-1 | 19505336 | 990 | 320 | 235 | 0.94 | 709 | 236 | 955 | 258 | 1039 | 216 | 869 | 148 | 2019-06-12 01:30 | 252.2 | 78.7 | 1166 | R | 105 | 98 | 97 | 8 | 0.1 |  | 2.1 | 97.8 |  |  |  |  | 154.34 | 231.27 | 231.27 | 186.31 | 540.42 | 464.19 | 482.16 | 509.15 | 0.3 | [7 empty] | 695.46 | 24.14 | 0.65 | 0.72
96 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS008 | 1S-DL-YP-CTC-DDRG-0101-JMS008 | GIRDHAR PANNA:ID | TG-JMS008A-2 | 19505724 | 990 | 320 | 234 | 0.99 | 787 | 335 | 1679 | 270 | 1342 | 182 | 872 | 702 | 2019-06-05 22:30 | 200.6 | 22.4 | 1679 | R | 124 | 103 | 73 | 51 | 0.1 | 0.1 | 1.5 | 98.4 |  | 0.3 | 0.3 | 0.3 | 0.3 | 22.3 | 22.3 | 25.3 | 597.48 | 691.18 | 376.53 | 693.18 | 120.3 | 5 |  |  | 0.3 |  |  |  | 719.18 | 0.42 | 0.7 | 0.8
97 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS008 | 1S-DL-YP-CTC-DDRG-0101-JMS008 | GIRDHAR PANNA:ID | TG-JMS008A-3 | 19506160 | 630 | 200 | 232.1921 | 0.9481 | 775.4229 | 247.0648 | 1089.5914 | 297.1256 | 1343.244 | 231.2325 | 1025.0123 | 291.3601 | 2019-06-03 04:30 | [15 empty] | 0 |  |  |  | 0 |  |  |  | 345.5 |  |  |  | 293.5 |  |  |  | 80.5 | 719.5 |  | 0.65748 | 1.2308
98 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS009 | 1S-DL-YP-CTC-DDRG-0101-JMS009 | HOTEL PRESIDENT:PL | TG-JMS009A-1 | 19500335 | 990 | 320 | 237 | 0.96 | 353 | 79 | 335 | 171 | 724 | 103 | 438 | 349 | 2019-06-30 | 97.9 | 36.8 | 724 | Y | 71 | 130 | 98 | 59 |  |  | 0.1 | 99.9 | 560.02 | 1.3 | 91.13 | 50 | 159.16 | 684.48 | 684.48 | 669.18 |  | 33 | [10 empty] | 719.18 | 0.42 | 0.7 | 0.36
99 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS010 | 1S-DL-YP-CTC-DDRG-0101-JMS010 | JAMA MASJID:ID | TG-JMS010A-1 | 19500209 | 990 | 320 | 245 | 0.97 | 466 | 161 | 657 | 147 | 600 | 157 | 634 | 50 | 2019-06-10 05:30 | 114.8 | -22.8 | 680 | R | 107 | 98 | 95 | 12 |  |  | 20.6 | 79.4 | 48 | 118 | 205.56 | 114.3 | 581.24 | 578.54 | 578.54 | 549.54 | 90.3 | 23 | 55.3 | 55.3 | [8 empty] | 719.54 | 0.06 | 0.57 | 0.47
100 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS010 | 1S-DL-YP-CTC-DDRG-0101-JMS010 | JAMA MASJID:ID | TG-JMS010A-2 | 19500094 | 990 | 320 | 231 | 0.95 | 574 | 161 | 717 | 220 | 977 | 192 | 854 | 226 | 2019-06-30 01:00 | 158.2 | 75.8 | 977 | Y | 88 | 113 | 99 | 25 |  | 0.1 | 3.1 | 96.8 | 1 |  |  |  | 472 | 104 | 104 | 282.3 | 246.55 | 615.55 | 427.55 | 437.25 | [8 empty] | 719.55 | 0.05 | 0.73 | 0.58
101 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS010 | 1S-DL-YP-CTC-DDRG-0101-JMS010 | JAMA MASJID:ID | TG-JMS010A-3 | 19505361 | 630 | 200 | 251 | 0.94 | 514 | 224 | 1001 | 137 | 585 | 152 | 620 | 400 | 2019-06-14 05:30 | 224 | 63.4 | 1001 | R | 105 | 94 | 100 | 11 | 9.9 | 45.7 | 42.8 | 1.6 |  |  |  |  | 46 | 74 | 74 | 50.3 | 666.28 | 645.58 | 686.58 | 668.58 | 7 |  | 0.3 | 0.3 | 0.3 |  |  |  | 719.58 | 0.02 | 0.66 | 0.82
102 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS012 | 1S-DL-YP-CTC-DDRG-0101-JMS012 | KASTURBA HOSPITAL:ID | TG-JMS012A-1 | 19500220 | 990 | 200 | 239 | 0.94 | 646 | 227 | 948 | 244 | 1023 | 175 | 723 | 271 | 2019-06-03 02:00 | 207.5 | 26.7 | 1078 | R | 100 | 125 | 74 | 51 |  | 0.3 | 69.3 | 30.5 | 1 | 1 | 29.01 | 1 | 424.44 | 166.44 | 166.44 | 411.14 | 292.59 | 550.59 | 27.3 | 306.29 | [8 empty] | 718.43 | 1.17 | 0.6 | 0.65
103 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS012 | 1S-DL-YP-CTC-DDRG-0101-JMS012 | KASTURBA HOSPITAL:ID | TG-JMS012A-2 | 19500219 | 990 | 320 | 236 | 0.95 | 590 | 244 | 1038 | 204 | 866 | 142 | 588 | 393 | 2019-06-28 01:30 | 188.4 | 89.1 | 1269 | R | 125 | 95 | 80 | 45 | 12.3 | 85.5 | 2.2 | [5 empty] | 17.3 | 239 | 239 | 122.3 | 698.54 | 479.54 | 191.55 | 596.24 | 2.3 | [7 empty] | 718.54 | 1.06 | 0.76 | 0.6
104 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS013 | 1S-DL-YP-CTC-DDRG-0101-JMS013 | KASTURBA P/M:PM | TG-JMS013A-1 | 19500206 | 990 | 320 | 242 | 0.95 | 784 | 287 | 1191 | 238 | 978 | 259 | 1066 | 186 | 2019-06-03 04:30 | 231.8 | 42.7 | 1205 | R | 101 | 98 | 101 | 3 | 0.1 | 0.1 | 58.3 | 41.6 |  | 1.3 | 1 | 1.3 | 23 | 25 | 25 | 15.3 | 685.27 | 692.27 | 692.27 | 702.27 | 11 | 0.3 | 3 | [5 empty] | 719.27 | 0.33 | 0.73 | 0.79
105 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS015 | 1S-DL-YP-CTC-DDRG-0101-JMS015 | KUCHA CHELAN-2:PL | TG-JMS015A-1 | 19506158 | 990 | 320 | 250 | 0.93 | 1004 | 329 | 1292 | 339 | 1320 | 335 | 1307 | 24 | 2019-06-05 04:30 | 403.5 | 135 | 2204 | Y | 106 | 123 | 71 | 52 | 0.4 | 23.8 | 53.3 | 22.5 |  |  |  |  | 1 | 0.01 | 0.01 | 1.31 | 444.23 | 233.2 | 614.41 | 510.54 | 233.05 | 277.57 | 0.3 | 173.55 | 8.52 | 176.02 | 1 | 1 | 687.2 | 32.4 | 0.7 | 1.01
106 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS015 | 1S-DL-YP-CTC-DDRG-0101-JMS015 | KUCHA CHELAN-2:PL | TG-JMS015A-2 | 19500358 | 400 | 120 | 237 | 0.93 | 429 | 167 | 721 | 140 | 599 | 122 | 519 | 177 | 2019-06-01 21:00 | 146 | 54.4 | 721 | R | 109 | 103 | 87 | 22 | 0.1 | 17.9 | 75.6 | 6.4 |  |  |  |  | 0.3 | 2 | 2 | 0.3 | 376.07 | 466.44 | 636.58 | 502.07 | 270 | 229.44 | 67 | 210.21 | 67.51 | 16 |  | 1.3 | 714.28 | 5.32 | 0.66 | 1.07
107 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS015 | 1S-DL-YP-CTC-DDRG-0101-JMS015 | KUCHA CHELAN-2:PL | TG-JMS015A-3 | 19505512 | 990 | 320 | 237 | 0.95 | 1339 | 499 | 2126 | 386 | 1633 | 454 | 1920 | 429 | 2019-06-26 22:30 | 450.2 | 146.9 | 2507 | Y | 90 | 103 | 107 | 17 | 1 | 14.3 | 51.1 | 33.6 |  |  |  |  | 0.31 | 0.02 | 0.02 |  | 373.18 | 289.07 | 122.08 | 189.52 | 196.44 | 189.38 | 328.02 | 381.21 | 142.03 | 233.49 | 262.26 | 141.23 | 712.36 | 7.24 | 0.65 | 1.35
108 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS017 | 1S-DL-YP-CTC-DDRG-0101-JMS017 | KUCHA DAKHINI RAI:PL | TG-JMS017A-1 | 19506016 | 990 | 320 | 228 | 0.95 | 1081 | 454 | 2200 | 219 | 1004 | 408 | 2140 | 1168 | 2019-06-01 19:00 | 447.7 | 48 | 2855 | B | 91 | 92 | 117 | 26 | 1.4 | 46.2 | 52.2 | 0.3 | 40.51 | 3.3 | 4.51 | 5.21 | 22 | 123.21 | 123.21 | 36 | 562.11 | 485.11 | 347.14 | 496.41 | 70.58 | 81.28 | 232.27 | 156.58 | 0.3 | 3 | 78.28 | 1.3 | 696.3 | 23.3 | 0.6 | 1.09
109 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS017 | 1S-DL-YP-CTC-DDRG-0101-JMS017 | KUCHA DAKHINI RAI:PL | TG-JMS017A-2 | 19506022 | 990 | 320 | 236 | 0.94 | 826 | 234 | 1026 | 391 | 1793 | 201 | 861 | 862 | 2019-06-11 05:00 | 331.5 | 112.3 | 1874 | B | 113 | 95 | 92 | 21 | 0.3 | 0.9 | 68.6 | 30.2 |  |  |  |  | 19.3 | 90.3 | 90.3 | 60 | 621.31 | 605.01 | 529.25 | 636.01 | 55 |  | 0.3 | 0.3 | 0.3 | 1 | 0.3 |  | 696.31 | 23.29 | 0.64 | 0.83
110 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS018 | 1S-DL-YP-CTC-DDRG-0101-JMS018 | MOHALLA QUABRISTAN:PL | TG-JMS018A-1 | 19501666 | 990 | 320 | 231 | 0.94 | 909 | 348 | 1504 | 270 | 1167 | 292 | 1264 | 300 | 2019-06-05 05:00 | 285.6 | 55.9 | 1526 | R | 111 | 93 | 96 | 18 | 0.6 | 14.3 | 9.5 | 75.7 | 0.3 | 0.3 | 0.3 | 0.3 |  | 3.3 | 3.3 | 1.3 | 373.37 | 678.34 | 611.25 | 592.48 | 332.52 | 35.25 | 101.3 | 123.11 | 11 |  |  |  | 717.59 | 2.01 | 0.77 | 0.92
111 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS019 | 1S-DL-YP-CTC-DDRG-0101-JMS019 | MOTHER DAIRY:K | TG-JMS019A-1 | 19500379 | 630 | 200 | 233 | 0.97 | 635 | 283 | 1194 | 169 | 704 | 183 | 769 | 461 | 2019-06-05 02:00 | 151.8 | 52 | 1224 | R | 112 | 85 | 103 | 27 |  |  | 14.4 | 85.6 |  |  |  |  | 4 | 20.59 | 20.59 | 7.3 | 452.2 | 655.43 | 539 | 618.12 | 174.52 | 16 | 141.42 | 66.3 | 61.3 |  | 1 | 0.3 | 712.49 | 7.11 | 0.66 | 1.01
112 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS021 | 1S-DL-YP-CTC-DDRG-0101-JMS021 | NEW DUJANA HOUSE 8 PANEL:ID | TG-JMS021A-1 | 19500204 | 990 | 320 | 238 | 0.95 | 544 | 181 | 797 | 167 | 737 | 196 | 877 | 121 | 2019-06-01 20:30 | 140.6 | 42 | 899 | R | 98 | 99 | 102 | 4 |  |  | 79.9 | 20.1 | 19 | 5 | 1.3 | 6 | 530.41 | 544.11 | 544.11 | 540.11 | 168.3 | 169 | 179.3 | 172 | [8 empty] | 718.11 | 1.49 | 0.64 | 0.55
113 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS021 | 1S-DL-YP-CTC-DDRG-0101-JMS021 | NEW DUJANA HOUSE 8 PANEL:ID | TG-JMS021A-2 | 19500205 | 990 | 320 | 238 | 0.93 | 588 | 179 | 750 | 186 | 780 | 223 | 926 | 163 | 2019-06-03 04:00 | 195.8 | 80.2 | 1010 | B | 89 | 98 | 113 | 24 | 0.1 |  | 75.2 | 24.7 | 1 | 0.3 |  |  | 488.12 | 354.12 | 354.12 | 349.12 | 229.58 | 364.28 | 489.28 | 369.58 | [8 empty] | 719.1 | 0.5 | 0.68 | 0.59
114 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS021 | 1S-DL-YP-CTC-DDRG-0101-JMS021 | NEW DUJANA HOUSE 8 PANEL:ID | TG-JMS021A-3 | 19503567 | 990 | 320 | 226 | 0.94 | 810 | 308 | 1352 | 270 | 1160 | 233 | 1005 | 301 | 2019-06-03 04:00 | 262.8 | 100.1 | 1352 | R | 107 | 105 | 88 | 19 | 3.8 | 49.4 | 43.1 | 3.8 |  |  |  |  | 7 | 5.3 | 5.3 | 11 | 693.05 | 708.19 | 651.33 | 706.33 | 18.58 | 5.14 |  | 1.3 |  |  |  |  | 719.03 | 0.57 | 0.73 | 0.82
115 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS021 | 1S-DL-YP-CTC-DDRG-0101-JMS021 | NEW DUJANA HOUSE 8 PANEL:ID | TG-JMS021A-4 | 19500203 | 990 | 320 | 230 | 0.95 | 1022 | 377 | 1608 | 272 | 1157 | 373 | 1597 | 445 | 2019-06-02 04:30 | 320.2 | 128.8 | 1718 | B | 104 | 80 | 115 | 35 |  |  | 33.5 | 66.5 | [5 empty] | 15 | 15 |  | 396.17 | 698.49 | 256.47 | 458.46 | 275.34 | 5 | 331.04 | 256.33 | 46.58 |  | 130.58 | 3.3 | 718.49 | 1.11 | 0.72 | 1.03
116 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS021 | 1S-DL-YP-CTC-DDRG-0101-JMS021 | NEW DUJANA HOUSE 8 PANEL:ID | TG-JMS021A-5 | 19500202 | 990 | 320 | 229 | 0.95 | 1084 | 416 | 1832 | 328 | 1436 | 341 | 1479 | 377 | 2019-06-11 00:30 | 339.3 | 64.8 | 1869 | R | 113 | 97 | 90 | 23 |  | 14.3 | 81.6 | 4.2 |  |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  | 187.3 | 401.3 | 489.3 | 348.3 | 311.4 | 291.35 | 218.04 | 319.35 | 219.24 | 25.29 | 9.3 | 50.29 | 719.04 | 0.56 | 0.73 | 1.09
117 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS021 | 1S-DL-YP-CTC-DDRG-0101-JMS021 | NEW DUJANA HOUSE 8 PANEL:ID | TG-JMS021A-6 | 19500201 | 990 | 320 | 237 | 0.96 | 830 | 334 | 1473 | 282 | 1220 | 214 | 930 | 471 | 2019-06-10 23:30 | 208.3 | 93.5 | 1550 | R | 108 | 101 | 92 | 16 |  | 0.6 | 72 | 27.4 |  |  |  |  | 3.3 | 6.3 | 6.3 | 3.3 | 659.28 | 706.58 | 694.58 | 711.58 | 55.3 | 6.3 |  | 4.3 | 1.3 |  |  |  | 719.58 | 0.02 | 0.71 | 0.84
118 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS021 | 1S-DL-YP-CTC-DDRG-0101-JMS021 | NEW DUJANA HOUSE 8 PANEL:ID | TG-JMS021A-7 | 19505289 | 990 | 320 | 239 | 0.94 | 713 | 395 | 1942 | 147 | 634 | 171 | 789 | 1238 | 2019-06-14 06:00 | 302.7 | 80.3 | 1942 | R | 115 | 80 | 106 | 35 | 0.4 | 0.1 | 88.7 | 10.8 |  | 0.3 |  |  | 71 | 533.58 | 533.58 | 199 | 625.28 | 162.3 | 547.58 | 497.58 |  |  |  |  | 0.3 |  | 0.3 |  | 696.58 | 23.02 | 0.61 | 0.72
119 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS021 | 1S-DL-YP-CTC-DDRG-0101-JMS021 | NEW DUJANA HOUSE 8 PANEL:ID | TG-JMS021A-8 | 19506157 | 990 | 320 | 244 | 0.93 | 824 | 299 | 1208 | 189 | 771 | 336 | 1400 | 558 | 2019-06-02 03:00 | 353 | 109.4 | 1812 | B | 108 | 86 | 105 | 22 | 0.2 | 0.4 | 15.7 | 83.6 | 1 | 1.3 | 1 | 1 | 23.3 | 62 | 62 | 20 | 630.3 | 632.28 | 658.28 | 672.58 | 40.58 | 0.3 | 15.3 | 2.3 | 0.3 |  | 1.3 |  | 696.28 | 23.32 | 0.7 | 0.83
120 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS022 | 1S-DL-YP-CTC-DDRG-0101-JMS022 | OLD DUJANA:K | TG-JMS022A-1 | 19506594 | 990 | 320 | 235 | 0.94 | 1180 | 361 | 1524 | 308 | 1305 | 510 | 2227 | 834 | 2019-06-02 04:00 | 442.9 | 146.9 | 2582 | B | 97 | 81 | 122 | 41 | 4.7 | 28.1 | 66.6 | 0.6 |  |  |  |  | 1.3 | 10 | 10 |  | 373 | 606.38 | 123.3 | 360.3 | 283.12 | 78.15 | 282.3 | 308.45 | 37.29 | 0.18 | 289.11 | 25.56 | 695.11 | 24.49 | 0.66 | 1.19
121 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS022 | 1S-DL-YP-CTC-DDRG-0101-JMS022 | OLD DUJANA:K | TG-JMS022A-2 | 19500383 | 990 | 320 | 230 | 0.95 | 1002 | 355 | 1585 | 266 | 1167 | 381 | 1717 | 497 | 2019-06-03 | 288.5 | 75.8 | 1852 | B | 94 | 91 | 116 | 25 |  | 8.1 | 68.2 | 23.6 |  | 0.3 |  |  | 7 | 4.3 | 4.3 | 4.3 | 579.03 | 609.54 | 259 | 473.33 | 124.49 | 104.28 | 358.33 | 237.49 | 8.3 |  | 98.49 | 3.3 | 719.22 | 0.38 | 0.73 | 1.01
122 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS023 | 1S-DL-YP-CTC-DDRG-0101-JMS023 | SHEESH MAHAL:K | TG-JMS023A-1 | 19501661 | 990 | 320 | 242 | 0.94 | 1003 | 384 | 1613 | 335 | 1410 | 284 | 1187 | 369 | 2019-06-30 01:30 | 337.8 | 141.3 | 1613 | R | 102 | 102 | 95 | 7 |  |  | 34.8 | 65.2 | [5 empty] | 0.3 | 0.3 | 0.3 | 436.13 | 442.12 | 483.13 | 465.12 | 255.29 | 273 | 198.29 | 248 | 25.3 | 1.3 | 16.3 | 3.3 | 717.12 | 2.48 | 0.73 | 1.01
123 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS023 | 1S-DL-YP-CTC-DDRG-0101-JMS023 | SHEESH MAHAL:K | TG-JMS023A-2 | 19506663 | 990 | 320 | 238 | 0.94 | 839 | 231 | 975 | 296 | 1261 | 312 | 1332 | 327 | 2019-06-30 01:30 | 292.8 | 105.3 | 1362 | B | 84 | 105 | 111 | 27 |  | 0.1 | 35.8 | 64.1 |  |  |  |  | 105.09 | 13.3 | 13.3 | 25.3 | 601.06 | 642.45 | 581.28 | 670.45 |  | 50 | 109.47 | 10 |  |  |  |  | 706.15 | 13.45 | 0.69 | 0.85
124 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS024 | 1S-DL-YP-CTC-DDRG-0101-JMS024 | SSA ROAD:PL:PG | TG-JMS024A-1 | 19503516 | 990 | 320 | 230 | 0.97 | 1035 | 388 | 1702 | 307 | 1336 | 341 | 1473 | 321 | 2019-06-30 02:30 | 242.9 | 88.3 | 1735 | R | 130 | 56 | 113 | 74 |  |  | 33.3 | 66.7 |  | 301.27 |  |  | 1 | 3.3 | 3.3 | 1 | 300.58 | 390.25 | 531.25 | 640.22 | 366.24 | 23 | 185.27 | 76 | 50 |  | 1.3 | 1 | 718.22 | 1.38 | 0.61 | 1.05
125 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS024 | 1S-DL-YP-CTC-DDRG-0101-JMS024 | SSA ROAD:PL:PG | TG-JMS024A-2 | 19500074 | 990 | 320 | 235 | 0.96 | 933 | 283 | 1225 | 389 | 1691 | 260 | 1104 | 537 | 2019-06-03 | 222.3 | 74.3 | 1736 | Y | 100 | 121 | 79 | 42 | 1.1 | 15.7 | 60 | 23.3 |  |  |  |  | 22.22 |  |  | 16.41 | 673.2 | 620.03 | 503.34 | 677.49 | 12.48 | 80.57 |  | 14 |  | 7.3 |  |  | 708.3 | 11.3 | 0.6 | 0.94
126 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS025 | 1S-DL-YP-CTC-DDRG-0101-JMS025 | TIRAHA BAIRAM KHAN:ID | TG-JMS025A-1 | 19500357 | 990 | 320 | 233 | 0.95 | 810 | 278 | 1188 | 269 | 1146 | 263 | 1113 | 65 | 2019-06-30 00:30 | 244.4 | 61.8 | 1301 | B | 99 | 97 | 104 | 7 |  |  | 5.3 | 94.7 |  | 0.08 | 0.3 |  | 23.53 | 44.1 | 44.1 | 13.43 | 684.53 | 660.28 | 683.32 | 695.03 | 2 | 6 | 14.56 | 2 |  |  |  |  | 710.46 | 9.14 | 0.7 | 0.82
127 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS025 | 1S-DL-YP-CTC-DDRG-0101-JMS025 | TIRAHA BAIRAM KHAN:ID | TG-JMS025A-2 | 19500359 | 990 | 320 | 233 | 0.96 | 1407 | 433 | 1843 | 488 | 2078 | 486 | 2085 | 239 | 2019-06-01 22:30 | 370.9 | 49.3 | 2191 | B | 96 | 94 | 110 | 16 |  |  | 25.6 | 74.4 | 0.3 | 0.3 | [5 empty] | 0.3 | 137.05 | 187.56 | 45.38 | 101.15 | 317.2 | 280.31 | 183.34 | 280.4 | 261.53 | 247.51 | 487.06 | 334.23 | 716.48 | 3.12 | 0.69 | 1.42
128 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS026 | 1S-DL-YP-CTC-DDRG-0101-JMS026 | URDU BAZAR:PG | TG-JMS026A-1 | 19506156 | 990 | 320 | 238 | 0.94 | 1074 | 272 | 1161 | 284 | 1164 | 519 | 2367 | 1205 | 2019-06-11 05:00 | 423 | 126.1 | 2367 | B | 102 | 98 | 100 | 4 | 0.3 | 1.1 | 49.2 | 49.5 |  |  |  |  | 2.3 | 5.3 | 5.3 | 3 | 614.41 | 660.52 | 608.11 | 635.11 | 77.3 | 29.19 | 78.3 | 57.3 | 1.3 | 0.3 | 4 | 0.3 | 696.11 | 23.49 | 0.6 | 1.09
129 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS026 | 1S-DL-YP-CTC-DDRG-0101-JMS026 | URDU BAZAR:PG | TG-JMS026A-2 | 19506751 | 990 | 320 | 238 | 0.95 | 979 | 323 | 1428 | 330 | 1510 | 326 | 1451 | 73 | 2019-06-29 22:00 | 279 | 88.3 | 1643 | Y | 102 | 97 | 101 | 5 | 86.4 | 13.6 | [6 empty] | 119.25 | 232.25 | 232.25 | 159.25 | 575.46 | 462.16 | 539.16 | 535.46 | 0.3 | 0.3 | 0.3 | 0.3 |  | 0.3 |  |  | 695.41 | 24.19 | 0.47 | 0.99
130 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS026 | 1S-DL-YP-CTC-DDRG-0101-JMS026 | URDU BAZAR:PG | TG-JMS026A-3 | 19506481 | 990 | 320 | 241 | 0.98 | 542 | 185 | 743 | 176 | 712 | 182 | 739 | 29 | 2019-06-26 17:30 | 149.8 | 9.6 | 1331 | R | 103 | 99 | 98 | 5 | 0.1 |  | 58.3 | 41.6 | 395.22 | 407.22 | 410.43 | 403.52 | 138.21 | 155.4 | 155.4 | 145.51 | 175.19 | 146 | 160 | 159.19 | [8 empty] | 709.02 | 10.58 | 0.41 | 0.55
131 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS033 | 1S-DL-YP-CTC-DDRG-0101-JMS033 | HOTEL BROADWAY:K | TG-JMS033A-1 | 19500330 | 990 | 320 | 234 | 0.95 | 1013 | 382 | 1671 | 348 | 1533 | 283 | 1218 | 402 | 2019-06-27 01:30 | 322.4 | 107.5 | 1671 | R | 109 | 106 | 85 | 24 |  | 4.7 | 68.4 | 27 |  |  |  |  | 7.3 | 7.59 | 7.59 | 12.29 | 418.38 | 453.1 | 627.39 | 498.39 | 210.3 | 233.59 | 50.3 | 206 | 82 | 23.3 |  | 1.3 | 718.38 | 1.22 | 0.69 | 1.02
132 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS033 | 1S-DL-YP-CTC-DDRG-0101-JMS033 | HOTEL BROADWAY:K | TG-JMS033A-2 | 19503512 | 990 | 320 | 237 | 0.95 | 806 | 256 | 1070 | 277 | 1162 | 273 | 1132 | 81 | 2019-06-26 17:00 | 262 | 13.2 | 1342 | B | 89 | 108 | 103 | 19 |  | 0.3 | 37 | 62.7 | 56.26 | 30.56 | 40.56 | 31.56 | 443.47 | 398.47 | 398.47 | 445.17 | 218.07 | 276.38 | 261.55 | 240.07 |  | 11.59 | 17.29 | 1 |  |  |  |  | 718.2 | 1.4 | 0.5 | 0.81
133 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS033 | 1S-DL-YP-CTC-DDRG-0101-JMS033 | HOTEL BROADWAY:K | TG-JMS033A-3 | 19506159 | 990 | 320 | 236 | 0.95 | 1087 | 471 | 2110 | 322 | 1386 | 294 | 1272 | 787 | 2019-06-02 03:00 | 346.2 | 65.3 | 2223 | R | 132 | 78 | 90 | 54 | 15.6 | 5.3 | 48.1 | 31 |  | 0.3 |  |  | 18.01 | 215.14 | 215.14 | 34.31 | 449.36 | 465.27 | 625.23 | 641.4 | 118.46 | 6.03 | 6.37 | 9.19 | 103.39 | 2.48 |  | 4.32 | 690.02 | 29.58 | 0.52 | 1.1
134 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS033 | 1S-DL-YP-CTC-DDRG-0101-JMS033 | HOTEL BROADWAY:K | TG-JMS033A-4 | 19505490 | 990 | 320 | 243 | 0.94 | 510 | 222 | 954 | 215 | 888 | 74 | 304 | 619 | 2019-06-25 05:00 | 197.1 | 49 | 1081 | R | 123 | 111 | 67 | 56 | 0.2 | 6.9 | 90.3 | 2.5 | 1.3 | 5.3 | 306.52 | 13 | 382.52 | 500.44 | 500.44 | 576.44 | 332.09 | 210.17 |  | 126.47 | [8 empty] | 716.31 | 3.29 | 0.63 | 0.52
135 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS034 | 1S-DL-YP-CTC-DDRG-0101-JMS034 | GIRIDHAR PANNA :PKG | TG-JMS034A-1 | 19505510 | 990 | 320 | 241 | 0.94 | 745 | 178 | 765 | 291 | 1276 | 277 | 1204 | 479 | 2019-06-05 23:00 | 340.5 | 97.6 | 1429 | B | 73 | 115 | 112 | 42 |  | 0.1 | 8.4 | 91.4 | 0.01 |  |  |  | 455.19 | 16.01 | 16.01 | 72.33 | 258.18 | 692.37 | 679.37 | 641.05 |  | 5 | 6 | [5 empty] | 713.38 | 6.22 | 0.68 | 0.75
136 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | JMS035 | 1S-DL-YP-CTC-DDRG-0101-JMS035 | URDU BAZAR TANGA STAND:PG | TG-JMS035A-1 | 19505151 | 990 | 320 | 239 | 0.94 | 734 | 383 | 1802 | 173 | 700 | 178 | 783 | 1063 | 2019-06-14 06:00 | 293.1 | 89.6 | 1802 | R | 96 | 103 | 101 | 7 | 0.2 | 0.9 | 52.3 | 46.7 | 0.3 | 0.3 | 0.3 | 0.3 | 106.3 | 100 | 100 | 76 | 588.58 | 595.58 | 621.28 | 619.58 |  |  | 0.3 |  | 0.3 |  | 0.3 |  | 696.28 | 23.32 | 0.65 | 0.74
137 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | MRD011 | 1S-DL-YP-CTC-DDRG-0107-MRD011 | KHATTA P/M:PL | TG-MRD011A-1 | 19501659 | 990 | 320 | 242 | 0.94 | 576 | 154 | 609 | 232 | 934 | 189 | 755 | 282 | 2019-06-03 17:00 | 208.3 | 13.2 | 980 | Y | 88 | 110 | 103 | 22 |  |  | 31.7 | 68.3 | 1 | 1 | 1 | 1 | 509.05 | 181.38 | 181.38 | 269.08 | 209.16 | 536.43 | 489.52 | 449.13 | [8 empty] | 719.21 | 0.39 | 0.72 | 0.58
138 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | JAMA MASJID | 1120 | MRD013 | 1S-DL-YP-CTC-DDRG-0107-MRD013 | LAXMI INSURANCE:ID | TG-MRD013A-1 | 19504170 | 990 | 320 | 242 | 0.92 | 401 | 125 | 521 | 144 | 602 | 132 | 553 | 71 | 2019-06-01 13:30 | 176.6 | 13.2 | 605 | Y | 97 | 103 | 100 | 6 |  | 0.1 | 16.8 | 83 | 508.17 | 496.47 | 491.47 | 500.17 | 207.05 | 204.05 | 204.05 | 213.35 |  | 14.3 | 15.3 | 1.3 | [8 empty] | 715.22 | 4.38 | 0.41 | 0.4
139 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD001 | 1S-DL-YP-CTC-DDRG-0107-MRD001 | 56 QTR:ID | TG-MRD001A-1 | 19506162 | 630 | 200 | 244 | 0.98 | 238 | 86 | 334 | 76 | 295 | 76 | 298 | 38 | 2019-06-12 00:30 | 90.8 | 4.4 | 372 | R | 113 | 95 | 91 | 22 |  |  |  | 100 | 297.02 | 429.32 | 447 | 397.01 | 408.58 | 281.28 | 281.28 | 313.59 | 5 | [11 empty] | 711 | 9 | 0.53 | 0.38
140 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD002 | 1S-DL-YP-CTC-DDRG-0107-MRD002 | DAG-1:ID | TG-MRD002A-1 | 19500361 | 990 | 320 | 241 | 0.97 | 366 | 114 | 480 | 139 | 581 | 113 | 475 | 104 | 2019-06-03 15:00 | 84.6 | 11 | 598 | Y | 87 | 115 | 98 | 28 |  |  | 3.1 | 96.9 | 472.18 | 409.31 | 454.31 | 436.31 | 242.59 | 296 | 296 | 278.46 |  | 9.46 | [10 empty] | 715.17 | 4.43 | 0.48 | 0.37
141 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD002 | 1S-DL-YP-CTC-DDRG-0107-MRD002 | DAG-1:ID | TG-MRD002A-2 | 19505846 | 990 | 320 | 240 | 0.93 | 360 | 111 | 479 | 132 | 567 | 117 | 503 | 79 | 2019-06-10 14:00 | 121 | 11.2 | 567 | Y | 83 | 102 | 114 | 31 | 0.1 |  | 7.9 | 92 | 640 | 525.11 | 537.11 | 547.11 | 66.26 | 181.15 | 181.15 | 159.15 | [12 empty] | 706.26 | 13.34 | 0.35 | 0.36
142 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD003 | 1S-DL-YP-CTC-DDRG-0107-MRD003 | DAG-2:ID | TG-MRD003A-1 | 19505249 | 990 | 320 | 243 | 0.97 | 533 | 178 | 753 | 186 | 785 | 169 | 717 | 59 | 2019-06-26 16:00 | 142.7 | 5.4 | 816 | Y | 99 | 110 | 91 | 19 |  | 0.1 |  | 99.9 | 329.58 | 279.28 | 374.58 | 320.58 | 238.35 | 255.07 | 255.07 | 246.05 | 139.56 | 173.54 | 102.56 | 141.26 | [8 empty] | 708.29 | 11.31 | 0.44 | 0.54
143 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD003 | 1S-DL-YP-CTC-DDRG-0107-MRD003 | DAG-2:ID | TG-MRD003A-2 | 19500559 | 630 | 200 | 237 | 0.98 | 140 | 56 | 246 | 56 | 246 | 27 | 117 | 129 | 2019-06-03 12:30 | 29.4 | 2.3 | 289 | Y | 118 | 142 | 40 | 102 |  |  |  | 100 | 592 | 538.3 | 719.29 | 694.3 | 127.29 | 180.59 | 180.59 | 24.59 | [12 empty] | 719.29 | 0.31 | 0.47 | 0.22
144 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD003 | 1S-DL-YP-CTC-DDRG-0107-MRD003 | DAG-2:ID | TG-MRD003A-3 | 19506847 | 990 | 320 | 245 | 0.98 | 244 | 69 | 279 | 95 | 385 | 80 | 327 | 92 | 2019-06-26 12:30 | 76.2 | -17.9 | 408 | Y | 93 | 112 | 95 | 19 |  |  | 0.2 | 99.8 | 675.29 | 549.29 | 648.29 | 616.59 | 32.3 | 158.3 | 158.3 | 91 | [12 empty] | 707.59 | 12.01 | 0.48 | 0.25
145 | 2019-06-02 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD004 | 1S-DL-YP-CTC-DDRG-0107-MRD004 | DEEN DAYA UPADHAYA:PACKAGE S/STN | TG-MRD004A-1 | 19501670 | 990 | 320 | 243 | 0.96 | 416 | 134 | 557 | 122 | 507 | 159 | 663 | 138 | 2019-06-13 13:00 | 108.2 | -26.5 | 681 | Y | 89 | 98 | 112 | 23 |  |  | 1.3 | 98.7 | 520.11 | 499.4 | 465.14 | 499.44 | 173.51 | 190.25 | 190.25 | 188.18 | 1 | 4.57 | 58.59 | 7 | [8 empty] | 695.02 | 0.58 | 0.41 | 0.42
146 | 2019-06-03 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD007 | 1S-DL-YP-CTC-DDRG-0107-MRD007 | GIRDHARI LAL:ID | TG-MRD007A-1 | 19500378 | 630 | 200 | 239 | 0.97 | 232 | 91 | 387 | 64 | 270 | 77 | 324 | 101 | 2019-06-27 11:30 | 45.1 | 11 | 439 | R | 114 | 90 | 95 | 24 |  |  | 5.7 | 94.3 | 329.35 | 522.51 | 495.12 | 492.08 | 326.11 | 147.2 | 147.2 | 178.03 | 14.25 | [11 empty] | 670.11 | 1.49 | 0.52 | 0.37
147 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD008 | 1S-DL-YP-CTC-DDRG-0107-MRD008 | GIRDHARI LAL :PACKAGE S/STN | TG-MRD008A-1 | 19500363 | 990 | 320 | 242 | 0.94 | 205 | 68 | 276 | 54 | 221 | 82 | 332 | 96 | 2019-06-11 01:00 | 28 | -60.4 | 342 | B | 97 | 88 | 115 | 27 | 0.1 |  | 79.4 | 20.6 | 708.29 | 719.29 | 502.05 | 713.59 | 11 |  |  | 5.3 | [12 empty] | 719.29 | 0.31 | 0.78 | 0.21
148 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD009 | 1S-DL-YP-CTC-DDRG-0107-MRD009 | HAZ MANJIL:K | TG-MRD009A-1 | 19500366 | 990 | 320 | 249 | 0.97 | 363 | 109 | 453 | 109 | 452 | 145 | 606 | 154 | 2019-06-10 14:00 | 82.4 | -29.4 | 623 | B | 101 | 85 | 114 | 29 |  |  | 0.1 | 99.9 | 242.03 | 485.43 | 176.17 | 395.23 | 474.48 | 231.08 | 231.08 | 321.28 |  |  | 16 | [9 empty] | 716.51 | 3.09 | 0.59 | 0.37
149 | 2019-06-02 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD009 | 1S-DL-YP-CTC-DDRG-0107-MRD009 | HAZ MANJIL:K | TG-MRD009A-2 | 19500367 | 630 | 200 | 243 | 0.97 | 211 | 57 | 240 | 74 | 314 | 80 | 340 | 90 | 2019-06-10 16:00 | 51.1 | 2.8 | 370 | B | 85 | 97 | 119 | 34 |  |  | 18.8 | 81.2 | 615.24 | 518.46 | 493.49 | 516.17 | 79.02 | 175.4 | 175.4 | 178.09 |  |  | 1.3 | [9 empty] | 694.26 | 1.34 | 0.39 | 0.34
150 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD012 | 1S-DL-YP-CTC-DDRG-0107-MRD012 | KOTLA RD.:PL | TG-MRD012A-1 | 19500331 | 630 | 200 | 240 | 0.95 | 535 | 173 | 744 | 189 | 819 | 173 | 749 | 72 | 2019-06-06 14:30 | 187.7 | 21.2 | 819 | Y | 95 | 107 | 99 | 12 |  |  | 6.6 | 93.4 | 27.3 | 5 | 36.3 | 10 | 395.55 | 320.25 | 320.25 | 400.55 | 289 | 372.3 | 309.04 | 299.3 | 7 | 21.3 | 8.26 | 9 |  |  |  |  | 719.25 | 0.35 | 0.51 | 0.85
151 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD014 | 1S-DL-YP-CTC-DDRG-0107-MRD014 | MAHAWAT KHAN:K | TG-MRD014A-1 | 19501681 | 630 | 200 | 242 | 0.97 | 409 | 131 | 538 | 115 | 474 | 162 | 668 | 171 | 2019-06-15 15:00 | 99.8 | 20.2 | 674 | B | 89 | 96 | 115 | 26 |  |  | 2.2 | 97.8 | 45.44 | 8.14 | 1.44 | 4.14 | 500.27 | 523.27 | 523.27 | 508.58 | 169.46 | 184.16 | 402.59 | 202.45 | [8 empty] | 715.57 | 4.03 | 0.56 | 0.65
152 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD015 | 1S-DL-YP-CTC-DDRG-0107-MRD015 | MASS MAILING:ID | TG-MRD015A-1 | 19501669 | 630 | 200 | 246 | 0.97 | 446 | 134 | 567 | 152 | 643 | 160 | 679 | 100 | 2019-06-10 15:30 | 101.2 | 32.2 | 684 | Y | 89 | 112 | 100 | 23 |  | 1.4 | 46.7 | 51.9 | 1.3 | 0.3 | 3.3 |  | 430.05 | 243.36 | 243.36 | 324.36 | 287.54 | 475.23 | 383.25 | 394.53 | [8 empty] | 719.29 | 0.31 | 0.6 | 0.71
153 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD016 | 1S-DL-YP-CTC-DDRG-0107-MRD016 | MATA SUNDARI GURUDWARA:PL | TG-MRD016A-1 | 19500336 | 990 | 320 | 234 | 0.94 | 735 | 241 | 1022 | 224 | 945 | 270 | 1137 | 167 | 2019-06-30 02:00 | 229.6 | 95.7 | 1137 | B | 104 | 92 | 104 | 12 | 0.1 |  | 58.8 | 41.2 |  |  |  |  | 59 | 212.13 | 212.13 | 101 | 660.08 | 506.55 | 609.08 | 618.08 |  |  | 2 | [5 empty] | 719.08 | 0.52 | 0.67 | 0.74
154 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD016 | 1S-DL-YP-CTC-DDRG-0107-MRD016 | MATA SUNDARI GURUDWARA:PL | TG-MRD016A-2 | 19505168 | 990 | 320 | 242 | 0.94 | 517 | 159 | 670 | 169 | 707 | 188 | 791 | 108 | 2019-06-24 15:30 | 182.7 | 82.9 | 803 | B | 97 | 92 | 111 | 19 |  |  | 10.5 | 89.5 |  |  |  |  | 413.08 | 517.08 | 517.08 | 388.38 | 296.58 | 192.58 | 485.24 | 321.28 | [8 empty] | 710.06 | 9.54 | 0.76 | 0.52
155 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD017 | 1S-DL-YP-CTC-DDRG-0107-MRD017 | MATA SUNDARI I/D:ID | TG-MRD017A-1 | 19500362 | 990 | 200 | 241 | 0.96 | 368 | 95 | 405 | 146 | 627 | 127 | 546 | 194 | 2019-06-30 01:30 | 96.1 | 24.8 | 629 | Y | 78 | 119 | 103 | 41 |  |  | 74.4 | 25.6 | 311.02 | 16.3 | 33 | 47 | 407.44 | 658.46 | 658.46 | 671.46 |  | 43.3 | [10 empty] | 718.46 | 1.14 | 0.71 | 0.37
156 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD017 | 1S-DL-YP-CTC-DDRG-0107-MRD017 | MATA SUNDARI I/D:ID | TG-MRD017A-2 | 19505539 | 630 | 200 | 235 | 0.96 | 583 | 343 | 1478 | 115 | 494 | 124 | 511 | 976 | 2019-06-02 06:00 | 227.4 | 37.4 | 1478 | R | 122 | 92 | 86 | 36 | 0.1 | 0.1 | 49.3 | 50.5 |  |  | 1.3 |  | 31.3 | 216.27 | 216.27 | 114.05 | 634.26 | 492.51 | 405.27 | 594.43 | 42.52 |  | 0.3 | 0.3 | 0.3 |  |  |  | 709.18 | 10.42 | 0.53 | 0.92
157 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD018 | 1S-DL-YP-CTC-DDRG-0107-MRD018 | MINTO RD. COMPLEX:ID | TG-MRD018A-1 | 19500321 | 630 | 200 | 232 | 0.99 | 218 | 73 | 302 | 63 | 259 | 82 | 336 | 67 | 2019-06-01 20:00 | 45.1 | -10.1 | 386 | B | 102 | 90 | 108 | 18 |  |  |  | 100 | 116.3 | 209.06 | 46.3 | 88 | 602.58 | 510.22 | 510.22 | 631.28 |  |  | 1 | [9 empty] | 719.28 | 0.32 | 0.71 | 0.35
158 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD018 | 1S-DL-YP-CTC-DDRG-0107-MRD018 | MINTO RD. COMPLEX:ID | TG-MRD018A-2 | 19500352 | 990 | 320 | 237 | 0.98 | 616 | 180 | 717 | 227 | 933 | 209 | 864 | 191 | 2019-06-11 23:30 | 103 | 23.6 | 1016 | Y | 92 | 107 | 101 | 15 | 100 |  |  |  | 184.08 | 110.38 | 168.38 | 144.38 | 362.47 | 392.48 | 392.48 | 382.18 | 172.28 | 215.57 | 190.58 | 192.27 | [8 empty] | 719.23 | 0.37 | 0.51 | 0.62
159 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD019 | 1S-DL-YP-CTC-DDRG-0107-MRD019 | MINTO RD. HOSTEL:ID | TG-MRD019A-1 | 19504852 | 630 | 200 | 237 | 0.95 | 70 | 28 | 116 | 27 | 116 | 15 | 63 | 53 | 2019-06-26 11:00 | 25.8 | 0.5 | 145 | Y | 102 | 139 | 60 | 79 |  |  | 1.9 | 98.1 | 719.16 | 719.16 | 719.16 | 719.16 | [16 empty] | 719.16 | 0.44 | 0.52 | 0.11
160 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD019 | 1S-DL-YP-CTC-DDRG-0107-MRD019 | MINTO RD. HOSTEL:ID | TG-MRD019A-2 | 19505239 | 630 | 200 | 247 | 0.98 | 366 | 108 | 449 | 89 | 370 | 169 | 709 | 307 | 2019-06-02 23:30 | 76.8 | 12 | 709 | B | 108 | 86 | 105 | 22 | 0.1 | 0.1 | 38.4 | 61.5 | 209.51 | 352.57 | 236 | 265.21 | 374.52 | 326.4 | 326.4 | 349.3 | 123.58 | 29.04 | 123.15 | 93.5 |  |  | 0.3 | [5 empty] | 708.41 | 11.19 | 0.45 | 0.58
161 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD020 | 1S-DL-YP-CTC-DDRG-0107-MRD020 | MIRDARD RD I/D:ID | TG-MRD020A-1 | 19500339 | 630 | 200 | 236 | 0.95 | 186 | 68 | 289 | 52 | 220 | 66 | 278 | 64 | 2019-06-06 16:00 | 52 | 6.4 | 312 | B | 118 | 64 | 118 | 54 |  |  | 0.4 | 99.6 | 587.23 | 638.23 | 594.53 | 601.53 | 131.33 | 80.33 | 80.33 | 117.03 | [12 empty] | 718.56 | 1.04 | 0.38 | 0.29
162 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD020 | 1S-DL-YP-CTC-DDRG-0107-MRD020 | MIRDARD RD I/D:ID | TG-MRD020A-2 | 19500340 | 990 | 320 | 235 | 0.99 | 426 | 139 | 602 | 142 | 619 | 146 | 630 | 24 | 2019-06-12 13:30 | 75.8 | -8.1 | 660 | B | 38 | 123 | 139 | 101 |  |  | 0.2 | 99.8 | 636.5 | 316.26 | 117.29 | 560.48 | 78.53 | 386.47 | 386.47 | 149.55 | 3 | 15.3 | 20.3 | 8 | [8 empty] | 718.43 | 1.17 | 0.41 | 0.43
163 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD021 | 1S-DL-YP-CTC-DDRG-0107-MRD021 | POLICE CHOKY L N J P HOSPITAL | TG-MRD021A-1 | 19500382 | 990 | 320 | 248 | 0.97 | 442 | 171 | 691 | 152 | 610 | 119 | 475 | 188 | 2019-06-30 00:30 | 99.4 | 28 | 691 | R | 115 | 108 | 77 | 38 |  |  | 4.4 | 95.6 | 15 | 16 | 50.28 | 26 | 56.26 | 58.26 | 58.26 | 49.26 | 8 | 5 |  | 4 | [8 empty] | 719.26 | 0.34 | 0.56 | 0.45
164 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD022 | 1S-DL-YP-CTC-DDRG-0107-MRD022 | ORIENTAL INSURANCE:PKG | TG-MRD022A-1 | 19500334 | 990 | 320 | 245 | 0.96 | 272 | 93 | 390 | 83 | 349 | 95 | 397 | 45 | 2019-06-07 13:30 | 95.7 | 2.2 | 435 | R | 106 | 102 | 92 | 14 |  | 0.1 | 10.8 | 89.2 | 546.19 | 570.19 | 603.49 | 570.19 | 172.59 | 148.59 | 148.59 | 148.59 | [12 empty] | 719.18 | 0.42 | 0.56 | 0.27
165 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD023 | 1S-DL-YP-CTC-DDRG-0107-MRD023 | PANT QTR:ID | TG-MRD023A-1 | 19500376 | 630 | 200 | 237 | 0.98 | 380 | 136 | 584 | 99 | 427 | 145 | 627 | 183 | 2019-06-02 23:30 | 64.9 | 18.4 | 681 | B | 108 | 76 | 117 | 41 |  |  | 0.1 | 99.9 | 23.15 | 209.34 | 16.29 | 31.15 | 430.43 | 450.16 | 450.16 | 469.38 | 265.22 | 59.3 | 333.5 | 218.27 | [8 empty] | 719.2 | 0.4 | 0.57 | 0.6
166 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD024 | 1S-DL-YP-CTC-DDRG-0107-MRD024 | RAJENDRA BHAWAN:ID | TG-MRD024A-1 | 19501682 | 990 | 320 | 243 | 0.8 | 150 | 43 | 180 | 52 | 217 | 55 | 227 | 43 | 2019-06-17 16:00 | 33.1 | -27.2 | 227 | B | 87 | 106 | 106 | 19 |  | 0.1 |  | 99.9 | 719.29 | 719.29 | 719.29 | 719.29 | [16 empty] | 719.29 | 0.31 | 0.33 | 0.15
167 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD024 | 1S-DL-YP-CTC-DDRG-0107-MRD024 | RAJENDRA BHAWAN:ID | TG-MRD024A-2 | 19501692 | 630 | 200 | 242 | 0.96 | 327 | 99 | 413 | 113 | 466 | 115 | 474 | 58 | 2019-06-12 16:30 | 96.1 | 0.5 | 520 | Y | 90 | 103 | 106 | 16 |  |  | 2.4 | 97.6 | 515.51 | 493.21 | 489.21 | 497.21 | 139.12 | 92.12 | 92.12 | 110.12 | 64.26 | 133.56 | 109.26 | 111.56 | [8 empty] | 719.29 | 0.31 | 0.33 | 0.52
168 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD025 | 1S-DL-YP-CTC-DDRG-0107-MRD025 | ROUSE AVENUE:K | TG-MRD025A-1 | 19500338 | 400 | 120 | 238 | 0.98 | 136 | 40 | 167 | 56 | 237 | 40 | 170 | 68 | 2019-06-03 | 41.1 | -0.6 | 402 | B | 86 | 109 | 105 | 23 |  | 0.1 | 13.4 | 86.5 | 527.05 | 389 | 445.05 | 471.05 | 191.3 | 328.05 | 328.05 | 247.3 |  | 1.3 | 28.3 | [9 empty] | 718.35 | 1.25 | 0.55 | 0.34
169 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD026 | 1S-DL-YP-CTC-DDRG-0107-MRD026 | SHAKTI SADAN:ID | TG-MRD026A-1 | 19501695 | 630 | 200 | 237 | 0.94 | 119 | 36 | 151 | 41 | 173 | 42 | 177 | 24 | 2019-06-25 15:00 | 33.1 | 3.2 | 188 | B | 86 | 106 | 108 | 22 |  |  | 1.7 | 98.3 | 718.32 | 718.32 | 717.32 | 718.32 | [16 empty] | 718.32 | 1.28 | 0.33 | 0.19
170 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD027 | 1S-DL-YP-CTC-DDRG-0107-MRD027 | SHIVAJI PARK:PL | TG-MRD027A-1 | 19500337 | 630 | 200 | 239 | 0.93 | 324 | 103 | 420 | 89 | 360 | 132 | 529 | 149 | 2019-06-14 01:00 | 118.7 | 14.3 | 548 | B | 98 | 84 | 118 | 34 |  | 0.3 | 76.2 | 23.5 | 7 | 20 | 4 | 4.3 | 479.07 | 637.05 | 637.05 | 476.37 | 232.58 | 62 | 362.58 | 237.58 | [8 empty] | 719.05 | 0.55 | 0.69 | 0.51
171 | 2019-06-02 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD028 | 1S-DL-YP-CTC-DDRG-0107-MRD028 | TAGORE RD HOSTEL:ID | TG-MRD028A-1 | 19500344 | 990 | 320 | 242 | 0.99 | 88 | 19 | 82 | 33 | 143 | 36 | 155 | 68 | 2019-06-30 23:30 | 11.8 | 0.7 | 155 | B | 76 | 106 | 118 | 42 |  |  | 1.1 | 98.9 | 695.28 | 695.28 | 695.28 | 695.28 | [16 empty] | 695.28 | 0.32 | 0.42 | 0.09
172 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD028 | 1S-DL-YP-CTC-DDRG-0107-MRD028 | TAGORE RD HOSTEL:ID | TG-MRD028A-2 | 19500345 | 630 | 200 | 242 | 0.97 | 108 | 37 | 152 | 34 | 139 | 38 | 156 | 16 | 2019-06-26 10:30 | 54.3 | 1.4 | 160 | B | 88 | 84 | 128 | 44 |  |  |  | 100 | 719.29 | 719.29 | 719.29 | 719.29 | [16 empty] | 719.29 | 0.31 | 0.44 | 0.17
173 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD054 | 1S-DL-YP-CTC-DDRG-0107-MRD054 | INDIAN HERITAGE D.D.U.MARG: | TG-MRD054A-1 | 19506163 | 100 | 40 | 241 | 0.95 | 36 | 24 | 101 | 12 | 50 | 0 | 0 | 87 | 2019-06-21 18:00 | 13.5 | -6.1 | 101 | R | 157 | 143 | 0 | 157 | 0.5 | 3.5 | 41.1 | 54.8 | 570.12 | 549.38 | 708.45 | 671.15 | 132.03 | 145.07 | 145.07 | 37.3 | 6.3 | 14 | [10 empty] | 708.45 | 11.15 | 0.23 | 0.36
174 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD066 | 1S-DL-YP-CTC-DDRG-0107-MRD066 | MINTO ROAD GRID :ID | TG-MRD066A-1 | 19506280 | 630 | 200 | 242 | 0.98 | 148 | 0 | 0 | 77 | 304 | 71 | 283 | 294 | 2019-06-28 13:00 | 85 | -39.2 | 332 | Y | 0 | 149 | 151 | 151 | 13.2 | 0.3 | 13 | 73.6 | 710.15 | 437.36 | 417.05 | 676.51 |  | 272.39 | 272.39 | 33.24 | [12 empty] | 710.15 | 9.45 | 0.57 | 0.24
175 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD070 | 1S-DL-YP-CTC-DDRG-0107-MRD070 | DDU MARG CPWD FLATS S/STN NO 1 | TG-MRD070A-1 | 19506167 | 630 | 200 | 239 | 0.97 | 48 | 1 | 3 | 4 | 15 | 44 | 187 | 179 | 2019-06-30 23:00 | 2.8 | -9 | 187 | B | 10 | 43 | 247 | 237 | 0.1 | 0.1 | 0.1 | 99.7 | 709.28 | 709.28 | 707.28 | 709.28 | [16 empty] | 709.28 | 10.32 | 0.45 | 0.08
176 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD070 | 1S-DL-YP-CTC-DDRG-0107-MRD070 | DDU MARG CPWD FLATS S/STN NO 1 | TG-MRD070A-2 | 19506168 | 630 | 200 | 233 | 0.99 | 104 | 47 | 193 | 31 | 129 | 26 | 105 | 78 | 2019-06-13 21:30 | 23.4 | -0.2 | 229 | Y | 82 | 124 | 94 | 42 | 0.1 |  | 0.3 | 99.6 | 707.58 | 690.58 | 709.28 | 709.28 | 1.3 | 18.3 | 18.3 | [13 empty] | 709.28 | 10.32 | 0.49 | 0.17
177 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD070 | 1S-DL-YP-CTC-DDRG-0107-MRD070 | DDU MARG CPWD FLATS S/STN NO 1 | TG-MRD070A-3 | 19505554 | 990 | 320 | 245 | 0.98 | 154 | 50 | 206 | 50 | 209 | 54 | 227 | 19 | 2019-06-12 | 29.4 | 3.8 | 236 | B | 98 | 102 | 100 | 4 | 0.1 |  | 1.3 | 98.7 | 709.28 | 709.28 | 709.28 | 709.28 | [16 empty] | 709.28 | 10.32 | 0.53 | 0.16
178 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD071 | 1S-DL-YP-CTC-DDRG-0107-MRD071 | DDU MARG CPWD FLATS S/STN NO 2 | TG-MRD071A-1 | 19506166 | 630 | 200 | 239 | 0.99 | 108 | 58 | 246 | 21 | 89 | 29 | 124 | 143 | 2019-06-13 23:00 | 16.6 | 0.4 | 248 | R | 147 | 70 | 82 | 77 |  |  |  | 100 | 604.59 | 709.59 | 709.59 | 709.59 | 105 | [15 empty] | 709.59 | 10.01 | 0.54 | 0.17
179 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD071 | 1S-DL-YP-CTC-DDRG-0107-MRD071 | DDU MARG CPWD FLATS S/STN NO 2 | TG-MRD071A-2 | 19506165 | 630 | 200 | 239 | 0.99 | 117 | 90 | 424 | 9 | 40 | 18 | 83 | 364 | 2019-06-05 22:00 | 40 | 1.8 | 424 | R | 183 | 43 | 74 | 140 |  | 0.1 | 0.1 | 99.8 | 485.29 | 709.59 | 709.59 | 709.59 | 224 |  |  |  | 0.3 | [11 empty] | 709.59 | 10.01 | 0.49 | 0.18
180 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD071 | 1S-DL-YP-CTC-DDRG-0107-MRD071 | DDU MARG CPWD FLATS S/STN NO 2 | TG-MRD071A-3 | 19506164 | 630 | 200 | 238 | 0.98 | 127 | 31 | 133 | 39 | 164 | 57 | 242 | 97 | 2019-06-05 23:00 | 34.4 | 2.6 | 351 | B | 63 | 81 | 156 | 93 |  | 0.1 | 0.3 | 99.6 | 710 | 710 | 526 | 709.3 |  |  |  | 0.3 | [12 empty] | 710 | 10 | 0.48 | 0.2
181 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD073 | 1S-DL-YP-CTC-DDRG-0107-MRD073 | SHAKOOR KI DANDI P/M | TG-MRD073A-1 | 19506142 | 630 | 200 | 245 | 0.95 | 586 | 206 | 853 | 198 | 824 | 181 | 754 | 88 | 2019-06-24 15:00 | 212.6 | 32.6 | 1052 | Y | 93 | 105 | 102 | 12 | 0.1 | 0.1 | 42.7 | 57.1 | 1.3 | 1.3 | 1 | 1.3 | 14.54 | 4 | 4 | 6.54 | 701.2 | 709.14 | 701.5 | 709.5 | 1 | 3.3 | 5.3 | 0.3 |  | 0.3 |  |  | 718.44 | 1.16 | 0.64 | 0.93
182 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD074 | 1S-DL-YP-CTC-DDRG-0107-MRD074 | LNJP Colony : PKG | TG-MRD074A-1 | 19505579 | 630 | 300 | 250 | 0.93 | 252 | 72 | 291 | 88 | 358 | 92 | 374 | 77 | 2019-06-30 17:30 | 90 | 32.1 | 374 | B | 75 | 117 | 107 | 42 |  |  | 0.1 | 99.9 | 638.31 | 41 | 135.53 | 169.56 | 80.58 | 677.59 | 677.59 | 549.03 |  | 0.3 | 0.3 | 0.3 | [8 empty] | 719.29 | 0.31 | 0.55 | 0.4
183 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD074 | 1S-DL-YP-CTC-DDRG-0107-MRD074 | LNJP Colony : PKG | TG-MRD074A-2 | 19506853 | 990 | 300 | 249 | 0.92 | 481 | 191 | 768 | 159 | 642 | 131 | 522 | 213 | 2019-06-24 15:00 | 189 | 56.1 | 768 | R | 125 | 94 | 81 | 44 |  |  | 10.6 | 89.4 | 1.3 | 6 | 22.3 | 2 | 227.3 | 686 | 686 | 638.3 | 475.58 | 12.58 |  | 64.28 | [8 empty] | 704.58 | 15.02 | 0.69 | 0.49
184 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD075 | 1S-DL-YP-CTC-DDRG-0107-MRD075 | Shakoor ki dandi PLM Tagore Road | TG-MRD075A-1 | 19506279 | 630 | 200 | 240 | 0.94 | 340 | 133 | 560 | 111 | 470 | 95 | 399 | 139 | 2019-06-24 15:00 | 140.4 | 8.6 | 597 | R | 116 | 105 | 80 | 36 |  |  | 2.2 | 97.8 | 0.3 | 0.3 | 1 | 0.3 | 192.53 | 258.14 | 258.14 | 356.44 | 525.16 | 459.55 | 8.3 | 361.25 | [8 empty] | 718.39 | 1.21 | 0.74 | 0.54
185 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD080 | 1S-DL-YP-CTC-DDRG-0107-MRD080 | BJP OFFICE,DDU MARG:OD | TG-MRD080A-1 | 19506143 | 400 | 120 | 252 | 0.98 | 108 | 21 | 87 | 41 | 168 | 45 | 184 | 90 | 2019-06-29 | 23.3 | -6.7 | 184 | B | 24 | 135 | 142 | 118 |  |  | 0.4 | 99.6 | 703.2 | 681.2 | 683.5 | 698.5 |  | 22 | 22 | 4.3 | [12 empty] | 703.2 | 16.4 | 0.18 | 0.27