## Underload DTs
MIS Report of Distribution Transformer - Jun19
Jun19 1120 DARYA GANJ (Underload DTs)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY009 | 1S-DL-YP-CTC-DDRG-0102-DRY009 | CNG:PM | TG-DRY009A-1 | 19500329 | 400 | 120 | 241 | 0.99 | 70 | 25 | 105 | 25 | 103 | 20 | 82 | 22 | 2019-06-07 19:30 | 9.9 | -6.3 | 131 | Y | 91 | 96 | 114 | 23 |  | 0.1 | 0.1 | 99.8 | 717.51 | 708.21 | 717.51 | 717.51 |  | 9.3 | 9.3 | [13 empty] | 717.51 | 2.09 | 0.62 | 0.18
2 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY018 | 1S-DL-YP-CTC-DDRG-0102-DRY018 | GULAB BHAWAN:ID | TG-DRY018A-1 | 19501653 | 990 | 320 | 238 | 0.95 | 147 | 58 | 246 | 43 | 184 | 46 | 193 | 59 | 2019-06-10 13:30 | 39 | -20.6 | 251 | R | 116 | 93 | 91 | 25 | 0.1 |  | 0.2 | 99.7 | 719.25 | 719.25 | 719.25 | 719.25 | [16 empty] | 719.25 | 0.35 | 0.29 | 0.15
3 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY023 | 1S-DL-YP-CTC-DDRG-0102-DRY023 | MADINA LIBRARY:ID | TG-DRY023A-1 | 19500354 | 400 | 120 | 244 | 0.99 | 100 | 39 | 168 | 29 | 127 | 33 | 140 | 36 | 2019-06-27 14:30 | 17.7 | -0.8 | 168 | R | 108 | 113 | 79 | 34 |  | 0.1 | 32.2 | 67.8 | 705.01 | 703.01 | 710.31 | 706.01 | 14.3 | 16.3 | 16.3 | 13.3 | [12 empty] | 719.31 | 0.29 | 0.3 | 0.25
4 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY024 | 1S-DL-YP-CTC-DDRG-0102-DRY024 | MAHAVIR VATIKA:K | TG-DRY024A-1 | 19501678 | 990 | 320 | 246 | 0.95 | 223 | 64 | 264 | 66 | 270 | 93 | 381 | 114 | 2019-06-30 | 78.8 | 14 | 390 | B | 32 | 123 | 145 | 113 |  |  | 0.2 | 99.8 | 686.04 | 673.08 | 508.11 | 698.47 | 31.3 | 44.26 | 44.26 | 18.47 | [12 empty] | 717.34 | 2.26 | 0.54 | 0.23
5 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY026 | 1S-DL-YP-CTC-DDRG-0102-DRY026 | MWK CLY | TG-DRY026A-1 | 19505273 | 400 | 120 | 242 | 0.95 | 44 | 17 | 68 | 26 | 104 | 0 | 0 | 91 | 2019-06-13 19:00 | 36.8 | -0.5 | 104 | Y | 139 | 161 | 1 | 160 | 35.2 | 30.9 | 18.7 | 15.3 | 711.05 | 711.05 | 711.05 | 711.05 | [16 empty] | 711.05 | 8.55 | 0.26 | 0.11
6 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY033 | 1S-DL-YP-CTC-DDRG-0102-DRY033 | SARASWATI SCHOOL:PG | TG-DRY033A-1 | 19506523 | 990 | 320 | 247 | 0.93 | 100 | 36 | 153 | 36 | 150 | 28 | 118 | 34 | 2019-06-29 13:00 | 34.2 | 8 | 194 | R | 104 | 100 | 96 | 8 |  | 0.3 | 0.5 | 99.2 | 694.03 | 694.03 | 694.03 | 694.03 | [16 empty] | 694.03 | 25.57 | 0.62 | 0.1
7 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY077 | 1S-DL-YP-CTC-DDRG-0102-DRY077 | S/STN NO-1 VELODROME ROAD | TG-DRY077A-1 | 19506628 | 100 | 40 | 249 | 0.71 | 16 | 0 | 0 | 7 | 30 | 8 | 32 | 31 | 2019-06-01 19:00 | 7.4 | -6 | 32 | Y | 5 | 121 | 174 | 169 |  |  | 2.5 | 97.5 | 704.33 | 695.33 | 671.03 | 704.33 |  | 9 | 9 | [13 empty] | 704.33 | 15.27 | 0.19 | 0.16
8 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY092 | 1S-DL-YP-CTC-DDRG-0102-DRY092 | PWD OFFICE,UNDER F/O NEAR IG STADIUM:LTC | TG-DRY092A-1 | 19505147 | 400 | 120 | 248 | 0.98 | 71 | 30 | 124 | 20 | 82 | 21 | 85 | 41 | 2019-06-25 16:00 | 15.7 | -0.6 | 128 | Y | 100 | 92 | 108 | 16 |  |  | 0.5 | 99.5 | 707.33 | 707.03 | 702.35 | 708.03 | 0.3 | 1 | 1 | [13 empty] | 708.03 | 11.57 | 0.32 | 0.18
9 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD003 | 1S-DL-YP-CTC-DDRG-0107-MRD003 | DAG-2:ID | TG-MRD003A-2 | 19500559 | 630 | 200 | 237 | 0.98 | 140 | 56 | 246 | 56 | 246 | 27 | 117 | 129 | 2019-06-03 12:30 | 29.4 | 2.3 | 289 | Y | 118 | 142 | 40 | 102 |  |  |  | 100 | 592 | 538.3 | 719.29 | 694.3 | 127.29 | 180.59 | 180.59 | 24.59 | [12 empty] | 719.29 | 0.31 | 0.47 | 0.22
10 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD008 | 1S-DL-YP-CTC-DDRG-0107-MRD008 | GIRDHARI LAL :PACKAGE S/STN | TG-MRD008A-1 | 19500363 | 990 | 320 | 242 | 0.94 | 205 | 68 | 276 | 54 | 221 | 82 | 332 | 96 | 2019-06-11 01:00 | 28 | -60.4 | 342 | B | 97 | 88 | 115 | 27 | 0.1 |  | 79.4 | 20.6 | 708.29 | 719.29 | 502.05 | 713.59 | 11 |  |  | 5.3 | [12 empty] | 719.29 | 0.31 | 0.78 | 0.21
11 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD019 | 1S-DL-YP-CTC-DDRG-0107-MRD019 | MINTO RD. HOSTEL:ID | TG-MRD019A-1 | 19504852 | 630 | 200 | 237 | 0.95 | 70 | 28 | 116 | 27 | 116 | 15 | 63 | 53 | 2019-06-26 11:00 | 25.8 | 0.5 | 145 | Y | 102 | 139 | 60 | 79 |  |  | 1.9 | 98.1 | 719.16 | 719.16 | 719.16 | 719.16 | [16 empty] | 719.16 | 0.44 | 0.52 | 0.11
12 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD024 | 1S-DL-YP-CTC-DDRG-0107-MRD024 | RAJENDRA BHAWAN:ID | TG-MRD024A-1 | 19501682 | 990 | 320 | 243 | 0.8 | 150 | 43 | 180 | 52 | 217 | 55 | 227 | 43 | 2019-06-17 16:00 | 33.1 | -27.2 | 227 | B | 87 | 106 | 106 | 19 |  | 0.1 |  | 99.9 | 719.29 | 719.29 | 719.29 | 719.29 | [16 empty] | 719.29 | 0.31 | 0.33 | 0.15
13 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD026 | 1S-DL-YP-CTC-DDRG-0107-MRD026 | SHAKTI SADAN:ID | TG-MRD026A-1 | 19501695 | 630 | 200 | 237 | 0.94 | 119 | 36 | 151 | 41 | 173 | 42 | 177 | 24 | 2019-06-25 15:00 | 33.1 | 3.2 | 188 | B | 86 | 106 | 108 | 22 |  |  | 1.7 | 98.3 | 718.32 | 718.32 | 717.32 | 718.32 | [16 empty] | 718.32 | 1.28 | 0.33 | 0.19
14 | 2019-06-02 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD028 | 1S-DL-YP-CTC-DDRG-0107-MRD028 | TAGORE RD HOSTEL:ID | TG-MRD028A-1 | 19500344 | 990 | 320 | 242 | 0.99 | 88 | 19 | 82 | 33 | 143 | 36 | 155 | 68 | 2019-06-30 23:30 | 11.8 | 0.7 | 155 | B | 76 | 106 | 118 | 42 |  |  | 1.1 | 98.9 | 695.28 | 695.28 | 695.28 | 695.28 | [16 empty] | 695.28 | 0.32 | 0.42 | 0.09
15 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD028 | 1S-DL-YP-CTC-DDRG-0107-MRD028 | TAGORE RD HOSTEL:ID | TG-MRD028A-2 | 19500345 | 630 | 200 | 242 | 0.97 | 108 | 37 | 152 | 34 | 139 | 38 | 156 | 16 | 2019-06-26 10:30 | 54.3 | 1.4 | 160 | B | 88 | 84 | 128 | 44 |  |  |  | 100 | 719.29 | 719.29 | 719.29 | 719.29 | [16 empty] | 719.29 | 0.31 | 0.44 | 0.17
16 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD054 | 1S-DL-YP-CTC-DDRG-0107-MRD054 | INDIAN HERITAGE D.D.U.MARG: | TG-MRD054A-1 | 19506163 | 100 | 40 | 241 | 0.95 | 36 | 24 | 101 | 12 | 50 | 0 | 0 | 87 | 2019-06-21 18:00 | 13.5 | -6.1 | 101 | R | 157 | 143 | 0 | 157 | 0.5 | 3.5 | 41.1 | 54.8 | 570.12 | 549.38 | 708.45 | 671.15 | 132.03 | 145.07 | 145.07 | 37.3 | 6.3 | 14 | [10 empty] | 708.45 | 11.15 | 0.23 | 0.36
17 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD066 | 1S-DL-YP-CTC-DDRG-0107-MRD066 | MINTO ROAD GRID :ID | TG-MRD066A-1 | 19506280 | 630 | 200 | 242 | 0.98 | 148 | 0 | 0 | 77 | 304 | 71 | 283 | 294 | 2019-06-28 13:00 | 85 | -39.2 | 332 | Y | 0 | 149 | 151 | 151 | 13.2 | 0.3 | 13 | 73.6 | 710.15 | 437.36 | 417.05 | 676.51 |  | 272.39 | 272.39 | 33.24 | [12 empty] | 710.15 | 9.45 | 0.57 | 0.24
18 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD070 | 1S-DL-YP-CTC-DDRG-0107-MRD070 | DDU MARG CPWD FLATS S/STN NO 1 | TG-MRD070A-3 | 19505554 | 990 | 320 | 245 | 0.98 | 154 | 50 | 206 | 50 | 209 | 54 | 227 | 19 | 2019-06-12 | 29.4 | 3.8 | 236 | B | 98 | 102 | 100 | 4 | 0.1 |  | 1.3 | 98.7 | 709.28 | 709.28 | 709.28 | 709.28 | [16 empty] | 709.28 | 10.32 | 0.53 | 0.16
19 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD070 | 1S-DL-YP-CTC-DDRG-0107-MRD070 | DDU MARG CPWD FLATS S/STN NO 1 | TG-MRD070A-1 | 19506167 | 630 | 200 | 239 | 0.97 | 48 | 1 | 3 | 4 | 15 | 44 | 187 | 179 | 2019-06-30 23:00 | 2.8 | -9 | 187 | B | 10 | 43 | 247 | 237 | 0.1 | 0.1 | 0.1 | 99.7 | 709.28 | 709.28 | 707.28 | 709.28 | [16 empty] | 709.28 | 10.32 | 0.45 | 0.08
20 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD070 | 1S-DL-YP-CTC-DDRG-0107-MRD070 | DDU MARG CPWD FLATS S/STN NO 1 | TG-MRD070A-2 | 19506168 | 630 | 200 | 233 | 0.99 | 104 | 47 | 193 | 31 | 129 | 26 | 105 | 78 | 2019-06-13 21:30 | 23.4 | -0.2 | 229 | Y | 82 | 124 | 94 | 42 | 0.1 |  | 0.3 | 99.6 | 707.58 | 690.58 | 709.28 | 709.28 | 1.3 | 18.3 | 18.3 | [13 empty] | 709.28 | 10.32 | 0.49 | 0.17
21 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD071 | 1S-DL-YP-CTC-DDRG-0107-MRD071 | DDU MARG CPWD FLATS S/STN NO 2 | TG-MRD071A-3 | 19506164 | 630 | 200 | 238 | 0.98 | 127 | 31 | 133 | 39 | 164 | 57 | 242 | 97 | 2019-06-05 23:00 | 34.4 | 2.6 | 351 | B | 63 | 81 | 156 | 93 |  | 0.1 | 0.3 | 99.6 | 710 | 710 | 526 | 709.3 |  |  |  | 0.3 | [12 empty] | 710 | 10 | 0.48 | 0.2
22 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD071 | 1S-DL-YP-CTC-DDRG-0107-MRD071 | DDU MARG CPWD FLATS S/STN NO 2 | TG-MRD071A-2 | 19506165 | 630 | 200 | 239 | 0.99 | 117 | 90 | 424 | 9 | 40 | 18 | 83 | 364 | 2019-06-05 22:00 | 40 | 1.8 | 424 | R | 183 | 43 | 74 | 140 |  | 0.1 | 0.1 | 99.8 | 485.29 | 709.59 | 709.59 | 709.59 | 224 |  |  |  | 0.3 | [11 empty] | 709.59 | 10.01 | 0.49 | 0.18
23 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD071 | 1S-DL-YP-CTC-DDRG-0107-MRD071 | DDU MARG CPWD FLATS S/STN NO 2 | TG-MRD071A-1 | 19506166 | 630 | 200 | 239 | 0.99 | 108 | 58 | 246 | 21 | 89 | 29 | 124 | 143 | 2019-06-13 23:00 | 16.6 | 0.4 | 248 | R | 147 | 70 | 82 | 77 |  |  |  | 100 | 604.59 | 709.59 | 709.59 | 709.59 | 105 | [15 empty] | 709.59 | 10.01 | 0.54 | 0.17
24 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD080 | 1S-DL-YP-CTC-DDRG-0107-MRD080 | BJP OFFICE,DDU MARG:OD | TG-MRD080A-1 | 19506143 | 400 | 120 | 252 | 0.98 | 108 | 21 | 87 | 41 | 168 | 45 | 184 | 90 | 2019-06-29 | 23.3 | -6.7 | 184 | B | 24 | 135 | 142 | 118 |  |  | 0.4 | 99.6 | 703.2 | 681.2 | 683.5 | 698.5 |  | 22 | 22 | 4.3 | [12 empty] | 703.2 | 16.4 | 0.18 | 0.27