## Complete Report
MIS Report of Distribution Transformer - Jun19
Jun19 1120 DARYA GANJ (Complete Report)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY077 | 1S-DL-YP-CTC-DDRG-0102-DRY077 | S/STN NO-1 VELODROME ROAD | TG-DRY077A-1 | 19506628 | 100 | 40 | 249 | 0.71 | 16 | 0 | 0 | 7 | 30 | 8 | 32 | 31 | 2019-06-01 19:00 | 7.4 | -6 | 32 | Y | 5 | 121 | 174 | 169 |  |  | 2.5 | 97.5 | 704.33 | 695.33 | 671.03 | 704.33 |  | 9 | 9 | [13 empty] | 704.33 | 15.27 | 0.19 | 0.16
2 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY078 | 1S-DL-YP-CTC-DDRG-0102-DRY078 | S/STN NO-2 VELODROME ROAD | TG-DRY078A-1 | 19506859 | 100 | 40 | 247 | 0.73 | 56 | 28 | 113 | 27 | 109 | 0 | 0 | 111 | 2019-06-24 19:00 | 50.4 | 0 | 116 | Y | 142 | 158 | 0 | 158 |  | 0.2 | 43.5 | 56.2 | 396.14 | 390.14 | 706.14 | 390.14 | 0.3 |  |  | 240.3 | 308 | 313.3 |  | 75.3 | 1.3 | 2.3 | [6 empty] | 706.14 | 13.46 | 0.31 | 0.56
3 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | DARYAGANJ | 1120 | DRY083 | 1S-DL-YP-CTC-DDRG-0102-DRY083 | ROSE BIRD-II | TG-DRY083A-1 | 19504690 | 100 | 40 | 245 | 0.71 | 83 | 28 | 115 | 29 | 118 | 25 | 102 | 15 | 2019-06-06 19:00 | 74.6 | -0.1 | 124 | Y | 100 | 116 | 84 | 32 |  |  | 2.1 | 97.9 | 401.11 | 401.11 | 402.11 | 401.11 | 1 | 1 | 1 | 1 | 311.56 | 304.56 | 286.56 | 314.26 | 4 | 11 |  | 1.3 |  |  |  |  | 718.07 | 1.53 | 0.28 | 0.83
4 | 2019-06-01 | 2019-06-30 23:30 | DARYA GANG | MINTO ROAD | 1120 | MRD024 | 1S-DL-YP-CTC-DDRG-0107-MRD024 | RAJENDRA BHAWAN:ID | TG-MRD024A-1 | 19501682 | 990 | 320 | 243 | 0.8 | 150 | 43 | 180 | 52 | 217 | 55 | 227 | 43 | 2019-06-17 16:00 | 33.1 | -27.2 | 227 | B | 87 | 106 | 106 | 19 |  | 0.1 |  | 99.9 | 719.29 | 719.29 | 719.29 | 719.29 | [16 empty] | 719.29 | 0.31 | 0.33 | 0.15