## Complete Report
MIS Report of Distribution Transformer - Jun19
Jun19 1130 PAHAR GANJ (Complete Report)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR001 | 1S-DL-YP-CTC-DPHG-0112-BGR001 | CANE MARKET:PL | TG-BGR001A-1 | 19506099 | 990 | 320 | 239 | 0.98 | 891 | 164 | 696 | 281 | 1307 | 446 | 1982 | 1114 | 2019-06-29 17:00 | 257.3 | 16.6 | 1982 | B | 90 | 91 | 119 | 29 | 0.1 |  | 24.9 | 75 | 327.27 | 428.27 | 344.57 | 402.27 | 178.12 | 70.14 | 70.14 | 80.14 | 190.09 | 196.37 | 126.18 | 212.37 |  | 0.3 | 97.49 | 0.3 |  |  | 2 |  | 695.48 | 24.12 | 0.34 | 0.9
2 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR002 | 1S-DL-YP-CTC-DPHG-0112-BGR002 | GALI ZAMEER P/M:PM | TG-BGR002A-1 | 19500078 | 400 | 120 | 243 | 0.96 | 271 | 85 | 357 | 85 | 359 | 100 | 421 | 63 | 2019-06-13 15:30 | 67.9 | 18.2 | 455 | Y | 92 | 107 | 101 | 15 |  | 0.1 | 58.2 | 41.6 | 2 |  |  | 0.3 | 175.3 | 42.3 | 42.3 | 75 | 540.34 | 674.04 | 606.34 | 642.34 |  | 1.3 | [6 empty] | 718.04 | 1.56 | 0.74 | 0.68
3 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR002 | 1S-DL-YP-CTC-DPHG-0112-BGR002 | GALI ZAMEER P/M:PM | TG-BGR002A-2 | 19500056 | 400 | 120 | 245 | 0.95 | 125 | 32 | 133 | 55 | 227 | 38 | 158 | 84 | 2019-06-06 00:30 | 40.8 | 6.3 | 241 | Y | 98 | 129 | 73 | 56 |  | 0.1 | 42.7 | 57.2 | 425.19 | 196.13 | 627.34 | 427.04 | 292.43 | 512.49 | 512.49 | 290.58 |  | 9 | [10 empty] | 718.02 | 1.58 | 0.62 | 0.31
4 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR003 | 1S-DL-YP-CTC-DPHG-0112-BGR003 | GALI BAHUJI: K | TG-BGR003A-1 | 19506463 | 990 | 320 | 244 | 0.96 | 869 | 295 | 1212 | 246 | 1006 | 328 | 1340 | 292 | 2019-06-12 17:30 | 265 | 54.7 | 1354 | B | 104 | 90 | 105 | 15 | 0.1 |  | 13.9 | 86 | 1 | 1 |  |  | 65 | 157 | 157 | 101 | 609.39 | 538.09 | 543.39 | 586.39 | 20.3 |  | 62.3 | 8.3 |  |  |  |  | 696.09 | 23.51 | 0.62 | 0.88
5 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR004 | 1S-DL-YP-CTC-DPHG-0112-BGR004 | MODEL BASTI:PL | TG-BGR004A-1 | 19503551 | 400 | 120 | 247 | 0.97 | 220 | 46 | 190 | 78 | 326 | 96 | 404 | 187 | 2019-06-30 01:00 | 62.7 | 12.7 | 404 | B | 70 | 99 | 131 | 61 |  | 3.1 | 81.4 | 15.5 | 55 | 1 |  | 0.3 | 662.12 | 467.12 | 467.12 | 458.15 | 1.3 | 250.3 | 613.12 | 259.57 | [8 empty] | 718.42 | 1.18 | 0.69 | 0.55
6 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR004 | 1S-DL-YP-CTC-DPHG-0112-BGR004 | MODEL BASTI:PL | TG-BGR004A-2 | 19503047 | 990 | 320 | 239 | 0.97 | 804 | 287 | 1192 | 245 | 1026 | 272 | 1139 | 146 | 2019-06-26 16:00 | 225.2 | 61.8 | 1221 | B | 104 | 98 | 98 | 6 |  |  | 50.4 | 49.6 |  |  |  |  | 16.11 | 36.3 | 36.3 | 23.11 | 692.01 | 682.12 | 642.01 | 693.01 | 10.3 |  | 10.3 | 2.3 |  |  |  |  | 718.42 | 1.18 | 0.69 | 0.81
7 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR005 | 1S-DL-YP-CTC-DPHG-0112-BGR005 | CHIMNI MIL PL/M:PL | TG-BGR005A-1 | 19503586 | 990 | 320 | 230 | 0.99 | 861 | 296 | 1304 | 286 | 1249 | 278 | 1226 | 69 | 2019-06-25 17:30 | 78 | -85.4 | 1387 | R | 103 | 97 | 100 | 6 |  |  | 27.8 | 72.2 |  | 0.3 | 0.3 |  | 112.3 | 185.57 | 185.57 | 117.3 | 524.02 | 452.22 | 598 | 547.19 | 79.39 | 77.22 | 17.41 | 51.22 |  |  |  |  | 716.11 | 3.49 | 0.64 | 0.87
8 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR005 | 1S-DL-YP-CTC-DPHG-0112-BGR005 | CHIMNI MIL PL/M:PL | TG-BGR005A-2 | 19500047 | 990 | 320 | 227 | 0.96 | 839 | 267 | 1199 | 289 | 1291 | 282 | 1269 | 84 | 2019-06-02 04:30 | 200.9 | 68.4 | 1291 | Y | 102 | 93 | 105 | 12 |  | 0.1 | 43.9 | 56 |  |  |  |  | 4.3 | 32.15 | 32.15 | 3 | 692.25 | 665.14 | 699.29 | 706.46 | 18.3 | 17.56 | 13.26 | 5.39 |  |  |  |  | 715.25 | 4.35 | 0.74 | 0.85
9 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR006 | 1S-DL-YP-CTC-DPHG-0112-BGR006 | CHIMNI MIL KIOSK:K | TG-BGR006A-1 | 19500185 | 990 | 320 | 234 | 0.96 | 460 | 180 | 757 | 107 | 451 | 173 | 722 | 291 | 2019-06-03 06:00 | 119.2 | 58.9 | 852 | R | 115 | 83 | 102 | 32 |  |  | 50.1 | 49.9 |  | 39 | 1.3 |  | 369.03 | 637.1 | 637.1 | 612.4 | 349.37 | 42.3 | 177 | 106 | [8 empty] | 718.4 | 1.2 | 0.74 | 0.46
10 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR006 | 1S-DL-YP-CTC-DPHG-0112-BGR006 | CHIMNI MIL KIOSK:K | TG-BGR006A-2 | 19504842 | 990 | 320 | 242 | 0.95 | 532 | 155 | 623 | 224 | 919 | 154 | 631 | 292 | 2019-06-03 04:30 | 155.3 | 76.5 | 927 | Y | 90 | 112 | 99 | 22 | 13.6 | 85.2 | 1.2 | [5 empty] | 517.2 | 219.49 | 219.49 | 299.2 | 201.45 | 499.16 | 339.15 | 419.45 | [8 empty] | 719.05 | 0.55 | 0.75 | 0.54
11 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR007 | 1S-DL-YP-CTC-DPHG-0112-BGR007 | BG ROAD DISP:PM | TG-BGR007A-1 | 19506186 | 990 | 320 | 232 | 0.95 | 631 | 310 | 1403 | 180 | 791 | 140 | 605 | 724 | 2019-06-11 04:30 | 227.5 | 40 | 1403 | R | 110 | 103 | 88 | 22 | 6.5 | 0.4 | 11 | 82.2 | 26.19 | 0.3 | 0.3 | 0.3 | 42.25 | 85.21 | 85.21 | 125.55 | 501.29 | 484.52 | 247.4 | 444.18 | 0.3 | [7 empty] | 689.36 | 30.24 | 0.69 | 0.64
12 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR007 | 1S-DL-YP-CTC-DPHG-0112-BGR007 | BG ROAD DISP:PM | TG-BGR007A-2 | 19505218 | 990 | 320 | 242 | 0.96 | 390 | 148 | 638 | 91 | 379 | 151 | 639 | 260 | 2019-06-11 05:00 | 136.6 | 22.4 | 771 | B | 90 | 82 | 129 | 47 | 0.3 | 0.1 | 0.5 | 99.1 | 62.15 | 138.48 | 3.3 | 13.3 | 635.05 | 559.32 | 559.32 | 684.5 | 1 |  | 148.22 | [9 empty] | 698.2 | 21.4 | 0.7 | 0.39
13 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR007 | 1S-DL-YP-CTC-DPHG-0112-BGR007 | BG ROAD DISP:PM | TG-BGR007A-3 | 19506100 | 630 | 200 | 241 | 0.95 | 365 | 82 | 345 | 197 | 853 | 86 | 365 | 498 | 2019-06-14 22:30 | 142 | 29.4 | 853 | Y | 95 | 117 | 89 | 28 | 0.1 | 0.2 | 85.2 | 14.4 | 1.3 | 0.3 | 0.3 | 0.3 | 310.46 | 58.3 | 58.3 | 156.54 | 377.4 | 629.56 | 253.11 | 532.32 |  | 1 | [6 empty] | 689.56 | 30.04 | 0.75 | 0.58
14 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR008 | 1S-DL-YP-CTC-DPHG-0112-BGR008 | CHOWK KISHAN GANJ:PL | TG-BGR008A-1 | 19504226 | 990 | 200 | 237 | 0.96 | 702 | 239 | 993 | 206 | 855 | 258 | 1066 | 186 | 2019-06-05 03:00 | 178.9 | 87.9 | 1126 | B | 99 | 91 | 110 | 19 | 0.1 | 7.1 | 74.6 | 18.2 |  |  |  |  | 185.3 | 197 | 197 | 101 | 533.19 | 521.49 | 672.49 | 617.49 | [8 empty] | 718.49 | 1.11 | 0.69 | 0.71
15 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR009 | 1S-DL-YP-CTC-DPHG-0112-BGR009 | SHIVAJI ROAD:PL | TG-BGR009A-1 | 19504814 | 990 | 320 | 243 | 0.97 | 695 | 183 | 768 | 251 | 1050 | 261 | 1081 | 299 | 2019-06-30 01:00 | 163.4 | 79.5 | 1081 | B | 87 | 104 | 109 | 22 |  |  | 72.6 | 27.4 |  |  |  |  | 172.58 | 33 | 33 | 43 | 545.51 | 685.49 | 704.49 | 675.49 | [8 empty] | 718.49 | 1.11 | 0.74 | 0.7
16 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR010 | 1S-DL-YP-CTC-DPHG-0112-BGR010 | GALI BAHUJI:PM | TG-BGR010A-1 | 19504361 | 990 | 320 | 251 | 0.96 | 604 | 259 | 1032 | 186 | 736 | 160 | 626 | 364 | 2019-06-15 15:00 | 178.8 | 36.8 | 1061 | R | 118 | 98 | 84 | 34 |  | 0.1 | 50.8 | 49.2 | 2 | 4 | 63 | 8 | 386 | 514.3 | 514.3 | 482.3 | 332 | 201.3 | 94.3 | 229.3 | [8 empty] | 720 | 0 | 0.6 | 0.61
17 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR011 | 1S-DL-YP-CTC-DPHG-0112-BGR011 | TOKARI WALAN OLD:PL | TG-BGR011A-1 | 19506183 | 990 | 320 | 238 | 0.97 | 670 | 173 | 730 | 218 | 921 | 279 | 1177 | 388 | 2019-06-29 17:30 | 168 | 57 | 1212 | B | 75 | 100 | 125 | 50 |  | 0.1 | 0.4 | 99.6 |  |  |  |  | 522.26 | 90 | 90 | 84 | 166.12 | 598.38 | 675.08 | 604.38 |  |  | 8 | [5 empty] | 688.38 | 31.22 | 0.7 | 0.68
18 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR012 | 1S-DL-YP-CTC-DPHG-0112-BGR012 | TOKARI WALAN NEW:PL | TG-BGR012A-1 | 19500048 | 400 | 120 | 245 | 0.97 | 233 | 17 | 70 | 34 | 137 | 181 | 750 | 649 | 2019-06-15 08:30 | 58.2 | 11.3 | 750 | B | 85 | 130 | 86 | 45 |  | 11.7 | 77.2 | 11.2 | 295.33 | 8.22 | 312.52 | 138.52 | 387.47 | 477.3 | 477.3 | 527.58 | 32.48 | 230.16 | 63.18 | 49.18 | [6 empty] | 1 |  | 716.08 | 3.52 | 0.48 | 0.58
19 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR013 | 1S-DL-YP-CTC-DPHG-0112-BGR013 | FOOTA ROAD KIOSK:K | TG-BGR013A-1 | 19504867 | 990 | 320 | 241 | 0.97 | 996 | 313 | 1331 | 405 | 1735 | 278 | 1167 | 506 | 2019-06-04 15:30 | 187.7 | 53.7 | 1769 | Y | 92 | 124 | 84 | 40 |  | 1.6 | 93.4 | 5 | 2 |  | 43 |  | 464.3 | 228 | 228 | 455 | 173.57 | 292.18 | 209.08 | 135.27 | 76.41 | 88.2 | 32 | 126.11 |  | 108.3 |  | 0.3 | 717.08 | 2.52 | 0.47 | 1.01
20 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR014 | 1S-DL-YP-CTC-DPHG-0112-BGR014 | DEPUTY GANJ OLD:PL | TG-BGR014A-1 | 19505198 | 630 | 200 | 245 | 0.97 | 375 | 94 | 382 | 143 | 587 | 139 | 576 | 200 | 2019-06-14 17:00 | 94 | 7.6 | 644 | B | 69 | 113 | 118 | 49 | 0.3 | 3.7 | 91.5 | 4.6 | 479 | 290.3 | 256.3 | 425.3 | 94 | 216 | 216 | 89.3 | 123.3 | 190 | 202.3 | 181.3 | [8 empty] | 696.3 | 23.3 | 0.44 | 0.6
21 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR015 | 1S-DL-YP-CTC-DPHG-0112-BGR015 | DEPUTY GANJ NEW:PM | TG-BGR015A-1 | 19504861 | 400 | 120 | 245 | 0.97 | 131 | 49 | 204 | 48 | 197 | 34 | 138 | 63 | 2019-06-13 16:30 | 31.2 | 2.8 | 237 | R | 125 | 99 | 76 | 49 |  | 0.1 | 42.1 | 57.8 | 250.3 | 510 | 582.3 | 500 | 468 | 210 | 210 | 220 | 1.3 | [11 empty] | 720 | 0 | 0.55 | 0.33
22 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR015 | 1S-DL-YP-CTC-DPHG-0112-BGR015 | DEPUTY GANJ NEW:PM | TG-BGR015A-2 | 19500097 | 400 | 120 | 244 | 0.96 | 173 | 46 | 195 | 56 | 229 | 71 | 296 | 89 | 2019-06-29 17:00 | 51.9 | 11.3 | 330 | B | 70 | 90 | 140 | 70 | 19 | 72.6 | 3.2 | 5.1 | 473.3 | 224 | 26.3 | 143 | 246.3 | 474.3 | 474.3 | 566 |  | 21.3 | 318 | 11 | [8 empty] | 720 | 0 | 0.62 | 0.43
23 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR016 | 1S-DL-YP-CTC-DPHG-0112-BGR016 | GALI NEEM WALI:K | TG-BGR016A-1 | 19500079 | 990 | 320 | 241 | 0.96 | 850 | 291 | 1200 | 267 | 1110 | 292 | 1220 | 101 | 2019-06-30 18:00 | 189.2 | 71.4 | 1220 | R | 98 | 100 | 102 | 4 |  |  | 43.5 | 56.5 | 1 |  |  |  | 59 | 34 | 34 | 34 | 641.38 | 677.38 | 670.35 | 677.08 | 16.3 | 6.3 | 14 | 7 |  |  |  |  | 718.08 | 1.52 | 0.66 | 0.86
24 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR017 | 1S-DL-YP-CTC-DPHG-0112-BGR017 | MATA WALI KIOSK:K | TG-BGR017A-1 | 19500059 | 990 | 320 | 238 | 0.97 | 480 | 180 | 743 | 159 | 642 | 141 | 591 | 134 | 2019-06-15 16:00 | 114.8 | 31.6 | 817 | R | 98 | 105 | 97 | 8 | 61.5 | 28.3 | 10.2 |  | 176.32 | 37 | 70.3 | 69 | 384.46 | 571.13 | 571.13 | 541.13 | 156.57 | 110.02 | 11 | 108.02 | [8 empty] | 718.15 | 1.45 | 0.61 | 0.49
25 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR017 | 1S-DL-YP-CTC-DPHG-0112-BGR017 | MATA WALI KIOSK:K | TG-BGR017A-2 | 19503798 | 630 | 200 | 244 | 0.95 | 232 | 81 | 330 | 79 | 317 | 72 | 289 | 36 | 2019-06-15 15:30 | 80.5 | 28.1 | 377 | Y | 103 | 98 | 99 | 5 |  | 1 | 45.5 | 53.6 | 40.29 | 73.3 | 38 | 30 | 677.19 | 638.48 | 638.48 | 689.18 | 1.3 | 7 | [10 empty] | 719.18 | 0.42 | 0.73 | 0.37
26 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR018 | 1S-DL-YP-CTC-DPHG-0112-BGR018 | DEPUTY GANJ KIOSK:K | TG-BGR018A-1 | 19500099 | 990 | 320 | 240 | 0.97 | 565 | 183 | 767 | 188 | 794 | 193 | 814 | 40 | 2019-06-12 15:30 | 138.4 | 22.8 | 891 | Y | 90 | 115 | 96 | 25 |  | 0.2 | 10.7 | 89.1 | 255 | 36.3 | 207 | 112.3 | 325.3 | 514 | 514 | 448 | 139.3 | 169.3 | 166.3 | 159.3 | [8 empty] | 720 | 0 | 0.52 | 0.57
27 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR019 | 1S-DL-YP-CTC-DPHG-0112-BGR019 | AJAD MKT:PKG | TG-BGR019A-1 | 19500176 | 990 | 320 | 244 | 0.98 | 431 | 130 | 539 | 162 | 671 | 140 | 572 | 119 | 2019-06-12 15:30 | 81 | 14.7 | 713 | B | 87 | 109 | 104 | 22 |  |  | 23.4 | 76.6 | 74.3 | 6 | 4.3 | 7 | 644.3 | 631.3 | 631.3 | 701.3 | 1 | 82.3 | 63 | 11.3 | [8 empty] | 720 | 0 | 0.71 | 0.44
28 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR019 | 1S-DL-YP-CTC-DPHG-0112-BGR019 | AJAD MKT:PKG | TG-BGR019A-2 | 19505639 | 990 | 300 | 245 | 0.97 | 514 | 168 | 713 | 170 | 727 | 176 | 746 | 29 | 2019-06-10 15:00 | 145.2 | 26.1 | 890 | Y | 102 | 99 | 99 | 3 | 19.1 | 26.6 | 36.5 | 17.8 | 171 | 213.3 | 275 | 210.3 | 396 | 381.3 | 381.3 | 364.3 | 139 | 111 | 139 | 131 | [8 empty] | 706 | 14 | 0.52 | 0.52
29 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR020 | 1S-DL-YP-CTC-DPHG-0112-BGR020 | AHATA KIDARA UNIT I:PM | TG-BGR020A-1 | 19506187 | 400 | 120 | 249 | 0.94 | 463 | 238 | 1022 | 119 | 483 | 105 | 456 | 553 | 2019-06-01 19:00 | 176.9 | 74 | 1022 | R | 106 | 109 | 85 | 24 | 0.4 | 0.4 | 43.6 | 55.7 | [8 empty] | 115.57 | 52 | 468.2 | 155.57 | 327.56 | 391.27 | 221 | 417.53 | 251.57 | 252.23 | 6.3 | 122 | 695.5 | 24.1 | 0.77 | 1.16
30 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR021 | 1S-DL-YP-CTC-DPHG-0112-BGR021 | FILMISTAN:ID | TG-BGR021A-1 | 19505640 | 990 | 300 | 247 | 0.99 | 767 | 254 | 1035 | 254 | 1039 | 260 | 1051 | 14 | 2019-06-29 16:00 | 144.3 | 14.1 | 1241 | R | 104 | 98 | 98 | 6 |  | 0.3 | 62.2 | 37.5 |  |  |  |  | 38.58 | 96.14 | 96.14 | 69.18 | 673.14 | 618.28 | 592.28 | 645.24 | 2.3 |  | 1 | [5 empty] | 714.42 | 5.18 | 0.7 | 0.78
31 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR022 | 1S-DL-YP-CTC-DPHG-0112-BGR022 | B. G. ROAD COMP CTR:ID | TG-BGR022A-1 | 19500084 | 990 | 320 | 236 | 0.98 | 544 | 194 | 849 | 167 | 738 | 183 | 798 | 96 | 2019-06-01 17:00 | 108.9 | 21.3 | 979 | R | 119 | 85 | 95 | 34 |  | 0.2 | 18.6 | 81.2 | 8 | 104.09 | 56.3 | 34 | 368.32 | 585.05 | 585.05 | 585.55 | 338.42 | 26 | 83.19 | 95.19 | [8 empty] | 715.14 | 4.46 | 0.58 | 0.55
32 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR022 | 1S-DL-YP-CTC-DPHG-0112-BGR022 | B. G. ROAD COMP CTR:ID | TG-BGR022A-2 | 19500091 | 990 | 320 | 235 | 0.97 | 541 | 148 | 640 | 170 | 729 | 223 | 966 | 292 | 2019-06-30 01:30 | 121.4 | 43.4 | 1013 | B | 100 | 92 | 108 | 16 |  | 0.1 | 23.2 | 76.8 | 1 | 24.3 | 0.3 | 0.3 | 422.28 | 449.59 | 449.59 | 412.59 | 295.11 | 244.1 | 415.09 | 305.1 | [8 empty] | 718.39 | 1.21 | 0.71 | 0.55
33 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR022 | 1S-DL-YP-CTC-DPHG-0112-BGR022 | B. G. ROAD COMP CTR:ID | TG-BGR022A-3 | 19500092 | 990 | 320 | 240 | 0.98 | 628 | 175 | 747 | 182 | 780 | 270 | 1150 | 388 | 2019-06-30 23:30 | 129.5 | 28 | 1161 | B | 89 | 94 | 116 | 27 |  | 0.4 | 47.7 | 51.9 | 12 | 14 |  | 3 | 483.38 | 413.31 | 413.31 | 353.49 | 218.13 | 286.2 | 491.56 | 357.02 |  |  | 1.3 | [5 empty] | 713.51 | 6.09 | 0.63 | 0.63
34 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR022 | 1S-DL-YP-CTC-DPHG-0112-BGR022 | B. G. ROAD COMP CTR:ID | TG-BGR022A-4 | 19505002 | 630 | 200 | 240 | 0.96 | 511 | 181 | 749 | 172 | 707 | 159 | 656 | 80 | 2019-06-11 03:30 | 126.5 | 57.5 | 819 | R | 108 | 102 | 89 | 19 |  |  | 8.6 | 91.4 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 0.3 | 0.3 | 1.3 | 670.23 | 695.46 | 673.51 | 712.16 | 43.23 | 18.3 |  | 1 |  |  |  |  | 715.16 | 4.44 | 0.73 | 0.81
35 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR024 | 1S-DL-YP-CTC-DPHG-0112-BGR024 | TIKONA PARK:PG | TG-BGR024A-1 | 19500163 | 990 | 320 | 244 | 0.96 | 395 | 167 | 698 | 110 | 450 | 119 | 489 | 231 | 2019-06-04 15:30 | 110.4 | 53.7 | 761 | R | 115 | 91 | 94 | 24 |  | 0.8 | 38.7 | 60.4 | 4.3 | 32 | 27.3 | 11.3 | 577.58 | 685.36 | 685.36 | 707.06 | 136.08 | 1 | 1 | [9 empty] | 718.36 | 1.24 | 0.74 | 0.4
36 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR024 | 1S-DL-YP-CTC-DPHG-0112-BGR024 | TIKONA PARK:PG | TG-BGR024A-2 | 19506262 | 400 | 120 | 240 | 0.98 | 84 | 20 | 83 | 28 | 120 | 36 | 156 | 63 | 2019-06-11 14:30 | 23.6 | 0.8 | 164 | B | 54 | 114 | 132 | 78 | 0.3 |  | 34.3 | 65.5 | 704.49 | 645.19 | 588.49 | 700.49 |  | 59.3 | 59.3 | 4 | [12 empty] | 704.49 | 15.11 | 0.36 | 0.21
37 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR025 | 1S-DL-YP-CTC-DPHG-0112-BGR025 | LIBRARY ROAD:PL | TG-BGR025A-1 | 19500077 | 630 | 200 | 238 | 0.97 | 338 | 137 | 589 | 128 | 546 | 72 | 308 | 262 | 2019-06-05 14:00 | 78.7 | 32.2 | 630 | Y | 116 | 118 | 67 | 51 |  |  | 0.7 | 99.3 | 2 | 2 | 143.3 | 4.3 | 298 | 265.3 | 265.3 | 471 | 420 | 452.3 |  | 244.3 | [8 empty] | 720 | 0 | 0.68 | 0.54
38 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR026 | 1S-DL-YP-CTC-DPHG-0112-BGR026 | PATHAR WALAN P/M:PM | TG-BGR026A-1 | 19506455 | 400 | 120 | 249 | 0.98 | 224 | 60 | 250 | 77 | 318 | 87 | 360 | 97 | 2019-06-29 16:00 | 47.9 | -14.8 | 405 | B | 79 | 104 | 118 | 39 | 0.1 |  | 10.3 | 89.6 | 498.57 | 454.57 | 464.27 | 467.57 | 155 | 85.3 | 85.3 | 73 | 50.3 | 164 | 194 | 163.3 | [8 empty] | 704.27 | 15.33 | 0.35 | 0.56
39 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR027 | 1S-DL-YP-CTC-DPHG-0112-BGR027 | JHABBAR MAL P/M:PG | TG-BGR027A-1 | 19504832 | 990 | 320 | 243 | 0.98 | 900 | 309 | 1305 | 285 | 1202 | 306 | 1289 | 96 | 2019-06-25 15:30 | 181.8 | -0.7 | 1337 | B | 103 | 97 | 100 | 6 |  | 0.1 | 8.9 | 90.9 | 432.57 | 437.57 | 452.27 | 440.57 | 59.36 | 60.36 | 60.36 | 53.36 | 149.22 | 161.25 | 121.11 | 140.22 | 74.3 | 56.27 | 101.11 | 81.3 |  |  |  |  | 716.25 | 3.35 | 0.31 | 0.91
40 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN001 | 1S-DL-YP-CTC-DPHG-0113-CHN001 | ARAM BAGH S/S NO. 1:ID | TG-CHN001A-1 | 19500062 | 990 | 320 | 238 | 0.97 | 594 | 261 | 1119 | 193 | 840 | 140 | 600 | 450 | 2019-06-30 | 146.5 | 49.3 | 1208 | R | 124 | 97 | 79 | 45 | 0.6 | 0.2 | 45.8 | 53.4 | 0.3 | 6.3 | 32.3 | 1 | 227.25 | 428.43 | 428.43 | 398.55 | 488.11 | 284.23 | 76 | 319.41 | 3.3 | [7 empty] | 719.36 | 0.24 | 0.65 | 0.6
41 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN001 | 1S-DL-YP-CTC-DPHG-0113-CHN001 | ARAM BAGH S/S NO. 1:ID | TG-CHN001A-2 | 19500030 | 990 | 320 | 251 | 0.97 | 314 | 69 | 288 | 133 | 544 | 111 | 463 | 227 | 2019-06-30 23:30 | 61.8 | 11.8 | 564 | B | 60 | 124 | 115 | 64 | 19.6 | 77.6 | 2.8 |  | 689.04 | 372.53 | 442.47 | 513.34 | 29 | 344.11 | 344.11 | 204.3 |  | 1 | 1.3 | [9 empty] | 718.04 | 1.56 | 0.52 | 0.32
42 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN002 | 1S-DL-YP-CTC-DPHG-0113-CHN002 | ARAM BAGH S/S NO. 2:ID | TG-CHN002A-1 | 19500055 | 990 | 320 | 240 | 0.98 | 353 | 83 | 341 | 127 | 529 | 144 | 597 | 229 | 2019-06-12 | 58.9 | 4.4 | 645 | B | 73 | 112 | 114 | 41 |  |  | 17 | 83 | 600.44 | 323.29 | 319.22 | 397.25 | 116.3 | 376.45 | 376.45 | 319.49 |  | 17 | 48.3 | [9 empty] | 717.14 | 2.46 | 0.56 | 0.36
43 | 2019-06-05 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN002 | 1S-DL-YP-CTC-DPHG-0113-CHN002 | ARAM BAGH S/S NO. 2:ID | TG-CHN002A-2 | 19504888 | 990 | 320 | 247 | 0.96 | 188 | 55 | 213 | 71 | 276 | 63 | 245 | 54 | 2019-06-06 06:30 | 106 | 0.7 | 276 | Y | 88 | 109 | 104 | 21 |  |  | 0.2 | 99.8 | 621.57 | 619.57 | 621.57 | 621.57 |  | 2 | 2 | [13 empty] | 621.57 | 2.03 | 0.31 | 0.19
44 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN003 | 1S-DL-YP-CTC-DPHG-0113-CHN003 | ARAM BAGH S/ST NO. 3:ID | TG-CHN003A-1 | 19500089 | 990 | 320 | 244 | 0.97 | 545 | 169 | 706 | 158 | 657 | 219 | 883 | 206 | 2019-06-05 14:00 | 161.2 | 30.9 | 933 | R | 107 | 91 | 102 | 16 | 99.5 | 0.5 |  |  | 3.31 | 8 | 6.3 | 3.3 | 361.14 | 548.22 | 548.22 | 390.45 | 353.51 | 162.14 | 343.05 | 324.21 | [8 empty] | 718.36 | 1.24 | 0.69 | 0.55
45 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN004 | 1S-DL-YP-CTC-DPHG-0113-CHN004 | ARAM BAGH S/ST. NO. 4:ID | TG-CHN004A-1 | 19506451 | 990 | 300 | 245 | 0.97 | 385 | 107 | 456 | 123 | 516 | 154 | 651 | 173 | 2019-06-29 23:30 | 91.8 | 29.4 | 690 | B | 81 | 98 | 120 | 39 | 0.3 | 0.1 | 6.1 | 93.6 | 349.51 | 194.57 | 64.57 | 159.32 | 367.58 | 522.22 | 522.22 | 558.47 | 0.3 | 1 | 96.54 | [9 empty] | 718.19 | 1.41 | 0.65 | 0.39
46 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN005 | 1S-DL-YP-CTC-DPHG-0113-CHN005 | CHITRA GUPTA RD.:K | TG-CHN005A-1 | 19504672 | 990 | 320 | 238 | 0.97 | 667 | 213 | 908 | 214 | 910 | 239 | 1020 | 111 | 2019-06-12 15:30 | 150.1 | 51.5 | 1072 | B | 96 | 95 | 109 | 14 |  |  | 3.7 | 96.3 |  |  |  |  | 257.07 | 297.07 | 297.07 | 210.37 | 460.59 | 420.59 | 608.59 | 507.29 | [8 empty] | 718.06 | 1.54 | 0.67 | 0.67
47 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN005 | 1S-DL-YP-CTC-DPHG-0113-CHN005 | CHITRA GUPTA RD.:K | TG-CHN005A-2 | 19505299 | 990 | 320 | 246 | 0.96 | 280 | 70 | 304 | 130 | 561 | 80 | 346 | 238 | 2019-06-03 15:00 | 78.1 | 15 | 561 | Y | 70 | 117 | 114 | 47 | 0.2 |  | 22.3 | 77.5 | 672.07 | 357.1 | 304.58 | 473.08 | 20.25 | 335.22 | 335.22 | 219.24 | [12 empty] | 692.32 | 27.28 | 0.63 | 0.28
48 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN006 | 1S-DL-YP-CTC-DPHG-0113-CHN006 | XYZ QTR.:PG | TG-CHN006A-1 | 19506897 | 990 | 300 | 245 | 0.96 | 547 | 156 | 660 | 180 | 757 | 211 | 890 | 199 | 2019-06-01 23:30 | 158.4 | 53.1 | 895 | B | 90 | 97 | 113 | 23 | 0.1 |  | 0.6 | 99.3 | 11.57 | 3.27 | 1.27 | 2.27 | 517.22 | 474.22 | 474.22 | 427.28 | 149.08 | 200.38 | 405.17 | 248.32 | [8 empty] | 678.27 | 41.33 | 0.68 | 0.55
49 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN006 | 1S-DL-YP-CTC-DPHG-0113-CHN006 | XYZ QTR.:PG | TG-CHN006A-2 | 19505167 | 990 | 320 | 245 | 0.98 | 641 | 221 | 902 | 237 | 961 | 183 | 743 | 195 | 2019-06-12 00:30 | 182.1 | 37.8 | 1054 | Y | 108 | 112 | 80 | 32 | 0.2 |  | 4.1 | 95.7 | 1 |  | 18 |  | 255.3 | 198 | 198 | 330 | 438.53 | 497.23 | 148.3 | 365.23 | [8 empty] | 696.23 | 23.37 | 0.64 | 0.65
50 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN007 | 1S-DL-YP-CTC-DPHG-0113-CHN007 | CHUNA MANDI:ID | TG-CHN007A-1 | 19505831 | 990 | 320 | 245 | 0.97 | 593 | 339 | 1646 | 90 | 414 | 164 | 768 | 1099 | 2019-06-28 15:00 | 236.5 | 27.2 | 1646 | R | 151 | 58 | 91 | 93 | 0.1 | 0.3 | 70.9 | 28.7 | 7.55 | 535.19 | 147.03 | 108.03 | 292.26 | 181.04 | 181.04 | 550.11 | 415.32 |  | 31.04 | 58.09 |  |  |  |  | 0.3 |  |  |  | 716.23 | 3.37 | 0.48 | 0.6
51 | 2019-06-02 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN007 | 1S-DL-YP-CTC-DPHG-0113-CHN007 | CHUNA MANDI:ID | TG-CHN007A-2 | 19504674 | 990 | 320 | 240 | 0.97 | 668 | 238 | 1004 | 224 | 947 | 206 | 877 | 110 | 2019-06-12 00:30 | 131 | 44.9 | 1088 | R | 110 | 96 | 93 | 17 |  |  | 2 | 98 |  | 2 | 2.3 | 1 | 131.02 | 258.08 | 258.08 | 218.01 | 563.14 | 434.08 | 392.03 | 475.15 | [8 empty] | 694.16 | 1.44 | 0.66 | 0.67
52 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN007 | 1S-DL-YP-CTC-DPHG-0113-CHN007 | CHUNA MANDI:ID | TG-CHN007A-3 | 19500085 | 990 | 320 | 244 | 0.97 | 912 | 302 | 1302 | 303 | 1303 | 308 | 1321 | 19 | 2019-06-11 | 209.8 | 71.4 | 1410 | R | 108 | 93 | 99 | 15 |  |  | 16 | 84 |  |  |  |  | 15.3 | 53.3 | 53.3 | 24.3 | 546.51 | 645.49 | 633.19 | 624.19 | 155.28 | 19 | 63.3 | 69.3 | 0.3 |  |  |  | 718.19 | 1.41 | 0.68 | 0.92
53 | 2019-06-02 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN007 | 1S-DL-YP-CTC-DPHG-0113-CHN007 | CHUNA MANDI:ID | TG-CHN007A-4 | 19502770 | 990 | 320 | 239 | 0.97 | 585 | 210 | 910 | 175 | 763 | 200 | 860 | 129 | 2019-06-11 00:30 | 126.6 | 53.7 | 968 | R | 107 | 90 | 103 | 17 |  |  | 16.6 | 83.4 |  | 0.3 |  |  | 187.42 | 423.39 | 423.39 | 252.52 | 504.2 | 267.53 | 483.28 | 439.1 | [8 empty] | 692.02 | 3.58 | 0.72 | 0.59
54 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN007 | 1S-DL-YP-CTC-DPHG-0113-CHN007 | CHUNA MANDI:ID | TG-CHN007A-5 | 19505582 | 990 | 320 | 245 | 0.98 | 705 | 225 | 928 | 170 | 697 | 310 | 1301 | 528 | 2019-06-12 00:30 | 242.9 | 49.3 | 1303 | B | 106 | 82 | 112 | 30 |  | 0.3 | 21 | 78.8 | 0.03 | 4.06 |  |  | 150.42 | 486.19 | 486.19 | 220.02 | 564.07 | 224.27 | 617.02 | 494.5 |  |  | 2 | [5 empty] | 714.52 | 5.08 | 0.62 | 0.71
55 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN008 | 1S-DL-YP-CTC-DPHG-0113-CHN008 | GALI NALWA:K | TG-CHN008A-1 | 19500138 | 990 | 320 | 242 | 0.97 | 784 | 303 | 1257 | 255 | 1053 | 226 | 925 | 290 | 2019-06-16 | 164.1 | 50.8 | 1273 | R | 111 | 95 | 94 | 17 |  |  | 25.6 | 74.4 |  |  |  |  | 15.11 | 114.28 | 114.28 | 54.06 | 654.17 | 597 | 537.21 | 657.22 | 42 |  | 16.59 | [5 empty] | 711.28 | 8.32 | 0.67 | 0.79
56 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN009 | 1S-DL-YP-CTC-DPHG-0113-CHN009 | KRISHNA MKT. (K):K | TG-CHN009A-1 | 19506843 | 990 | 320 | 241 | 0.97 | 1032 | 353 | 1532 | 337 | 1451 | 343 | 1472 | 73 | 2019-06-29 22:00 | 333.4 | 61.8 | 2176 | R | 103 | 99 | 98 | 5 | 0.3 | 0.1 | 32.7 | 66.9 |  |  |  |  | 0.3 | 6.3 | 6.3 | 1 | 453.06 | 496.36 | 535.59 | 492.36 | 214.1 | 179.1 | 149.44 | 192.37 | 26.57 | 12.27 | 7 | 8.3 | 694.43 | 25.17 | 0.68 | 1.04
57 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN010 | 1S-DL-YP-CTC-DPHG-0113-CHN010 | R. K. MISSION:PL | TG-CHN010A-1 | 19504702 | 630 | 200 | 244 | 0.95 | 207 | 76 | 312 | 70 | 289 | 61 | 251 | 54 | 2019-06-13 13:00 | 78.2 | 9.2 | 327 | R | 106 | 108 | 86 | 22 |  |  | 16.1 | 83.9 | 512.46 | 506.48 | 571.38 | 532.46 | 205.21 | 211.19 | 211.19 | 185.21 | [12 empty] | 718.07 | 1.53 | 0.46 | 0.33
58 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN011 | 1S-DL-YP-CTC-DPHG-0113-CHN011 | MOTHER DAIRY RATAN MKT:PL | TG-CHN011A-1 | 19504707 | 630 | 200 | 244 | 0.97 | 234 | 80 | 324 | 74 | 300 | 80 | 322 | 23 | 2019-06-16 | 60.7 | 12 | 390 | R | 105 | 96 | 99 | 9 |  |  | 4 | 96 | 48.13 | 100.47 | 93.47 | 34 | 664.17 | 617.13 | 617.13 | 684 | 5.3 |  | 1.3 | [9 empty] | 718 | 2 | 0.71 | 0.37
59 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN012 | 1S-DL-YP-CTC-DPHG-0113-CHN012 | RATTAN MKT.:PL | TG-CHN012A-1 | 19500032 | 630 | 200 | 240 | 0.95 | 349 | 120 | 506 | 112 | 473 | 117 | 489 | 29 | 2019-06-14 17:30 | 102.6 | 18.4 | 577 | R | 115 | 88 | 96 | 27 |  | 0.1 | 47.6 | 52.2 | 54.4 | 303.06 | 243.15 | 227.39 | 428.47 | 267.19 | 267.19 | 310.18 | 231.51 | 144.53 | 168.22 | 177.21 | [8 empty] | 715.18 | 4.42 | 0.54 | 0.55
60 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN013 | 1S-DL-YP-CTC-DPHG-0113-CHN013 | NEHRU BAZAR:PL | TG-CHN013A-1 | 19506723 | 400 | 120 | 234 | 0.94 | 216 | 85 | 365 | 58 | 249 | 72 | 307 | 100 | 2019-06-14 13:00 | 80.9 | 9.7 | 435 | R | 94 | 86 | 120 | 34 | 0.4 | 0.3 | 49.6 | 49.8 | 284.54 | 270.53 | 39.29 | 233.53 | 191.36 | 333.58 | 333.58 | 247.07 | 229.17 | 100.56 | 300.17 | 224.47 | [8 empty] | 705.47 | 14.13 | 0.57 | 0.54
61 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN014 | 1S-DL-YP-CTC-DPHG-0113-CHN014 | RAILWAY COLONY:ID | TG-CHN014A-1 | 19503747 | 990 | 320 | 240 | 0.96 | 512 | 111 | 464 | 245 | 1042 | 156 | 662 | 509 | 2019-06-12 15:00 | 143.5 | 32.4 | 1042 | Y | 71 | 128 | 101 | 57 |  |  | 52.6 | 47.4 | 61.52 | 1 | 0.58 | 2.22 | 656.36 | 200.56 | 200.56 | 536.17 |  | 516.32 | 193.19 | 179.49 | [8 empty] | 718.28 | 1.32 | 0.69 | 0.52
62 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN014 | 1S-DL-YP-CTC-DPHG-0113-CHN014 | RAILWAY COLONY:ID | TG-CHN014A-2 | 19500147 | 990 | 320 | 241 | 0.94 | 109 | 58 | 246 | 18 | 77 | 33 | 141 | 148 | 2019-06-30 00:30 | 38.3 | 8.8 | 246 | R | 147 | 57 | 96 | 90 | 1 | 0.7 | 82.4 | 16 | 718.26 | 718.26 | 718.26 | 718.26 | [16 empty] | 718.26 | 1.34 | 0.62 | 0.11
63 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN015 | 1S-DL-YP-CTC-DPHG-0113-CHN015 | LADOO GHATI:PL | TG-CHN015A-1 | 19500137 | 630 | 200 | 238 | 0.96 | 663 | 228 | 1005 | 230 | 1007 | 206 | 896 | 110 | 2019-06-11 23:30 | 160.1 | 52 | 1077 | R | 106 | 94 | 100 | 12 |  | 0.1 | 33.3 | 66.6 |  |  |  |  | 27 | 90 | 90 | 35 | 522.44 | 509.14 | 583.44 | 548.14 | 129 | 112 | 113.3 | 129 | 38.3 | 6 | 1.3 | 5 | 717.14 | 2.46 | 0.6 | 1.05
64 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN016 | 1S-DL-YP-CTC-DPHG-0113-CHN016 | 6: TOOTI PL/M:PL | TG-CHN016A-1 | 19506300 | 990 | 320 | 240 | 0.98 | 774 | 424 | 2038 | 182 | 758 | 168 | 760 | 1279 | 2019-06-06 02:30 | 252.2 | 55 | 2038 | R | 106 | 100 | 94 | 12 | 0.5 | 0.1 | 12.5 | 87 |  |  |  |  | 77 | 112.11 | 112.11 | 99 | 625 | 594.19 | 547 | 607.3 | 3.3 |  |  |  | 1 |  |  |  | 706.3 | 13.3 | 0.63 | 0.78
65 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN016 | 1S-DL-YP-CTC-DPHG-0113-CHN016 | 6: TOOTI PL/M:PL | TG-CHN016A-2 | 19504706 | 990 | 200 | 228 | 0.98 | 818 | 258 | 1164 | 311 | 1404 | 249 | 1113 | 270 | 2019-06-30 00:30 | 191.4 | 63 | 1432 | Y | 89 | 119 | 92 | 30 |  |  | 13.9 | 86.1 |  |  |  |  | 74.3 | 5 | 5 | 16.3 | 643.33 | 599.33 | 669.33 | 700.33 |  | 113.3 |  | 1 |  |  |  |  | 718.03 | 1.57 | 0.69 | 0.83
66 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN017 | 1S-DL-YP-CTC-DPHG-0113-CHN017 | 6: TOOTI:K | TG-CHN017A-1 | 19500148 | 630 | 200 | 246 | 0.94 | 199 | 69 | 289 | 50 | 210 | 79 | 326 | 102 | 2019-06-30 14:00 | 70.4 | 19.8 | 376 | B | 112 | 65 | 123 | 58 |  |  | 7.6 | 92.4 | 221.03 | 635.25 | 143.39 | 372.58 | 497.22 | 83 | 83 | 345.27 |  |  | 0.3 | [9 empty] | 718.25 | 1.35 | 0.63 | 0.32
67 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN019 | 1S-DL-YP-CTC-DPHG-0113-CHN019 | KHANNA CINEMA KIOSK:ID | TG-CHN019A-1 | 19500022 | 990 | 320 | 240.0466 | 0.97588 | 513.5645 | 121.3708 | 525.0739 | 213.3562 | 919.3615 | 178.8374 | 763.8054 | 343.9863 | 2019-06-11 23:30 | [15 empty] | 15 |  |  |  | 558 |  |  |  | 147 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.64325 | 0.51875
68 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN019 | 1S-DL-YP-CTC-DPHG-0113-CHN019 | KHANNA CINEMA KIOSK:ID | TG-CHN019A-2 | 19505723 | 990 | 320 | 241 | 0.97 | 739 | 393 | 1856 | 141 | 582 | 205 | 916 | 1144 | 2019-06-06 02:30 | 255 | 15 | 1856 | R | 113 | 85 | 102 | 28 | 0.4 | 0.2 | 8 | 91.4 | 1 | 22.53 | 2 | 1.01 | 273.22 | 483.57 | 483.57 | 389.51 | 442.55 | 211.27 | 344.25 | 327.25 | 0.3 |  | 0.3 |  | 0.3 |  |  |  | 718.17 | 1.43 | 0.55 | 0.75
69 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN020 | 1S-DL-YP-CTC-DPHG-0113-CHN020 | BASANT ROAD:K | TG-CHN020A-1 | 19504708 | 990 | 320 | 244 | 0.96 | 872 | 306 | 1253 | 273 | 1116 | 294 | 1204 | 120 | 2019-06-05 23:30 | 190.6 | 75.1 | 1404 | R | 113 | 88 | 99 | 25 |  |  | 1.7 | 98.3 |  | 1 |  |  | 52.28 | 286.45 | 286.45 | 131.11 | 574.56 | 427.23 | 516.36 | 561.27 | 87.09 | 0.55 | 37.55 | 23.25 | 1.3 |  |  |  | 716.03 | 3.57 | 0.59 | 0.88
70 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN020 | 1S-DL-YP-CTC-DPHG-0113-CHN020 | BASANT ROAD:K | TG-CHN020A-2 | 19506304 | 630 | 200 | 251 | 0.96 | 285 | 135 | 534 | 79 | 310 | 71 | 280 | 241 | 2019-06-11 23:30 | 86.8 | 18.4 | 691 | R | 140 | 81 | 79 | 61 | 0.2 |  | 1.7 | 98.1 | 6.59 | 295.05 | 335.46 | 114.48 | 456.13 | 397.28 | 397.28 | 562.45 | 229.51 | 0.3 |  | 15.3 | [8 empty] | 693.03 | 26.57 | 0.58 | 0.45
71 | 2019-06-06 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN021 | 1S-DL-YP-CTC-DPHG-0113-CHN021 | TANGA STAND KIOSK:PG | TG-CHN021A-1 | 19504704 | 990 | 320 | 244 | 0.97 | 801 | 240 | 993 | 269 | 1116 | 293 | 1209 | 188 | 2019-06-11 | 157.5 | 43.4 | 1274 | B | 94 | 97 | 110 | 16 |  |  | 1.1 | 98.9 |  |  |  |  | 179.31 | 138.42 | 138.42 | 110.12 | 417.47 | 458.06 | 521.03 | 486.06 |  | 0.3 | 13.25 | 1 |  |  |  |  | 597.18 | 2.42 | 0.61 | 0.81
72 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN021 | 1S-DL-YP-CTC-DPHG-0113-CHN021 | TANGA STAND KIOSK:PG | TG-CHN021A-2 | 19506039 | 630 | 200 | 238 | 0.97 | 439 | 113 | 482 | 148 | 635 | 178 | 763 | 244 | 2019-06-01 22:00 | 143.4 | 36 | 918 | B | 82 | 97 | 121 | 39 | 0.1 | 0.1 | 5.8 | 94.1 |  |  |  |  | 444.18 | 217.21 | 217.21 | 170.47 | 256.04 | 483.01 | 644.22 | 529.35 |  |  | 9.23 | [5 empty] | 700.22 | 19.38 | 0.66 | 0.7
73 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN022 | 1S-DL-YP-CTC-DPHG-0113-CHN022 | GALI MANTOLA:PL | TG-CHN022A-1 | 19500029 | 630 | 200 | 243 | 0.96 | 542 | 219 | 893 | 194 | 791 | 129 | 523 | 331 | 2019-06-06 01:00 | 190.9 | 36.8 | 893 | R | 116 | 111 | 73 | 43 |  |  | 3 | 97 |  |  | 6 |  | 32.09 | 48.39 | 48.39 | 104.09 | 566.05 | 589.05 | 296.29 | 605.05 | 115.26 | 77.56 |  | 6.26 | 2 |  |  |  | 715.4 | 4.2 | 0.62 | 0.86
74 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN022 | 1S-DL-YP-CTC-DPHG-0113-CHN022 | GALI MANTOLA:PL | TG-CHN022A-2 | 19500035 | 630 | 200 | 237 | 0.97 | 454 | 158 | 661 | 123 | 513 | 174 | 733 | 195 | 2019-06-06 01:00 | 110.9 | 25.3 | 761 | B | 102 | 85 | 114 | 29 |  | 0.3 | 3.4 | 96.2 | 1 | 10.3 |  |  | 280.19 | 469.55 | 469.55 | 307.19 | 434.19 | 235.13 | 550.08 | 408.19 |  |  | 0.47 | [5 empty] | 715.38 | 4.22 | 0.6 | 0.72
75 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN022 | 1S-DL-YP-CTC-DPHG-0113-CHN022 | GALI MANTOLA:PL | TG-CHN022A-3 | 19504552 | 990 | 320 | 238 | 0.96 | 499 | 192 | 800 | 156 | 652 | 151 | 629 | 161 | 2019-06-12 | 117.8 | 36.1 | 812 | R | 114 | 99 | 87 | 27 |  |  | 0.9 | 99.1 | 11.3 | 28.01 | 180.47 | 22.3 | 546.59 | 629.53 | 629.53 | 610.57 | 156.47 | 57.22 | 38.5 | 81.49 | [8 empty] | 715.16 | 4.44 | 0.58 | 0.5
76 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN023 | 1S-DL-YP-CTC-DPHG-0113-CHN023 | DARIBA PAN KIOSK:K | TG-CHN023A-1 | 19500167 | 990 | 320 | 249 | 0.96 | 723 | 262 | 1058 | 244 | 979 | 217 | 877 | 157 | 2019-06-10 23:30 | 177.4 | 91.3 | 1117 | R | 111 | 97 | 92 | 19 |  |  | 6.3 | 93.7 |  |  |  |  | 23.14 | 117.05 | 117.05 | 60.17 | 692 | 599.09 | 585.24 | 655.57 | 1 | [7 empty] | 716.14 | 3.46 | 0.69 | 0.73
77 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN023 | 1S-DL-YP-CTC-DPHG-0113-CHN023 | DARIBA PAN KIOSK:K | TG-CHN023A-2 | 19502876 | 990 | 320 | 251 | 0.95 | 587 | 221 | 923 | 157 | 623 | 209 | 852 | 272 | 2019-06-30 01:00 | 196.5 | 47.8 | 923 | R | 110 | 80 | 109 | 30 | 62.3 | 34.9 | 2.5 | 0.3 | 0.3 | 54.02 | 1 | 0.3 | 418.25 | 607.53 | 607.53 | 498.51 | 296.55 | 53.55 | 323.25 | 216.29 | [8 empty] | 715.5 | 4.1 | 0.6 | 0.59
78 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN023 | 1S-DL-YP-CTC-DPHG-0113-CHN023 | DARIBA PAN KIOSK:K | TG-CHN023A-3 | 19506193 | 630 | 200 | 244 | 0.98 | 568 | 205 | 846 | 201 | 821 | 162 | 658 | 176 | 2019-06-11 01:00 | 132.6 | 16.6 | 1079 | R | 112 | 103 | 85 | 27 | 0.1 | 0.4 | 29.5 | 70 | 0.3 | 9.3 | 32.51 | 4 | 211.11 | 280.09 | 280.09 | 287.28 | 452.15 | 398.14 | 335.25 | 410.25 | 49.57 | 28 | 0.3 | 14 | 2 |  |  |  | 715.53 | 4.07 | 0.51 | 0.9
79 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN024 | 1S-DL-YP-CTC-DPHG-0113-CHN024 | MOHALLA BAOLI:PM | TG-CHN024A-1 | 19505359 | 630 | 200 | 243 | 0.96 | 495 | 156 | 633 | 169 | 685 | 170 | 692 | 56 | 2019-06-06 00:30 | 168.6 | 37.6 | 850 | Y | 99 | 103 | 98 | 5 | 0.1 | 0.1 | 13.6 | 86.2 | 2.3 |  | 0.3 |  | 261.13 | 186.24 | 186.24 | 223.22 | 452.08 | 528.27 | 485.33 | 492.29 |  | 1 | 0.3 | [5 empty] | 715.51 | 4.09 | 0.59 | 0.79
80 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN025 | 1S-DL-YP-CTC-DPHG-0113-CHN025 | PHG DISP.:ID | TG-CHN025A-1 | 19504613 | 990 | 320 | 240 | 0.98 | 497 | 126 | 552 | 240 | 1062 | 132 | 579 | 497 | 2019-06-03 16:00 | 95.7 | 13.2 | 1062 | Y | 82 | 130 | 89 | 48 |  |  | 0.6 | 99.4 | 302.08 | 8 | 131 | 71 | 388.38 | 453.03 | 453.03 | 564.46 | 28 | 257.43 | 4.3 | 83 | [8 empty] | 718.46 | 1.14 | 0.57 | 0.5
81 | 2019-06-03 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN025 | 1S-DL-YP-CTC-DPHG-0113-CHN025 | PHG DISP.:ID | TG-CHN025A-2 | 19504701 | 990 | 320 | 242 | 0.99 | 450 | 153 | 652 | 134 | 567 | 164 | 704 | 120 | 2019-06-13 16:30 | 81.7 | -16.2 | 737 | B | 109 | 87 | 103 | 22 |  | 1.2 | 62.5 | 36.3 | 5.16 | 34.46 | 10.46 | 11.16 | 565.31 | 633 | 633 | 625.18 | 97.29 | 0.3 | 86.56 | 31.42 | [8 empty] | 668.16 | 3.44 | 0.68 | 0.45
82 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN025 | 1S-DL-YP-CTC-DPHG-0113-CHN025 | PHG DISP.:ID | TG-CHN025A-3 | 19504675 | 990 | 320 | 235 | 0.98 | 1066 | 344 | 1548 | 369 | 1675 | 353 | 1592 | 111 | 2019-06-10 22:30 | 197.2 | 41.2 | 1727 | Y | 91 | 101 | 108 | 17 |  | 0.1 | 7.4 | 92.5 | 0.44 | 0.44 | 0.44 | 0.44 | 11.06 | 4.06 | 4.06 | 5.06 | 633.17 | 542.46 | 443.24 | 553.25 | 69.27 | 154.58 | 218.3 | 147.19 | 0.3 | 12.3 | 48.2 | 8.3 | 715.04 | 4.56 | 0.66 | 1.08
83 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN025 | 1S-DL-YP-CTC-DPHG-0113-CHN025 | PHG DISP.:ID | TG-CHN025A-4 | 19506038 | 630 | 200 | 239 | 0.97 | 920 | 293 | 1287 | 265 | 1163 | 363 | 1655 | 443 | 2019-06-11 23:30 | 280.2 | 41 | 1655 | B | 104 | 101 | 95 | 9 | 0.9 | 0.4 | 22.5 | 76.2 |  |  |  |  | 5 | 18 | 18 | 13 | 610.48 | 624.48 | 619.48 | 635.18 | 62 | 45.3 | 37 | 38 | 21.3 | 11 | 12.3 | 13 | 699.18 | 20.42 | 0.43 | 1.46
84 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN026 | 1S-DL-YP-CTC-DPHG-0113-CHN026 | GALI SCHOOL WALI:PL | TG-CHN026A-1 | 19504851 | 990 | 320 | 246 | 0.96 | 910 | 373 | 1578 | 278 | 1164 | 260 | 1087 | 458 | 2019-06-29 23:00 | 261.3 | 29.4 | 1585 | R | 117 | 98 | 85 | 32 | 0.3 | 0.3 | 11.8 | 87.6 | 1 | 1.32 | 1.32 | 1.32 | 14.22 | 77.12 | 77.12 | 66.04 | 575.4 | 611.5 | 503.25 | 614.57 | 99.31 | 19.29 |  | 27.3 | 19.3 |  |  |  | 710.03 | 9.57 | 0.59 | 0.92
85 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN026 | 1S-DL-YP-CTC-DPHG-0113-CHN026 | GALI SCHOOL WALI:PL | TG-CHN026A-2 | 19500026 | 990 | 200 | 239 | 0.97 | 978 | 300 | 1317 | 297 | 1304 | 382 | 1719 | 409 | 2019-06-02 23:30 | 229.5 | 29 | 1719 | B | 100 | 98 | 102 | 4 |  | 0.1 | 1.5 | 98.5 | 0.27 | 0.27 | 0.11 | 0.27 | 43.14 | 25.23 | 25.23 | 34.05 | 443.45 | 495 | 456.18 | 464.07 | 65.46 | 34.22 | 65.3 | 56.33 | 2 |  | 0.22 |  | 702.12 | 17.48 | 0.61 | 0.99
86 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN027 | 1S-DL-YP-CTC-DPHG-0113-CHN027 | PAHAR GANJ POLICE STN:ID | TG-CHN027A-1 | 19500083 | 630 | 200 | 243 | 0.96 | 426 | 146 | 608 | 138 | 574 | 142 | 598 | 31 | 2019-06-11 23:00 | 121 | 26.2 | 636 | Y | 92 | 103 | 105 | 13 |  |  | 23 | 77 | 9 | 11.3 | 21.3 | 10 | 435.26 | 272.09 | 272.09 | 311.07 | 273.53 | 434.4 | 448.12 | 397.12 | [8 empty] | 718.19 | 1.41 | 0.62 | 0.68
87 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN030 | 1S-DL-YP-CTC-DPHG-0113-CHN030 | BASANT ROAD MUNJHE CHOWK:PG | TG-CHN030A-1 | 19503746 | 990 | 320 | 245 | 0.97 | 524 | 200 | 820 | 164 | 668 | 161 | 653 | 160 | 2019-06-11 | 111.9 | 28 | 840 | R | 112 | 97 | 91 | 21 |  | 0.1 | 54.1 | 45.8 |  | 1 | 1.02 |  | 296.16 | 575.01 | 575.01 | 501.24 | 416.32 | 136.47 | 118.41 | 211.24 | [8 empty] | 712.48 | 7.12 | 0.7 | 0.53
88 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM001 | 1S-DL-YP-CTC-DPHG-0114-RAM001 | HANUMAN MANDIR:PL | TG-RAM001A-1 | 19502877 | 630 | 200 | 238 | 0.97 | 593 | 190 | 845 | 199 | 889 | 204 | 905 | 54 | 2019-06-10 23:30 | 153.6 | 45.1 | 964 | B | 93 | 95 | 112 | 19 |  |  | 6.4 | 93.6 |  |  |  |  | 73.35 | 52.21 | 52.21 | 37 | 597.25 | 619.09 | 519.3 | 609 | 43.3 | 43 | 177 | 68.3 |  |  | 4 |  | 714.3 | 5.3 | 0.65 | 0.94
89 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM001 | 1S-DL-YP-CTC-DPHG-0114-RAM001 | HANUMAN MANDIR:PL | TG-RAM001A-2 | 19506112 | 990 | 320 | 240 | 0.97 | 839 | 247 | 1055 | 329 | 1405 | 264 | 1119 | 323 | 2019-06-30 00:30 | 223.4 | 57.6 | 1611 | R | 86 | 118 | 96 | 32 | 0.2 | 0.1 | 3.3 | 96.3 |  |  | 0.3 |  | 222.51 | 17.3 | 17.3 | 78.51 | 468.58 | 607.49 | 577.28 | 606.28 |  | 65.3 | 2 | 7 | 0.3 | 1.3 |  |  | 692.19 | 27.41 | 0.63 | 0.85
90 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM002 | 1S-DL-YP-CTC-DPHG-0114-RAM002 | JHANDEWALAN (K):K | TG-RAM002A-1 | 19505973 | 990 | 320 | 238 | 0.98 | 403 | 207 | 955 | 142 | 663 | 54 | 246 | 617 | 2019-06-07 12:30 | 132.8 | 1 | 955 | R | 136 | 106 | 58 | 78 | 0.1 | 0.1 | 0.3 | 99.5 | 466.23 | 492.53 | 707.4 | 508.47 | 172.32 | 205.52 | 205.52 | 207.23 | 77.45 | 17.55 |  | 0.3 | [8 empty] | 716.4 | 3.2 | 0.4 | 0.41
91 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM002 | 1S-DL-YP-CTC-DPHG-0114-RAM002 | JHANDEWALAN (K):K | TG-RAM002A-2 | 19504930 | 990 | 320 | 249 | 0.97 | 314 | 99 | 416 | 138 | 576 | 77 | 319 | 224 | 2019-06-29 16:00 | 77.3 | 15.5 | 576 | Y | 107 | 118 | 75 | 43 |  |  | 9.3 | 90.7 | 550.29 | 448.03 | 706.09 | 589.27 | 166.1 | 268.06 | 268.06 | 127.12 |  | 0.3 | [10 empty] | 716.39 | 3.21 | 0.51 | 0.32
92 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM003 | 1S-DL-YP-CTC-DPHG-0114-RAM003 | KILA KADAM SHARIF:PG | TG-RAM003A-1 | 19500294 | 990 | 320 | 232 | 0.97 | 811 | 313 | 1342 | 281 | 1258 | 218 | 962 | 345 | 2019-06-28 23:30 | 185.5 | 16.9 | 1353 | R | 106 | 108 | 86 | 22 | 100 |  |  |  | 1 | 1 | 1 | 1 | 16 | 37 | 37 | 52 | 664.22 | 646.09 | 537.08 | 659.34 | 33.31 | 30.44 |  | 2.19 |  |  |  |  | 714.53 | 5.07 | 0.67 | 0.82
93 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM004 | 1S-DL-YP-CTC-DPHG-0114-RAM004 | PRADHAN CHOWK:PL | TG-RAM004A-1 | 19500169 | 630 | 200 | 252 | 0.96 | 418 | 114 | 450 | 162 | 639 | 142 | 558 | 164 | 2019-06-11 23:00 | 138.5 | 43.2 | 727 | Y | 69 | 120 | 112 | 51 |  |  | 11 | 89 | 3.3 |  |  |  | 571.41 | 4 | 4 | 56 | 142 | 710.11 | 699.41 | 661.11 |  | 3 | 4 | [5 empty] | 717.11 | 2.49 | 0.75 | 0.66
94 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM004 | 1S-DL-YP-CTC-DPHG-0114-RAM004 | PRADHAN CHOWK:PL | TG-RAM004A-2 | 19506515 | 630 | 200 | 241 | 0.98 | 382 | 118 | 502 | 112 | 478 | 151 | 644 | 155 | 2019-06-28 16:00 | 81.6 | 19.8 | 648 | B | 83 | 84 | 133 | 50 |  |  | 1.8 | 98.2 | 45.3 | 116.3 | 0.3 | 4.3 | 538.43 | 420.55 | 420.55 | 496.55 | 122.29 | 169.17 | 583.47 | 205.17 | [8 empty] | 706.42 | 13.18 | 0.6 | 0.61
95 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM004 | 1S-DL-YP-CTC-DPHG-0114-RAM004 | PRADHAN CHOWK:PL | TG-RAM004A-3 | 19504292 | 400 | 120 | 241 | 0.97 | 191 | 76 | 308 | 41 | 166 | 74 | 301 | 139 | 2019-06-10 16:00 | 52.4 | 10.2 | 308 | R | 112 | 78 | 111 | 34 |  |  | 37.7 | 62.3 | 6.3 | 155.56 | 3 | 8.28 | 583.1 | 561.14 | 561.14 | 671.42 | 127.3 |  | 121.3 | 37 | [8 empty] | 717.1 | 2.5 | 0.64 | 0.48
96 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM004 | 1S-DL-YP-CTC-DPHG-0114-RAM004 | PRADHAN CHOWK:PL | TG-RAM004A-4 | 19504876 | 400 | 120 | 247 | 0.96 | 235 | 88 | 357 | 77 | 316 | 70 | 281 | 65 | 2019-06-28 17:30 | 79.5 | 13.8 | 406 | R | 109 | 93 | 98 | 16 |  |  | 7.1 | 92.9 | 5.3 | 7 | 5 | 3.3 | 350.15 | 546.44 | 546.44 | 481.29 | 361.26 | 163.27 | 197.54 | 232.12 | [8 empty] | 717.11 | 2.49 | 0.63 | 0.59
97 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM004 | 1S-DL-YP-CTC-DPHG-0114-RAM004 | PRADHAN CHOWK:PL | TG-RAM004A-5 | 19505166 | 990 | 320 | 242 | 0.97 | 672 | 224 | 909 | 138 | 604 | 310 | 1377 | 674 | 2019-06-30 | 204.8 | 60.5 | 1520 | B | 110 | 75 | 116 | 41 | 100 |  |  |  |  | 2.3 |  |  | 96.52 | 603.12 | 603.12 | 184.03 | 588.49 | 83.59 | 549.43 | 505.38 | 4 |  | 13.51 | [5 empty] | 689.41 | 30.19 | 0.68 | 0.68
98 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM005 | 1S-DL-YP-CTC-DPHG-0114-RAM005 | NABI KARIM KIOSK:K | TG-RAM005A-1 | 19506587 | 990 | 320 | 247 | 0.96 | 631 | 211 | 863 | 200 | 812 | 220 | 893 | 71 | 2019-06-03 15:30 | 259.8 | 54.7 | 967 | B | 95 | 97 | 107 | 12 |  |  | 2.7 | 97.3 |  |  |  |  | 300.3 | 273.47 | 273.47 | 235.44 | 392.51 | 419.34 | 555.06 | 457.37 | [8 empty] | 693.21 | 26.39 | 0.69 | 0.64
99 | 2019-06-02 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM005 | 1S-DL-YP-CTC-DPHG-0114-RAM005 | NABI KARIM KIOSK:K | TG-RAM005A-2 | 19504847 | 630 | 200 | 242 | 0.98 | 375 | 116 | 494 | 144 | 592 | 115 | 492 | 99 | 2019-06-26 16:00 | 55.2 | 12 | 594 | Y | 103 | 109 | 88 | 21 | 100 |  |  |  | 349.38 | 358.08 | 441.36 | 426.08 | 167.48 | 125.24 | 125.24 | 72.48 | 175.58 | 209.52 | 177.58 | 194.28 | [8 empty] | 693.24 | 2.36 | 0.44 | 0.59
100 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM006 | 1S-DL-YP-CTC-DPHG-0114-RAM006 | CHOWK SINGARA:ID | TG-RAM006A-1 | 19505286 | 990 | 320 | 241 | 0.97 | 621 | 184 | 771 | 189 | 793 | 248 | 1040 | 258 | 2019-06-08 16:30 | 172.5 | 39 | 1134 | B | 101 | 100 | 99 | 2 | 0.1 | 0.1 | 5.5 | 94.3 | 5 | 3 | 1 | 2 | 319.43 | 365.07 | 365.07 | 357.4 | 392.34 | 349.1 | 297.41 | 357.37 | [8 empty] | 717.17 | 2.43 | 0.64 | 0.63
101 | 2019-06-06 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM006 | 1S-DL-YP-CTC-DPHG-0114-RAM006 | CHOWK SINGARA:ID | TG-RAM006A-2 | 19504846 | 400 | 120 | 235 | 0.98 | 255 | 75 | 325 | 85 | 370 | 95 | 412 | 76 | 2019-06-26 16:00 | 38.9 | 11.9 | 416 | B | 102 | 95 | 103 | 8 |  |  | 17.5 | 82.5 | 20.57 | 89.57 | 23.3 | 23.27 | 359.4 | 317.34 | 317.34 | 385.4 | 216.46 | 189.52 | 202.46 | 188.16 | [8 empty] | 597.23 | 2.37 | 0.56 | 0.64
102 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM007 | 1S-DL-YP-CTC-DPHG-0114-RAM007 | ASHOK BASTI:PL | TG-RAM007A-1 | 19500110 | 990 | 320 | 244 | 0.96 | 726 | 236 | 992 | 224 | 937 | 266 | 1124 | 167 | 2019-06-01 16:30 | 253.2 | 43.4 | 1124 | B | 96 | 91 | 113 | 22 |  |  | 8.1 | 91.9 |  |  |  |  | 105.48 | 160.18 | 160.18 | 64.48 | 612.12 | 557.42 | 698.3 | 653.12 |  |  | 3 | [5 empty] | 718 | 2 | 0.69 | 0.73
103 | 2019-06-02 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM007 | 1S-DL-YP-CTC-DPHG-0114-RAM007 | ASHOK BASTI:PL | TG-RAM007A-2 | 19500196 | 990 | 320 | 249 | 0.95 | 616 | 190 | 745 | 228 | 898 | 197 | 781 | 138 | 2019-06-03 15:00 | 268.6 | 44.2 | 898 | Y | 93 | 111 | 96 | 18 |  |  | 5.2 | 94.8 | 0.3 |  |  |  | 407.2 | 184.18 | 184.18 | 308.51 | 286.22 | 509.54 | 325.39 | 385.21 | [8 empty] | 694.12 | 1.48 | 0.66 | 0.62
104 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM008 | 1S-DL-YP-CTC-DPHG-0114-RAM008 | AMAR PURI:PL | TG-RAM008A-1 | 19505319 | 990 | 320 | 252 | 0.95 | 375 | 110 | 428 | 130 | 512 | 134 | 526 | 92 | 2019-06-26 17:00 | 173.1 | 23.4 | 540 | B | 93 | 96 | 111 | 18 |  | 0.1 | 4.5 | 95.4 | 187.04 | 132.49 | 15.3 | 68.49 | 506.5 | 561.05 | 561.05 | 625.05 |  |  | 5.53 | [9 empty] | 693.54 | 26.06 | 0.66 | 0.38
105 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM008 | 1S-DL-YP-CTC-DPHG-0114-RAM008 | AMAR PURI:PL | TG-RAM008A-2 | 19504969 | 990 | 320 | 232 | 0.98 | 616 | 187 | 800 | 227 | 983 | 202 | 849 | 164 | 2019-06-01 22:00 | 181.1 | 18.4 | 1027 | Y | 89 | 117 | 94 | 28 | 22.1 | 75.6 | 2.2 | [5 empty] | 429.13 | 89.53 | 89.53 | 282.47 | 288.13 | 627.33 | 370.09 | 434.39 | [8 empty] | 717.26 | 2.34 | 0.7 | 0.62
106 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM010 | 1S-DL-YP-CTC-DPHG-0114-RAM010 | MCD PARK:PG | TG-RAM010A-1 | 19500021 | 990 | 320 | 243 | 0.97 | 789 | 270 | 1106 | 237 | 969 | 281 | 1153 | 165 | 2019-06-26 17:30 | 249.5 | 42 | 1153 | B | 100 | 95 | 106 | 11 | 0.1 |  | 2.9 | 97 |  |  |  |  | 90.57 | 145.52 | 145.52 | 92.57 | 624.26 | 570.31 | 651.56 | 623.26 | 1 |  | 3 | [5 empty] | 716.23 | 3.37 | 0.63 | 0.8
107 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM010 | 1S-DL-YP-CTC-DPHG-0114-RAM010 | MCD PARK:PG | TG-RAM010A-2 | 19500025 | 990 | 320 | 243 | 0.97 | 669 | 220 | 904 | 239 | 978 | 210 | 860 | 103 | 2019-06-11 23:00 | 223 | 51.5 | 980 | Y | 102 | 104 | 94 | 10 |  |  | 0.2 | 99.8 |  |  |  |  | 51.01 | 40.31 | 40.31 | 71.01 | 648.13 | 658.43 | 532.05 | 628.13 | [8 empty] | 699.14 | 20.46 | 0.73 | 0.68
108 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM010 | 1S-DL-YP-CTC-DPHG-0114-RAM010 | MCD PARK:PG | TG-RAM010A-3 | 19504836 | 630 | 200 | 243 | 0.96 | 582 | 189 | 775 | 181 | 745 | 211 | 870 | 113 | 2019-06-30 06:30 | 223.6 | 44.2 | 922 | B | 95 | 103 | 102 | 8 |  |  | 0.2 | 99.8 |  |  |  |  | 33 | 5.3 | 5.3 | 11.3 | 633.26 | 616.01 | 595.04 | 624.3 | 49.58 | 94.53 | 110.08 | 80.24 |  |  | 1.12 |  | 716.24 | 3.36 | 0.69 | 0.92
109 | 2019-06-19 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM011 | 1S-DL-YP-CTC-DPHG-0114-RAM011 | YOG MAYA:PG | TG-RAM011A-1 | 19505128 | 990 | 320 | 239 | 0.96 | 864 | 348 | 1504 | 249 | 1080 | 267 | 1158 | 391 | 2019-06-27 01:00 | 279.7 | 64.6 | 1504 | R | 109 | 97 | 94 | 15 |  |  | 1.1 | 98.9 | [5 empty] | 1 | 1 |  | 225.19 | 271.19 | 271.19 | 263.49 | 49 | 2.3 | 1.3 | 11 | 0.3 |  |  |  | 274.49 | 13.11 | 0.74 | 0.87
110 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM012 | 1S-DL-YP-CTC-DPHG-0114-RAM012 | PREM NAGAR:PG | TG-RAM012A-1 | 19500036 | 990 | 320 | 240 | 0.97 | 668 | 227 | 972 | 230 | 981 | 211 | 898 | 79 | 2019-06-01 01:30 | 264.2 | 14.7 | 992 | R | 102 | 102 | 97 | 5 |  |  | 6.7 | 93.3 |  |  | 0.3 |  | 281.28 | 286.31 | 286.31 | 292.13 | 435.58 | 430.55 | 408.22 | 425.13 | [8 empty] | 717.26 | 2.34 | 0.64 | 0.67
111 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM013 | 1S-DL-YP-CTC-DPHG-0114-RAM013 | TELL MILL:PL | TG-RAM013A-1 | 19505477 | 990 | 320 | 244 | 0.97 | 688 | 190 | 797 | 178 | 740 | 320 | 1352 | 585 | 2019-06-30 | 245.4 | 61.4 | 1352 | B | 91 | 78 | 131 | 53 | 0.1 | 0.1 | 10.8 | 89 |  |  |  |  | 189.2 | 423.51 | 423.51 | 55.3 | 502.54 | 268.23 | 606.51 | 636.44 |  |  | 84.53 | [5 empty] | 692.14 | 27.46 | 0.72 | 0.69
112 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM014 | 1S-DL-YP-CTC-DPHG-0114-RAM014 | HOTEL KABIR:PL | TG-RAM014A-1 | 19500086 | 990 | 320 | 234 | 0.99 | 625 | 228 | 985 | 199 | 860 | 197 | 849 | 130 | 2019-06-12 02:00 | 94.9 | -36.8 | 1031 | R | 103 | 103 | 94 | 9 |  |  | 5.1 | 94.9 |  |  |  |  | 276.16 | 272.17 | 272.17 | 304.02 | 442.45 | 446.44 | 326.29 | 414.59 | [8 empty] | 719.01 | 0.59 | 0.67 | 0.63
113 | 2019-06-06 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM014 | 1S-DL-YP-CTC-DPHG-0114-RAM014 | HOTEL KABIR:PL | TG-RAM014A-2 | 19505448 | 630 | 200 | 244 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [7 empty] | 23.1 | 76.9 | 573.44 | 573.44 | 573.44 | 573.44 | [16 empty] | 573.44 | 26.16 |  | 0
114 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM015 | 1S-DL-YP-CTC-DPHG-0114-RAM015 | RAM NAGAR COMP. CTR:ID | TG-RAM015A-1 | 19500067 | 990 | 320 | 236 | 0.98 | 693 | 214 | 886 | 240 | 1001 | 238 | 997 | 112 | 2019-06-12 00:30 | 150.1 | 39 | 1065 | Y | 97 | 98 | 105 | 8 | 22.2 | 12.6 | 35.8 | 29.4 | 0.02 |  |  |  | 131.15 | 104.01 | 104.01 | 106.02 | 585.21 | 612.37 | 611.42 | 610.36 | [8 empty] | 716.38 | 3.22 | 0.71 | 0.7
115 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM015 | 1S-DL-YP-CTC-DPHG-0114-RAM015 | RAM NAGAR COMP. CTR:ID | TG-RAM015A-2 | 19500758 | 990 | 320 | 243.2741 | 0.9779 | 601.891 | 198.938 | 800.1366 | 184.397 | 741.6523 | 218.5561 | 883.9477 | 123.8804 | 2019-06-12 01:00 | [15 empty] | 0.5 |  |  |  | 481 |  |  |  | 238.5 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.61427 | 0.60797
116 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM015 | 1S-DL-YP-CTC-DPHG-0114-RAM015 | RAM NAGAR COMP. CTR:ID | TG-RAM015A-3 | 19500070 | 990 | 320 | 239 | 0.97 | 629 | 236 | 990 | 187 | 784 | 206 | 862 | 180 | 2019-06-11 | 153.8 | 27.2 | 1007 | R | 105 | 95 | 100 | 10 |  |  | 0.8 | 99.2 | 0.5 | 9.51 | 0.51 | 0.21 | 312.13 | 401.5 | 401.5 | 380.19 | 400.28 | 301.5 | 347.21 | 332.51 | [8 empty] | 713.31 | 6.29 | 0.63 | 0.64
117 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM016 | 1S-DL-YP-CTC-DPHG-0114-RAM016 | ST. ANTHONY SCHOOL:PL | TG-RAM016A-1 | 19500054 | 990 | 200 | 239 | 0.97 | 631 | 195 | 820 | 216 | 914 | 220 | 929 | 102 | 2019-06-16 01:00 | 141.2 | 52.9 | 960 | B | 99 | 100 | 101 | 2 |  |  | 16.9 | 83.1 |  |  |  |  | 271.49 | 269.16 | 269.16 | 265.16 | 446.13 | 448.46 | 442.31 | 452.46 | [8 empty] | 718.02 | 1.58 | 0.68 | 0.64
118 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM016 | 1S-DL-YP-CTC-DPHG-0114-RAM016 | ST. ANTHONY SCHOOL:PL | TG-RAM016A-2 | 19505365 | 400 | 120 | 241 | 0.99 | 329 | 115 | 486 | 95 | 401 | 119 | 502 | 93 | 2019-06-15 02:30 | 73.2 | -16.8 | 502 | B | 112 | 90 | 97 | 22 |  |  | 3.6 | 96.4 | 240.37 | 527.52 | 403 | 369.36 | 434.25 | 142.1 | 142.1 | 301.56 | 32.3 | 38.3 | 36.3 | 36.3 | 1.3 | 0.3 | 1 | 1 |  |  |  |  | 709.02 | 10.58 | 0.26 | 0.82
119 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM016 | 1S-DL-YP-CTC-DPHG-0114-RAM016 | ST. ANTHONY SCHOOL:PL | TG-RAM016A-3 | 19506113 | 990 | 320 | 241 | 0.99 | 758 | 266 | 1160 | 249 | 1089 | 244 | 1071 | 81 | 2019-06-10 23:30 | 160 | -17.9 | 1485 | B | 105 | 101 | 94 | 11 | 0.2 | 0.1 | 0.3 | 99.4 | 1.4 | 1.4 | 1.4 | 1.4 | 82.09 | 64.1 | 64.1 | 88.31 | 625.36 | 648.05 | 553.29 | 624.14 | 5 | 0.3 | 1 | [5 empty] | 714.25 | 5.35 | 0.66 | 0.77
120 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM017 | 1S-DL-YP-CTC-DPHG-0114-RAM017 | LOA MANDI:PM | TG-RAM017A-1 | 19503753 | 990 | 320 | 246 | 0.97 | 343 | 115 | 474 | 124 | 511 | 103 | 426 | 75 | 2019-06-14 17:00 | 95.7 | -5.9 | 601 | Y | 94 | 106 | 99 | 12 |  |  | 0.3 | 99.7 | 503.48 | 466.01 | 495.31 | 477.31 | 214.33 | 249.5 | 249.5 | 240.5 |  | 2.3 | [10 empty] | 718.21 | 1.39 | 0.43 | 0.35
121 | 2019-06-02 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM018 | 1S-DL-YP-CTC-DPHG-0114-RAM018 | M.S.BLOCK NO.2:ID | TG-RAM018A-1 | 19500007 | 400 | 120 | 242 | 0.98 | 105 | 41 | 181 | 31 | 129 | 33 | 145 | 46 | 2019-06-02 23:00 | 20.1 | 2.5 | 185 | R | 119 | 91 | 90 | 29 | 100 |  |  |  | 502.25 | 581.16 | 604.1 | 573.45 | 190.45 | 111.54 | 111.54 | 119.25 | [12 empty] | 693.1 | 2.5 | 0.55 | 0.26
122 | 2019-06-06 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM019 | 1S-DL-YP-CTC-DPHG-0114-RAM019 | M.S.BLOCK NO.5:ID | TG-RAM019A-1 | 19500003 | 400 | 120 | 242 | 0.97 | 111 | 40 | 169 | 34 | 141 | 37 | 157 | 24 | 2019-06-13 22:30 | 32.6 | 2.8 | 183 | B | 108 | 91 | 101 | 17 |  | 0.1 | 2.8 | 97.2 | 430.21 | 539.1 | 465.54 | 512.13 | 166.43 | 57.54 | 57.54 | 84.51 | [12 empty] | 597.04 | 2.56 | 0.58 | 0.28
123 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM020 | 1S-DL-YP-CTC-DPHG-0114-RAM020 | C-BLOCK MOTIA KHAN:ID | TG-RAM020A-1 | 19500008 | 630 | 200 | 241 | 0.96 | 217 | 62 | 252 | 81 | 334 | 74 | 302 | 72 | 2019-06-11 23:00 | 71.8 | 8.7 | 362 | B | 88 | 105 | 107 | 19 |  |  | 1 | 99 | 458.4 | 289.24 | 300.46 | 343.55 | 258.23 | 427.39 | 427.39 | 373.08 |  |  | 0.3 | [9 empty] | 717.03 | 2.57 | 0.6 | 0.34
124 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM020 | 1S-DL-YP-CTC-DPHG-0114-RAM020 | C-BLOCK MOTIA KHAN:ID | TG-RAM020A-2 | 19500005 | 990 | 320 | 243 | 0.97 | 361 | 106 | 451 | 171 | 728 | 84 | 353 | 337 | 2019-06-02 | 77.3 | 21.3 | 728 | Y | 97 | 123 | 79 | 44 | 0 | 0.1 | 3.9 | 96 | 389.09 | 198.05 | 535.42 | 363.56 | 326.07 | 475.11 | 475.11 | 351.2 |  | 42 | [10 empty] | 715.16 | 4.44 | 0.57 | 0.36
125 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM021 | 1S-DL-YP-CTC-DPHG-0114-RAM021 | D-BLOCK MOTIA KHAN:ID | TG-RAM021A-1 | 19500009 | 990 | 300 | 242 | 0.97 | 643 | 196 | 781 | 243 | 1004 | 205 | 846 | 199 | 2019-06-12 | 122.8 | 22.8 | 1032 | Y | 89 | 109 | 102 | 20 | 98.2 | 1.8 |  |  | 87.3 | 51.05 | 36.11 | 50.33 | 486.39 | 428.21 | 428.21 | 476.43 | 142.58 | 237.41 | 196.18 | 189.51 | [8 empty] | 717.07 | 2.53 | 0.52 | 0.65
126 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM021 | 1S-DL-YP-CTC-DPHG-0114-RAM021 | D-BLOCK MOTIA KHAN:ID | TG-RAM021A-2 | 19500010 | 630 | 200 | 242 | 0.97 | 348 | 123 | 520 | 97 | 411 | 128 | 544 | 123 | 2019-06-03 | 64.4 | 19.3 | 629 | B | 105 | 77 | 118 | 41 |  |  | 0.8 | 99.2 | 34.33 | 250.3 | 23.32 | 50.3 | 519.01 | 430.38 | 430.38 | 518.04 | 163.34 | 36 | 249.39 | 148.34 | [8 empty] | 717.08 | 2.52 | 0.57 | 0.55
127 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM022 | 1S-DL-YP-CTC-DPHG-0114-RAM022 | M.M ROAD BAJAJ AUTO:PL | TG-RAM022A-1 | 19500051 | 990 | 320 | 245 | 0.95 | 482 | 144 | 583 | 183 | 736 | 154 | 621 | 137 | 2019-06-27 13:00 | 149.4 | 5.2 | 775 | Y | 99 | 112 | 89 | 23 |  |  | 13.9 | 86.1 | 474.03 | 466.33 | 479.33 | 473.03 | 120.18 | 82.29 | 82.29 | 118.44 | 123.58 | 169.17 | 57.24 | 126.32 | [8 empty] | 718.19 | 1.41 | 0.37 | 0.49
128 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM023 | 1S-DL-YP-CTC-DPHG-0114-RAM023 | M.M ROAD KIOSK:K | TG-RAM023A-1 | 19500149 | 990 | 320 | 245 | 0.96 | 605 | 185 | 782 | 213 | 901 | 208 | 892 | 116 | 2019-06-06 15:30 | 164.9 | 17.7 | 1050 | Y | 91 | 116 | 93 | 25 |  |  | 5.6 | 94.4 | 380.01 | 292.01 | 382.31 | 366.04 | 142 | 186.3 | 186.3 | 128.57 | 196.1 | 239.4 | 215.4 | 223.1 | [8 empty] | 718.11 | 1.49 | 0.46 | 0.61
129 | 2019-06-02 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM023 | 1S-DL-YP-CTC-DPHG-0114-RAM023 | M.M ROAD KIOSK:K | TG-RAM023A-2 | 19504945 | 630 | 200 | 245 | 0.97 | 357 | 110 | 436 | 152 | 607 | 95 | 375 | 208 | 2019-06-24 16:30 | 96.1 | -22.1 | 647 | Y | 83 | 131 | 86 | 48 |  |  | 27.1 | 72.9 | 445.19 | 359.22 | 433.49 | 425.19 | 138.28 | 118.5 | 118.5 | 110.15 | 108.48 | 214.23 | 79.57 | 157.01 | [8 empty] | 692.35 | 3.25 | 0.4 | 0.57
130 | 2019-06-02 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM024 | 1S-DL-YP-CTC-DPHG-0114-RAM024 | MOTIA KHAN P/M:PKG | TG-RAM024A-1 | 19500015 | 990 | 320 | 245 | 0.97 | 522 | 152 | 617 | 181 | 741 | 188 | 773 | 143 | 2019-06-26 16:00 | 120 | 21.3 | 874 | B | 88 | 96 | 116 | 28 |  |  | 33 | 67 | 346.04 | 303.34 | 39.33 | 239.37 | 228.19 | 215.12 | 215.12 | 274.07 | 119.35 | 175.12 | 207.57 | 180.14 | [8 empty] | 693.58 | 2.02 | 0.54 | 0.53
131 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM025 | 1S-DL-YP-CTC-DPHG-0114-RAM025 | CHARA MANDI:K | TG-RAM025A-1 | 19500107 | 990 | 320 | 243 | 0.97 | 725 | 266 | 1124 | 224 | 951 | 236 | 1008 | 153 | 2019-06-11 | 174.4 | 26.5 | 1155 | R | 109 | 97 | 95 | 14 |  |  | 5.7 | 94.3 | 0.3 | 1.3 | 2 | 1.3 | 19 | 65.57 | 65.57 | 46.3 | 694.06 | 650.39 | 603.54 | 670.06 | 4.3 | [7 empty] | 718.06 | 1.54 | 0.71 | 0.73
132 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM025 | 1S-DL-YP-CTC-DPHG-0114-RAM025 | CHARA MANDI:K | TG-RAM025A-2 | 19505958 | 630 | 200 | 237 | 0.96 | 555 | 206 | 865 | 174 | 737 | 174 | 731 | 132 | 2019-06-27 23:30 | 169.2 | 51 | 865 | R | 100 | 96 | 104 | 8 |  | 0.9 | 36.1 | 63 |  |  |  |  | 49.43 | 17.3 | 17.3 | 5 | 523.13 | 698.05 | 652.47 | 663.47 | 145.09 | 2.3 | 59.18 | 49.18 |  |  |  |  | 718.05 | 1.55 | 0.69 | 0.88
133 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM026 | 1S-DL-YP-CTC-DPHG-0114-RAM026 | BAGICHI ALLUDDIN:K | TG-RAM026A-1 | 19504530 | 990 | 320 | 239 | 0.97 | 757 | 222 | 925 | 277 | 1149 | 258 | 1070 | 197 | 2019-06-06 04:30 | 186.9 | 62.6 | 1239 | Y | 97 | 104 | 99 | 7 |  |  | 2.9 | 97.1 | 1 | 1 | 1 | 1 | 59.3 | 49.3 | 49.3 | 55 | 656.04 | 656.05 | 648.04 | 660.34 |  | 9.59 | [6 empty] | 716.34 | 3.26 | 0.7 | 0.77
134 | 2019-06-05 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM026 | 1S-DL-YP-CTC-DPHG-0114-RAM026 | BAGICHI ALLUDDIN:K | TG-RAM026A-2 | 19504529 | 990 | 320 | 253 | 0.96 | 805 | 317 | 1310 | 249 | 1023 | 238 | 984 | 308 | 2019-06-29 23:00 | 259.8 | 43.4 | 1391 | R | 117 | 93 | 90 | 27 |  | 0 | 4.3 | 95.6 | 9 | 9 | 9 | 9 | 4 | 52.3 | 52.3 | 19 | 513.01 | 558.46 | 539.16 | 592.46 | 95.45 | 2.3 |  | 2 | 1 |  |  |  | 622.46 | 1.14 | 0.68 | 0.81
135 | 2019-06-06 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM027 | 1S-DL-YP-CTC-DPHG-0114-RAM027 | ARP QUARTERS.:K | TG-RAM027A-1 | 19504722 | 990 | 320 | 239 | 0.97 | 609 | 208 | 889 | 213 | 912 | 188 | 800 | 102 | 2019-06-30 | 153.1 | 8.8 | 1105 | R | 114 | 94 | 92 | 22 |  | 1.1 | 22.7 | 76.2 | 9.28 | 12.58 | 29.28 | 9.28 | 247.53 | 373.51 | 373.51 | 341.22 | 338.07 | 208.39 | 208.06 | 244.38 | [8 empty] | 595.28 | 4.32 | 0.63 | 0.61
136 | 2019-06-02 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM027 | 1S-DL-YP-CTC-DPHG-0114-RAM027 | ARP QUARTERS.:K | TG-RAM027A-2 | 19504649 | 990 | 320 | 230 | 0.98 | 851 | 297 | 1276 | 229 | 985 | 325 | 1400 | 370 | 2019-06-11 23:30 | 136.9 | 52.3 | 1432 | B | 100 | 86 | 113 | 27 |  |  | 0.7 | 99.3 |  | 1.3 |  |  | 241.18 | 373.1 | 373.1 | 240.08 | 435.13 | 317.21 | 493.4 | 441.53 | 15.3 |  | 74 | 10 |  |  |  |  | 692.01 | 3.59 | 0.56 | 0.86
137 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM028 | 1S-DL-YP-CTC-DPHG-0114-RAM028 | SHYAM JI MAL LANE:PL | TG-RAM028A-1 | 19503751 | 990 | 320 | 242 | 0.97 | 629 | 201 | 847 | 279 | 1192 | 149 | 626 | 494 | 2019-06-12 16:00 | 179.6 | 55.9 | 1254 | Y | 97 | 131 | 72 | 59 |  |  | 69.5 | 30.5 |  |  | 4.3 |  | 321.44 | 45 | 45 | 267.33 | 395.24 | 665.08 | 35.55 | 449.35 |  | 7 | [6 empty] | 717.08 | 2.52 | 0.68 | 0.64
138 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM028 | 1S-DL-YP-CTC-DPHG-0114-RAM028 | SHYAM JI MAL LANE:PL | TG-RAM028A-2 | 19505233 | 990 | 320 | 240 | 0.97 | 718 | 258 | 1108 | 253 | 1089 | 207 | 889 | 210 | 2019-06-30 | 232.6 | 37.4 | 1328 | R | 110 | 106 | 84 | 26 | 0.1 |  | 1.2 | 98.7 |  |  |  |  | 41.08 | 58.33 | 58.33 | 81.23 | 644.32 | 634.37 | 415.16 | 612.17 | 8 | 0.3 | [6 empty] | 693.4 | 26.2 | 0.7 | 0.72
139 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM029 | 1S-DL-YP-CTC-DPHG-0114-RAM029 | JHANDEWALAN P/M:PL | TG-RAM029A-1 | 19503789 | 630 | 200 | 236 | 0.98 | 524 | 164 | 698 | 164 | 705 | 196 | 837 | 135 | 2019-06-03 16:00 | 103 | 19.8 | 837 | B | 98 | 111 | 91 | 20 |  |  | 4.2 | 95.8 | 8.3 | 2.3 | 66.32 | 9.3 | 409.12 | 252.33 | 252.33 | 417.18 | 299.24 | 458.03 | 197.24 | 288.18 |  | 4 | 16.3 | 2 |  |  |  |  | 717.06 | 2.54 | 0.5 | 0.83
140 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM030 | 1S-DL-YP-CTC-DPHG-0114-RAM030 | KABIR BASTI:PL | TG-RAM030A-1 | 19504709 | 630 | 200 | 230 | 0.97 | 503 | 141 | 598 | 202 | 872 | 160 | 689 | 241 | 2019-06-03 21:30 | 189.5 | 5.1 | 872 | Y | 81 | 116 | 103 | 35 |  |  | 12.8 | 87.2 | 14 |  |  |  | 521.38 | 219.22 | 219.22 | 358.11 | 157.28 | 439.44 | 355.16 | 334.55 |  | 34 | 0.3 | [5 empty] | 693.06 | 2.54 | 0.52 | 0.8
141 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM031 | 1S-DL-YP-CTC-DPHG-0114-RAM031 | GALI NO. 5 MULTANI DHANDA:PKG | TG-RAM031A-1 | 19506192 | 990 | 320 | 244.772 | 0.97365 | 965.3712 | 429.1978 | 1810.5028 | 257.1789 | 1050.9537 | 278.9945 | 1149.4499 | 715.4045 | 2019-06-03 02:30 | [15 empty] | 0 |  |  |  | 8.5 |  |  |  | 560 |  |  |  | 150 |  |  |  | 0 | 718.5 |  | 0.70056 | 0.97512
142 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM032 | 1S-DL-YP-CTC-DPHG-0114-RAM032 | IDGAHA (K):K | TG-RAM032A-1 | 19503323 | 990 | 320 | 240 | 0.96 | 601 | 163 | 691 | 218 | 934 | 220 | 938 | 245 | 2019-06-30 | 134 | 64.8 | 1019 | Y | 88 | 107 | 105 | 19 |  |  | 10.1 | 89.9 |  |  |  |  | 517.05 | 292.59 | 292.59 | 384.08 | 202 | 426.06 | 473.54 | 334.57 | [8 empty] | 719.05 | 0.55 | 0.68 | 0.61
143 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM032 | 1S-DL-YP-CTC-DPHG-0114-RAM032 | IDGAHA (K):K | TG-RAM032A-2 | 19506189 | 400 | 120 | 242 | 0.95 | 205 | 74 | 307 | 78 | 323 | 53 | 219 | 97 | 2019-06-08 22:30 | 82 | 5.8 | 424 | Y | 78 | 120 | 102 | 42 | 0.3 | 0.3 | 36 | 63.4 | 114 | 5 | 1.3 |  | 578.53 | 373 | 373 | 560.23 | 3 | 317.53 | 134.3 | 135.3 | [8 empty] | 695.53 | 24.07 | 0.66 | 0.51
144 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM033 | 1S-DL-YP-CTC-DPHG-0114-RAM033 | LAXMAN PURI:PKG | TG-RAM033A-1 | 19500293 | 990 | 320 | 239 | 0.97 | 551 | 141 | 587 | 198 | 826 | 211 | 875 | 267 | 2019-06-30 05:00 | 187.7 | 29.4 | 882 | B | 88 | 105 | 108 | 20 |  | 0.1 | 6.5 | 93.4 | 2.3 |  |  |  | 629 | 321.47 | 321.47 | 389.14 | 86.59 | 396.42 | 419.12 | 329.15 | [8 empty] | 718.29 | 1.31 | 0.7 | 0.56
145 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM035 | 1S-DL-YP-CTC-DPHG-0114-RAM035 | AARAKASHA ROAD:PKG | TG-RAM035A-1 | 19505996 | 990 | 320 | 242.8864 | 0.99292 | 1011.4528 | 398.7016 | 1631.2153 | 306.5522 | 1233.5606 | 306.199 | 1241.3307 | 393.8271 | 2019-06-12 01:00 | [15 empty] | 0 |  |  |  | 28 |  |  |  | 558.5 |  |  |  | 125.5 |  |  |  | 5 | 717 |  | 0.63127 | 1.0217
146 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM035 | 1S-DL-YP-CTC-DPHG-0114-RAM035 | AARAKASHA ROAD:PKG | TG-RAM035A-2 | 19505638 | 990 | 200 | 236 | 0.98 | 908 | 105 | 450 | 434 | 1873 | 369 | 1584 | 1303 | 2019-06-28 23:30 | 279.4 | 25.2 | 1873 | Y | 34 | 139 | 127 | 105 | 0.1 |  | 1.1 | 98.8 | 448.54 |  |  |  | 249.54 | 4.12 | 4.12 | 152.27 | 2.44 | 523.2 | 574.22 | 544.06 |  | 130.57 | 112.48 | 4.59 |  | 43.03 | 3.14 |  | 701.32 | 18.28 | 0.55 | 0.92
147 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM036 | 1S-DL-YP-CTC-DPHG-0114-RAM036 | R G COMPLEX:PKG | TG-RAM036A-1 | 19500001 | 990 | 320 | 246 | 0.97 | 219 | 73 | 308 | 61 | 255 | 85 | 351 | 83 | 2019-06-06 16:00 | 61.1 | -0.7 | 371 | B | 106 | 88 | 106 | 18 |  | 36.4 | 63.5 | 0.1 | 681.31 | 717.5 | 611.47 | 688.29 | 36.49 | 0.3 | 0.3 | 29.51 | [12 empty] | 718.2 | 1.4 | 0.34 | 0.22
148 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM038 | 1S-DL-YP-CTC-DPHG-0114-RAM038 | M.S BLOCK-1 | TG-RAM038A-2 | 19504325 | 630 | 200 | 243 | 0.97 | 159 | 60 | 253 | 31 | 131 | 68 | 283 | 140 | 2019-06-13 23:30 | 34 | 6.4 | 283 | B | 105 | 81 | 114 | 33 |  |  | 2.5 | 97.5 | 598.4 | 715.4 | 581.13 | 667.1 | 118 | 1 | 1 | 49.3 | [12 empty] | 716.4 | 3.2 | 0.54 | 0.25
149 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM040 | 1S-DL-YP-CTC-DPHG-0114-RAM040 | MULTI STORIED BLK NO-03, MOTIA KHAN | TG-RAM040A-1 | 19506700 | 400 | 120 | 243 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [6 empty] | 0.1 | 11.6 | 88.3 | 693.4 | 693.4 | 693.4 | 693.4 | [16 empty] | 693.4 | 26.2 |  | 0
150 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM040 | 1S-DL-YP-CTC-DPHG-0114-RAM040 | MULTI STORIED BLK NO-03, MOTIA KHAN | TG-RAM040A-2 | 19506844 | 400 | 120 | 237 | 0.99 | 230 | 179 | 764 | 28 | 116 | 23 | 94 | 659 | 2019-06-05 04:30 | 38.8 | 2.5 | 764 | R | 89 | 91 | 119 | 30 | 0 | 0.2 | 1.7 | 98.1 | 320.18 | 341.44 | 130.36 | 239.55 | 356.3 | 313.38 | 313.38 | 413.23 | 15 | 37 | 125.1 | 39.04 | 0.3 |  |  |  | 0.04 |  |  |  | 692.22 | 27.38 | 0.43 | 0.58
151 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM041 | 1S-DL-YP-CTC-DPHG-0114-RAM041 | MULTI STORIED BLK NO-04, MOTIA KHAN | TG-RAM041A-2 | 19506406 | 400 | 120 | 237 | 0.99 | 161 | 74 | 306 | 36 | 150 | 51 | 211 | 136 | 2019-06-12 00:30 | 28.2 | 2.9 | 308 | R | 128 | 75 | 97 | 53 | 0.1 |  | 7.8 | 92.1 | 235.5 | 552.54 | 401.3 | 384.03 | 391.41 | 140.46 | 140.46 | 309.07 | 66.09 |  | 9 | 0.3 | [8 empty] | 693.4 | 26.2 | 0.5 | 0.4
152 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM043 | 1S-DL-YP-CTC-DPHG-0114-RAM043 | VARDHMAN COMPLEX | TG-RAM043A-1 | 19500002 | 990 | 320 | 246 | 0.98 | 377 | 118 | 493 | 138 | 579 | 121 | 513 | 78 | 2019-06-06 14:30 | 72.1 | 3.7 | 625 | Y | 94 | 109 | 97 | 15 |  |  | 9.9 | 90.1 | 517.31 | 497.01 | 511.31 | 508.01 | 200.47 | 210.52 | 210.52 | 210.17 |  | 10.25 | [10 empty] | 718.18 | 1.42 | 0.34 | 0.38
153 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM044 | 1S-DL-YP-CTC-DPHG-0114-RAM044 | DB GUPTA ROAD BUS STOP | TG-RAM044A-1 | 19506758 | 630 | 200 | 242 | 0.97 | 757 | 177 | 724 | 225 | 997 | 355 | 1680 | 852 | 2019-06-06 02:30 | 271.4 | 49.4 | 1680 | B | 105 | 79 | 115 | 36 | 0.4 | 5.5 | 68.9 | 25.3 |  |  |  |  | 46.57 | 291 | 291 | 57.27 | 557 | 366.27 | 533.59 | 576.3 | 73.54 | 47.24 | 119.22 | 54.54 | 29.3 | 2.3 | 37.3 | 18.3 | 707.21 | 12.39 | 0.49 | 1.2
154 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ001 | 1S-DL-YP-CTC-DPHG-0111-PPQ001 | RAILWAY BOOKING P/M:PL | TG-PPQ001A-1 | 19505722 | 990 | 320 | 240 | 0.98 | 711 | 227 | 967 | 240 | 1015 | 245 | 1029 | 57 | 2019-06-04 14:30 | 164.8 | 5.1 | 1053 | B | 91 | 109 | 100 | 18 | 0.3 | 0.3 | 68.3 | 31.2 | 472.26 | 455.26 | 461.26 | 464.26 | 130.49 | 88.32 | 88.32 | 100.02 | 112.53 | 172.1 | 145.4 | 151.4 | [8 empty] | 716.08 | 3.52 | 0.31 | 0.72
155 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ001 | 1S-DL-YP-CTC-DPHG-0111-PPQ001 | RAILWAY BOOKING P/M:PL | TG-PPQ001A-2 | 19504817 | 400 | 120 | 266 | 0.96 | 366 | 114 | 426 | 133 | 489 | 120 | 451 | 55 | 2019-06-15 16:00 | 95.8 | 0.6 | 545 | B | 86 | 109 | 105 | 23 | 8.6 | 80.4 | 11 |  | 472.29 | 455.57 | 468.27 | 471.27 | 35.11 | 42.43 | 42.43 | 27.43 | 203.59 | 107.29 | 115.59 | 128.29 | 4.3 | 110 | 101.3 | 88.3 |  |  | 0.29 |  | 716.09 | 3.51 | 0.31 | 0.92
156 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ002 | 1S-DL-YP-CTC-DPHG-0111-PPQ002 | TANGA STAND QUTAB ROAD:PL | TG-PPQ002A-1 | 19500141 | 990 | 320 | 244 | 0.97 | 468 | 128 | 526 | 159 | 654 | 181 | 751 | 196 | 2019-06-12 16:00 | 97.9 | 21.3 | 751 | B | 103 | 103 | 95 | 8 |  |  | 31.8 | 68.2 | 183.59 | 261.57 | 484.27 | 364.27 | 527.23 | 413.55 | 413.55 | 276.3 | 8.3 | 44 | 147.25 | 78.55 | [8 empty] | 719.52 | 0.08 | 0.5 | 0.47
157 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ003 | 1S-DL-YP-CTC-DPHG-0111-PPQ003 | KHURSHEED MARKET:ID | TG-PPQ003A-1 | 19500125 | 990 | 320 | 242 | 0.97 | 811 | 285 | 1228 | 264 | 1129 | 262 | 1126 | 100 | 2019-06-29 15:00 | 188.4 | -8.8 | 1230 | R | 103 | 100 | 96 | 7 |  |  | 28.5 | 71.5 | 464.24 | 473.24 | 464.24 | 464.24 | 40.3 | 31.3 | 31.3 | 38.3 | 200.51 | 211.07 | 217.07 | 216.07 | 13.46 | 3.3 |  | 0.3 |  |  |  |  | 719.31 | 0.29 | 0.29 | 0.82
158 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ003 | 1S-DL-YP-CTC-DPHG-0111-PPQ003 | KHURSHEED MARKET:ID | TG-PPQ003A-2 | 19500124 | 990 | 320 | 245 | 0.98 | 605 | 179 | 729 | 227 | 934 | 198 | 821 | 178 | 2019-06-12 16:30 | 133.2 | -1.5 | 962 | Y | 99 | 114 | 87 | 27 |  | 0.1 | 49.9 | 49.9 | 493.03 | 489.03 | 516.33 | 498.33 | 125.3 | 66.3 | 66.3 | 117.3 | 100.36 | 163.36 | 98.06 | 103.06 | [8 empty] | 719.09 | 0.51 | 0.25 | 0.61
159 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ003 | 1S-DL-YP-CTC-DPHG-0111-PPQ003 | KHURSHEED MARKET:ID | TG-PPQ003A-3 | 19504631 | 400 | 120 | 248 | 0.97 | 264 | 97 | 395 | 92 | 371 | 75 | 304 | 82 | 2019-06-29 17:30 | 62.4 | -1.7 | 433 | R | 106 | 110 | 83 | 27 |  |  | 16.9 | 83.1 | 479.54 | 488.54 | 491.24 | 491.24 | 28 | 30 | 30 | 26 | 211.37 | 200.37 | 168.45 | 202.07 | [8 empty] | 719.31 | 0.29 | 0.29 | 0.66
160 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ004 | 1S-DL-YP-CTC-DPHG-0111-PPQ004 | CLOTH MARKET:K | TG-PPQ004A-1 | 19500173 | 990 | 320 | 235 | 0.97 | 673 | 200 | 885 | 243 | 1084 | 230 | 1021 | 176 | 2019-06-29 16:30 | 161.2 | 52.3 | 1225 | Y | 101 | 110 | 89 | 21 |  | 0.4 | 27.2 | 72.4 | 1.3 | 1 | 6.28 | 0.3 | 333.39 | 280.06 | 280.06 | 354.2 | 380.34 | 430.39 | 264.58 | 361.23 | 0.3 | 4.28 | [6 empty] | 716.13 | 3.47 | 0.62 | 0.68
161 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ004 | 1S-DL-YP-CTC-DPHG-0111-PPQ004 | CLOTH MARKET:K | TG-PPQ004A-2 | 19500128 | 990 | 320 | 236 | 0.96 | 267 | 107 | 446 | 94 | 394 | 65 | 272 | 155 | 2019-06-12 | 81.7 | 30.2 | 470 | R | 112 | 114 | 74 | 40 |  |  | 3.1 | 96.9 | 227.06 | 191.12 | 711.52 | 345.05 | 489.16 | 525.1 | 525.1 | 371.17 | [12 empty] | 716.22 | 3.38 | 0.73 | 0.27
162 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ004 | 1S-DL-YP-CTC-DPHG-0111-PPQ004 | CLOTH MARKET:K | TG-PPQ004A-3 | 19505707 | 630 | 200 | 238 | 0.98 | 275 | 79 | 339 | 81 | 348 | 115 | 492 | 148 | 2019-06-26 16:00 | 68.4 | 0.4 | 549 | B | 90 | 97 | 113 | 23 |  | 0.1 | 0.3 | 99.6 | 503.14 | 491.49 | 481.49 | 486.19 | 210.31 | 211.02 | 211.02 | 204.59 | 2 | 12.54 | 141.53 | 24.27 | [8 empty] | 715.45 | 4.15 | 0.32 | 0.44
163 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ005 | 1S-DL-YP-CTC-DPHG-0111-PPQ005 | 12 TOOTI CHOWK:PG | TG-PPQ005A-1 | 19505684 | 990 | 320 | 243 | 0.99 | 975 | 325 | 1417 | 310 | 1345 | 341 | 1478 | 116 | 2019-06-29 15:00 | 156.8 | -160.6 | 1563 | B | 109 | 89 | 102 | 20 | 0.2 | 0.1 | 1.5 | 98.2 | 408.38 | 469.07 | 457.37 | 421.08 | 69 | 53.3 | 53.3 | 91.29 | 109.13 | 88.47 | 80.45 | 80.32 | 123 | 99.27 | 122.48 | 117.42 | 1 |  | 14.11 |  | 710.51 | 9.09 | 0.29 | 0.99
164 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ005 | 1S-DL-YP-CTC-DPHG-0111-PPQ005 | 12 TOOTI CHOWK:PG | TG-PPQ005A-2 | 19506191 | 990 | 320 | 242 | 0.97 | 624 | 170 | 702 | 208 | 858 | 247 | 1027 | 282 | 2019-06-12 17:30 | 178.2 | 35.8 | 1032 | B | 86 | 100 | 114 | 28 | 0.1 |  | 2.1 | 97.8 | 15.3 | 2.3 |  | 2.3 | 560.18 | 472.56 | 472.56 | 487.56 | 139.26 | 239.48 | 383.41 | 224.48 | [8 empty] | 715.14 | 4.46 | 0.6 | 0.63
165 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ006 | 1S-DL-YP-CTC-DPHG-0111-PPQ006 | WEST END CINEMA:ID | TG-PPQ006A-1 | 19500135 | 630 | 200 | 241 | 0.99 | 512 | 199 | 843 | 157 | 658 | 157 | 661 | 183 | 2019-06-29 13:00 | 78.2 | -0.5 | 887 | R | 117 | 97 | 86 | 31 |  | 0.1 | 34 | 66 | 381 | 372 | 415 | 389.3 | 85.3 | 110 | 110 | 98 | 154.28 | 237.57 | 211.27 | 230.57 | 98.59 |  |  | 1.3 |  |  |  |  | 719.57 | 0.03 | 0.34 | 0.81
166 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ006 | 1S-DL-YP-CTC-DPHG-0111-PPQ006 | WEST END CINEMA:ID | TG-PPQ006A-2 | 19506190 | 630 | 200 | 243 | 0.99 | 981 | 359 | 1521 | 364 | 1549 | 258 | 1079 | 456 | 2019-06-14 16:30 | 143.6 | -4 | 1665 | R | 115 | 88 | 97 | 27 |  |  | 10.4 | 89.6 | 349.3 | 397 | 378 | 376.3 | 69.3 | 51.3 | 51.3 | 59.3 | 65.2 | 55.2 | 55.23 | 56.2 | 18.03 | 41.33 | 28.3 | 21.33 | 191.37 | 148.37 | 173.37 | 180.07 | 694 | 26 | 0.3 | 1.56
167 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ007 | 1S-DL-YP-CTC-DPHG-0111-PPQ007 | GALI DARJIAN P/M:PG | TG-PPQ007A-1 | 19500095 | 990 | 320 | 238 | 0.95 | 686 | 199 | 816 | 197 | 814 | 290 | 1209 | 394 | 2019-06-11 16:00 | 253.2 | 96.4 | 1209 | B | 98 | 93 | 109 | 16 |  | 0.6 | 46.7 | 52.6 |  |  |  |  | 29.3 | 66.09 | 66.09 | 24 | 665.03 | 628.24 | 678.03 | 670.33 |  |  | 1.3 | [5 empty] | 718.03 | 1.57 | 0.77 | 0.69
168 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ008 | 1S-DL-YP-CTC-DPHG-0111-PPQ008 | FIRE STATION:K | TG-PPQ008A-1 | 19503552 | 990 | 320 | 243 | 0.98 | 502 | 179 | 741 | 158 | 659 | 165 | 688 | 72 | 2019-06-12 16:00 | 110.4 | 1.5 | 863 | R | 109 | 91 | 100 | 18 |  |  | 12.4 | 87.6 | 481.57 | 505.27 | 497.27 | 491.57 | 54.3 | 143 | 143 | 79 | 183.3 | 71.3 | 113.3 | 149 | [8 empty] | 719.57 | 0.03 | 0.33 | 0.51
169 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ008 | 1S-DL-YP-CTC-DPHG-0111-PPQ008 | FIRE STATION:K | TG-PPQ008A-2 | 19500073 | 990 | 320 | 248 | 0.97 | 650 | 220 | 912 | 224 | 919 | 206 | 847 | 69 | 2019-06-29 17:00 | 155.3 | 3.7 | 958 | B | 94 | 99 | 106 | 12 |  |  | 31.1 | 68.9 | 486.57 | 485.27 | 470.27 | 477.27 | 35.3 | 38 | 38 | 45.3 | 196.54 | 195.54 | 205.24 | 196.24 | [8 empty] | 719.21 | 0.39 | 0.34 | 0.66
170 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ009 | 1S-DL-YP-CTC-DPHG-0111-PPQ009 | 24 QUARTERS:PL | TG-PPQ009A-1 | 19505708 | 990 | 320 | 243 | 0.96 | 523 | 184 | 761 | 138 | 564 | 201 | 832 | 240 | 2019-06-12 18:00 | 184.3 | 49.9 | 1106 | B | 96 | 79 | 124 | 45 | 0.3 | 0.2 | 84.9 | 14.5 | 8.3 | 39.3 |  | 2.3 | 512.24 | 642.54 | 642.54 | 482.24 | 175 | 13.3 | 483.14 | 211 | [8 empty] | 695.54 | 24.06 | 0.69 | 0.53
171 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ010 | 1S-DL-YP-CTC-DPHG-0111-PPQ010 | PP QUARTERS:ID | TG-PPQ010A-1 | 19500071 | 990 | 320 | 241 | 0.96 | 585 | 231 | 950 | 199 | 819 | 155 | 625 | 283 | 2019-06-02 23:00 | 184.7 | 60.4 | 993 | R | 108 | 108 | 84 | 24 |  | 1 | 92.7 | 6.3 | 0.3 |  | 5.3 |  | 199.39 | 176.27 | 176.27 | 245.09 | 423.11 | 446.53 | 179.2 | 378.11 | [8 empty] | 623.2 | 24.4 | 0.72 | 0.59
172 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ011 | 1S-DL-YP-CTC-DPHG-0111-PPQ011 | SARAI KHALILA:ID | TG-PPQ011A-1 | 19503754 | 990 | 320 | 242 | 0.97 | 668 | 210 | 860 | 214 | 872 | 244 | 993 | 128 | 2019-06-02 06:30 | 213.4 | 36.1 | 993 | B | 94 | 101 | 105 | 11 |  | 0.1 | 38.5 | 61.4 | 6.3 | 7.3 | 8 | 6 | 395.04 | 352.34 | 352.34 | 351.34 | 292.08 | 333.38 | 377.08 | 336.08 | [8 empty] | 717.05 | 2.55 | 0.6 | 0.67
173 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ012 | 1S-DL-YP-CTC-DPHG-0111-PPQ012 | A K TANKI P/M:ID | TG-PPQ012A-1 | 19500116 | 990 | 320 | 237 | 0.96 | 514 | 209 | 896 | 165 | 701 | 141 | 602 | 260 | 2019-06-30 01:00 | 146.5 | 36.8 | 896 | R | 118 | 99 | 84 | 34 |  | 0.1 | 13.5 | 86.5 | 0.3 | 1.3 | 20.02 | 2 | 313.51 | 555.34 | 555.34 | 541.28 | 401.49 | 159.06 | 5 | 172.42 | [8 empty] | 716.1 | 3.5 | 0.68 | 0.52
174 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ012 | 1S-DL-YP-CTC-DPHG-0111-PPQ012 | A K TANKI P/M:ID | TG-PPQ012A-2 | 19500120 | 990 | 320 | 237 | 0.97 | 503 | 143 | 610 | 166 | 698 | 195 | 838 | 200 | 2019-06-30 00:30 | 134.7 | 30.2 | 838 | B | 88 | 99 | 113 | 25 | 0.4 | 98.7 | 0.9 |  | 2 | 0.3 |  |  | 689.4 | 509.36 | 509.36 | 529.33 | 24.3 | 206.04 | 403.49 | 186.37 | [8 empty] | 716.1 | 3.5 | 0.72 | 0.51
175 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ012 | 1S-DL-YP-CTC-DPHG-0111-PPQ012 | A K TANKI P/M:ID | TG-PPQ012A-3 | 19500117 | 990 | 320 | 249 | 0.97 | 621 | 200 | 810 | 222 | 898 | 198 | 799 | 94 | 2019-06-29 17:30 | 212.7 | 39.7 | 1015 | Y | 88 | 111 | 102 | 23 |  |  | 0.2 | 99.8 |  |  |  |  | 328.47 | 77.3 | 77.3 | 141.3 | 387.23 | 638.4 | 596.37 | 574.4 | [8 empty] | 716.1 | 3.5 | 0.73 | 0.63
176 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ012 | 1S-DL-YP-CTC-DPHG-0111-PPQ012 | A K TANKI P/M:ID | TG-PPQ012A-4 | 19504724 | 400 | 120 | 238 | 0.96 | 328 | 111 | 488 | 106 | 470 | 111 | 490 | 19 | 2019-06-14 17:30 | 157.9 | -24 | 490 | B | 101 | 95 | 104 | 9 |  | 0.1 | 10.3 | 89.6 | 518.32 | 543.53 | 518.02 | 518.32 | 68.18 | 43.57 | 43.57 | 68.18 | 128.53 | 128.2 | 128.53 | 128.53 | 0.27 |  | 0.57 | 0.27 |  |  |  |  | 716.1 | 3.5 | 0.18 | 0.82
177 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ013 | 1S-DL-YP-CTC-DPHG-0111-PPQ013 | CHOOTI MASJID:PL | TG-PPQ013A-1 | 19503745 | 990 | 320 | 238 | 0.94 | 691 | 225 | 939 | 174 | 726 | 291 | 1222 | 431 | 2019-06-12 01:30 | 230.4 | 82.4 | 1222 | B | 100 | 80 | 120 | 40 |  | 0.1 | 13.5 | 86.4 |  | 3.3 |  |  | 170.32 | 442.12 | 442.12 | 161.06 | 545.43 | 270.33 | 667.18 | 555.09 |  |  | 14 | [5 empty] | 716.15 | 3.45 | 0.68 | 0.7
178 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ013 | 1S-DL-YP-CTC-DPHG-0111-PPQ013 | CHOOTI MASJID:PL | TG-PPQ013A-2 | 19506111 | 400 | 120 | 243 | 0.93 | 303 | 142 | 637 | 79 | 334 | 82 | 331 | 304 | 2019-06-06 02:30 | 116.2 | 39.7 | 637 | R | 101 | 97 | 102 | 5 | 0.3 | 0.2 | 19.6 | 80 |  |  |  |  | 61.19 | 115.58 | 115.58 | 63.46 | 631.01 | 576.52 | 621.31 | 629.34 | 0.3 | 0.3 | 1 |  | 0.3 |  |  |  | 693.2 | 26.4 | 0.69 | 0.76
179 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ014 | 1S-DL-YP-CTC-DPHG-0111-PPQ014 | NEW QASAB PURA:K | TG-PPQ014A-1 | 19506188 | 990 | 320 | 236 | 0.95 | 712 | 196 | 834 | 253 | 1084 | 263 | 1132 | 277 | 2019-06-06 04:00 | 211.8 | 67.5 | 1324 | Y | 83 | 112 | 105 | 29 | 0.2 | 0.2 | 23.9 | 75.7 | 3 |  |  |  | 305.08 | 37.04 | 37.04 | 87.5 | 384.08 | 651.42 | 604.21 | 604.26 |  | 3.3 | 0.3 | [5 empty] | 692.16 | 27.44 | 0.68 | 0.72
180 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ014 | 1S-DL-YP-CTC-DPHG-0111-PPQ014 | NEW QASAB PURA:K | TG-PPQ014A-2 | 19506584 | 990 | 320 | 237 | 0.95 | 599 | 231 | 1005 | 183 | 789 | 185 | 794 | 213 | 2019-06-30 01:30 | 209 | 63.4 | 1034 | R | 111 | 95 | 93 | 18 | 0.2 | 0.1 | 21.2 | 78.5 |  | 1 | 1.3 |  | 235.37 | 392.5 | 392.5 | 342.08 | 479.4 | 321.27 | 306.15 | 373.09 | [8 empty] | 715.17 | 4.43 | 0.68 | 0.6
181 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ015 | 1S-DL-YP-CTC-DPHG-0111-PPQ015 | OLD QASAB PURA:K | TG-PPQ015A-1 | 19503520 | 990 | 320 | 235 | 0.97 | 776 | 283 | 1182 | 224 | 934 | 269 | 1124 | 225 | 2019-06-12 02:00 | 189.2 | 66.2 | 1260 | R | 108 | 88 | 104 | 20 |  | 0.5 | 24.4 | 75.1 |  |  |  |  | 8.3 | 71.55 | 71.55 | 23.57 | 689.41 | 643.16 | 687.19 | 691.14 | 17 |  | 4.25 | [5 empty] | 715.11 | 4.49 | 0.71 | 0.78
182 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ015 | 1S-DL-YP-CTC-DPHG-0111-PPQ015 | OLD QASAB PURA:K | TG-PPQ015A-2 | 19506695 | 630 | 200 | 243 | 0.96 | 340 | 102 | 433 | 129 | 541 | 110 | 464 | 96 | 2019-06-30 00:30 | 101.6 | 26 | 695 | B | 95 | 95 | 110 | 15 | 0.1 | 0.2 | 10.7 | 89 | 6.27 | 4.32 |  | 0.3 | 490.27 | 518.19 | 518.19 | 460.04 | 217.47 | 191.5 | 418.07 | 254.07 | [8 empty] | 714.41 | 5.19 | 0.7 | 0.54
183 | 2019-06-06 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ016 | 1S-DL-YP-CTC-DPHG-0111-PPQ016 | 4 POLS P. P. QUARTER:K | TG-PPQ016A-1 | 19503497 | 990 | 200 | 238 | 0.97 | 581 | 217 | 946 | 168 | 726 | 195 | 834 | 190 | 2019-06-30 01:30 | 135.2 | 22.5 | 946 | R | 112 | 90 | 98 | 22 |  |  | 35.6 | 64.4 |  | 3 | 2.3 | 0.3 | 118.47 | 405.14 | 405.14 | 255.31 | 477.04 | 187.37 | 304.39 | 339.5 | [8 empty] | 595.51 | 4.09 | 0.7 | 0.59
184 | 2019-06-06 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ016 | 1S-DL-YP-CTC-DPHG-0111-PPQ016 | 4 POLS P. P. QUARTER:K | TG-PPQ016A-2 | 19504142 | 400 | 120 | 246 | 0.98 | 126 | 46 | 195 | 40 | 167 | 40 | 167 | 28 | 2019-06-30 | 28.7 | -0.3 | 203 | B | 83 | 103 | 114 | 31 |  |  | 23.9 | 76.1 | 413.24 | 248.58 | 104.28 | 250.01 | 182.21 | 346.47 | 346.47 | 345.44 | [12 empty] | 595.45 | 4.15 | 0.66 | 0.31
185 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ017 | 1S-DL-YP-CTC-DPHG-0111-PPQ017 | CHAMELIAN ROAD:PL | TG-PPQ017A-1 | 19506412 | 990 | 320 | 237 | 0.96 | 683 | 347 | 1628 | 178 | 787 | 159 | 656 | 914 | 2019-06-06 02:30 | 221.4 | 64.6 | 1628 | R | 108 | 94 | 98 | 14 | 0.1 | 0.1 | 15.1 | 84.7 |  |  |  |  | 33.3 | 173.29 | 173.29 | 77 | 658.46 | 519.17 | 578.24 | 615.46 |  |  |  |  | 0.3 |  |  |  | 692.46 | 27.14 | 0.69 | 0.69
186 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ018 | 1S-DL-YP-CTC-DPHG-0111-PPQ018 | A. K. CHOWK:PL | TG-PPQ018A-1 | 19503744 | 990 | 320 | 233 | 0.95 | 691 | 230 | 1003 | 237 | 1021 | 224 | 974 | 41 | 2019-06-30 02:30 | 208.3 | 103.8 | 1045 | Y | 99 | 99 | 102 | 3 | 0.1 |  | 62.1 | 37.9 |  |  |  |  | 48.12 | 25.3 | 25.3 | 18.3 | 671.27 | 694.09 | 710.39 | 701.09 | [8 empty] | 719.39 | 0.21 | 0.77 | 0.7
187 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ019 | 1S-DL-YP-CTC-DPHG-0111-PPQ019 | IDGAHA P/M:PL | TG-PPQ019A-1 | 19503570 | 400 | 120 | 248 | 0.94 | 210 | 91 | 375 | 51 | 206 | 68 | 276 | 147 | 2019-06-02 18:00 | 72 | 25.9 | 375 | R | 114 | 88 | 98 | 26 |  | 0.3 | 48.2 | 51.5 |  | 10.3 | 1 |  | 409.53 | 675.23 | 675.23 | 648.23 | 309.3 | 33.3 | 93.3 | 71 | [8 empty] | 719.23 | 0.37 | 0.65 | 0.53
188 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ019 | 1S-DL-YP-CTC-DPHG-0111-PPQ019 | IDGAHA P/M:PL | TG-PPQ019A-2 | 19504992 | 990 | 320 | 237 | 0.96 | 540 | 197 | 856 | 182 | 785 | 161 | 690 | 144 | 2019-06-30 01:30 | 150.9 | 60.4 | 876 | R | 115 | 97 | 88 | 27 |  |  | 67.2 | 32.8 |  | 3 | 4.3 |  | 175.59 | 397.59 | 397.59 | 370.59 | 543.24 | 318.24 | 143.54 | 348.24 | [8 empty] | 719.23 | 0.37 | 0.72 | 0.55
189 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ020 | 1S-DL-YP-CTC-DPHG-0111-PPQ020 | NAWAB ROAD NO 1:PL | TG-PPQ020A-1 | 19500012 | 990 | 320 | 236 | 0.96 | 414 | 131 | 550 | 182 | 763 | 101 | 420 | 300 | 2019-06-15 02:30 | 123.6 | 34.6 | 886 | Y | 37 | 160 | 103 | 123 |  | 0.1 | 51.7 | 48.1 | 507.45 |  | 51.26 | 147.25 | 207.24 | 363.33 | 363.33 | 555.14 | 1 | 352.36 |  | 13.3 | [8 empty] | 716.09 | 3.51 | 0.6 | 0.42
190 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ021 | 1S-DL-YP-CTC-DPHG-0111-PPQ021 | SADAR THANA:K | TG-PPQ021A-1 | 19500112 | 990 | 320 | 242 | 0.97 | 516 | 198 | 833 | 145 | 605 | 173 | 717 | 198 | 2019-06-12 16:00 | 135.4 | 33.9 | 879 | R | 114 | 90 | 96 | 24 |  |  | 27.2 | 72.8 | 10.3 | 48 | 52 | 24 | 499.54 | 610.54 | 610.54 | 544.24 | 209 | 60.3 | 167.3 | 151 | [8 empty] | 719.24 | 0.36 | 0.62 | 0.52
191 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ021 | 1S-DL-YP-CTC-DPHG-0111-PPQ021 | SADAR THANA:K | TG-PPQ021A-2 | 19505685 | 400 | 120 | 244 | 0.97 | 280 | 137 | 598 | 85 | 364 | 58 | 247 | 310 | 2019-06-21 14:30 | 113.2 | -0.4 | 598 | R | 151 | 85 | 64 | 87 | 0.2 | 1.1 | 58.9 | 39.8 | 358.54 | 488.24 | 518.24 | 473.54 | 163 | 177 | 177 | 137 | 174 | 31 | 1.3 | 85.3 |  |  |  |  | 0.3 |  |  |  | 696.24 | 23.36 | 0.26 | 0.7
192 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ022 | 1S-DL-YP-CTC-DPHG-0111-PPQ022 | NAWAB ROAD NO. 2:PL | TG-PPQ022A-1 | 19506299 | 990 | 320 | 229 | 0.96 | 736 | 248 | 1097 | 260 | 1146 | 227 | 1004 | 124 | 2019-06-12 01:30 | 232.3 | 34.6 | 1436 | R | 106 | 102 | 92 | 14 | 0.2 | 0.4 | 4.3 | 95.1 | 0.3 | 0.3 | 1 | 0.3 | 129.01 | 166.01 | 166.01 | 178.01 | 560.46 | 526.46 | 434.46 | 516.16 | 4.3 | 1.3 | 0.3 | [5 empty] | 694.47 | 25.13 | 0.65 | 0.74
193 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ023 | 1S-DL-YP-CTC-DPHG-0111-PPQ023 | NARIAN MARKET:K | TG-PPQ023A-1 | 19504809 | 990 | 200 | 239 | 0.97 | 914 | 277 | 1181 | 265 | 1110 | 371 | 1561 | 420 | 2019-06-25 16:00 | 200.1 | 5.5 | 1572 | B | 93 | 96 | 110 | 17 |  | 2.2 | 38.5 | 59.3 | 396.38 | 311.04 | 59.34 | 284.01 | 102.53 | 197.27 | 197.27 | 222 | 203.35 | 206.04 | 150.41 | 175.05 | 12.59 | 1.3 | 36.54 | 34.59 |  |  | 19.59 |  | 716.05 | 3.55 | 0.36 | 0.92
194 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ023 | 1S-DL-YP-CTC-DPHG-0111-PPQ023 | NARIAN MARKET:K | TG-PPQ023A-2 | 19504968 | 990 | 320 | 244 | 0.95 | 569 | 176 | 699 | 178 | 699 | 216 | 853 | 154 | 2019-06-26 18:30 | 198 | 68.4 | 863 | B | 96 | 103 | 101 | 7 |  |  | 23.7 | 76.3 |  | 1 | 0.3 |  | 470.06 | 310.36 | 310.36 | 401.36 | 248.3 | 407 | 310.16 | 317 | [8 empty] | 718.36 | 1.24 | 0.69 | 0.58
195 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ024 | 1S-DL-YP-CTC-DPHG-0111-PPQ024 | RUI MANDI P/M:PM | TG-PPQ024A-1 | 19500184 | 400 | 200 | 244 | 0.98 | 269 | 98 | 400 | 80 | 326 | 91 | 370 | 64 | 2019-06-13 18:00 | 54.3 | -1.4 | 402 | R | 116 | 90 | 95 | 26 | 3.3 | 6.8 | 50.9 | 38.9 | 449.27 | 464.57 | 459.27 | 461.27 | 40 | 41 | 41 | 34.3 | 228.03 | 211.33 | 223.03 | 221.33 | [8 empty] | 717.3 | 2.3 | 0.31 | 0.67
196 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ025 | 1S-DL-YP-CTC-DPHG-0111-PPQ025 | CHOWK SINGHARA PL/M:ID | TG-PPQ025A-1 | 19500121 | 990 | 200 | 241 | 0.96 | 210 | 112 | 475 | 17 | 71 | 82 | 349 | 358 | 2019-06-06 15:00 | 65.8 | 17.5 | 475 | R | 145 | 26 | 129 | 119 |  |  | 9.3 | 90.7 | 353.37 | 693.38 | 442.06 | 682.38 | 340.01 |  |  | 11 | [12 empty] | 717.15 | 2.45 | 0.67 | 0.21
197 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ026 | 1S-DL-YP-CTC-DPHG-0111-PPQ026 | SADAR DISPENSARY:K | TG-PPQ026A-1 | 19503785 | 990 | 320 | 241 | 0.96 | 714 | 189 | 787 | 246 | 1027 | 279 | 1172 | 337 | 2019-06-29 18:00 | 210.5 | 70.7 | 1172 | B | 87 | 97 | 115 | 28 |  |  | 20.1 | 79.9 |  |  |  |  | 144.16 | 61.47 | 61.47 | 34.21 | 572.18 | 654.47 | 705.36 | 682.13 |  |  | 4.58 | [5 empty] | 716.34 | 3.26 | 0.73 | 0.72
198 | 2019-06-01 | 2019-06-16 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ027 | 1S-DL-YP-CTC-DPHG-0111-PPQ027 | BASTI HARPOOL SINGH:PL | TG-PPQ027A-1 | 19500018 | 990 | 320 | 228.7753 | 0.97455 | 449.9465 | 133.9601 | 588.9132 | 141.3139 | 614.4083 | 174.6725 | 763.262 | 163.1026 | 2019-06-15 16:00 | [15 empty] | 4.5 |  |  |  | 357 |  |  |  | 22 |  |  |  | 0 |  |  |  | 0 | 383.5 |  | 0.69158 | 0.45449
199 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ028 | 1S-DL-YP-CTC-DPHG-0111-PPQ028 | SLAUGHTER HOUSE:PL | TG-PPQ028A-1 | 19505006 | 990 | 320 | 238 | 0.97 | 416 | 127 | 556 | 124 | 548 | 166 | 723 | 172 | 2019-06-29 22:30 | 106.7 | 39 | 723 | B | 89 | 91 | 120 | 31 |  |  | 89 | 11 | 69.3 | 56 |  | 11 | 649.53 | 663.23 | 663.23 | 703.53 |  |  | 181.54 | 4.3 | [8 empty] | 719.23 | 0.37 | 0.71 | 0.42
200 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ028 | 1S-DL-YP-CTC-DPHG-0111-PPQ028 | SLAUGHTER HOUSE:PL | TG-PPQ028A-2 | 19504703 | 630 | 200 | 231 | 0.97 | 177 | 70 | 313 | 80 | 350 | 27 | 118 | 216 | 2019-06-28 22:00 | 44.2 | 16.6 | 350 | Y | 128 | 119 | 53 | 75 |  |  | 10.9 | 89.1 | 48 | 117.3 | 719.24 | 287.32 | 671.24 | 601.54 | 601.54 | 431.52 | [12 empty] | 719.24 | 0.36 | 0.74 | 0.28
201 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ029 | 1S-DL-YP-CTC-DPHG-0111-PPQ029 | NEW SARAI KHALIL | TG-PPQ029A-1 | 19504491 | 400 | 120 | 256 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [7 empty] | 21.4 | 78.6 | 718.18 | 718.18 | 718.18 | 718.18 | [16 empty] | 718.18 | 1.42 |  | 0
202 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ029 | 1S-DL-YP-CTC-DPHG-0111-PPQ029 | NEW SARAI KHALIL | TG-PPQ029A-2 | 19500144 | 400 | 120 | 261 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [7 empty] | 0.3 | 99.7 | 718.18 | 718.18 | 718.18 | 718.18 | [16 empty] | 718.18 | 1.42 |  | 0
203 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ030 | 1S-DL-YP-CTC-DPHG-0111-PPQ030 | AK TANKI OUTSIDE P/M | TG-PPQ030A-1 | 19500016 | 990 | 320 | 231 | 0.98 | 596 | 198 | 881 | 189 | 848 | 208 | 931 | 72 | 2019-06-28 18:00 | 156.8 | 16.2 | 998 | B | 97 | 97 | 105 | 8 |  | 0.1 | 5 | 95 |  |  |  |  | 270.34 | 296.26 | 296.26 | 235.01 | 443.5 | 417.58 | 540.29 | 479.23 | [8 empty] | 714.24 | 5.36 | 0.72 | 0.6
204 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ030 | 1S-DL-YP-CTC-DPHG-0111-PPQ030 | AK TANKI OUTSIDE P/M | TG-PPQ030A-2 | 19500019 | 990 | 320 | 232 | 0.98 | 443 | 144 | 647 | 130 | 585 | 169 | 760 | 154 | 2019-06-01 12:00 | 124.4 | 12.5 | 760 | B | 97 | 93 | 110 | 17 |  |  | 6.3 | 93.7 | 37 | 61.3 | 6 | 22 | 663.56 | 649.51 | 649.51 | 672.41 | 13.3 | 3.05 | 110.04 | 19.45 | [8 empty] | 714.26 | 5.34 | 0.67 | 0.45
205 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ031 | 1S-DL-YP-CTC-DPHG-0111-PPQ031 | CHAMELIAN ROAD:PG | TG-PPQ031A-1 | 19506526 | 990 | 320 | 249 | 0.96 | 38 | 15 | 59 | 7 | 26 | 16 | 65 | 36 | 2019-06-04 08:00 | 13.1 | 0.3 | 76 | R | 175 | 83 | 42 | 133 |  | 0.1 | 78.5 | 21.3 | 696.27 | 696.27 | 696.27 | 696.27 | [16 empty] | 696.27 | 23.33 | 0.16 | 0.04