## Loading Condition > 80%
MIS Report of Distribution Transformer - Jun19
Jun19 1130 PAHAR GANJ (Loading Condition > 80% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR001 | 1S-DL-YP-CTC-DPHG-0112-BGR001 | CANE MARKET:PL | TG-BGR001A-1 | 19506099 | 990 | 320 | 239 | 0.98 | 891 | 164 | 696 | 281 | 1307 | 446 | 1982 | 1114 | 2019-06-29 17:00 | 257.3 | 16.6 | 1982 | B | 90 | 91 | 119 | 29 | 0.1 |  | 24.9 | 75 | 327.27 | 428.27 | 344.57 | 402.27 | 178.12 | 70.14 | 70.14 | 80.14 | 190.09 | 196.37 | 126.18 | 212.37 |  | 0.3 | 97.49 | 0.3 |  |  | 2 |  | 695.48 | 24.12 | 0.34 | 0.9
2 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR003 | 1S-DL-YP-CTC-DPHG-0112-BGR003 | GALI BAHUJI: K | TG-BGR003A-1 | 19506463 | 990 | 320 | 244 | 0.96 | 869 | 295 | 1212 | 246 | 1006 | 328 | 1340 | 292 | 2019-06-12 17:30 | 265 | 54.7 | 1354 | B | 104 | 90 | 105 | 15 | 0.1 |  | 13.9 | 86 | 1 | 1 |  |  | 65 | 157 | 157 | 101 | 609.39 | 538.09 | 543.39 | 586.39 | 20.3 |  | 62.3 | 8.3 |  |  |  |  | 696.09 | 23.51 | 0.62 | 0.88
3 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR005 | 1S-DL-YP-CTC-DPHG-0112-BGR005 | CHIMNI MIL PL/M:PL | TG-BGR005A-1 | 19503586 | 990 | 320 | 230 | 0.99 | 861 | 296 | 1304 | 286 | 1249 | 278 | 1226 | 69 | 2019-06-25 17:30 | 78 | -85.4 | 1387 | R | 103 | 97 | 100 | 6 |  |  | 27.8 | 72.2 |  | 0.3 | 0.3 |  | 112.3 | 185.57 | 185.57 | 117.3 | 524.02 | 452.22 | 598 | 547.19 | 79.39 | 77.22 | 17.41 | 51.22 |  |  |  |  | 716.11 | 3.49 | 0.64 | 0.87
4 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR022 | 1S-DL-YP-CTC-DPHG-0112-BGR022 | B. G. ROAD COMP CTR:ID | TG-BGR022A-4 | 19505002 | 630 | 200 | 240 | 0.96 | 511 | 181 | 749 | 172 | 707 | 159 | 656 | 80 | 2019-06-11 03:30 | 126.5 | 57.5 | 819 | R | 108 | 102 | 89 | 19 |  |  | 8.6 | 91.4 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 0.3 | 0.3 | 1.3 | 670.23 | 695.46 | 673.51 | 712.16 | 43.23 | 18.3 |  | 1 |  |  |  |  | 715.16 | 4.44 | 0.73 | 0.81
5 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR027 | 1S-DL-YP-CTC-DPHG-0112-BGR027 | JHABBAR MAL P/M:PG | TG-BGR027A-1 | 19504832 | 990 | 320 | 243 | 0.98 | 900 | 309 | 1305 | 285 | 1202 | 306 | 1289 | 96 | 2019-06-25 15:30 | 181.8 | -0.7 | 1337 | B | 103 | 97 | 100 | 6 |  | 0.1 | 8.9 | 90.9 | 432.57 | 437.57 | 452.27 | 440.57 | 59.36 | 60.36 | 60.36 | 53.36 | 149.22 | 161.25 | 121.11 | 140.22 | 74.3 | 56.27 | 101.11 | 81.3 |  |  |  |  | 716.25 | 3.35 | 0.31 | 0.91
6 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN007 | 1S-DL-YP-CTC-DPHG-0113-CHN007 | CHUNA MANDI:ID | TG-CHN007A-3 | 19500085 | 990 | 320 | 244 | 0.97 | 912 | 302 | 1302 | 303 | 1303 | 308 | 1321 | 19 | 2019-06-11 | 209.8 | 71.4 | 1410 | R | 108 | 93 | 99 | 15 |  |  | 16 | 84 |  |  |  |  | 15.3 | 53.3 | 53.3 | 24.3 | 546.51 | 645.49 | 633.19 | 624.19 | 155.28 | 19 | 63.3 | 69.3 | 0.3 |  |  |  | 718.19 | 1.41 | 0.68 | 0.92
7 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN008 | 1S-DL-YP-CTC-DPHG-0113-CHN008 | GALI NALWA:K | TG-CHN008A-1 | 19500138 | 990 | 320 | 242 | 0.97 | 784 | 303 | 1257 | 255 | 1053 | 226 | 925 | 290 | 2019-06-16 | 164.1 | 50.8 | 1273 | R | 111 | 95 | 94 | 17 |  |  | 25.6 | 74.4 |  |  |  |  | 15.11 | 114.28 | 114.28 | 54.06 | 654.17 | 597 | 537.21 | 657.22 | 42 |  | 16.59 | [5 empty] | 711.28 | 8.32 | 0.67 | 0.79
8 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN009 | 1S-DL-YP-CTC-DPHG-0113-CHN009 | KRISHNA MKT. (K):K | TG-CHN009A-1 | 19506843 | 990 | 320 | 241 | 0.97 | 1032 | 353 | 1532 | 337 | 1451 | 343 | 1472 | 73 | 2019-06-29 22:00 | 333.4 | 61.8 | 2176 | R | 103 | 99 | 98 | 5 | 0.3 | 0.1 | 32.7 | 66.9 |  |  |  |  | 0.3 | 6.3 | 6.3 | 1 | 453.06 | 496.36 | 535.59 | 492.36 | 214.1 | 179.1 | 149.44 | 192.37 | 26.57 | 12.27 | 7 | 8.3 | 694.43 | 25.17 | 0.68 | 1.04
9 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN016 | 1S-DL-YP-CTC-DPHG-0113-CHN016 | 6: TOOTI PL/M:PL | TG-CHN016A-2 | 19504706 | 990 | 200 | 228 | 0.98 | 818 | 258 | 1164 | 311 | 1404 | 249 | 1113 | 270 | 2019-06-30 00:30 | 191.4 | 63 | 1432 | Y | 89 | 119 | 92 | 30 |  |  | 13.9 | 86.1 |  |  |  |  | 74.3 | 5 | 5 | 16.3 | 643.33 | 599.33 | 669.33 | 700.33 |  | 113.3 |  | 1 |  |  |  |  | 718.03 | 1.57 | 0.69 | 0.83
10 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN020 | 1S-DL-YP-CTC-DPHG-0113-CHN020 | BASANT ROAD:K | TG-CHN020A-1 | 19504708 | 990 | 320 | 244 | 0.96 | 872 | 306 | 1253 | 273 | 1116 | 294 | 1204 | 120 | 2019-06-05 23:30 | 190.6 | 75.1 | 1404 | R | 113 | 88 | 99 | 25 |  |  | 1.7 | 98.3 |  | 1 |  |  | 52.28 | 286.45 | 286.45 | 131.11 | 574.56 | 427.23 | 516.36 | 561.27 | 87.09 | 0.55 | 37.55 | 23.25 | 1.3 |  |  |  | 716.03 | 3.57 | 0.59 | 0.88
11 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN022 | 1S-DL-YP-CTC-DPHG-0113-CHN022 | GALI MANTOLA:PL | TG-CHN022A-1 | 19500029 | 630 | 200 | 243 | 0.96 | 542 | 219 | 893 | 194 | 791 | 129 | 523 | 331 | 2019-06-06 01:00 | 190.9 | 36.8 | 893 | R | 116 | 111 | 73 | 43 |  |  | 3 | 97 |  |  | 6 |  | 32.09 | 48.39 | 48.39 | 104.09 | 566.05 | 589.05 | 296.29 | 605.05 | 115.26 | 77.56 |  | 6.26 | 2 |  |  |  | 715.4 | 4.2 | 0.62 | 0.86
12 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN023 | 1S-DL-YP-CTC-DPHG-0113-CHN023 | DARIBA PAN KIOSK:K | TG-CHN023A-3 | 19506193 | 630 | 200 | 244 | 0.98 | 568 | 205 | 846 | 201 | 821 | 162 | 658 | 176 | 2019-06-11 01:00 | 132.6 | 16.6 | 1079 | R | 112 | 103 | 85 | 27 | 0.1 | 0.4 | 29.5 | 70 | 0.3 | 9.3 | 32.51 | 4 | 211.11 | 280.09 | 280.09 | 287.28 | 452.15 | 398.14 | 335.25 | 410.25 | 49.57 | 28 | 0.3 | 14 | 2 |  |  |  | 715.53 | 4.07 | 0.51 | 0.9
13 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN025 | 1S-DL-YP-CTC-DPHG-0113-CHN025 | PHG DISP.:ID | TG-CHN025A-4 | 19506038 | 630 | 200 | 239 | 0.97 | 920 | 293 | 1287 | 265 | 1163 | 363 | 1655 | 443 | 2019-06-11 23:30 | 280.2 | 41 | 1655 | B | 104 | 101 | 95 | 9 | 0.9 | 0.4 | 22.5 | 76.2 |  |  |  |  | 5 | 18 | 18 | 13 | 610.48 | 624.48 | 619.48 | 635.18 | 62 | 45.3 | 37 | 38 | 21.3 | 11 | 12.3 | 13 | 699.18 | 20.42 | 0.43 | 1.46
14 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN026 | 1S-DL-YP-CTC-DPHG-0113-CHN026 | GALI SCHOOL WALI:PL | TG-CHN026A-2 | 19500026 | 990 | 200 | 239 | 0.97 | 978 | 300 | 1317 | 297 | 1304 | 382 | 1719 | 409 | 2019-06-02 23:30 | 229.5 | 29 | 1719 | B | 100 | 98 | 102 | 4 |  | 0.1 | 1.5 | 98.5 | 0.27 | 0.27 | 0.11 | 0.27 | 43.14 | 25.23 | 25.23 | 34.05 | 443.45 | 495 | 456.18 | 464.07 | 65.46 | 34.22 | 65.3 | 56.33 | 2 |  | 0.22 |  | 702.12 | 17.48 | 0.61 | 0.99
15 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN026 | 1S-DL-YP-CTC-DPHG-0113-CHN026 | GALI SCHOOL WALI:PL | TG-CHN026A-1 | 19504851 | 990 | 320 | 246 | 0.96 | 910 | 373 | 1578 | 278 | 1164 | 260 | 1087 | 458 | 2019-06-29 23:00 | 261.3 | 29.4 | 1585 | R | 117 | 98 | 85 | 32 | 0.3 | 0.3 | 11.8 | 87.6 | 1 | 1.32 | 1.32 | 1.32 | 14.22 | 77.12 | 77.12 | 66.04 | 575.4 | 611.5 | 503.25 | 614.57 | 99.31 | 19.29 |  | 27.3 | 19.3 |  |  |  | 710.03 | 9.57 | 0.59 | 0.92
16 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM001 | 1S-DL-YP-CTC-DPHG-0114-RAM001 | HANUMAN MANDIR:PL | TG-RAM001A-1 | 19502877 | 630 | 200 | 238 | 0.97 | 593 | 190 | 845 | 199 | 889 | 204 | 905 | 54 | 2019-06-10 23:30 | 153.6 | 45.1 | 964 | B | 93 | 95 | 112 | 19 |  |  | 6.4 | 93.6 |  |  |  |  | 73.35 | 52.21 | 52.21 | 37 | 597.25 | 619.09 | 519.3 | 609 | 43.3 | 43 | 177 | 68.3 |  |  | 4 |  | 714.3 | 5.3 | 0.65 | 0.94
17 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM001 | 1S-DL-YP-CTC-DPHG-0114-RAM001 | HANUMAN MANDIR:PL | TG-RAM001A-2 | 19506112 | 990 | 320 | 240 | 0.97 | 839 | 247 | 1055 | 329 | 1405 | 264 | 1119 | 323 | 2019-06-30 00:30 | 223.4 | 57.6 | 1611 | R | 86 | 118 | 96 | 32 | 0.2 | 0.1 | 3.3 | 96.3 |  |  | 0.3 |  | 222.51 | 17.3 | 17.3 | 78.51 | 468.58 | 607.49 | 577.28 | 606.28 |  | 65.3 | 2 | 7 | 0.3 | 1.3 |  |  | 692.19 | 27.41 | 0.63 | 0.85
18 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM003 | 1S-DL-YP-CTC-DPHG-0114-RAM003 | KILA KADAM SHARIF:PG | TG-RAM003A-1 | 19500294 | 990 | 320 | 232 | 0.97 | 811 | 313 | 1342 | 281 | 1258 | 218 | 962 | 345 | 2019-06-28 23:30 | 185.5 | 16.9 | 1353 | R | 106 | 108 | 86 | 22 | 100 |  |  |  | 1 | 1 | 1 | 1 | 16 | 37 | 37 | 52 | 664.22 | 646.09 | 537.08 | 659.34 | 33.31 | 30.44 |  | 2.19 |  |  |  |  | 714.53 | 5.07 | 0.67 | 0.82
19 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM010 | 1S-DL-YP-CTC-DPHG-0114-RAM010 | MCD PARK:PG | TG-RAM010A-3 | 19504836 | 630 | 200 | 243 | 0.96 | 582 | 189 | 775 | 181 | 745 | 211 | 870 | 113 | 2019-06-30 06:30 | 223.6 | 44.2 | 922 | B | 95 | 103 | 102 | 8 |  |  | 0.2 | 99.8 |  |  |  |  | 33 | 5.3 | 5.3 | 11.3 | 633.26 | 616.01 | 595.04 | 624.3 | 49.58 | 94.53 | 110.08 | 80.24 |  |  | 1.12 |  | 716.24 | 3.36 | 0.69 | 0.92
20 | 2019-06-19 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM011 | 1S-DL-YP-CTC-DPHG-0114-RAM011 | YOG MAYA:PG | TG-RAM011A-1 | 19505128 | 990 | 320 | 239 | 0.96 | 864 | 348 | 1504 | 249 | 1080 | 267 | 1158 | 391 | 2019-06-27 01:00 | 279.7 | 64.6 | 1504 | R | 109 | 97 | 94 | 15 |  |  | 1.1 | 98.9 | [5 empty] | 1 | 1 |  | 225.19 | 271.19 | 271.19 | 263.49 | 49 | 2.3 | 1.3 | 11 | 0.3 |  |  |  | 274.49 | 13.11 | 0.74 | 0.87
21 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM013 | 1S-DL-YP-CTC-DPHG-0114-RAM013 | TELL MILL:PL | TG-RAM013A-1 | 19505477 | 990 | 320 | 244 | 0.97 | 688 | 190 | 797 | 178 | 740 | 320 | 1352 | 585 | 2019-06-30 | 245.4 | 61.4 | 1352 | B | 91 | 78 | 131 | 53 | 0.1 | 0.1 | 10.8 | 89 |  |  |  |  | 189.2 | 423.51 | 423.51 | 55.3 | 502.54 | 268.23 | 606.51 | 636.44 |  |  | 84.53 | [5 empty] | 692.14 | 27.46 | 0.72 | 0.69
22 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM025 | 1S-DL-YP-CTC-DPHG-0114-RAM025 | CHARA MANDI:K | TG-RAM025A-2 | 19505958 | 630 | 200 | 237 | 0.96 | 555 | 206 | 865 | 174 | 737 | 174 | 731 | 132 | 2019-06-27 23:30 | 169.2 | 51 | 865 | R | 100 | 96 | 104 | 8 |  | 0.9 | 36.1 | 63 |  |  |  |  | 49.43 | 17.3 | 17.3 | 5 | 523.13 | 698.05 | 652.47 | 663.47 | 145.09 | 2.3 | 59.18 | 49.18 |  |  |  |  | 718.05 | 1.55 | 0.69 | 0.88
23 | 2019-06-05 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM026 | 1S-DL-YP-CTC-DPHG-0114-RAM026 | BAGICHI ALLUDDIN:K | TG-RAM026A-2 | 19504529 | 990 | 320 | 253 | 0.96 | 805 | 317 | 1310 | 249 | 1023 | 238 | 984 | 308 | 2019-06-29 23:00 | 259.8 | 43.4 | 1391 | R | 117 | 93 | 90 | 27 |  | 0 | 4.3 | 95.6 | 9 | 9 | 9 | 9 | 4 | 52.3 | 52.3 | 19 | 513.01 | 558.46 | 539.16 | 592.46 | 95.45 | 2.3 |  | 2 | 1 |  |  |  | 622.46 | 1.14 | 0.68 | 0.81
24 | 2019-06-02 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM027 | 1S-DL-YP-CTC-DPHG-0114-RAM027 | ARP QUARTERS.:K | TG-RAM027A-2 | 19504649 | 990 | 320 | 230 | 0.98 | 851 | 297 | 1276 | 229 | 985 | 325 | 1400 | 370 | 2019-06-11 23:30 | 136.9 | 52.3 | 1432 | B | 100 | 86 | 113 | 27 |  |  | 0.7 | 99.3 |  | 1.3 |  |  | 241.18 | 373.1 | 373.1 | 240.08 | 435.13 | 317.21 | 493.4 | 441.53 | 15.3 |  | 74 | 10 |  |  |  |  | 692.01 | 3.59 | 0.56 | 0.86
25 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM030 | 1S-DL-YP-CTC-DPHG-0114-RAM030 | KABIR BASTI:PL | TG-RAM030A-1 | 19504709 | 630 | 200 | 230 | 0.97 | 503 | 141 | 598 | 202 | 872 | 160 | 689 | 241 | 2019-06-03 21:30 | 189.5 | 5.1 | 872 | Y | 81 | 116 | 103 | 35 |  |  | 12.8 | 87.2 | 14 |  |  |  | 521.38 | 219.22 | 219.22 | 358.11 | 157.28 | 439.44 | 355.16 | 334.55 |  | 34 | 0.3 | [5 empty] | 693.06 | 2.54 | 0.52 | 0.8
26 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ001 | 1S-DL-YP-CTC-DPHG-0111-PPQ001 | RAILWAY BOOKING P/M:PL | TG-PPQ001A-2 | 19504817 | 400 | 120 | 266 | 0.96 | 366 | 114 | 426 | 133 | 489 | 120 | 451 | 55 | 2019-06-15 16:00 | 95.8 | 0.6 | 545 | B | 86 | 109 | 105 | 23 | 8.6 | 80.4 | 11 |  | 472.29 | 455.57 | 468.27 | 471.27 | 35.11 | 42.43 | 42.43 | 27.43 | 203.59 | 107.29 | 115.59 | 128.29 | 4.3 | 110 | 101.3 | 88.3 |  |  | 0.29 |  | 716.09 | 3.51 | 0.31 | 0.92
27 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ005 | 1S-DL-YP-CTC-DPHG-0111-PPQ005 | 12 TOOTI CHOWK:PG | TG-PPQ005A-1 | 19505684 | 990 | 320 | 243 | 0.99 | 975 | 325 | 1417 | 310 | 1345 | 341 | 1478 | 116 | 2019-06-29 15:00 | 156.8 | -160.6 | 1563 | B | 109 | 89 | 102 | 20 | 0.2 | 0.1 | 1.5 | 98.2 | 408.38 | 469.07 | 457.37 | 421.08 | 69 | 53.3 | 53.3 | 91.29 | 109.13 | 88.47 | 80.45 | 80.32 | 123 | 99.27 | 122.48 | 117.42 | 1 |  | 14.11 |  | 710.51 | 9.09 | 0.29 | 0.99
28 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ006 | 1S-DL-YP-CTC-DPHG-0111-PPQ006 | WEST END CINEMA:ID | TG-PPQ006A-1 | 19500135 | 630 | 200 | 241 | 0.99 | 512 | 199 | 843 | 157 | 658 | 157 | 661 | 183 | 2019-06-29 13:00 | 78.2 | -0.5 | 887 | R | 117 | 97 | 86 | 31 |  | 0.1 | 34 | 66 | 381 | 372 | 415 | 389.3 | 85.3 | 110 | 110 | 98 | 154.28 | 237.57 | 211.27 | 230.57 | 98.59 |  |  | 1.3 |  |  |  |  | 719.57 | 0.03 | 0.34 | 0.81
29 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ023 | 1S-DL-YP-CTC-DPHG-0111-PPQ023 | NARIAN MARKET:K | TG-PPQ023A-1 | 19504809 | 990 | 200 | 239 | 0.97 | 914 | 277 | 1181 | 265 | 1110 | 371 | 1561 | 420 | 2019-06-25 16:00 | 200.1 | 5.5 | 1572 | B | 93 | 96 | 110 | 17 |  | 2.2 | 38.5 | 59.3 | 396.38 | 311.04 | 59.34 | 284.01 | 102.53 | 197.27 | 197.27 | 222 | 203.35 | 206.04 | 150.41 | 175.05 | 12.59 | 1.3 | 36.54 | 34.59 |  |  | 19.59 |  | 716.05 | 3.55 | 0.36 | 0.92

## Loading Condition > 100%
MIS Report of Distribution Transformer - Jun19
Jun19 1130 PAHAR GANJ (Loading Condition > 100% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR013 | 1S-DL-YP-CTC-DPHG-0112-BGR013 | FOOTA ROAD KIOSK:K | TG-BGR013A-1 | 19504867 | 990 | 320 | 241 | 0.97 | 996 | 313 | 1331 | 405 | 1735 | 278 | 1167 | 506 | 2019-06-04 15:30 | 187.7 | 53.7 | 1769 | Y | 92 | 124 | 84 | 40 |  | 1.6 | 93.4 | 5 | 2 |  | 43 |  | 464.3 | 228 | 228 | 455 | 173.57 | 292.18 | 209.08 | 135.27 | 76.41 | 88.2 | 32 | 126.11 |  | 108.3 |  | 0.3 | 717.08 | 2.52 | 0.47 | 1.01
2 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | B G ROAD | 1130 | BGR020 | 1S-DL-YP-CTC-DPHG-0112-BGR020 | AHATA KIDARA UNIT I:PM | TG-BGR020A-1 | 19506187 | 400 | 120 | 249 | 0.94 | 463 | 238 | 1022 | 119 | 483 | 105 | 456 | 553 | 2019-06-01 19:00 | 176.9 | 74 | 1022 | R | 106 | 109 | 85 | 24 | 0.4 | 0.4 | 43.6 | 55.7 | [8 empty] | 115.57 | 52 | 468.2 | 155.57 | 327.56 | 391.27 | 221 | 417.53 | 251.57 | 252.23 | 6.3 | 122 | 695.5 | 24.1 | 0.77 | 1.16
3 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN015 | 1S-DL-YP-CTC-DPHG-0113-CHN015 | LADOO GHATI:PL | TG-CHN015A-1 | 19500137 | 630 | 200 | 238 | 0.96 | 663 | 228 | 1005 | 230 | 1007 | 206 | 896 | 110 | 2019-06-11 23:30 | 160.1 | 52 | 1077 | R | 106 | 94 | 100 | 12 |  | 0.1 | 33.3 | 66.6 |  |  |  |  | 27 | 90 | 90 | 35 | 522.44 | 509.14 | 583.44 | 548.14 | 129 | 112 | 113.3 | 129 | 38.3 | 6 | 1.3 | 5 | 717.14 | 2.46 | 0.6 | 1.05
4 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | CHN025 | 1S-DL-YP-CTC-DPHG-0113-CHN025 | PHG DISP.:ID | TG-CHN025A-3 | 19504675 | 990 | 320 | 235 | 0.98 | 1066 | 344 | 1548 | 369 | 1675 | 353 | 1592 | 111 | 2019-06-10 22:30 | 197.2 | 41.2 | 1727 | Y | 91 | 101 | 108 | 17 |  | 0.1 | 7.4 | 92.5 | 0.44 | 0.44 | 0.44 | 0.44 | 11.06 | 4.06 | 4.06 | 5.06 | 633.17 | 542.46 | 443.24 | 553.25 | 69.27 | 154.58 | 218.3 | 147.19 | 0.3 | 12.3 | 48.2 | 8.3 | 715.04 | 4.56 | 0.66 | 1.08
5 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM035 | 1S-DL-YP-CTC-DPHG-0114-RAM035 | AARAKASHA ROAD:PKG | TG-RAM035A-2 | 19505638 | 990 | 200 | 236 | 0.98 | 908 | 105 | 450 | 434 | 1873 | 369 | 1584 | 1303 | 2019-06-28 23:30 | 279.4 | 25.2 | 1873 | Y | 34 | 139 | 127 | 105 | 0.1 |  | 1.1 | 98.8 | 448.54 |  |  |  | 249.54 | 4.12 | 4.12 | 152.27 | 2.44 | 523.2 | 574.22 | 544.06 |  | 130.57 | 112.48 | 4.59 |  | 43.03 | 3.14 |  | 701.32 | 18.28 | 0.55 | 0.92
6 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | CHUNA MANDI & RAM NAGAR | 1130 | RAM044 | 1S-DL-YP-CTC-DPHG-0114-RAM044 | DB GUPTA ROAD BUS STOP | TG-RAM044A-1 | 19506758 | 630 | 200 | 242 | 0.97 | 757 | 177 | 724 | 225 | 997 | 355 | 1680 | 852 | 2019-06-06 02:30 | 271.4 | 49.4 | 1680 | B | 105 | 79 | 115 | 36 | 0.4 | 5.5 | 68.9 | 25.3 |  |  |  |  | 46.57 | 291 | 291 | 57.27 | 557 | 366.27 | 533.59 | 576.3 | 73.54 | 47.24 | 119.22 | 54.54 | 29.3 | 2.3 | 37.3 | 18.3 | 707.21 | 12.39 | 0.49 | 1.2
7 | 2019-06-01 | 2019-06-30 23:30 | PAHAR GANG | PP QUARTERS | 1130 | PPQ006 | 1S-DL-YP-CTC-DPHG-0111-PPQ006 | WEST END CINEMA:ID | TG-PPQ006A-2 | 19506190 | 630 | 200 | 243 | 0.99 | 981 | 359 | 1521 | 364 | 1549 | 258 | 1079 | 456 | 2019-06-14 16:30 | 143.6 | -4 | 1665 | R | 115 | 88 | 97 | 27 |  |  | 10.4 | 89.6 | 349.3 | 397 | 378 | 376.3 | 69.3 | 51.3 | 51.3 | 59.3 | 65.2 | 55.2 | 55.23 | 56.2 | 18.03 | 41.33 | 28.3 | 21.33 | 191.37 | 148.37 | 173.37 | 180.07 | 694 | 26 | 0.3 | 1.56