## Complete Report
MIS Report of Distribution Transformer - Jun19
Jun19 1140 SHANKAR ROAD (Complete Report)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW019 | 1S-DL-YP-CTC-DSRD-1404-CPW019 | CHAPPARWALA ZONAL OFFICE:ID | TG-CPW019A-1 | 19504559 | 990 | 320 | 240 | 0.97 | 505 | 181 | 779 | 187 | 807 | 137 | 587 | 207 | 2019-06-11 17:00 | 113.3 | -10.3 | 840 | Y | 113 | 110 | 77 | 36 |  |  | 4.4 | 95.6 | 243.37 | 352.07 | 477.37 | 375.37 | 424.53 | 255.3 | 255.3 | 301.23 | 51 | 111.53 | 14.3 | 42.3 | [8 empty] | 719.3 | 0.3 | 0.44 | 0.51
2 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW019 | 1S-DL-YP-CTC-DSRD-1404-CPW019 | CHAPPARWALA ZONAL OFFICE:ID | TG-CPW019A-2 | 19503536 | 630 | 200 | 241 | 0.99 | 450 | 180 | 763 | 149 | 621 | 120 | 503 | 226 | 2019-06-11 15:00 | 76.8 | -12.9 | 763 | R | 114 | 103 | 83 | 31 |  | 0.2 | 42.3 | 57.5 | 177 | 145.3 | 302.37 | 186.3 | 293.04 | 380.34 | 380.34 | 338.34 | 245.06 | 192.27 | 118.27 | 193.27 | 3.21 | [7 empty] | 718.31 | 1.29 | 0.44 | 0.71
3 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW019 | 1S-DL-YP-CTC-DSRD-1404-CPW019 | CHAPPARWALA ZONAL OFFICE:ID | TG-CPW019A-3 | 19503583 | 990 | 320 | 246 | 0.96 | 753 | 248 | 1013 | 281 | 1152 | 224 | 906 | 214 | 2019-06-29 16:30 | 199.5 | 25.8 | 1152 | Y | 97 | 106 | 97 | 9 |  |  | 64.1 | 35.9 | 315.52 | 132.22 | 138.04 | 175.52 | 177.12 | 348.12 | 348.12 | 319.12 | 225.27 | 236.57 | 206.57 | 223.27 |  | 1 | [6 empty] | 718.31 | 1.29 | 0.44 | 0.76
4 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW031 | 1S-DL-YP-CTC-DSRD-1404-CPW031 | JOSHI ROAD P/M:ID | TG-CPW031A-1 | 19503300 | 990 | 320 | 240 | 0.97 | 636 | 231 | 998 | 218 | 928 | 187 | 804 | 169 | 2019-06-13 17:00 | 146.5 | 36.8 | 1019 | R | 120 | 90 | 90 | 30 |  | 0.3 | 72.2 | 27.6 | 2.3 | 114.3 | 30 | 11 | 262.57 | 392.27 | 392.27 | 489.57 | 454.3 | 213 | 198.3 | 219 | [8 empty] | 719.57 | 0.03 | 0.57 | 0.64
5 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW032 | 1S-DL-YP-CTC-DSRD-1404-CPW032 | JOSHI ROAD KIOSK:K | TG-CPW032A-1 | 19506293 | 990 | 320 | 245 | 0.98 | 870 | 287 | 1191 | 257 | 1079 | 326 | 1377 | 261 | 2019-06-03 | 216.3 | 8.6 | 1518 | B | 105 | 94 | 101 | 11 | 40.1 | 0.8 | 34.1 | 24.9 |  | 1.3 |  |  | 36.3 | 136.58 | 136.58 | 60 | 609.44 | 572.16 | 635.44 | 636.44 | 72.3 | 9 | 28.3 | 23 | 1 |  | 3 |  | 719.44 | 0.16 | 0.64 | 0.88
6 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW032 | 1S-DL-YP-CTC-DSRD-1404-CPW032 | JOSHI ROAD KIOSK:K | TG-CPW032A-2 | 19505957 | 630 | 200 | 246 | 0.97 | 408 | 116 | 487 | 166 | 709 | 126 | 536 | 202 | 2019-06-10 23:30 | 105.2 | 35.4 | 716 | Y | 88 | 111 | 101 | 23 | 0.4 | 1.3 | 89 | 9.3 | 5.3 | 3 | 1 | 1 | 402.13 | 218.43 | 218.43 | 280.13 | 299 | 484.3 | 443.46 | 425.3 |  | 0.3 | [6 empty] | 706.43 | 13.17 | 0.66 | 0.65
7 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW033 | 1S-DL-YP-CTC-DSRD-1404-CPW033 | KHAJOORI ROAD (K):K | TG-CPW033A-1 | 19504950 | 990 | 320 | 245 | 0.96 | 650 | 227 | 943 | 209 | 881 | 214 | 900 | 54 | 2019-06-14 16:00 | 200.2 | 40.5 | 966 | R | 110 | 94 | 97 | 16 |  |  | 46.4 | 53.6 |  | 2.07 | 5.07 | 1.07 | 212.04 | 425.19 | 425.19 | 312 | 502.5 | 287.28 | 361.36 | 401.47 | [8 empty] | 714.54 | 5.06 | 0.64 | 0.66
8 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW033 | 1S-DL-YP-CTC-DSRD-1404-CPW033 | KHAJOORI ROAD (K):K | TG-CPW033A-2 | 19502521 | 400 | 120 | 247 | 0.98 | 109 | 39 | 157 | 47 | 190 | 23 | 94 | 85 | 2019-06-03 15:00 | 26.2 | 1.9 | 205 | Y | 88 | 151 | 61 | 90 | 0.1 | 1.9 | 92.1 | 5.8 | 577.16 | 387.01 | 717.3 | 630.46 | 140.44 | 330.59 | 330.59 | 87.14 | [12 empty] | 718 | 2 | 0.48 | 0.27
9 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW034 | 1S-DL-YP-CTC-DSRD-1404-CPW034 | SUJAN SING AJMAL KHAN ROAD:PL | TG-CPW034A-1 | 19503760 | 990 | 320 | 240 | 0.96 | 403 | 137 | 559 | 129 | 523 | 137 | 550 | 33 | 2019-06-15 15:30 | 103.8 | 32.4 | 624 | R | 110 | 93 | 97 | 17 | 0.1 | 2.6 | 68.2 | 29.2 | 57.57 | 177.57 | 151.3 | 78.57 | 634.58 | 539.22 | 539.22 | 637.52 | 25.24 | 1 | 9.3 | 1.3 | [8 empty] | 718.19 | 1.41 | 0.64 | 0.41
10 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW035 | 1S-DL-YP-CTC-DSRD-1404-CPW035 | AJMAL KHAN KIOSK | TG-CPW035A-1 | 19500400 | 990 | 320 | 240 | 0.96 | 563 | 232 | 947 | 182 | 757 | 150 | 624 | 282 | 2019-06-26 14:30 | 136.9 | 39 | 976 | R | 110 | 101 | 89 | 21 | 0.3 | 98.4 | 1.3 |  | 130 | 164.3 | 189 | 163 | 350.57 | 373.27 | 373.27 | 369.57 | 238.56 | 181.56 | 88.56 | 186.56 | [8 empty] | 719.53 | 0.07 | 0.53 | 0.57
11 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW035 | 1S-DL-YP-CTC-DSRD-1404-CPW035 | AJMAL KHAN KIOSK | TG-CPW035A-2 | 19505173 | 400 | 120 | 241 | 0.96 | 314 | 155 | 685 | 80 | 354 | 78 | 342 | 337 | 2019-06-03 14:30 | 85.4 | 14 | 685 | R | 121 | 89 | 89 | 32 | 0.1 | 0.1 | 33.1 | 66.7 | 9 | 180 | 69.3 | 25 | 400.57 | 291.57 | 291.57 | 426.57 | 204 | 224.26 | 208.56 | 244.26 | 76.56 |  |  |  | 5.3 |  |  |  | 696.23 | 23.37 | 0.48 | 0.78
12 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW036 | 1S-DL-YP-CTC-DSRD-1404-CPW036 | TIBBIA COLLEGE:PL | TG-CPW036A-1 | 19504501 | 630 | 200 | 245 | 0.97 | 449 | 137 | 550 | 178 | 725 | 135 | 546 | 177 | 2019-06-12 16:00 | 82.8 | -5.5 | 774 | Y | 86 | 110 | 104 | 24 |  |  | 82.7 | 17.3 | 3.3 | 2 | 2 | 2 | 495.27 | 217.27 | 217.27 | 283.27 | 219.47 | 495.47 | 491.47 | 433.17 |  | 3.3 | [6 empty] | 718.44 | 1.16 | 0.6 | 0.71
13 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW037 | 1S-DL-YP-CTC-DSRD-1404-CPW037 | 53 BLOCK RAMJAS ROAD:K | TG-CPW037A-1 | 19500315 | 990 | 320 | 244 | 0.97 | 923 | 248 | 1003 | 268 | 1103 | 407 | 1664 | 617 | 2019-06-03 02:00 | 242.9 | 67.7 | 1703 | B | 97 | 97 | 106 | 9 | 32.3 | 11.8 | 49.3 | 6.6 | 0.3 |  |  |  | 137.16 | 130.19 | 130.19 | 91.46 | 566.43 | 575.17 | 545.59 | 610.5 | 7 | 5.53 | 56.3 | 8.53 |  |  | 11.53 |  | 711.29 | 8.31 | 0.57 | 0.93
14 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW038 | 1S-DL-YP-CTC-DSRD-1404-CPW038 | 61 BLOCK RAMJAS ROAD PL/M:PL | TG-CPW038A-1 | 19504948 | 990 | 320 | 238 | 0.97 | 799 | 290 | 1238 | 254 | 1086 | 256 | 1058 | 167 | 2019-06-03 00:30 | 156.8 | 24.3 | 1270 | R | 105 | 100 | 95 | 10 | 66.7 | 32.9 | 0.5 |  | 0.3 | 0.3 | 0.3 | 0.3 | 38.3 | 92 | 92 | 74 | 674.4 | 626.1 | 580.4 | 644.4 | 6 | 1 | 4 | 0.3 |  |  |  |  | 719.4 | 0.2 | 0.65 | 0.81
15 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW039 | 1S-DL-YP-CTC-DSRD-1404-CPW039 | RAMJAS ROAD KIOSK:ID | TG-CPW039A-1 | 19504499 | 990 | 320 | 245 | 0.98 | 686 | 189 | 777 | 259 | 1076 | 238 | 981 | 264 | 2019-06-11 01:00 | 132.5 | 30.9 | 1164 | Y | 97 | 109 | 94 | 15 |  |  | 7.2 | 92.8 | 7 | 5 | 5.3 | 1.3 | 446.4 | 342.1 | 342.1 | 417.4 | 266 | 370.3 | 236 | 300.3 |  | 2 | [6 empty] | 719.4 | 0.2 | 0.56 | 0.69
16 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW039 | 1S-DL-YP-CTC-DSRD-1404-CPW039 | RAMJAS ROAD KIOSK:ID | TG-CPW039A-2 | 19505083 | 630 | 200 | 247 | 0.97 | 273 | 66 | 275 | 125 | 516 | 82 | 339 | 217 | 2019-06-01 23:30 | 59.8 | 11.5 | 560 | Y | 79 | 134 | 87 | 55 |  |  | 0.1 | 99.9 | 432.16 | 73.45 | 379.46 | 253.54 | 285.3 | 511.01 | 511.01 | 451.22 |  | 133 | 0.3 | 12.3 | [8 empty] | 717.46 | 2.14 | 0.54 | 0.43
17 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW045 | 1S-DL-YP-CTC-DSRD-1404-CPW045 | KHALSA COLLEGE P/M | TG-CPW045A-1 | 19505176 | 990 | 320 | 241 | 0.97 | 671 | 231 | 933 | 232 | 938 | 209 | 835 | 100 | 2019-06-06 16:30 | 191.4 | 14.7 | 1001 | Y | 106 | 102 | 92 | 14 | 0.1 | 0.4 | 70.4 | 29 | 18 | 42.3 | 159.3 | 52 | 424.57 | 397.27 | 397.27 | 405.27 | 253.3 | 256.3 | 226 | 239 | [8 empty] | 696.27 | 23.33 | 0.53 | 0.68
18 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW047 | 1S-DL-YP-CTC-DSRD-1404-CPW047 | CPWD HOSTEL:ID | TG-CPW047A-1 | 19500420 | 400 | 120 | 247 | 0.98 | 43 | 9 | 38 | 16 | 68 | 18 | 74 | 33 | 2019-06-11 23:00 | 9.7 | 0.3 | 91 | Y | 54 | 150 | 96 | 96 |  |  | 7.6 | 92.4 | 720 | 720 | 720 | 720 | [16 empty] | 720 | 0 | 0.44 | 0.11
19 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW048 | 1S-DL-YP-CTC-DSRD-1404-CPW048 | KHAJOOR ROAD PL/M | TG-CPW048A-1 | 19505010 | 990 | 320 | 247 | 0.98 | 683 | 227 | 959 | 227 | 961 | 228 | 955 | 5 | 2019-06-07 15:00 | 147.9 | 23.6 | 961 | Y | 104 | 102 | 94 | 10 |  |  | 74.9 | 25.1 |  |  | 2.3 |  | 296.52 | 302.22 | 302.22 | 339.22 | 423 | 417.3 | 310.3 | 380.3 | [8 empty] | 719.52 | 0.08 | 0.6 | 0.69
20 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW049 | 1S-DL-YP-CTC-DSRD-1404-CPW049 | N JOSHI MEMORIAL HOSPITAL | TG-CPW049A-1 | 19506706 | 630 | 200 | 246 | 0.95 | 340 | 109 | 458 | 116 | 490 | 115 | 480 | 28 | 2019-06-10 12:00 | 102.6 | 28.6 | 602 | Y | 101 | 107 | 92 | 15 | 0.3 | 0.1 | 43.1 | 56.6 | 37.3 | 4 | 102 | 15.3 | 616.36 | 636.17 | 636.17 | 650.17 | 64.38 | 78.27 | 50.57 | 52.57 | [8 empty] | 718.44 | 1.16 | 0.55 | 0.54
21 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW049 | 1S-DL-YP-CTC-DSRD-1404-CPW049 | N JOSHI MEMORIAL HOSPITAL | TG-CPW049A-2 | 19504664 | 630 | 200 | 240 | 0.97 | 291 | 95 | 409 | 83 | 356 | 113 | 482 | 110 | 2019-06-30 23:00 | 76.4 | 16.1 | 519 | B | 100 | 91 | 109 | 18 |  | 0.1 | 36.7 | 63.2 | 101 | 135 | 59.3 | 64.3 | 597.44 | 582.14 | 582.14 | 643.14 | 20 | 1.3 | 66.3 | 11 | [8 empty] | 718.44 | 1.16 | 0.59 | 0.46
22 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW050 | 1S-DL-YP-CTC-DSRD-1404-CPW050 | 53 BLK RAMJAS ROAD:PL\M | TG-CPW050A-1 | 19500396 | 990 | 320 | 252 | 0.98 | 496 | 135 | 568 | 152 | 638 | 208 | 881 | 285 | 2019-06-06 16:00 | 73.6 | 7.4 | 904 | B | 87 | 105 | 108 | 21 |  |  | 6.6 | 93.4 | 363 | 116 | 176.3 | 170 | 324.07 | 544.38 | 544.38 | 467.07 | 32.3 | 58.59 | 125.07 | 82.3 | [8 empty] | 719.37 | 0.23 | 0.53 | 0.5
23 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW056 | 1S-DL-YP-CTC-DSRD-1404-CPW056 | 20 ROHTAK ROAD | TG-CPW056A-1 | 19506791 | 990 | 320 | 248 | 0.94 | 290 | 100 | 408 | 104 | 419 | 86 | 348 | 66 | 2019-06-03 10:30 | 145.9 | 7.4 | 448 | R | 114 | 113 | 73 | 41 |  | 0.1 | 36.4 | 63.5 | 544.27 | 566.03 | 699.14 | 614.03 | 161.17 | 139.41 | 139.41 | 91.41 | [12 empty] | 705.44 | 14.16 | 0.45 | 0.29
24 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW001 | 1S-DL-YP-CTC-DSRD-1401-KKW001 | NANAK HOTEL K. BAGH:PL | TG-KKW001A-1 | 19503278 | 990 | 320 | 239 | 0.98 | 1029 | 380 | 1675 | 319 | 1409 | 330 | 1452 | 248 | 2019-06-04 16:00 | 170 | 0.7 | 1725 | R | 117 | 90 | 93 | 27 |  |  | 2 | 98 | 142.3 | 372 | 272.52 | 311 | 282.23 | 65.23 | 65.23 | 121.23 | 98.3 | 160 | 201.57 | 142 | 96.27 | 96.57 | 45.3 | 114.57 | 74.3 |  | 0.3 | 5 | 694.2 | 1.4 | 0.38 | 1.04
25 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW002 | 1S-DL-YP-CTC-DSRD-1401-KKW002 | MASJID WALA K. BAGH.:PL | TG-KKW002A-1 | 19506653 | 990 | 320 | 246 | 0.97 | 995 | 328 | 1340 | 318 | 1305 | 349 | 1433 | 114 | 2019-06-15 16:00 | 266.6 | 22.7 | 1894 | B | 107 | 91 | 102 | 16 | 0.3 |  | 0.2 | 99.5 | 39 | 248.59 | 140.54 | 110.59 | 399.2 | 200.21 | 200.21 | 335.21 | 121.03 | 135.55 | 90.45 | 110.15 | 133.02 | 109.1 | 142.2 | 137.2 | 2 |  | 15 | 0.3 | 694.25 | 25.35 | 0.43 | 1.01
26 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW003 | 1S-DL-YP-CTC-DSRD-1401-KKW003 | ELAHI BUX:PL | TG-KKW003A-1 | 19503286 | 990 | 320 | 245 | 0.96 | 831 | 271 | 1169 | 287 | 1235 | 273 | 1177 | 62 | 2019-06-29 15:30 | 206.8 | 38.3 | 1275 | Y | 94 | 108 | 98 | 14 |  |  |  | 100 | 2.41 | 0.41 | 4.11 | 0.41 | 233.17 | 173.42 | 173.42 | 221.17 | 162.06 | 190.23 | 171.43 | 171.36 | 2.3 | 35.48 | 8.23 | 7 |  |  |  |  | 400.34 | 31.26 | 0.54 | 0.84
27 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW003 | 1S-DL-YP-CTC-DSRD-1401-KKW003 | ELAHI BUX:PL | TG-KKW003A-2 | 19503288 | 990 | 320 | 245 | 0.97 | 630 | 253 | 1068 | 180 | 757 | 197 | 833 | 281 | 2019-06-12 15:00 | 145.7 | 14 | 1095 | R | 106 | 95 | 98 | 11 |  |  | 0.6 | 99.4 | 275.36 | 122.36 | 208.48 | 173.06 | 197.17 | 442.42 | 442.42 | 332.47 | 244.4 | 152.15 | 213.4 | 211.4 | [8 empty] | 717.33 | 2.27 | 0.49 | 0.64
28 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW004 | 1S-DL-YP-CTC-DSRD-1401-KKW004 | BIRLA FLATS K. BAGH:PL | TG-KKW004A-1 | 19504500 | 990 | 320 | 239 | 0.97 | 842 | 238 | 1027 | 282 | 1225 | 323 | 1404 | 326 | 2019-06-29 16:30 | 185.5 | 7.4 | 1404 | B | 88 | 94 | 118 | 30 |  |  | 1.3 | 98.7 | 17 | 30.3 | 0.3 | 1.3 | 433.25 | 407.55 | 407.55 | 405.37 | 266.25 | 261.55 | 483.24 | 301.43 | 0.3 | 17 | 48 | 8.3 |  |  |  |  | 717.2 | 2.4 | 0.52 | 0.85
29 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW004 | 1S-DL-YP-CTC-DSRD-1401-KKW004 | BIRLA FLATS K. BAGH:PL | TG-KKW004A-2 | 19500429 | 990 | 320 | 245 | 0.97 | 838 | 247 | 1028 | 296 | 1234 | 294 | 1218 | 199 | 2019-06-15 15:30 | 203.9 | 14.7 | 1359 | B | 82 | 102 | 115 | 33 |  |  | 0.1 | 99.9 | 253.24 | 84.3 | 30.3 | 90.3 | 233.05 | 382.29 | 382.29 | 375.59 | 230.5 | 194.2 | 142.11 | 226.5 |  | 56 | 130.46 | 24 |  |  |  |  | 717.19 | 2.41 | 0.47 | 0.85
30 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW010 | 1S-DL-YP-CTC-DSRD-1401-KKW010 | POLICE QTR. K. BAGH:PL | TG-KKW010A-1 | 19500312 | 990 | 320 | 240 | 0.97 | 743 | 216 | 941 | 244 | 1065 | 283 | 1226 | 248 | 2019-06-11 16:30 | 196.5 | -14 | 1247 | B | 92 | 97 | 111 | 19 |  | 0.1 | 29.8 | 70.1 | 426.17 | 418.47 | 416.47 | 419.47 | 66 | 66.3 | 66.3 | 61 | 225.42 | 232.42 | 209.12 | 237.12 |  |  | 34 | [5 empty] | 717.59 | 2.01 | 0.37 | 0.75
31 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW010 | 1S-DL-YP-CTC-DSRD-1401-KKW010 | POLICE QTR. K. BAGH:PL | TG-KKW010A-2 | 19500430 | 990 | 320 | 241 | 0.97 | 352 | 115 | 488 | 129 | 550 | 108 | 455 | 83 | 2019-06-26 12:00 | 78.8 | -30.9 | 559 | Y | 93 | 110 | 96 | 17 |  |  | 43.9 | 56.1 | 550.43 | 520.43 | 518.43 | 534.43 | 167.23 | 197.23 | 197.23 | 183.23 | [12 empty] | 718.06 | 1.54 | 0.38 | 0.36
32 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW010 | 1S-DL-YP-CTC-DSRD-1401-KKW010 | POLICE QTR. K. BAGH:PL | TG-KKW010A-3 | 19501358 | 630 | 200 | 242 | 0.98 | 313 | 113 | 485 | 103 | 439 | 96 | 413 | 63 | 2019-06-11 14:30 | 57.5 | -2.3 | 490 | R | 108 | 108 | 83 | 25 |  |  | 0.1 | 99.9 | 453.47 | 447.17 | 480.17 | 462.47 | 155 | 212.53 | 212.53 | 196.23 | 109.23 | 58 | 26.3 | 59 | [8 empty] | 718.1 | 1.5 | 0.35 | 0.5
33 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW011 | 1S-DL-YP-CTC-DSRD-1401-KKW011 | P.O. NO. 3 K. BAGH:PL | TG-KKW011A-1 | 19504498 | 990 | 320 | 252 | 0.96 | 616 | 237 | 947 | 204 | 815 | 175 | 697 | 217 | 2019-06-15 16:30 | 162.7 | 4.4 | 995 | R | 112 | 99 | 88 | 24 |  |  |  | 100 | 436.34 | 447.02 | 465.32 | 446.02 | 70.58 | 97.3 | 97.3 | 87 | 210.53 | 173.53 | 136.53 | 185.23 | [8 empty] | 718.25 | 1.35 | 0.35 | 0.62
34 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW012 | 1S-DL-YP-CTC-DSRD-1401-KKW012 | PO NO. 7 K. BAGH:PL | TG-KKW012A-1 | 19500422 | 990 | 320 | 236 | 0.98 | 624 | 221 | 983 | 211 | 938 | 193 | 846 | 120 | 2019-06-01 15:30 | 139.8 | -5.9 | 983 | R | 106 | 100 | 94 | 12 |  | 0.2 | 25.6 | 74.2 | 457.32 | 464.32 | 461.32 | 461.02 | 48.15 | 61.15 | 61.15 | 52.45 | 209.27 | 189.27 | 195.57 | 201.27 | [8 empty] | 715.14 | 4.46 | 0.33 | 0.63
35 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW013 | 1S-DL-YP-CTC-DSRD-1401-KKW013 | PO NO. 1 K. BAGH:PL | TG-KKW013A-1 | 19500426 | 990 | 320 | 248 | 0.95 | 817 | 298 | 1258 | 275 | 1155 | 244 | 1015 | 212 | 2019-06-11 17:00 | 214.2 | 11.8 | 1258 | R | 109 | 99 | 92 | 17 |  | 0.3 | 45.4 | 54.3 | 426.21 | 428.21 | 434.51 | 428.51 | 77.27 | 75.27 | 75.27 | 77.57 | 205.22 | 211.02 | 194.02 | 208.32 | 6.4 | 1 |  | 0.3 |  |  |  |  | 715.5 | 4.1 | 0.3 | 0.83
36 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW013 | 1S-DL-YP-CTC-DSRD-1401-KKW013 | PO NO. 1 K. BAGH:PL | TG-KKW013A-2 | 19505447 | 990 | 320 | 248 | 0.97 | 817 | 258 | 1091 | 300 | 1278 | 259 | 1089 | 188 | 2019-06-12 14:00 | 228.8 | -1 | 1420 | Y | 109 | 100 | 91 | 18 | 0.3 | 0.1 | 10.7 | 88.8 | 401.59 | 414.29 | 436.29 | 416.59 | 86.11 | 75.41 | 75.41 | 72.41 | 180.01 | 195.17 | 212.17 | 207.47 | 34.11 | 16.25 | 0.25 | 4.55 |  | 0.3 |  |  | 702.22 | 17.38 | 0.36 | 0.83
37 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW014 | 1S-DL-YP-CTC-DSRD-1401-KKW014 | PO NO. 2 K. BAGH:PG | TG-KKW014A-1 | 19503277 | 990 | 320 | 248 | 0.98 | 747 | 276 | 1119 | 224 | 909 | 247 | 992 | 183 | 2019-06-11 16:30 | 136.9 | -100.1 | 1155 | R | 111 | 95 | 95 | 16 |  |  | 1.9 | 98.1 | 377.13 | 388.13 | 386.13 | 379.13 | 96 | 119.3 | 119.3 | 109 | 237.22 | 210.22 | 217.52 | 229.52 | 7.3 | [7 empty] | 718.05 | 1.55 | 0.36 | 0.75
38 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW015 | 1S-DL-YP-CTC-DSRD-1401-KKW015 | PO NO. 4 K. BAGH:PL | TG-KKW015A-1 | 19500428 | 990 | 320 | 243 | 0.98 | 571 | 173 | 742 | 225 | 954 | 173 | 733 | 217 | 2019-06-11 12:30 | 142.8 | -2.9 | 954 | Y | 88 | 112 | 99 | 24 |  | 0.1 | 1.7 | 98.3 | 465.27 | 448.57 | 451.27 | 454.57 | 209.56 | 51 | 51 | 103.57 | 44.28 | 219.54 | 114.3 | 160.57 | [8 empty] | 719.51 | 0.09 | 0.34 | 0.58
39 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW016 | 1S-DL-YP-CTC-DSRD-1401-KKW016 | PO NO. 6 K. BAGH :PKG | TG-KKW016A-1 | 19503293 | 990 | 320 | 246 | 0.98 | 539 | 165 | 696 | 204 | 831 | 171 | 727 | 123 | 2019-06-15 14:30 | 81 | 5.9 | 863 | Y | 95 | 106 | 99 | 11 | 100 |  |  |  | 451.3 | 442 | 451 | 447 | 110.3 | 84.3 | 84.3 | 106 | 133.57 | 169.27 | 106.27 | 142.57 | [8 empty] | 695.57 | 0.03 | 0.35 | 0.54
40 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW017 | 1S-DL-YP-CTC-DSRD-1401-KKW017 | PO NO. 5 K. BAGH:PG | TG-KKW017A-1 | 19503298 | 990 | 320 | 240 | 0.99 | 888 | 310 | 1352 | 301 | 1308 | 276 | 1196 | 139 | 2019-06-29 13:00 | 111.1 | 1.5 | 1465 | R | 107 | 99 | 94 | 13 |  |  | 13.1 | 86.9 | 433.22 | 434.52 | 434.22 | 435.22 | 30 | 31 | 31 | 30.3 | 114.57 | 193.57 | 214.57 | 170.27 | 140.3 | 59 | 29 | 82.3 |  |  |  |  | 718.49 | 1.11 | 0.34 | 0.9
41 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW018 | 1S-DL-YP-CTC-DSRD-1401-KKW018 | H S ROAD BASEMENT:ID | TG-KKW018A-1 | 19500620 | 990 | 320 | 239.3893 | 0.97391 | 949.1251 | 316.2925 | 1364.2707 | 345.4483 | 1484.1396 | 287.3842 | 1222.5994 | 226.7626 | 2019-06-04 16:30 | [15 empty] | 431 |  |  |  | 30.5 |  |  |  | 101.5 |  |  |  | 155.5 |  |  |  | 0 | 718.5 |  | 0.34958 | 0.95871
42 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW018 | 1S-DL-YP-CTC-DSRD-1401-KKW018 | H S ROAD BASEMENT:ID | TG-KKW018A-2 | 19500417 | 990 | 320 | 249 | 0.98 | 808 | 279 | 1105 | 260 | 1016 | 269 | 1063 | 77 | 2019-06-30 14:30 | 171.5 | 2.9 | 1256 | R | 101 | 104 | 95 | 9 | 0.1 | 1.3 | 41.7 | 56.9 | 433.46 | 431.16 | 434.16 | 433.46 | 39.24 | 39.24 | 39.24 | 36.54 | 179.45 | 245.12 | 242.15 | 243.12 | 65.27 | 2.3 | 6 | 4.3 |  |  |  |  | 718.22 | 1.38 | 0.35 | 0.82
43 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW018 | 1S-DL-YP-CTC-DSRD-1401-KKW018 | H S ROAD BASEMENT:ID | TG-KKW018A-3 | 19500418 | 990 | 320 | 249 | 0.97 | 988 | 322 | 1341 | 294 | 1221 | 372 | 1543 | 282 | 2019-06-15 15:30 | 239.9 | -6.6 | 1559 | B | 98 | 92 | 110 | 18 |  |  | 1.9 | 98.1 | 432.24 | 436.24 | 428.24 | 433.24 | 39.3 | 35 | 35 | 35.3 | 112 | 170.3 | 52.3 | 93.3 | 134.3 | 77.3 | 131.3 | 157 | 1 |  | 76 |  | 719.24 | 0.36 | 0.34 | 1
44 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW018 | 1S-DL-YP-CTC-DSRD-1401-KKW018 | H S ROAD BASEMENT:ID | TG-KKW018A-4 | 19502004 | 630 | 200 | 251 | 0.98 | 234 | 63 | 253 | 113 | 462 | 58 | 236 | 218 | 2019-06-02 15:00 | 41.4 | -6.9 | 480 | Y | 90 | 138 | 72 | 66 |  | 0.1 | 17.5 | 82.4 | 500.07 | 475.07 | 579.37 | 495.07 | 219.3 | 110.3 | 110.3 | 224.3 |  | 134 | [10 empty] | 719.37 | 0.23 | 0.3 | 0.37
45 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW018 | 1S-DL-YP-CTC-DSRD-1401-KKW018 | H S ROAD BASEMENT:ID | TG-KKW018A-5 | 19502915 | 630 | 200 | 241 | 0.97 | 218 | 80 | 339 | 75 | 317 | 63 | 266 | 65 | 2019-06-02 18:30 | 43.7 | 0.9 | 340 | R | 103 | 109 | 89 | 20 |  |  | 1.3 | 98.7 | 496 | 485 | 542.53 | 493.3 | 221.53 | 232.53 | 232.53 | 224.23 | [12 empty] | 717.53 | 2.07 | 0.31 | 0.35
46 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW019 | 1S-DL-YP-CTC-DSRD-1401-KKW019 | MCD CAR PARKING:ID | TG-KKW019A-1 | 19505069 | 990 | 320 | 243 | 0.97 | 558 | 183 | 773 | 223 | 958 | 153 | 642 | 275 | 2019-06-29 15:30 | 116.3 | 3.7 | 958 | Y | 96 | 121 | 82 | 39 | 14.8 | 15.3 | 60.6 | 9.2 | 280.5 | 261.5 | 288.2 | 278.5 | 29.59 | 35.29 | 35.29 | 29.29 | 128.25 | 141.55 | 98.55 | 130.55 | [8 empty] | 718.46 | 1.14 | 0.38 | 0.56
47 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN029 | 1S-DL-YP-CTC-DSRD-1403-RJN029 | JHANDENWALAN NO. 3:ID | TG-RJN029A-1 | 19500387 | 990 | 320 | 248 | 0.96 | 421 | 163 | 688 | 95 | 400 | 163 | 672 | 280 | 2019-06-14 15:00 | 120 | 32.4 | 789 | R | 116 | 79 | 105 | 37 |  | 0.4 | 47.1 | 52.6 | 11 | 146.27 | 33.3 | 28 | 493.57 | 549.25 | 549.25 | 647.22 | 190.55 |  | 77.3 | 20.3 | [8 empty] | 695.52 | 0.08 | 0.7 | 0.43
48 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN029 | 1S-DL-YP-CTC-DSRD-1403-RJN029 | JHANDENWALAN NO. 3:ID | TG-RJN029A-2 | 19500390 | 990 | 320 | 246 | 0.97 | 487 | 186 | 764 | 161 | 659 | 140 | 567 | 170 | 2019-06-29 23:30 | 106.7 | 36.1 | 764 | R | 114 | 97 | 89 | 25 |  |  | 75.8 | 24.2 | 1 | 11 | 8 | 7 | 400.39 | 474.09 | 474.09 | 473.39 | 293.03 | 209.33 | 19 | 214.03 | [8 empty] | 694.42 | 1.18 | 0.7 | 0.49
49 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN030 | 1S-DL-YP-CTC-DSRD-1403-RJN030 | SP.MUKERJI MKT. FAIZ RD. P/M NO. 2:PL | TG-RJN030A-1 | 19503297 | 990 | 320 | 244 | 0.99 | 675 | 201 | 827 | 262 | 1077 | 213 | 872 | 231 | 2019-06-30 | 113.3 | -11.8 | 1155 | Y | 97 | 111 | 92 | 19 |  | 1.4 | 45.1 | 53.4 |  |  |  |  | 188.24 | 81.24 | 81.24 | 144.56 | 525.17 | 630.17 | 477.34 | 568.45 |  | 2 | [6 empty] | 713.41 | 6.19 | 0.7 | 0.68
50 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN030 | 1S-DL-YP-CTC-DSRD-1403-RJN030 | SP.MUKERJI MKT. FAIZ RD. P/M NO. 2:PL | TG-RJN030A-2 | 19505972 | 400 | 120 | 243 | 0.98 | 393 | 76 | 311 | 112 | 458 | 206 | 881 | 513 | 2019-06-02 02:00 | 108.8 | 8 | 888 | B | 89 | 97 | 115 | 26 | 2.5 | 1.1 | 48.1 | 48.3 |  | 1.3 | 1 | 1 | 207.07 | 102.59 | 102.59 | 49.57 | 483.48 | 571.15 | 603.59 | 634 | 23.26 | 27.37 | 70.22 | 29.24 |  | 11 | 15.3 |  | 714.21 | 5.39 | 0.57 | 0.98
51 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN031 | 1S-DL-YP-CTC-DSRD-1403-RJN031 | FAIZ ROAD NO. 1:PM | TG-RJN031A-1 | 19504505 | 630 | 200 | 244 | 0.96 | 368 | 149 | 592 | 112 | 459 | 106 | 429 | 151 | 2019-06-25 23:00 | 99.4 | 43.2 | 616 | R | 112 | 98 | 90 | 22 | 96.4 | 3.1 | 0.1 | 0.4 |  |  |  |  | 75 | 191.13 | 191.13 | 155.37 | 640.44 | 524.31 | 370.2 | 560.07 | [8 empty] | 715.44 | 4.16 | 0.77 | 0.58
52 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN032 | 1S-DL-YP-CTC-DSRD-1403-RJN032 | KHANNA ICE FACTROY JHANDENWALAN:ID | TG-RJN032A-1 | 19506405 | 990 | 320 | 246 | 0.94 | 319 | 121 | 477 | 86 | 362 | 112 | 479 | 116 | 2019-06-27 16:00 | 177 | 9 | 590 | B | 116 | 82 | 101 | 34 | 100 |  |  |  | 311.06 | 542.09 | 451.31 | 409.01 | 379.4 | 148.37 | 148.37 | 281.45 |  |  | 0.3 | [9 empty] | 690.46 | 29.14 | 0.55 | 0.32
53 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN033 | 1S-DL-YP-CTC-DSRD-1403-RJN033 | F. FACTORY G BLOCK:ID | TG-RJN033A-1 | 19500692 | 990 | 300 | 246 | 0.95 | 58 | 12 | 47 | 20 | 78 | 26 | 104 | 50 | 2019-06-17 14:30 | 23.5 | 0.7 | 115 | B | 21 | 106 | 173 | 152 |  |  | 1.6 | 98.4 | 718.21 | 718.21 | 718.21 | 718.21 | [16 empty] | 718.21 | 1.39 | 0.18 | 0.06
54 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN034 | 1S-DL-YP-CTC-DSRD-1403-RJN034 | F. FACTORY E BLOCK:ID | TG-RJN034A-1 | 19502919 | 990 | 300 | 246 | 0.95 | 14 | 5 | 19 | 5 | 19 | 4 | 16 | 3 | 2019-06-17 16:30 | 0.7 | -0.7 | 22 | Y | 124 | 122 | 54 | 70 |  |  | 2.5 | 97.5 | 718.24 | 718.24 | 718.24 | 718.24 | [16 empty] | 718.24 | 1.36 | 0.23 | 0.01
55 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN034 | 1S-DL-YP-CTC-DSRD-1403-RJN034 | F. FACTORY E BLOCK:ID | TG-RJN034A-2 | 19503587 | 990 | 300 | 247 | 0.93 | 26 | 11 | 47 | 13 | 54 | 1 | 6 | 45 | 2019-06-12 14:00 | 8.3 | 0.7 | 55 | Y | 140 | 129 | 31 | 109 |  |  | 34.6 | 65.4 | 717.54 | 717.54 | 717.54 | 717.54 | [16 empty] | 717.54 | 2.06 | 0.2 | 0.03
56 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN035 | 1S-DL-YP-CTC-DSRD-1403-RJN035 | F. FACTORY C BLOCK:ID | TG-RJN035A-1 | 19500412 | 990 | 300 | 247 | 0.97 | 283 | 117 | 491 | 82 | 343 | 85 | 355 | 143 | 2019-06-10 14:30 | 55.9 | -20 | 526 | R | 121 | 92 | 87 | 34 |  |  | 0.2 | 99.8 | 506.24 | 561.45 | 610.4 | 526.59 | 210.55 | 155.34 | 155.34 | 190.2 | [12 empty] | 717.19 | 2.41 | 0.3 | 0.29
57 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN036 | 1S-DL-YP-CTC-DSRD-1403-RJN036 | F. FACTORY A BLOCK:ID | TG-RJN036A-1 | 19500705 | 990 | 300 | 246.3447 | 0.9681 | 243.9094 | 78.3598 | 334.3424 | 77.0115 | 330.8624 | 88.5381 | 382.2721 | 49.7611 | 2019-06-11 15:30 | [15 empty] | 626.5 |  |  |  | 67 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 693.5 |  | 0.28033 | 0.24637
58 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN036 | 1S-DL-YP-CTC-DSRD-1403-RJN036 | F. FACTORY A BLOCK:ID | TG-RJN036A-2 | 19503559 | 990 | 300 | 247 | 0.98 | 147 | 47 | 209 | 42 | 186 | 57 | 252 | 59 | 2019-06-11 15:30 | 25.5 | -0.7 | 252 | B | 94 | 88 | 118 | 30 |  |  | 4.9 | 95.1 | 690.27 | 690.27 | 690.27 | 690.27 | [16 empty] | 690.27 | 5.33 | 0.27 | 0.15
59 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN037 | 1S-DL-YP-CTC-DSRD-1403-RJN037 | 2E JHANDEWALAN PL/M(PARK):PL | TG-RJN037A-1 | 19500714 | 990 | 320 | 247.3867 | 0.96766 | 854.6998 | 308.1731 | 1295.8252 | 263.9132 | 1106.508 | 282.6135 | 1182.6315 | 164.9979 | 2019-06-11 15:00 | [15 empty] | 348.5 |  |  |  | 158 |  |  |  | 211.5 |  |  |  | 2 |  |  |  | 0 | 720 |  | 0.36091 | 0.86333
60 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN037 | 1S-DL-YP-CTC-DSRD-1403-RJN037 | 2E JHANDEWALAN PL/M(PARK):PL | TG-RJN037A-2 | 19500411 | 990 | 320 | 249 | 0.96 | 401 | 126 | 510 | 166 | 671 | 109 | 440 | 206 | 2019-06-03 13:00 | 54.5 | -36.8 | 677 | Y | 99 | 111 | 90 | 21 |  |  | 0.1 | 99.9 | 469.53 | 457.23 | 473.23 | 467.23 | 222.56 | 148.35 | 148.35 | 225.56 | 2.3 | 89.21 |  | 2 | [8 empty] | 718.33 | 1.27 | 0.4 | 0.41
61 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN037 | 1S-DL-YP-CTC-DSRD-1403-RJN037 | 2E JHANDEWALAN PL/M(PARK):PL | TG-RJN037A-3 | 19503558 | 990 | 320 | 243 | 0.97 | 680 | 218 | 899 | 248 | 1022 | 214 | 874 | 137 | 2019-06-21 12:00 | 156.8 | -7.4 | 1046 | Y | 94 | 107 | 99 | 13 |  |  | 29.8 | 70.2 | 472.27 | 455.57 | 474.27 | 468.27 | 103.57 | 79.59 | 79.59 | 83.32 | 115.5 | 156.18 | 124.15 | 140.15 | [8 empty] | 692.14 | 3.46 | 0.27 | 0.69
62 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN038 | 1S-DL-YP-CTC-DSRD-1403-RJN038 | 2E JHANDEWALAN(K):K | TG-RJN038A-1 | 19503355 | 990 | 320 | 243 | 0.98 | 633 | 216 | 902 | 204 | 861 | 213 | 893 | 37 | 2019-06-06 13:00 | 110.4 | 5.2 | 1001 | B | 85 | 104 | 111 | 26 |  |  | 40.7 | 59.3 | 496.57 | 478.27 | 461.57 | 473.57 | 106.32 | 82.55 | 82.55 | 89.55 | 115.29 | 157.36 | 164.06 | 155.06 | [8 empty] | 718.58 | 1.02 | 0.31 | 0.64
63 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN039 | 1S-DL-YP-CTC-DSRD-1403-RJN039 | 4E GURUDWARA:K | TG-RJN039A-1 | 19503757 | 990 | 320 | 243 | 0.98 | 430 | 146 | 602 | 146 | 600 | 138 | 570 | 31 | 2019-06-14 16:30 | 69.9 | -17.7 | 649 | B | 95 | 104 | 100 | 9 |  |  | 1.7 | 98.3 | 510.43 | 496.43 | 503.43 | 504.13 | 191.11 | 182.41 | 182.41 | 192.11 | 16 | 38.3 | 22.3 | 21.3 | [8 empty] | 717.54 | 2.06 | 0.32 | 0.43
64 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN039 | 1S-DL-YP-CTC-DSRD-1403-RJN039 | 4E GURUDWARA:K | TG-RJN039A-2 | 19503560 | 630 | 200 | 248 | 0.99 | 402 | 144 | 598 | 144 | 593 | 114 | 473 | 122 | 2019-06-06 15:00 | 74.5 | -11.5 | 598 | R | 108 | 102 | 90 | 18 |  |  | 1 | 99 | 412.53 | 443.49 | 476.42 | 442.19 | 204.1 | 175.44 | 175.44 | 184.14 | 100.48 | 98.18 | 78.18 | 91.18 | [8 empty] | 717.51 | 2.09 | 0.31 | 0.64
65 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN040 | 1S-DL-YP-CTC-DSRD-1403-RJN040 | DELHI PRESS:ID | TG-RJN040A-1 | 19503360 | 990 | 320 | 242 | 0.98 | 383 | 126 | 557 | 149 | 660 | 108 | 478 | 159 | 2019-06-04 14:00 | 84.6 | 0.7 | 660 | Y | 101 | 114 | 86 | 28 |  |  | 2.2 | 97.8 | 501.24 | 478.59 | 525.12 | 500.24 | 216.46 | 221.13 | 221.13 | 217.46 |  | 17.58 | [10 empty] | 718.1 | 1.5 | 0.35 | 0.39
66 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN041 | 1S-DL-YP-CTC-DSRD-1403-RJN041 | JHANDENWALAN NO. 1:ID | TG-RJN041A-1 | 19500386 | 990 | 320 | 239 | 0.98 | 812 | 244 | 1049 | 250 | 1063 | 318 | 1367 | 311 | 2019-06-14 13:00 | 176.6 | -10.3 | 1447 | B | 90 | 95 | 115 | 25 |  |  | 26.9 | 73.1 | 333.45 | 367.45 | 325.15 | 343.15 | 168.3 | 117 | 117 | 135.3 | 214.12 | 231.12 | 190.01 | 235.42 |  | 0.3 | 66.12 | 2 |  |  |  |  | 716.27 | 3.33 | 0.4 | 0.82
67 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN041 | 1S-DL-YP-CTC-DSRD-1403-RJN041 | JHANDENWALAN NO. 1:ID | TG-RJN041A-2 | 19504595 | 990 | 320 | 233 | 0.96 | 532 | 155 | 699 | 170 | 769 | 207 | 930 | 205 | 2019-06-04 14:00 | 122.9 | 8.1 | 930 | B | 96 | 102 | 103 | 7 |  | 5.3 | 64 | 30.8 | 433.14 | 427.14 | 414.15 | 426.44 | 166.59 | 150.13 | 150.13 | 146.16 | 116.15 | 139.01 | 163.28 | 143.28 | [8 empty] | 716.28 | 3.32 | 0.38 | 0.54
68 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN042 | 1S-DL-YP-CTC-DSRD-1403-RJN042 | JANTA MKT. JHANDEWALAN:PL | TG-RJN042A-1 | 19503271 | 630 | 200 | 246 | 0.95 | 407 | 128 | 547 | 127 | 547 | 151 | 651 | 104 | 2019-06-11 16:00 | -9.7 | -122.4 | 651 | B | 95 | 101 | 104 | 9 |  |  | 14.5 | 85.5 | 6 | 4 | 1.3 | 2.3 | 325.12 | 265.1 | 265.1 | 275.1 | 359.01 | 421.03 | 459.29 | 412.33 | [8 empty] | 690.13 | 5.47 | 0.68 | 0.65
69 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN042 | 1S-DL-YP-CTC-DSRD-1403-RJN042 | JANTA MKT. JHANDEWALAN:PL | TG-RJN042A-2 | 19504547 | 400 | 120 | 246 | 0.98 | 109 | 32 | 139 | 47 | 203 | 30 | 129 | 69 | 2019-06-28 16:30 | 26.8 | -11.6 | 203 | Y | 95 | 115 | 90 | 25 |  |  | 12.9 | 87.1 | 607.49 | 491.37 | 627.32 | 571.36 | 82.2 | 198.32 | 198.32 | 118.33 | [12 empty] | 690.09 | 5.51 | 0.47 | 0.27
70 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN063 | 1S-DL-YP-CTC-DSRD-1403-RJN063 | BHOOTH NATH (K):ID | TG-RJN063A-1 | 19500403 | 990 | 320 | 246 | 0.94 | 374 | 111 | 466 | 142 | 602 | 121 | 492 | 125 | 2019-06-13 13:00 | 91.3 | -78 | 602 | Y | 90 | 108 | 103 | 18 | 96.1 | 2.5 | 1.1 | 0.3 | 566.5 | 515.56 | 521.56 | 534.26 | 150.23 | 198.47 | 198.47 | 182.47 |  | 2.3 | 1 | [9 empty] | 717.13 | 2.47 | 0.37 | 0.38
71 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN063 | 1S-DL-YP-CTC-DSRD-1403-RJN063 | BHOOTH NATH (K):ID | TG-RJN063A-2 | 19506701 | 990 | 320 | 252 | 0.97 | 724 | 177 | 701 | 201 | 830 | 347 | 1513 | 756 | 2019-06-25 10:30 | 245.1 | 2.6 | 1558 | B | 90 | 110 | 100 | 20 | 0.3 | 0.1 | 7.2 | 92.4 | 441.02 | 414.32 | 432.32 | 430.02 | 86.59 | 86 | 86 | 76.3 | 165.5 | 193.19 | 202.19 | 187.19 | [6 empty] | 1 |  | 693.51 | 26.09 | 0.34 | 0.73
72 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN093 | 1S-DL-YP-CTC-DSRD-1403-RJN093 | Ashoka Pahari | TG-RJN093A-1 | 19506386 | 990 | 300 | 243 | 0.96 | 172 | 53 | 214 | 59 | 251 | 60 | 257 | 40 | 2019-06-13 23:30 | 43.2 | 8.4 | 300 | R | 80 | 98 | 122 | 42 | 100 |  |  |  | 706.41 | 707.11 | 707.11 | 707.11 | 0.3 | [15 empty] | 707.11 | 12.49 | 0.57 | 0.17
73 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | EPN001 | 1S-DL-YP-CTC-DSRD-1402-EPN001 | LINK ROAD PACKAGE S/STN | TG-EPN001A-1 | 19506294 | 990 | 320 | 243 | 0.97 | 447 | 159 | 653 | 156 | 650 | 132 | 546 | 105 | 2019-06-27 12:30 | 106.9 | 12.8 | 784 | Y | 109 | 112 | 79 | 33 |  | 0.3 | 25.5 | 74.2 | 261.08 | 252.58 | 463.38 | 378.38 | 363.27 | 364.34 | 364.34 | 287.36 | 68.39 | 75.42 | 0.3 | 27 | [8 empty] | 693.14 | 26.46 | 0.51 | 0.45
74 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | EPN001 | 1S-DL-YP-CTC-DSRD-1402-EPN001 | LINK ROAD PACKAGE S/STN | TG-EPN001A-2 | 19505493 | 990 | 320 | 244 | 0.97 | 163 | 54 | 221 | 60 | 248 | 49 | 200 | 41 | 2019-06-26 11:30 | 49 | 1 | 439 | B | 71 | 111 | 118 | 47 | 0.2 | 0.1 | 8 | 91.8 | 693.29 | 692.19 | 692.29 | 693.29 |  | 1.1 | 1.1 | [13 empty] | 693.29 | 26.31 | 0.37 | 0.16
75 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW005 | 1S-DL-YP-CTC-DSRD-1401-KKW005 | SATBHRAWA :PACKAGE S/STN | TG-KKW005A-1 | 19500011 | 990 | 320 | 250 | 0.96 | 165 | 55 | 219 | 49 | 193 | 60 | 235 | 37 | 2019-06-28 17:00 | 50.8 | 2.2 | 240 | R | 100 | 90 | 111 | 21 |  |  | 8.9 | 91.1 | 718.33 | 718.33 | 718.33 | 718.33 | [16 empty] | 718.33 | 1.27 | 0.46 | 0.17
76 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW005 | 1S-DL-YP-CTC-DSRD-1401-KKW005 | SATBHRAWA :PACKAGE S/STN | TG-KKW005A-2 | 19500017 | 990 | 320 | 248 | 0.95 | 719 | 225 | 892 | 252 | 994 | 241 | 958 | 90 | 2019-06-28 17:30 | 252.4 | 30.2 | 1067 | Y | 97 | 100 | 104 | 7 |  |  | 3 | 97 | 113.37 | 127.07 | 37.37 | 89.37 | 354.53 | 327.47 | 327.47 | 365.53 | 248.45 | 262.21 | 288.03 | 261.45 | [8 empty] | 717.15 | 2.45 | 0.53 | 0.73
77 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW006 | 1S-DL-YP-CTC-DSRD-1401-KKW006 | SATBHRAWA (K) STN.:ID | TG-KKW006A-1 | 19506040 | 990 | 320 | 250 | 0.98 | 611 | 207 | 866 | 184 | 768 | 220 | 917 | 131 | 2019-06-03 15:00 | 153.6 | 4.5 | 1194 | B | 99 | 97 | 104 | 7 | 0.2 |  | 13.1 | 86.7 | 115 | 80.3 | 72.3 | 73.3 | 374.3 | 433.16 | 433.16 | 410 | 207.03 | 182.47 | 220.03 | 213.03 | [8 empty] | 696.33 | 23.27 | 0.52 | 0.62
78 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW006 | 1S-DL-YP-CTC-DSRD-1401-KKW006 | SATBHRAWA (K) STN.:ID | TG-KKW006A-2 | 19505386 | 630 | 200 | 249 | 0.98 | 507 | 171 | 717 | 175 | 725 | 162 | 680 | 41 | 2019-06-11 16:00 | 143.8 | -2.6 | 984 | R | 98 | 101 | 101 | 3 | 0.3 | 0.1 | 15.1 | 84.6 | 21.3 | 15.3 | 5 | 8 | 308 | 265 | 265 | 314.3 | 360.32 | 412.32 | 353.32 | 372.32 | 5.3 | 2.3 | 0.3 | 1 | 0.3 | 0.3 |  |  | 696.02 | 23.58 | 0.55 | 0.8
79 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW007 | 1S-DL-YP-CTC-DSRD-1401-KKW007 | SHASTRI PARK (INDOOR):ID | TG-KKW007A-1 | 19503317 | 990 | 320 | 243 | 0.97 | 825 | 239 | 1019 | 300 | 1284 | 286 | 1216 | 239 | 2019-06-14 13:30 | 223 | 12.5 | 1325 | Y | 90 | 104 | 106 | 16 |  |  | 0.8 | 99.2 | 337 | 325 | 295.3 | 323.3 | 159.3 | 101.3 | 101.3 | 129.3 | 223.3 | 232 | 222.3 | 242 |  | 61.3 | 65 | 25 |  |  |  |  | 720 | 0 | 0.43 | 0.83
80 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW007 | 1S-DL-YP-CTC-DSRD-1401-KKW007 | SHASTRI PARK (INDOOR):ID | TG-KKW007A-2 | 19503312 | 990 | 320 | 241 | 0.96 | 587 | 194 | 845 | 194 | 853 | 199 | 874 | 26 | 2019-06-06 15:30 | 163.4 | 29.4 | 930 | Y | 103 | 99 | 98 | 5 |  |  | 5 | 95 | 10.3 | 20 | 71 | 17 | 440 | 454.3 | 454.3 | 442.3 | 269.3 | 245.3 | 268 | 260.3 | [8 empty] | 720 | 0 | 0.6 | 0.59
81 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW007 | 1S-DL-YP-CTC-DSRD-1401-KKW007 | SHASTRI PARK (INDOOR):ID | TG-KKW007A-3 | 19500106 | 990 | 320 | 242 | 0.98 | 743 | 251 | 1053 | 231 | 967 | 260 | 1080 | 102 | 2019-06-12 17:00 | 150.1 | 25 | 1164 | R | 103 | 95 | 101 | 8 | 14.4 | 1.8 | 25.7 | 58.2 |  |  |  |  | 175.3 | 219.3 | 219.3 | 196 | 251.02 | 208.02 | 246.32 | 231.32 | 1 |  | 0.3 | [5 empty] | 717.26 | 2.34 | 0.62 | 0.75
82 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW008 | 1S-DL-YP-CTC-DSRD-1401-KKW008 | JESSA RAM HOSPITAL PACKAGE S/STN | TG-KKW008A-1 | 19503352 | 990 | 320 | 245 | 0.97 | 160 | 78 | 322 | 55 | 227 | 27 | 110 | 184 | 2019-06-14 18:00 | 43.4 | 2.9 | 322 | R | 149 | 107 | 44 | 105 |  |  | 1.4 | 98.6 | 642 | 696 | 696 | 696 | 54 | [15 empty] | 696 | 0 | 0.45 | 0.16
83 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW008 | 1S-DL-YP-CTC-DSRD-1401-KKW008 | JESSA RAM HOSPITAL PACKAGE S/STN | TG-KKW008A-2 | 19503322 | 990 | 320 | 246 | 0.98 | 156 | 37 | 155 | 53 | 223 | 66 | 276 | 105 | 2019-06-29 16:00 | 25.8 | 2.2 | 279 | B | 67 | 105 | 128 | 61 |  |  | 1.9 | 98.1 | 695.51 | 695.51 | 695.21 | 695.51 | [16 empty] | 695.51 | 0.09 | 0.59 | 0.16
84 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW008 | 1S-DL-YP-CTC-DSRD-1401-KKW008 | JESSA RAM HOSPITAL PACKAGE S/STN | TG-KKW008A-3 | 19505210 | 630 | 200 | 245 | 0.96 | 731 | 255 | 1060 | 235 | 987 | 241 | 1015 | 64 | 2019-06-08 17:30 | 180.6 | 42.8 | 1197 | Y | 102 | 95 | 103 | 8 | 0.3 | 0.1 | 10.3 | 89.4 |  |  |  |  | 222 | 320 | 320 | 271 | 254 | 165.3 | 277 | 203 | 208.3 | 207.3 | 199 | 221 | 12 | 3.3 | 21.3 | 1.3 | 696.3 | 23.3 | 0.51 | 1.16
85 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW020 | 1S-DL-YP-CTC-DSRD-1401-KKW020 | 39, BEEDEN PURA (W):PL | TG-KKW020A-1 | 19503258 | 990 | 320 | 246 | 0.97 | 637 | 181 | 752 | 218 | 906 | 237 | 983 | 204 | 2019-06-12 16:30 | 143.5 | 25 | 1035 | Y | 89 | 107 | 104 | 18 |  |  | 0.1 | 99.9 | 238.3 | 174 | 192.3 | 200 | 291.3 | 309 | 309 | 296.3 | 189.57 | 236.57 | 230.27 | 223.27 | [8 empty] | 719.57 | 0.03 | 0.5 | 0.64
86 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW020 | 1S-DL-YP-CTC-DSRD-1401-KKW020 | 39, BEEDEN PURA (W):PL | TG-KKW020A-2 | 19505869 | 630 | 200 | 245 | 0.96 | 513 | 158 | 678 | 183 | 782 | 172 | 734 | 90 | 2019-06-29 15:30 | 144 | 27.2 | 1012 | R | 87 | 111 | 102 | 24 | 0.2 | 0.1 | 0.3 | 99.5 | 226.01 | 8.01 | 28.01 | 30.31 | 239.3 | 428.16 | 428.16 | 420.46 | 239.43 | 226.57 | 244.27 | 252.27 |  | 42.3 | 9.3 | 2 | 0.3 |  |  |  | 705.44 | 14.16 | 0.49 | 0.81
87 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW021 | 1S-DL-YP-CTC-DSRD-1401-KKW021 | PNB KAROL BAGH:PL | TG-KKW021A-1 | 19505450 | 630 | 200 | 248 | 0.97 | 307 | 106 | 436 | 138 | 577 | 64 | 262 | 273 | 2019-06-02 16:30 | 104 | 12.4 | 655 | Y | 117 | 118 | 64 | 54 | 0.4 | 0.1 | 6.9 | 92.7 | 66.3 | 166 | 517.58 | 242.3 | 503.38 | 361.38 | 361.38 | 408.58 | 125.44 | 168.14 |  | 44.24 | [8 empty] | 695.52 | 24.08 | 0.52 | 0.49
88 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW021 | 1S-DL-YP-CTC-DSRD-1401-KKW021 | PNB KAROL BAGH:PL | TG-KKW021A-2 | 19503766 | 990 | 320 | 248 | 0.98 | 638 | 192 | 806 | 207 | 875 | 239 | 1018 | 187 | 2019-06-29 15:00 | 151.6 | -2.9 | 1018 | B | 95 | 98 | 107 | 12 |  | 0.1 | 29.8 | 70 | 426.38 | 417.38 | 403.18 | 419.08 | 71 | 96 | 96 | 78.3 | 221.44 | 205.44 | 230.44 | 221.44 | [8 empty] | 719.22 | 0.38 | 0.39 | 0.64
89 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW022 | 1S-DL-YP-CTC-DSRD-1401-KKW022 | CHRISTIAN COLONY:PL | TG-KKW022A-1 | 19505870 | 990 | 320 | 242 | 0.98 | 723 | 224 | 967 | 231 | 1000 | 268 | 1152 | 171 | 2019-06-29 15:30 | 137.6 | 28.5 | 1225 | B | 92 | 94 | 113 | 21 | 1.7 | 2.4 | 8.2 | 87.7 | 6 | 7 | 0.3 | 2 | 319.56 | 345.26 | 345.26 | 305.26 | 248.25 | 221.55 | 334.55 | 266.55 |  |  | 6.3 | [5 empty] | 719.4 | 0.2 | 0.57 | 0.73
90 | 2019-06-03 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW024 | 1S-DL-YP-CTC-DSRD-1401-KKW024 | 26 Pusa Road Karol Bagh PKG | TG-KKW024A-1 | 19504623 | 990 | 320 | 241.2065 | 0.97431 | 356.101 | 123.3014 | 542.0557 | 120.1507 | 524.4925 | 112.6489 | 492.7342 | 43.2994 | 2019-06-11 13:30 | [15 empty] | 547.5 |  |  |  | 124.5 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 672 |  | 0.29136 | 0.3597
91 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW025 | 1S-DL-YP-CTC-DSRD-1401-KKW025 | 8 C WEA KAROL BAGH JASSA RAM | TG-KKW025A-1 | 19506095 | 990 | 320 | 245 | 0.98 | 1011 | 346 | 1482 | 309 | 1320 | 356 | 1521 | 185 | 2019-06-11 14:00 | 234.9 | -41.3 | 1521 | B | 101 | 97 | 102 | 5 | 0.3 |  | 0.8 | 98.9 | 64.29 | 62.33 | 43.29 | 49.59 | 236.48 | 250.44 | 250.44 | 242.48 | 306.53 | 321.49 | 341.17 | 320.05 | 91.03 | 71.33 | 92.43 | 91.47 | 7.26 |  | 4.52 | 2 | 706.39 | 13.21 | 0.49 | 1.02
92 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW025 | 1S-DL-YP-CTC-DSRD-1401-KKW025 | 8 C WEA KAROL BAGH JASSA RAM | TG-KKW025A-2 | 19506378 | 400 | 120 | 240 | 0.97 | 404 | 131 | 553 | 145 | 618 | 128 | 536 | 75 | 2019-06-24 16:00 | 107 | 3.5 | 712 | Y | 89 | 102 | 109 | 20 | 0.4 | 1.4 | 59.4 | 38.9 | 195.04 | 146 | 43.3 | 160 | 131.55 | 126.05 | 126.05 | 113.05 | 326.31 | 357.57 | 363.01 | 358.57 | 53.26 | 69.24 | 71.28 | 73.24 |  | 7.3 | 12.56 | 1.3 | 706.56 | 13.04 | 0.45 | 1.01
93 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW028 | 1S-DL-YP-CTC-DSRD-1401-KKW028 | H.S.RD. KHATTAWAL K. BAGH:PL | TG-KKW028A-1 | 19505272 | 990 | 320 | 237 | 0.96 | 959 | 287 | 1205 | 390 | 1653 | 282 | 1188 | 457 | 2019-06-01 | 264.6 | 97.3 | 1653 | Y | 103 | 100 | 97 | 6 | 51.2 | 2.7 | 20.8 | 25.3 |  |  |  |  | 6.3 | 8 | 8 | 6.3 | 538.36 | 509.36 | 584.36 | 552.06 | 144.3 | 175 | 102.3 | 136.3 | 5.3 | 2.3 | 0.3 |  | 695.06 | 24.54 | 0.71 | 0.97
94 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW028 | 1S-DL-YP-CTC-DSRD-1401-KKW028 | H.S.RD. KHATTAWAL K. BAGH:PL | TG-KKW028A-2 | 19505496 | 990 | 320 | 248 | 0.96 | 914 | 296 | 1235 | 352 | 1473 | 265 | 1109 | 320 | 2019-06-29 16:00 | 271 | 80.6 | 1534 | R | 100 | 109 | 91 | 18 | 3.8 | 0.1 | 2.4 | 93.7 |  |  |  |  | 35 | 15 | 15 | 29 | 601.05 | 581.35 | 644.16 | 624.35 | 81 | 116.3 | 5.3 | 65 | 1.3 | 5.3 |  |  | 718.35 | 1.25 | 0.67 | 0.92
95 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW029 | 1S-DL-YP-CTC-DSRD-1401-KKW029 | PYAUWALA H. S. ROAD:PM | TG-KKW029A-1 | 19505483 | 400 | 120 | 248 | 0.95 | 301 | 92 | 375 | 115 | 469 | 93 | 377 | 93 | 2019-06-01 22:30 | 106.9 | 17.3 | 509 | Y | 80 | 115 | 104 | 35 |  | 0.1 | 25.8 | 74.2 | 121 |  |  |  | 81.53 | 15 | 15 | 36 | 502.05 | 638.28 | 651.28 | 668.58 |  | 51.3 | 8 | [5 empty] | 704.58 | 15.02 | 0.72 | 0.75
96 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW030 | 1S-DL-YP-CTC-DSRD-1401-KKW030 | NALA WALA H. S. RD.:PL | TG-KKW030A-1 | 19503266 | 990 | 320 | 244 | 0.96 | 784 | 228 | 940 | 259 | 1079 | 296 | 1232 | 253 | 2019-06-30 14:30 | 211.2 | 81.7 | 1232 | B | 90 | 104 | 106 | 16 |  |  | 11.8 | 88.2 |  |  |  |  | 212.51 | 87 | 87 | 130.3 | 482.57 | 608.48 | 573.48 | 565.18 |  |  | 15.3 | [5 empty] | 695.48 | 0.12 | 0.65 | 0.79
97 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW031 | 1S-DL-YP-CTC-DSRD-1401-KKW031 | 13 BLK WEA K. BAGH:PACKAGE S/STN | TG-KKW031A-1 | 19504622 | 990 | 320 | 234 | 0.98 | 576 | 181 | 814 | 194 | 873 | 201 | 902 | 78 | 2019-06-14 12:30 | 134 | -13.2 | 918 | B | 91 | 107 | 101 | 16 |  |  | 20.1 | 79.9 | 349.33 | 338.33 | 350.33 | 345.33 | 129.22 | 97.52 | 97.52 | 104.22 | 215.51 | 258.21 | 255.21 | 244.51 | [8 empty] | 694.46 | 1.14 | 0.43 | 0.58
98 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW031 | 1S-DL-YP-CTC-DSRD-1401-KKW031 | 13 BLK WEA K. BAGH:PACKAGE S/STN | TG-KKW031A-2 | 19504549 | 990 | 320 | 246 | 0.98 | 862 | 287 | 1217 | 316 | 1331 | 259 | 1093 | 206 | 2019-06-26 14:00 | 148.7 | -4.4 | 1331 | Y | 100 | 107 | 93 | 14 |  |  | 3.8 | 96.2 | 425.24 | 411.24 | 422.24 | 420.54 | 43 | 54 | 54 | 48.3 | 199.54 | 112.52 | 245.44 | 198.24 | 50.5 | 140.52 | 3 | 51.2 |  |  |  |  | 719.08 | 0.52 | 0.37 | 0.87
99 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW031 | 1S-DL-YP-CTC-DSRD-1401-KKW031 | 13 BLK WEA K. BAGH:PACKAGE S/STN | TG-KKW031A-3 | 19504607 | 990 | 320 | 247 | 0.96 | 417 | 127 | 538 | 146 | 622 | 144 | 610 | 78 | 2019-06-04 14:00 | 44.2 | -52.3 | 645 | B | 91 | 104 | 105 | 14 |  |  |  | 100 | 425.23 | 406.32 | 407.02 | 410.32 | 292.51 | 294.42 | 294.42 | 297.42 | 0.3 | 17.3 | 58 | 10.3 | [8 empty] | 718.44 | 1.16 | 0.43 | 0.42
100 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW031 | 1S-DL-YP-CTC-DSRD-1401-KKW031 | 13 BLK WEA K. BAGH:PACKAGE S/STN | TG-KKW031A-4 | 19505207 | 630 | 200 | 248 | 0.98 | 491 | 121 | 477 | 239 | 1025 | 131 | 535 | 522 | 2019-06-12 19:00 | 154.8 | -1.2 | 1025 | Y | 94 | 91 | 115 | 24 | 0.1 |  | 1.6 | 98.3 | 426.39 | 436.09 | 426.39 | 432.09 | 36 | 35 | 35 | 29 | 233.3 | 224.3 | 236.3 | 235 |  |  | 10.3 |  |  | 0.3 | 0.3 |  | 696.09 | 23.51 | 0.32 | 0.78
101 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW032 | 1S-DL-YP-CTC-DSRD-1401-KKW032 | 5WEA K BAGH KIOSK:PACKAGE S/STN | TG-KKW032A-1 | 19504636 | 990 | 320 | 234 | 0.99 | 696 | 237 | 1033 | 211 | 916 | 248 | 1084 | 150 | 2019-06-15 17:00 | 134 | 6.6 | 1090 | B | 98 | 94 | 109 | 15 |  | 0.4 | 20.9 | 78.7 | 61.3 | 48 | 30 | 43 | 334.3 | 356.3 | 356.3 | 347 | 323.1 | 314.4 | 339.1 | 329.1 | [8 empty] | 719.1 | 0.5 | 0.56 | 0.7
102 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW032 | 1S-DL-YP-CTC-DSRD-1401-KKW032 | 5WEA K BAGH KIOSK:PACKAGE S/STN | TG-KKW032A-2 | 19504614 | 990 | 320 | 236 | 0.97 | 893 | 279 | 1135 | 314 | 1293 | 300 | 1228 | 137 | 2019-06-14 13:00 | 225.2 | 19.1 | 1384 | Y | 94 | 112 | 94 | 18 |  | 0.6 | 25.1 | 74.3 | 133.56 | 43 | 110 | 79.3 | 278.3 | 331.56 | 331.56 | 321.56 | 305.35 | 263.35 | 298.35 | 311.05 | 1 | 80.3 | 2.3 | 6.3 |  |  |  |  | 719.01 | 0.59 | 0.47 | 0.9
103 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW032 | 1S-DL-YP-CTC-DSRD-1401-KKW032 | 5WEA K BAGH KIOSK:PACKAGE S/STN | TG-KKW032A-3 | 19505867 | 630 | 200 | 240 | 0.98 | 358 | 122 | 531 | 122 | 534 | 114 | 498 | 34 | 2019-06-04 15:00 | 90.8 | 5.8 | 648 | Y | 100 | 108 | 92 | 16 | 0.2 |  | 20.9 | 78.9 | 44.3 | 31 | 173.3 | 48 | 448 | 409.3 | 409.3 | 409 | 226.43 | 278.43 | 225.13 | 262.13 | [8 empty] | 719.13 | 0.47 | 0.59 | 0.57
104 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW033 | 1S-DL-YP-CTC-DSRD-1401-KKW033 | ARYA SAMAJ RD. NO.1:PACKAGE S/STN | TG-KKW033A-1 | 19505868 | 990 | 320 | 241 | 0.98 | 463 | 136 | 581 | 154 | 662 | 173 | 737 | 135 | 2019-06-04 17:00 | 113.9 | 6.4 | 934 | Y | 94 | 99 | 107 | 13 | 0.2 |  | 0.9 | 98.9 | 435.3 | 436 | 413 | 433 | 215.22 | 151.22 | 151.22 | 171.52 | 46 | 109.3 | 117.27 | 92 | [8 empty] | 696.52 | 23.08 | 0.39 | 0.47
105 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW034 | 1S-DL-YP-CTC-DSRD-1401-KKW034 | NALA (K) A.S. RD. S/ST.:PAVKAGE S/STN | TG-KKW034A-1 | 19500395 | 990 | 320 | 237 | 0.96 | 734 | 253 | 1095 | 262 | 1114 | 219 | 944 | 161 | 2019-06-30 14:30 | 180.3 | 72.1 | 1280 | Y | 105 | 103 | 92 | 13 | 4.9 | 17.1 | 36.4 | 41.6 |  |  |  |  | 191.3 | 223 | 223 | 220.3 | 527.57 | 490.57 | 470.57 | 499.27 | 0.3 | 6 | [6 empty] | 719.57 | 0.03 | 0.65 | 0.74
106 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW034 | 1S-DL-YP-CTC-DSRD-1401-KKW034 | NALA (K) A.S. RD. S/ST.:PAVKAGE S/STN | TG-KKW034A-2 | 19504621 | 990 | 320 | 248 | 0.95 | 627 | 199 | 833 | 215 | 911 | 214 | 916 | 81 | 2019-06-29 15:00 | 184 | 44.9 | 924 | Y | 101 | 104 | 94 | 10 | 0.2 | 9.4 | 52.4 | 38 | 14.3 | 2.3 | 24 | 13 | 384.44 | 391.44 | 391.44 | 409.14 | 296.18 | 301.18 | 221.18 | 273.18 | [8 empty] | 695.32 | 0.28 | 0.59 | 0.63
107 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW035 | 1S-DL-YP-CTC-DSRD-1401-KKW035 | HATHIWAL CHOWK A.S RD:PL | TG-KKW035A-1 | 19503318 | 990 | 320 | 248 | 0.96 | 744 | 248 | 973 | 240 | 946 | 256 | 1009 | 55 | 2019-06-30 14:30 | 208.3 | 65.5 | 1093 | R | 108 | 97 | 95 | 13 |  |  | 1.6 | 98.4 |  | 0.3 | 1 |  | 100.3 | 236 | 236 | 194 | 619.3 | 483.3 | 489.3 | 526 | [8 empty] | 720 | 0 | 0.64 | 0.75
108 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW037 | 1S-DL-YP-CTC-DSRD-1401-KKW037 | 26 BEEDEN PURA P.L RD.:PL | TG-KKW037A-1 | 19504238 | 990 | 320 | 239 | 0.97 | 967 | 356 | 1465 | 272 | 1155 | 339 | 1443 | 300 | 2019-06-12 16:00 | 231.1 | 68.4 | 1542 | B | 107 | 90 | 103 | 17 | 75.8 | 23.9 | 0.2 | 0.1 |  |  |  |  | 21 | 80 | 80 | 36.3 | 546.27 | 637.19 | 563.31 | 605.19 | 146.52 | 1.54 | 123.42 | 77.24 | 4.54 |  | 4 |  | 719.13 | 0.47 | 0.63 | 0.98
109 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW038 | 1S-DL-YP-CTC-DSRD-1401-KKW038 | BACCHARUDDIN S/ST.:PL | TG-KKW038A-1 | 19500392 | 990 | 320 | 244 | 0.96 | 773 | 299 | 1288 | 230 | 990 | 244 | 1048 | 274 | 2019-06-29 14:00 | 206.1 | 78.8 | 1332 | R | 119 | 89 | 93 | 30 |  |  | 1.5 | 98.5 |  |  |  |  | 37 | 255 | 255 | 146.3 | 659.54 | 464.14 | 509.44 | 572.44 | 22.2 | [7 empty] | 719.14 | 0.46 | 0.64 | 0.78
110 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW038 | 1S-DL-YP-CTC-DSRD-1401-KKW038 | BACCHARUDDIN S/ST.:PL | TG-KKW038A-2 | 19505871 | 630 | 200 | 240 | 0.97 | 352 | 158 | 713 | 107 | 448 | 87 | 376 | 307 | 2019-06-06 03:00 | 101.6 | 29.4 | 713 | R | 96 | 101 | 103 | 7 | 0.2 |  | 2.6 | 97.2 | 9 | 10 | 4 | 1.3 | 508.57 | 427.57 | 427.57 | 469.57 | 202 | 282 | 279.57 | 248.3 | [8 empty] | 719.57 | 0.03 | 0.66 | 0.56
111 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW039 | 1S-DL-YP-CTC-DSRD-1401-KKW039 | 40 REGER PURA P/M:PL | TG-KKW039A-1 | 19506093 | 990 | 320 | 238 | 0.96 | 950 | 295 | 1301 | 231 | 968 | 423 | 1966 | 880 | 2019-06-06 02:30 | 302.4 | 104 | 1966 | B | 110 | 99 | 91 | 19 | 0.2 | 0.1 |  | 99.7 |  |  |  |  | 6.3 | 19 | 19 | 13.3 | 497.27 | 613.18 | 615.48 | 599.18 | 178.51 | 61.3 | 38.3 | 81 | 11 |  | 0.3 |  | 693.48 | 26.12 | 0.67 | 0.96
112 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW040 | 1S-DL-YP-CTC-DSRD-1401-KKW040 | KHALSA COLLEGE S/ST:K | TG-KKW040A-1 | 19503768 | 990 | 320 | 243 | 0.97 | 281 | 124 | 533 | 73 | 315 | 83 | 358 | 200 | 2019-06-11 | 61.1 | 17.7 | 533 | R | 119 | 82 | 99 | 37 |  |  | 1.3 | 98.7 | 262.41 | 606.39 | 441.56 | 425.41 | 456.28 | 112.3 | 112.3 | 293.28 | [12 empty] | 719.09 | 0.51 | 0.66 | 0.28
113 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW040 | 1S-DL-YP-CTC-DSRD-1401-KKW040 | KHALSA COLLEGE S/ST:K | TG-KKW040A-2 | 19506710 | 630 | 200 | 244 | 0.95 | 144 | 52 | 226 | 47 | 203 | 45 | 194 | 28 | 2019-06-10 11:30 | 47 | 4.2 | 263 | Y | 154 | 79 | 67 | 87 | 0.3 |  | 0.6 | 99.1 | 631.09 | 666.09 | 700.39 | 683.09 | 75.3 | 40.3 | 40.3 | 23.3 | [12 empty] | 706.39 | 13.21 | 0.34 | 0.23
114 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW045 | 1S-DL-YP-CTC-DSRD-1401-KKW045 | 6 WEA K BAGH (MOTHER):PACKAGE S/STN | TG-KKW045A-1 | 19503330 | 990 | 320 | 246 | 0.96 | 685 | 239 | 1016 | 222 | 940 | 224 | 945 | 74 | 2019-06-12 17:00 | 189.9 | -4.4 | 1067 | R | 109 | 101 | 90 | 19 |  |  | 12.9 | 87.1 | 346 | 353.3 | 369.3 | 355 | 76 | 99 | 99 | 93.3 | 297.56 | 267.26 | 238.3 | 271.26 | [8 empty] | 719.56 | 0.04 | 0.42 | 0.69
115 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW045 | 1S-DL-YP-CTC-DSRD-1401-KKW045 | 6 WEA K BAGH (MOTHER):PACKAGE S/STN | TG-KKW045A-2 | 19503628 | 990 | 320 | 246 | 0.96 | 723 | 238 | 1002 | 239 | 1050 | 246 | 1071 | 61 | 2019-06-01 15:00 | 205.3 | 30.2 | 1078 | Y | 95 | 102 | 102 | 7 | 100 |  |  |  | 294 | 89 | 179.3 | 200 | 131 | 342 | 342 | 227.3 | 295 | 289 | 300.3 | 292.3 | [8 empty] | 720 | 0 | 0.5 | 0.73
116 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW046 | 1S-DL-YP-CTC-DSRD-1401-KKW046 | PUSA RD. CAMP CENTRE:ID | TG-KKW046A-1 | 19503332 | 990 | 320 | 242 | 0.96 | 875 | 267 | 1101 | 289 | 1190 | 319 | 1330 | 200 | 2019-06-30 00:30 | 199.5 | 55.9 | 1350 | Y | 88 | 101 | 111 | 23 |  |  | 26.2 | 73.8 | 0.3 | 0.3 |  |  | 171.29 | 88.25 | 88.25 | 69 | 521.33 | 555.07 | 625.02 | 605.32 | 2 | 51.3 | 54.3 | 21 |  |  |  |  | 695.32 | 0.28 | 0.62 | 0.88
117 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW046 | 1S-DL-YP-CTC-DSRD-1401-KKW046 | PUSA RD. CAMP CENTRE:ID | TG-KKW046A-2 | 19503315 | 990 | 320 | 235 | 0.98 | 957 | 279 | 1198 | 338 | 1472 | 340 | 1457 | 267 | 2019-06-11 23:30 | 152.4 | 63.3 | 1747 | B | 85 | 102 | 113 | 28 |  | 1.4 | 43.7 | 54.8 |  |  |  |  | 101.33 | 22.04 | 22.04 | 21.04 | 573.17 | 534.55 | 442 | 554.16 | 36.19 | 152.4 | 206.09 | 135.49 |  | 1.3 | 54 |  | 711.09 | 8.51 | 0.66 | 0.97
118 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW046 | 1S-DL-YP-CTC-DSRD-1401-KKW046 | PUSA RD. CAMP CENTRE:ID | TG-KKW046A-3 | 19503546 | 990 | 320 | 240 | 0.97 | 761 | 262 | 1102 | 248 | 1036 | 251 | 1051 | 60 | 2019-06-28 23:30 | 176.6 | 63.3 | 1129 | R | 101 | 95 | 104 | 9 |  |  | 0.7 | 99.3 |  |  |  |  | 58.3 | 117 | 117 | 60.3 | 637 | 579 | 653.3 | 635.3 | 0.3 | [7 empty] | 696 | 0 | 0.69 | 0.77
119 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW046 | 1S-DL-YP-CTC-DSRD-1401-KKW046 | PUSA RD. CAMP CENTRE:ID | TG-KKW046A-4 | 19505842 | 990 | 320 | 243 | 0.98 | 1023 | 353 | 1495 | 327 | 1380 | 343 | 1445 | 100 | 2019-06-30 15:00 | 327 | 32 | 1781 | R | 100 | 101 | 99 | 2 | 0.4 |  | 0.4 | 99.2 |  |  |  |  | 21.37 | 10.07 | 10.07 | 17.37 | 550 | 598.3 | 531.54 | 564.3 | 131 | 98.3 | 135.06 | 124 | 5 | 0.3 | 8 | 1.3 | 707.37 | 12.23 | 0.63 | 1.03
120 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW047 | 1S-DL-YP-CTC-DSRD-1401-KKW047 | 21 WEA K. BAGH TIKONA PARK:PACKAGE S/STN | TG-KKW047A-1 | 19504620 | 990 | 320 | 243 | 0.98 | 454 | 190 | 791 | 138 | 585 | 126 | 520 | 245 | 2019-06-30 16:30 | 95.7 | 27.2 | 796 | R | 113 | 94 | 92 | 21 | 0.1 | 7.1 | 92.6 | 0.3 | 1 | 40 | 26 | 8.3 | 488 | 660.58 | 660.58 | 666.28 | 230.58 | 19 | 20 | 45 | [8 empty] | 719.58 | 0.02 | 0.7 | 0.46
121 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW047 | 1S-DL-YP-CTC-DSRD-1401-KKW047 | 21 WEA K. BAGH TIKONA PARK:PACKAGE S/STN | TG-KKW047A-2 | 19504606 | 990 | 320 | 236 | 0.96 | 946 | 346 | 1522 | 305 | 1324 | 295 | 1302 | 210 | 2019-06-28 | 184.7 | 60.4 | 1522 | R | 116 | 93 | 91 | 25 | 1.5 | 12.7 | 53.1 | 32.7 |  | 1 |  |  | 138.42 | 326.34 | 326.34 | 240.04 | 552.46 | 384.24 | 396.24 | 473.54 | 26.3 | 6.3 | 3.3 | 4.3 | 0.3 |  |  |  | 718.28 | 1.32 | 0.48 | 0.96
122 | 2019-06-03 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW048 | 1S-DL-YP-CTC-DSRD-1401-KKW048 | 12 WEA K. BAGH:PKG | TG-KKW048A-1 | 19503345 | 990 | 320 | 246.46 | 0.9734 | 664.3251 | 219.7388 | 937.5724 | 204.2476 | 869.768 | 240.3387 | 1024.4614 | 134.3079 | 2019-06-29 14:30 | [15 empty] | 404.5 |  |  |  | 40 |  |  |  | 227.5 |  |  |  | 0 |  |  |  | 0 | 672 |  | 0.42104 | 0.67104
123 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW048 | 1S-DL-YP-CTC-DSRD-1401-KKW048 | 12 WEA K. BAGH:PKG | TG-KKW048A-2 | 19502272 | 990 | 320 | 246.3784 | 0.98241 | 541.5335 | 191.2085 | 764.1004 | 199.2943 | 817.4501 | 151.0307 | 624.7909 | 172.2946 | 2019-06-30 16:30 | [15 empty] | 235 |  |  |  | 287 |  |  |  | 197.5 |  |  |  | 0 |  |  |  | 0 | 719.5 |  | 0.51981 | 0.547
124 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW049 | 1S-DL-YP-CTC-DSRD-1401-KKW049 | R. K. DASS-1 K. BAGH:K | TG-KKW049A-1 | 19504998 | 990 | 320 | 253 | 0.95 | 1175 | 393 | 1574 | 393 | 1574 | 389 | 1535 | 39 | 2019-06-30 00:30 | 380.5 | 131.7 | 1654 | R | 106 | 98 | 96 | 10 |  | 2.5 | 64.7 | 32.8 | [5 empty] | 0.3 | 0.3 |  | 381 | 458.3 | 471 | 441.3 | 240.3 | 217 | 183 | 213.3 | 98.3 | 44 | 65 | 65 | 720 | 0 | 0.65 | 1.19
125 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW049 | 1S-DL-YP-CTC-DSRD-1401-KKW049 | R. K. DASS-1 K. BAGH:K | TG-KKW049A-2 | 19503292 | 990 | 320 | 248 | 0.96 | 810 | 271 | 1061 | 293 | 1158 | 246 | 970 | 163 | 2019-06-30 15:00 | 221.5 | 76.5 | 1196 | Y | 101 | 99 | 100 | 2 |  | 0.1 | 34.7 | 65.2 |  |  |  |  | 111.3 | 104 | 104 | 103.3 | 577.07 | 579.37 | 576.37 | 585.37 | 6 | 11 | 5.3 | 5.3 |  |  |  |  | 694.37 | 1.23 | 0.66 | 0.82
126 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW050 | 1S-DL-YP-CTC-DSRD-1401-KKW050 | R.K.DASS-1/2 K. BAGH:K | TG-KKW050A-1 | 19503319 | 990 | 320 | 248 | 0.97 | 780 | 296 | 1208 | 240 | 980 | 244 | 986 | 225 | 2019-06-30 00:30 | 154.6 | 50.8 | 1208 | R | 113 | 92 | 95 | 21 |  | 0.1 | 37.6 | 62.3 |  | 1 | 0.3 |  | 88.3 | 276 | 276 | 168 | 604.3 | 443 | 519 | 552 | 27 | [7 empty] | 720 | 0 | 0.62 | 0.79
127 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW050 | 1S-DL-YP-CTC-DSRD-1401-KKW050 | R.K.DASS-1/2 K. BAGH:K | TG-KKW050A-2 | 19506694 | 990 | 320 | 242 | 0.97 | 697 | 277 | 1161 | 183 | 759 | 238 | 989 | 349 | 2019-06-30 | 189.8 | 58.9 | 1207 | R | 120 | 79 | 102 | 41 | 0.1 |  | 9 | 90.8 |  | 8.3 |  |  | 82 | 464 | 464 | 223 | 628.3 | 247.3 | 501.3 | 497 | 9.3 |  | 0.3 | [5 empty] | 720 | 0 | 0.65 | 0.7
128 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW051 | 1S-DL-YP-CTC-DSRD-1401-KKW051 | R.K.DASS NO 2 (5A WEA):K | TG-KKW051A-1 | 19503320 | 990 | 320 | 241 | 0.97 | 737 | 272 | 1136 | 246 | 1028 | 219 | 906 | 199 | 2019-06-30 00:30 | 139.8 | 62.6 | 1182 | R | 106 | 101 | 93 | 13 |  | 0.4 | 86.8 | 12.8 |  |  | 1.3 |  | 281.3 | 307.3 | 307.3 | 321 | 436 | 412.3 | 341.3 | 399 | 2.3 | [7 empty] | 720 | 0 | 0.58 | 0.74
129 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW051 | 1S-DL-YP-CTC-DSRD-1401-KKW051 | R.K.DASS NO 2 (5A WEA):K | TG-KKW051A-2 | 19503375 | 990 | 320 | 229 | 0.98 | 719 | 275 | 1235 | 212 | 943 | 232 | 1022 | 261 | 2019-06-29 23:30 | 114.8 | 37.5 | 1235 | R | 116 | 89 | 95 | 27 |  | 2.7 | 87.2 | 10.1 |  | 12 | 5.3 | 1 | 181.3 | 442 | 442 | 346.3 | 536.3 | 266 | 327.3 | 372.3 | 2 | [7 empty] | 720 | 0 | 0.58 | 0.73
130 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW051 | 1S-DL-YP-CTC-DSRD-1401-KKW051 | R.K.DASS NO 2 (5A WEA):K | TG-KKW051A-3 | 19505162 | 990 | 320 | 230 | 0.97 | 692 | 196 | 875 | 246 | 1096 | 249 | 1103 | 224 | 2019-06-30 | 141.4 | 47 | 1205 | B | 92 | 101 | 107 | 15 | 0.3 | 0.2 | 32.6 | 66.9 | 3 | 1 |  |  | 430.55 | 370.55 | 370.55 | 360.25 | 262.3 | 324.3 | 419.25 | 336 | [8 empty] | 696.25 | 23.35 | 0.59 | 0.7
131 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW052 | 1S-DL-YP-CTC-DSRD-1401-KKW052 | RAMA ICE FACTORY:ID | TG-KKW052A-1 | 19503351 | 990 | 320 | 239 | 0.99 | 398 | 111 | 465 | 145 | 616 | 143 | 599 | 143 | 2019-06-07 23:30 | 93.5 | 8.8 | 663 | Y | 82 | 110 | 108 | 28 |  |  | 47.4 | 52.6 | 381 | 136.54 | 108 | 170.55 | 334.3 | 554.21 | 554.21 | 544.19 |  | 24.15 | 10.02 | 0.16 | [8 empty] | 715.3 | 4.3 | 0.6 | 0.4
132 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW053 | 1S-DL-YP-CTC-DSRD-1401-KKW053 | 8A K. BAGH WATER BOOSTER:PL | TG-KKW053A-1 | 19503357 | 990 | 320 | 238 | 0.98 | 694 | 244 | 1025 | 254 | 1065 | 196 | 830 | 217 | 2019-06-30 01:00 | 125.1 | 20.6 | 1165 | R | 115 | 101 | 84 | 31 |  |  | 2.2 | 97.8 | 0.3 | 15 | 37 | 6 | 318.35 | 419.02 | 419.02 | 447.31 | 398.02 | 284.05 | 139.04 | 264.36 | 1 | [7 empty] | 718.07 | 1.53 | 0.55 | 0.7
133 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW053 | 1S-DL-YP-CTC-DSRD-1401-KKW053 | 8A K. BAGH WATER BOOSTER:PL | TG-KKW053A-2 | 19505584 | 630 | 200 | 243 | 0.96 | 365 | 109 | 453 | 138 | 571 | 118 | 484 | 106 | 2019-06-30 | 119 | 28.4 | 829 | R | 92 | 115 | 93 | 23 | 0 |  | 3.1 | 96.9 | 43.3 | 1.3 | 27 | 7 | 536.34 | 390.47 | 390.47 | 524.29 | 114.3 | 302.19 | 117.35 | 163.07 | 0.02 | [7 empty] | 694.36 | 25.24 | 0.59 | 0.58
134 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW054 | 1S-DL-YP-CTC-DSRD-1401-KKW054 | 9A KAROL BAGH:PM | TG-KKW054A-1 | 19503358 | 990 | 320 | 243 | 0.99 | 728 | 203 | 856 | 269 | 1130 | 256 | 1087 | 256 | 2019-06-29 16:30 | 125.1 | 8.1 | 1151 | B | 89 | 107 | 104 | 18 |  |  | 0.1 | 99.9 |  |  |  |  | 209.29 | 75.3 | 75.3 | 100.59 | 486.02 | 618.01 | 616.02 | 594.32 |  | 2 | 1 | [5 empty] | 695.31 | 0.29 | 0.69 | 0.74
135 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW055 | 1S-DL-YP-CTC-DSRD-1401-KKW055 | 7A WEA (MOTHER DAIRY)PACKAGE S/STN | TG-KKW055A-1 | 19503354 | 990 | 320 | 244 | 0.98 | 127 | 52 | 226 | 8 | 33 | 67 | 288 | 231 | 2019-06-06 | 24.3 | 2.9 | 298 | B | 156 | 13 | 130 | 143 |  |  | 54.2 | 45.8 | 695.15 | 695.15 | 690.45 | 695.15 | [16 empty] | 695.15 | 0.45 | 0.59 | 0.13
136 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW055 | 1S-DL-YP-CTC-DSRD-1401-KKW055 | 7A WEA (MOTHER DAIRY)PACKAGE S/STN | TG-KKW055A-2 | 19503316 | 990 | 320 | 244 | 0.97 | 261 | 68 | 274 | 106 | 429 | 86 | 346 | 134 | 2019-06-30 17:30 | 67 | 17.7 | 459 | B | 82 | 116 | 102 | 34 |  |  | 20.4 | 79.6 | 689.46 | 386.17 | 496.39 | 572.48 | 5.3 | 308.59 | 308.59 | 122.28 | [12 empty] | 695.16 | 0.44 | 0.64 | 0.26
137 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW056 | 1S-DL-YP-CTC-DSRD-1401-KKW056 | KARACHI SWEET | TG-KKW056A-1 | 19503334 | 990 | 320 | 243 | 0.97 | 530 | 180 | 740 | 166 | 680 | 183 | 758 | 70 | 2019-06-30 00:30 | 120 | 45.6 | 833 | R | 101 | 98 | 102 | 4 |  |  | 3 | 97 | 0.3 | 2 | 2.3 |  | 458.37 | 523.49 | 523.49 | 482.38 | 260 | 193.18 | 262.14 | 236.29 | [8 empty] | 719.07 | 0.53 | 0.69 | 0.54
138 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW056 | 1S-DL-YP-CTC-DSRD-1401-KKW056 | KARACHI SWEET | TG-KKW056A-2 | 19503327 | 990 | 320 | 243 | 0.98 | 270 | 110 | 453 | 74 | 308 | 86 | 353 | 128 | 2019-06-13 23:00 | 49.3 | 5.2 | 495 | R | 139 | 64 | 97 | 75 |  |  | 1 | 99 | 213.07 | 695.39 | 602.53 | 572.44 | 502.32 | 20 | 20 | 142.55 | [12 empty] | 715.39 | 4.21 | 0.61 | 0.27
139 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW057 | 1S-DL-YP-CTC-DSRD-1401-KKW057 | 14 A KAROL BAGH:PKG | TG-KKW057A-1 | 19504665 | 990 | 320 | 238 | 0.98 | 743 | 232 | 1068 | 255 | 1091 | 255 | 973 | 109 | 2019-06-30 | 119.2 | 25 | 1091 | Y | 109 | 99 | 92 | 17 | 100 |  |  |  |  | 0.3 | 1 |  | 302.02 | 345.34 | 345.34 | 321.03 | 417.29 | 373.27 | 411.28 | 398.28 | [8 empty] | 719.31 | 0.29 | 0.57 | 0.75
140 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW058 | 1S-DL-YP-CTC-DSRD-1401-KKW058 | 73 BEEDEN PURA:PL | TG-KKW058A-1 | 19503280 | 990 | 320 | 248 | 0.96 | 590 | 201 | 831 | 176 | 754 | 213 | 903 | 129 | 2019-06-29 15:30 | 170.8 | 44.9 | 962 | R | 103 | 93 | 104 | 11 | 19.8 | 80.2 |  |  | 9.3 | 37 | 8 | 9.3 | 407 | 493 | 493 | 455.3 | 303.3 | 190 | 269.3 | 255 | [8 empty] | 720 | 0 | 0.61 | 0.6
141 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW059 | 1S-DL-YP-CTC-DSRD-1401-KKW059 | BAPU BHAWAN S/ST.:PL | TG-KKW059A-1 | 19504541 | 990 | 320 | 233 | 0.97 | 852 | 306 | 1337 | 279 | 1206 | 267 | 1123 | 187 | 2019-06-30 00:30 | 172.2 | 77.3 | 1337 | R | 102 | 96 | 102 | 6 | 99.8 | 0.2 | [6 empty] | 40 | 58 | 58 | 42 | 668.31 | 656.31 | 652.31 | 670.01 | 10.3 | 4.3 | 30.3 | 7 |  |  |  |  | 719.01 | 0.59 | 0.65 | 0.86
142 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW066 | 1S-DL-YP-CTC-DSRD-1401-KKW066 | 3A WEA (SAT NAGAR DHOBHI GHAT) P/M | TG-KKW066A-1 | 19506096 | 630 | 200 | 241 | 0.96 | 405 | 85 | 379 | 215 | 1023 | 105 | 439 | 617 | 2019-06-06 02:30 | 142.4 | 28.6 | 1023 | Y | 94 | 97 | 109 | 15 | 0.3 | 0.3 | 36.7 | 62.7 | 56 | 53 | 15 | 21.3 | 517.25 | 510.25 | 510.25 | 530.25 | 146.3 | 156 | 249 | 168 | [5 empty] | 0.3 |  |  | 719.55 | 0.05 | 0.52 | 0.64
143 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW067 | 1S-DL-YP-CTC-DSRD-1401-KKW067 | 5 BLOCK WEA KAROL BAGH KIOSK | TG-KKW067A-1 | 19503314 | 990 | 320 | 245 | 0.97 | 929 | 287 | 1250 | 289 | 1255 | 353 | 1534 | 281 | 2019-06-11 15:00 | 212 | -31.6 | 1554 | B | 89 | 97 | 114 | 25 |  |  | 3.2 | 96.8 | 253.3 | 251.3 | 246 | 249.3 | 42.3 | 43 | 43 | 39 | 173.35 | 115.05 | 73.35 | 107.05 | 22 | 82 | 122 | 96 |  |  | 22 |  | 695.35 | 0.25 | 0.39 | 0.94
144 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW067 | 1S-DL-YP-CTC-DSRD-1401-KKW067 | 5 BLOCK WEA KAROL BAGH KIOSK | TG-KKW067A-2 | 19505495 | 990 | 320 | 245 | 0.97 | 1094 | 527 | 2312 | 304 | 1252 | 264 | 1050 | 1173 | 2019-06-12 19:00 | 340.5 | 77.1 | 2312 | R | 100 | 101 | 98 | 3 | 0.2 |  | 2.1 | 97.7 |  |  |  |  | 124 | 114.3 | 114.3 | 93.3 | 448.36 | 464.36 | 578.36 | 501.36 | 143 | 132.3 | 67.3 | 124 | 4 | 8 |  | 0.3 | 719.36 | 0.24 | 0.52 | 1.11
145 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW067 | 1S-DL-YP-CTC-DSRD-1401-KKW067 | 5 BLOCK WEA KAROL BAGH KIOSK | TG-KKW067A-3 | 19505709 | 630 | 200 | 247 | 0.97 | 256 | 82 | 339 | 85 | 352 | 88 | 364 | 22 | 2019-06-15 17:00 | 73 | -5 | 450 | B | 98 | 90 | 111 | 21 | 0.1 |  | 0.6 | 99.4 | 419.51 | 427.3 | 397 | 416.21 | 272.15 | 277.06 | 277.06 | 287.45 | 15 | 2.3 | 11.3 | 3 | [8 empty] | 707.06 | 12.54 | 0.43 | 0.41
146 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | EPN002 | 1S-DL-YP-CTC-DSRD-1402-EPN002 | 39 BLK. O R NAGAR:PL | TG-EPN002A-1 | 19503340 | 990 | 320 | 242 | 0.96 | 588 | 202 | 830 | 203 | 826 | 183 | 742 | 86 | 2019-06-12 | 197.2 | 58.1 | 926 | Y | 98 | 106 | 96 | 10 |  | 0.1 | 57.1 | 42.8 | 1 |  | 0.32 |  | 362.02 | 261.02 | 261.02 | 329.02 | 355.54 | 457.54 | 348.24 | 389.54 | [8 empty] | 718.56 | 1.04 | 0.69 | 0.59
147 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | EPN003 | 1S-DL-YP-CTC-DSRD-1402-EPN003 | 21 BLK. O. R. NAGAR:K | TG-EPN003A-1 | 19503328 | 990 | 320 | 236 | 0.97 | 923 | 295 | 1240 | 318 | 1335 | 310 | 1295 | 83 | 2019-06-30 01:00 | 178.8 | 51.5 | 1383 | Y | 95 | 102 | 103 | 8 |  |  | 9.2 | 90.8 |  |  |  |  | 134.3 | 87.3 | 87.3 | 84.3 | 561.3 | 590 | 598.3 | 597.3 | 24 | 42.3 | 53.3 | 38 |  |  |  |  | 720 | 0 | 0.59 | 0.93
148 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | EPN003 | 1S-DL-YP-CTC-DSRD-1402-EPN003 | 21 BLK. O. R. NAGAR:K | TG-EPN003A-2 | 19503329 | 990 | 320 | 238 | 0.97 | 500 | 106 | 438 | 180 | 752 | 213 | 894 | 404 | 2019-06-30 00:30 | 102.3 | 25.8 | 954 | B | 87 | 120 | 92 | 33 |  |  | 67.6 | 32.4 | 214.3 | 34 | 209 | 106 | 466 | 493.3 | 493.3 | 523.3 | 39.3 | 192.3 | 59.3 | 90.3 | [8 empty] | 720 | 0 | 0.56 | 0.5
149 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | EPN003 | 1S-DL-YP-CTC-DSRD-1402-EPN003 | 21 BLK. O. R. NAGAR:K | TG-EPN003A-3 | 19504344 | 990 | 320 | 239 | 0.98 | 913 | 327 | 1493 | 306 | 1402 | 280 | 1270 | 194 | 2019-06-10 13:00 | 212 | 30.2 | 1493 | R | 114 | 103 | 84 | 30 |  | 0.1 | 3.1 | 96.8 | 1.15 | 1.15 | 1.15 | 1.15 | 30 | 62 | 62 | 69.3 | 586.11 | 629.51 | 484.4 | 622.51 | 100.05 | 25.25 | 2 | 24.55 | 1 |  |  |  | 718.31 | 1.29 | 0.6 | 0.92
150 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN001 | 1S-DL-YP-CTC-DSRD-1403-RJN001 | GANGA RAM HOSP.:ID | TG-RJN001A-1 | 19503339 | 990 | 320 | 238 | 0.97 | 745 | 202 | 841 | 279 | 1164 | 264 | 1108 | 299 | 2019-06-30 | 153.8 | 44.9 | 1228 | Y | 83 | 111 | 105 | 28 |  |  | 2.1 | 97.9 | 11 |  |  | 0.3 | 427 | 206.3 | 206.3 | 267 | 282 | 498.3 | 495 | 452.3 |  | 15 | 1 | [5 empty] | 720 | 0 | 0.6 | 0.75
151 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN002 | 1S-DL-YP-CTC-DSRD-1403-RJN002 | SINDHI PARK:ID | TG-RJN002A-1 | 19500711 | 990 | 320 | 236.5712 | 0.98795 | 425.455 | 105.2686 | 454.057 | 154.1617 | 668.2635 | 166.0247 | 723.2931 | 246.3744 | 2019-06-29 16:00 | [15 empty] | 215 |  |  |  | 499.5 |  |  |  | 3 |  |  |  | 0 |  |  |  | 0 | 717.5 |  | 0.56123 | 0.42975
152 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN002 | 1S-DL-YP-CTC-DSRD-1403-RJN002 | SINDHI PARK:ID | TG-RJN002A-2 | 19500712 | 990 | 320 | 235.8184 | 0.97409 | 607.9191 | 241.9997 | 1059.5896 | 141.0837 | 614.6368 | 224.8357 | 990.4218 | 414.7177 | 2019-06-30 23:30 | [15 empty] | 4 |  |  |  | 493.5 |  |  |  | 222.5 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.58679 | 0.61406
153 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN003 | 1S-DL-YP-CTC-DSRD-1403-RJN003 | 51-52 BLOCK O. R. NGR:K | TG-RJN003A-1 | 19503331 | 990 | 320 | 236 | 0.97 | 671 | 173 | 746 | 245 | 1075 | 253 | 1097 | 340 | 2019-06-29 23:30 | 124.4 | 54.5 | 1097 | B | 89 | 112 | 99 | 23 |  |  | 14.3 | 85.7 |  |  |  |  | 152.48 | 41.58 | 41.58 | 78.53 | 167.12 | 278.02 | 225.07 | 241.07 | [8 empty] | 719 | 1 | 0.67 | 0.68
154 | 2019-06-05 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN003 | 1S-DL-YP-CTC-DSRD-1403-RJN003 | 51-52 BLOCK O. R. NGR:K | TG-RJN003A-2 | 19504273 | 990 | 320 | 243 | 0.97 | 554 | 206 | 857 | 196 | 823 | 152 | 633 | 209 | 2019-06-30 | 108.9 | 39.7 | 881 | R | 105 | 108 | 87 | 21 |  |  | 7.2 | 92.8 | 2 | 2.3 | 5.58 | 0.3 | 408.17 | 375.47 | 375.47 | 454.4 | 212.47 | 244.47 | 45 | 167.54 | [8 empty] | 623.04 | 0.56 | 0.63 | 0.56
155 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN003 | 1S-DL-YP-CTC-DSRD-1403-RJN003 | 51-52 BLOCK O. R. NGR:K | TG-RJN003A-3 | 19503256 | 630 | 200 | 247 | 0.96 | 426 | 111 | 455 | 190 | 789 | 125 | 517 | 307 | 2019-06-29 16:00 | 108.6 | 22.5 | 857 | Y | 74 | 131 | 95 | 57 |  |  | 1.1 | 98.9 | 52.3 | 1 | 1 | 0.3 | 590.12 | 76.3 | 76.3 | 254.19 | 76.23 | 628.05 | 375.46 | 464.16 |  | 13.3 | [6 empty] | 719.05 | 0.55 | 0.63 | 0.68
156 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN004 | 1S-DL-YP-CTC-DSRD-1403-RJN004 | JANKI DEVI:ID | TG-RJN004A-1 | 19503765 | 990 | 320 | 240 | 0.97 | 623 | 203 | 881 | 203 | 890 | 216 | 939 | 54 | 2019-06-10 12:00 | 133.2 | 45.6 | 1001 | Y | 94 | 101 | 106 | 12 |  |  | 8.3 | 91.7 | 43.3 | 6 |  | 0.3 | 439.04 | 489.32 | 489.32 | 478.34 | 236.02 | 223.04 | 259.56 | 239.32 | [8 empty] | 718.36 | 1.24 | 0.58 | 0.63
157 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN004 | 1S-DL-YP-CTC-DSRD-1403-RJN004 | JANKI DEVI:ID | TG-RJN004A-2 | 19503764 | 990 | 320 | 240 | 0.97 | 734 | 261 | 1138 | 242 | 1044 | 231 | 993 | 127 | 2019-06-29 16:00 | 157.5 | 40.5 | 1138 | R | 92 | 102 | 106 | 14 |  |  | 1.4 | 98.6 |  |  |  |  | 411.43 | 288.13 | 288.13 | 289.43 | 307.3 | 431 | 496.11 | 429.3 | [8 empty] | 719.13 | 0.47 | 0.58 | 0.74
158 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN004 | 1S-DL-YP-CTC-DSRD-1403-RJN004 | JANKI DEVI:ID | TG-RJN004A-3 | 19505362 | 630 | 200 | 241 | 0.99 | 313 | 103 | 439 | 95 | 413 | 115 | 497 | 75 | 2019-06-29 14:00 | 78.4 | -3.2 | 701 | B | 96 | 93 | 110 | 17 | 0.2 | 2.3 | 89.6 | 7.9 | 140.32 | 187.02 | 87.02 | 137.32 | 508.3 | 472.41 | 472.41 | 470.41 | 61.11 | 50.3 | 193.3 | 102 | [8 empty] | 710.13 | 9.47 | 0.58 | 0.5
159 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN005 | 1S-DL-YP-CTC-DSRD-1403-RJN005 | 17 B BAZAR MARG (TAXI STAND):PL | TG-RJN005A-1 | 19503337 | 990 | 320 | 242 | 0.96 | 599 | 204 | 885 | 196 | 845 | 198 | 854 | 37 | 2019-06-29 13:30 | 148.7 | 47.1 | 957 | Y | 101 | 103 | 96 | 7 |  |  | 0.3 | 99.7 | 6 | 3.3 | 13 | 4 | 401.28 | 398.58 | 398.58 | 430.58 | 311.31 | 316.31 | 246.01 | 284.01 | [8 empty] | 718.59 | 1.01 | 0.63 | 0.6
160 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN006 | 1S-DL-YP-CTC-DSRD-1403-RJN006 | TIKONA PARK BAZAR MARG:PL | TG-RJN006A-1 | 19503361 | 990 | 320 | 242 | 0.97 | 917 | 365 | 1577 | 256 | 1089 | 296 | 1261 | 429 | 2019-06-30 23:30 | 165.6 | 47.8 | 1577 | R | 96 | 97 | 108 | 12 |  |  | 11.9 | 88.1 |  |  |  |  | 166.05 | 111.25 | 111.25 | 100.44 | 521.52 | 590.56 | 557.59 | 585.37 | 29.24 | 16 | 75.54 | 32 | 1 |  | 9.3 |  | 718.21 | 1.39 | 0.59 | 0.93
161 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN006 | 1S-DL-YP-CTC-DSRD-1403-RJN006 | TIKONA PARK BAZAR MARG:PL | TG-RJN006A-2 | 19505747 | 990 | 320 | 236 | 0.98 | 791 | 241 | 1075 | 307 | 1377 | 243 | 1079 | 300 | 2019-06-01 16:00 | 236.5 | 41 | 1392 | R | 92 | 105 | 104 | 13 | 0.3 | 0.4 | 2.1 | 97.2 | 0.3 | 0.3 |  | 0.3 | 154.01 | 74.33 | 74.33 | 77.01 | 562.14 | 629.12 | 633.17 | 640.14 | 1 | 13.3 | 11.3 | [5 empty] | 717.45 | 2.15 | 0.67 | 0.8
162 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN006 | 1S-DL-YP-CTC-DSRD-1403-RJN006 | TIKONA PARK BAZAR MARG:PL | TG-RJN006A-3 | 19505136 | 630 | 200 | 243 | 0.97 | 594 | 106 | 435 | 288 | 1255 | 199 | 862 | 710 | 2019-06-06 03:00 | 222 | 21 | 1255 | Y | 92 | 93 | 115 | 23 | 0.9 | 50.8 | 15.2 | 33.2 | 0.49 | 3.12 | 1.12 | 1.12 | 202.51 | 218.57 | 218.57 | 154.57 | 486.41 | 463.42 | 531.36 | 515.48 | 4 | 8.3 | 50.24 | 22.54 | 0.3 | 0.3 | 29.3 |  | 694.51 | 25.09 | 0.55 | 0.94
163 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN007 | 1S-DL-YP-CTC-DSRD-1403-RJN007 | BAZAR MARG (K):K | TG-RJN007A-1 | 19503364 | 990 | 320 | 243 | 0.97 | 589 | 184 | 760 | 204 | 841 | 201 | 834 | 78 | 2019-06-30 01:00 | 121.4 | 19.1 | 904 | R | 93 | 109 | 97 | 16 |  |  | 1.9 | 98.1 | 41.58 | 8.28 | 42.58 | 17.28 | 525.3 | 451.3 | 451.3 | 518 | 128.3 | 236 | 153 | 160.3 | [8 empty] | 695.58 | 0.02 | 0.57 | 0.59
164 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN007 | 1S-DL-YP-CTC-DSRD-1403-RJN007 | BAZAR MARG (K):K | TG-RJN007A-2 | 19505084 | 630 | 200 | 236 | 0.97 | 702 | 253 | 1099 | 208 | 889 | 241 | 1032 | 186 | 2019-06-30 00:30 | 129.3 | 38.6 | 1224 | R | 111 | 88 | 101 | 23 |  | 0.3 | 41 | 58.7 |  |  |  |  | 23.58 | 106.28 | 106.28 | 36.28 | 471.3 | 554 | 528.3 | 541.3 | 135 | 34.3 | 108 | 105 | 65.3 | 1 | 15.3 | 13 | 695.58 | 0.02 | 0.57 | 1.11
165 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN008 | 1S-DL-YP-CTC-DSRD-1403-RJN008 | AGGARWAL SWEET:K | TG-RJN008A-1 | 19503366 | 990 | 320 | 243 | 0.97 | 431 | 127 | 531 | 166 | 701 | 138 | 578 | 153 | 2019-06-15 15:00 | 100.8 | 25.8 | 755 | Y | 99 | 114 | 87 | 27 |  |  | 69 | 31 | 46.3 | 14.3 | 104.28 | 30.3 | 644.28 | 541.58 | 541.58 | 669.58 | 29 | 163.3 | 1 | 19.3 | [8 empty] | 719.58 | 0.02 | 0.69 | 0.44
166 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN008 | 1S-DL-YP-CTC-DSRD-1403-RJN008 | AGGARWAL SWEET:K, DOUBLE BUSHING | TG-RJN008A-2 | 19504653 | 990 | 320 | 243 | 0.97 | 415 | 107 | 446 | 151 | 624 | 157 | 653 | 194 | 2019-06-30 | 86.8 | 24.3 | 706 | B | 80 | 104 | 116 | 36 |  |  | 2.6 | 97.4 | 381.58 | 169.28 | 80.28 | 176.58 | 338 | 514.3 | 514.3 | 538 |  | 36 | 65.3 | 5 | [8 empty] | 719.58 | 0.02 | 0.59 | 0.42
167 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN008 | 1S-DL-YP-CTC-DSRD-1403-RJN008 | AGGARWAL SWEET:K, | TG-RJN008A-3 | 19502796 | 630 | 200 | 236 | 0.98 | 321 | 135 | 591 | 98 | 425 | 88 | 380 | 192 | 2019-06-15 14:00 | 57.5 | 17.5 | 633 | R | 120 | 99 | 82 | 38 |  |  | 31.6 | 68.4 | 16.3 | 16 | 70.3 | 11.3 | 315.28 | 578.58 | 578.58 | 547.58 | 388 | 125 | 18.3 | 160.3 | [8 empty] | 719.58 | 0.02 | 0.67 | 0.51
168 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN009 | 1S-DL-YP-CTC-DSRD-1403-RJN009 | RAJENDER PARK:ID | TG-RJN009A-1 | 19503199 | 990 | 320 | 244 | 0.98 | 433 | 136 | 554 | 120 | 491 | 178 | 728 | 213 | 2019-06-29 23:30 | 96.4 | 8.8 | 728 | B | 89 | 98 | 113 | 24 |  |  | 0.4 | 99.6 | 153.3 | 109 | 22.3 | 62 | 554.11 | 587.34 | 587.34 | 644.41 | 7 | 18.07 | 93.19 | 8 | [8 empty] | 714.41 | 5.19 | 0.64 | 0.44
169 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN010 | 1S-DL-YP-CTC-DSRD-1403-RJN010 | RAJINDER PARK P/M:PL | TG-RJN010A-1 | 19506436 | 990 | 320 | 239 | 0.96 | 577 | 198 | 809 | 176 | 715 | 202 | 830 | 106 | 2019-06-12 16:00 | 153.6 | 17 | 875 | R | 116 | 94 | 90 | 26 | 0.2 |  | 0.6 | 99.2 | 248 | 417 | 419 | 382 | 266 | 130 | 130 | 158 | 193 | 160 | 116 | 167 | [8 empty] | 707 | 13 | 0.44 | 0.58
170 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN010 | 1S-DL-YP-CTC-DSRD-1403-RJN010 | RAJINDER PARK P/M:PL | TG-RJN010A-2 | 19506614 | 630 | 200 | 244 | 0.95 | 236 | 79 | 305 | 74 | 288 | 83 | 319 | 27 | 2019-06-12 17:30 | 99.6 | 18.8 | 392 | R | 106 | 88 | 106 | 18 | 0.2 | 0.1 | 0.8 | 98.9 | 137 | 339 | 101 | 184 | 565 | 367.3 | 367.3 | 523 | 5 | 0.3 | 1 | [9 empty] | 707 | 13 | 0.64 | 0.37
171 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN011 | 1S-DL-YP-CTC-DSRD-1403-RJN011 | SALWAN SCHOOL OLD:PL | TG-RJN011A-1 | 19506581 | 990 | 320 | 244 | 0.95 | 982 | 321 | 1367 | 320 | 1357 | 341 | 1445 | 83 | 2019-06-01 12:30 | 291.8 | 39 | 1445 | B | 96 | 105 | 99 | 9 | 0.1 |  | 1.4 | 98.5 | 133.3 | 22.3 | 92 | 84 | 268 | 351.3 | 351.3 | 299.3 | 236.17 | 218.3 | 257.47 | 234.17 | 66.21 | 111.38 | 66.3 | 86.21 |  |  | 0.51 |  | 704.08 | 15.52 | 0.46 | 0.99
172 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN011 | 1S-DL-YP-CTC-DSRD-1403-RJN011 | SALWAN SCHOOL OLD:PL | TG-RJN011A-2 | 19504280 | 630 | 200 | 245 | 0.97 | 392 | 161 | 656 | 113 | 459 | 118 | 482 | 186 | 2019-06-01 03:00 | 86 | 21.6 | 656 | R | 111 | 89 | 100 | 22 |  |  | 5.2 | 94.8 | 64.3 | 139.3 | 78.3 | 77.3 | 425.03 | 497.03 | 497.03 | 484.33 | 229.34 | 82.34 | 140.28 | 157.04 | [8 empty] | 719.07 | 0.53 | 0.5 | 0.62
173 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN011 | 1S-DL-YP-CTC-DSRD-1403-RJN011 | SALWAN SCHOOL OLD:PL | TG-RJN011A-3 | 19504346 | 990 | 320 | 245 | 0.97 | 650 | 215 | 907 | 217 | 919 | 217 | 919 | 12 | 2019-06-01 15:30 | 150.9 | 24.3 | 936 | R | 99 | 101 | 99 | 2 |  |  | 8.4 | 91.6 | 39.02 | 18.32 | 23.32 | 13.32 | 480.56 | 490.26 | 490.26 | 521.26 | 198.22 | 209.22 | 180.56 | 183.22 | [8 empty] | 718.2 | 1.4 | 0.53 | 0.66
174 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN011 | 1S-DL-YP-CTC-DSRD-1403-RJN011 | SALWAN SCHOOL OLD:PL | TG-RJN011A-4 | 19505433 | 630 | 200 | 246 | 0.97 | 366 | 132 | 550 | 112 | 468 | 122 | 510 | 71 | 2019-06-03 14:00 | 114.6 | -65.2 | 569 | R | 107 | 94 | 99 | 13 | 0.1 |  | 22.8 | 77.1 | 221.14 | 339.13 | 307.43 | 293.13 | 309.35 | 230.06 | 230.06 | 247.06 | 171.56 | 133.26 | 174.26 | 162.26 | [8 empty] | 702.45 | 17.15 | 0.47 | 0.58
175 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN012 | 1S-DL-YP-CTC-DSRD-1403-RJN012 | SALWAN SCHOOL NEW:K | TG-RJN012A-1 | 19503377 | 990 | 320 | 236 | 0.98 | 931 | 273 | 1149 | 337 | 1426 | 322 | 1370 | 253 | 2019-06-30 | 167.1 | 23.6 | 1587 | Y | 95 | 109 | 95 | 14 |  |  | 1.3 | 98.7 | 1 | 0.3 | 2.3 | 0.3 | 232.33 | 119.46 | 119.46 | 193.46 | 474.28 | 551.45 | 440.15 | 505.45 | 8 | 42 | 15 | 16 |  | 2 |  |  | 716.01 | 3.59 | 0.52 | 0.94
176 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN012 | 1S-DL-YP-CTC-DSRD-1403-RJN012 | SALWAN SCHOOL NEW:K | TG-RJN012A-2 | 19504309 | 990 | 320 | 238 | 0.97 | 224 | 88 | 360 | 95 | 393 | 41 | 166 | 213 | 2019-06-30 02:00 | 46.4 | 11 | 431 | Y | 113 | 122 | 65 | 57 |  | 0.1 | 15.1 | 84.8 | 674.24 | 590.24 | 718.05 | 713.22 | 43.41 | 127.41 | 127.41 | 4.43 | [12 empty] | 718.05 | 1.55 | 0.57 | 0.23
177 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN012 | 1S-DL-YP-CTC-DSRD-1403-RJN012 | SALWAN SCHOOL NEW:K | TG-RJN012A-3 | 19506445 | 990 | 320 | 232 | 0.98 | 714 | 279 | 1288 | 216 | 982 | 219 | 995 | 300 | 2019-06-01 23:30 | 184 | 32.3 | 1330 | R | 115 | 97 | 88 | 27 | 0.2 |  | 40.9 | 58.9 | 2.3 | 8.3 | 10 | 3 | 265.3 | 414 | 414 | 395.3 | 431.24 | 281.37 | 190.37 | 305.37 | 4.43 | [7 empty] | 704.07 | 15.53 | 0.56 | 0.72
178 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN013 | 1S-DL-YP-CTC-DSRD-1403-RJN013 | SETHI PETROL PUMP:ID | TG-RJN013A-1 | 19500413 | 990 | 320 | 242 | 0.96 | 565 | 222 | 919 | 179 | 740 | 164 | 683 | 214 | 2019-06-30 01:30 | 152.4 | 47.1 | 933 | R | 108 | 101 | 91 | 17 |  |  | 5.9 | 94.1 | 4 | 28.28 | 21 | 13 | 376.22 | 398.54 | 398.54 | 432.22 | 336.59 | 289.59 | 152.3 | 271.59 | [8 empty] | 717.21 | 2.39 | 0.65 | 0.57
179 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN013 | 1S-DL-YP-CTC-DSRD-1403-RJN013 | SETHI PETROL PUMP:ID | TG-RJN013A-2 | 19504685 | 990 | 320 | 242 | 0.97 | 1161 | 355 | 1483 | 309 | 1276 | 497 | 2094 | 736 | 2019-06-30 01:00 | 219.3 | 79.5 | 2098 | B | 96 | 90 | 114 | 24 |  | 0.1 | 32.3 | 67.6 |  |  |  |  | 40.28 | 43.58 | 43.58 | 27.28 | 550.5 | 609.49 | 439.08 | 547.5 | 115.19 | 61.59 | 183.51 | 122.29 | 9.09 |  | 79.19 | 17.59 | 715.46 | 4.14 | 0.56 | 1.17
180 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN013 | 1S-DL-YP-CTC-DSRD-1403-RJN013 | SETHI PETROL PUMP:ID | TG-RJN013A-3 | 19503046 | 630 | 120 | 244 | 0.97 | 171 | 68 | 273 | 29 | 118 | 74 | 301 | 170 | 2019-06-12 00:30 | 37.5 | 8 | 348 | B | 122 | 55 | 123 | 68 |  |  | 18.8 | 81.2 | 289.07 | 717.59 | 335.07 | 549.07 | 428.52 |  |  | 168.52 | [12 empty] | 717.59 | 2.01 | 0.64 | 0.27
181 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN014 | 1S-DL-YP-CTC-DSRD-1403-RJN014 | DI KHAN:ID | TG-RJN014A-1 | 19500406 | 630 | 200 | 244 | 0.97 | 465 | 169 | 691 | 156 | 644 | 140 | 565 | 110 | 2019-06-12 | 110.9 | 25.8 | 744 | Y | 104 | 106 | 90 | 16 | 0.3 | 20.2 | 78.5 | 1 | 2.3 | 2 | 11.3 | 2 | 279.05 | 264.05 | 264.05 | 308.35 | 437.3 | 453 | 318.3 | 409 | 0.3 | 0.3 | [6 empty] | 719.35 | 0.25 | 0.59 | 0.74
182 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN014 | 1S-DL-YP-CTC-DSRD-1403-RJN014 | DI KHAN:ID | TG-RJN014A-2 | 19503372 | 630 | 200 | 244 | 0.97 | 340 | 135 | 559 | 96 | 397 | 109 | 446 | 143 | 2019-06-11 23:30 | 81 | 23 | 579 | R | 108 | 86 | 106 | 22 |  |  | 0.4 | 99.6 | 1 | 30.3 | 1.3 | 2 | 380.05 | 596.35 | 596.35 | 466.35 | 338.3 | 92.3 | 337.17 | 251 | [8 empty] | 719.35 | 0.25 | 0.68 | 0.54
183 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN015 | 1S-DL-YP-CTC-DSRD-1403-RJN015 | R. BLOCK N. R. NAGAR:ID | TG-RJN015A-1 | 19500431 | 990 | 320 | 237 | 0.97 | 510 | 159 | 663 | 161 | 672 | 189 | 789 | 122 | 2019-06-30 | 102.3 | 30.9 | 874 | B | 97 | 95 | 108 | 13 |  |  | 5.1 | 94.9 | 36 | 16 | 26.3 | 15 | 587 | 661 | 661 | 586 | 97 | 43 | 221.3 | 119 | [8 empty] | 720 | 0 | 0.63 | 0.51
184 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN015 | 1S-DL-YP-CTC-DSRD-1403-RJN015 | R. BLOCK N. R. NAGAR:ID | TG-RJN015A-2 | 19503384 | 990 | 320 | 237 | 0.98 | 568 | 229 | 1013 | 176 | 772 | 162 | 712 | 276 | 2019-06-30 23:30 | 117.8 | 33.1 | 1013 | R | 114 | 97 | 89 | 25 |  |  | 18.6 | 81.4 | 0.3 | 4.3 | 14 | 2 | 348.3 | 498 | 498 | 479.3 | 371 | 217.3 | 139.3 | 238.3 | [8 empty] | 720 | 0 | 0.64 | 0.57
185 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN016 | 1S-DL-YP-CTC-DSRD-1403-RJN016 | MICROWAVE:PL | TG-RJN016A-1 | 19503303 | 400 | 120 | 246 | 0.99 | 116 | 39 | 160 | 38 | 158 | 39 | 162 | 3 | 2019-06-03 14:30 | 24.3 | -19.3 | 162 | R | 105 | 98 | 97 | 8 |  |  | 0.5 | 99.5 | 288.3 | 442.29 | 475.59 | 409.29 | 431.05 | 277.06 | 277.06 | 310.06 | [12 empty] | 719.35 | 0.25 | 0.68 | 0.29
186 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN017 | 1S-DL-YP-CTC-DSRD-1403-RJN017 | NPL QTR. OUTSIDE P/M:PL | TG-RJN017A-1 | 19505746 | 990 | 320 | 238 | 0.97 | 444 | 164 | 662 | 134 | 535 | 146 | 582 | 111 | 2019-06-12 04:30 | 153.3 | 26.9 | 977 | R | 119 | 90 | 91 | 29 | 0.3 | 0.1 | 79.1 | 20.5 | 4 | 80.53 | 75.3 | 21 | 550.03 | 634.4 | 634.4 | 672.33 | 164.3 | 3 | 19.3 | 25 | [8 empty] | 718.33 | 1.27 | 0.66 | 0.45
187 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN017 | 1S-DL-YP-CTC-DSRD-1403-RJN017 | NPL QTR. OUTSIDE P/M:PL | TG-RJN017A-2 | 19504385 | 400 | 120 | 239 | 0.98 | 82 | 25 | 105 | 30 | 126 | 27 | 111 | 18 | 2019-06-11 23:00 | 15.5 | 1.9 | 133 | R | 108 | 102 | 91 | 17 |  |  | 64.8 | 35.2 | 706.03 | 704.03 | 716.33 | 717.33 | 12.3 | 14.3 | 14.3 | 1 | [12 empty] | 718.33 | 1.27 | 0.52 | 0.21
188 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN018 | 1S-DL-YP-CTC-DSRD-1403-RJN018 | NPL COLONY INSIDE:ID | TG-RJN018A-1 | 19503336 | 400 | 120 | 245 | 0.98 | 45 | 13 | 54 | 21 | 85 | 10 | 42 | 39 | 2019-06-29 23:30 | 9.4 | 0.3 | 86 | Y | 87 | 146 | 67 | 79 |  |  | 0.3 | 99.7 | 718.08 | 718.08 | 718.08 | 718.08 | [16 empty] | 718.08 | 1.52 | 0.41 | 0.11
189 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN018 | 1S-DL-YP-CTC-DSRD-1403-RJN018 | NPL COLONY INSIDE:ID | TG-RJN018A-2 | 19503386 | 400 | 120 | 245 | 0.99 | 29 | 10 | 41 | 6 | 24 | 14 | 57 | 28 | 2019-06-14 23:30 | 3.6 | -0.6 | 60 | B | 68 | 92 | 140 | 72 |  |  | 1.5 | 98.5 | 718.13 | 718.13 | 718.13 | 718.13 | [16 empty] | 718.13 | 1.47 | 0.4 | 0.07
190 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN019 | 1S-DL-YP-CTC-DSRD-1403-RJN019 | SRD BUILDING OFFICE:ID | TG-RJN019A-1 | 19503282 | 990 | 320 | 238 | 0.97 | 872 | 310 | 1318 | 247 | 1046 | 314 | 1340 | 284 | 2019-06-29 23:30 | 182.5 | 61.8 | 1432 | B | 101 | 85 | 114 | 29 |  |  | 26.3 | 73.7 |  |  |  |  | 71.3 | 185 | 185 | 61 | 621.25 | 533.55 | 615.55 | 646.55 | 26 |  | 84 | 11 |  |  | 1.3 |  | 718.55 | 1.05 | 0.63 | 0.88
191 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN019 | 1S-DL-YP-CTC-DSRD-1403-RJN019 | SRD BUILDING OFFICE:ID | TG-RJN019A-2 | 19503296 | 990 | 320 | 244 | 0.96 | 266 | 97 | 420 | 80 | 345 | 89 | 373 | 65 | 2019-06-12 15:00 | 70.7 | -3.7 | 420 | R | 103 | 97 | 100 | 6 | 17.8 | 82.2 | 0.1 |  | 590.28 | 711.49 | 661.19 | 662.19 | 129.21 | 8 | 8 | 57.3 | [12 empty] | 719.49 | 0.11 | 0.43 | 0.27
192 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN020 | 1S-DL-YP-CTC-DSRD-1403-RJN020 | MANAVSTHALI (K):ID | TG-RJN020A-1 | 19500410 | 630 | 200 | 244 | 0.97 | 463 | 172 | 704 | 147 | 606 | 145 | 590 | 107 | 2019-06-13 23:30 | 109.5 | 28.1 | 704 | R | 99 | 98 | 103 | 5 |  | 0.3 | 80.7 | 19 |  | 0.3 |  |  | 199 | 233.3 | 233.3 | 158.3 | 519.39 | 485.39 | 561.39 | 561.09 | 1 | [7 empty] | 719.39 | 0.21 | 0.62 | 0.74
193 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN020 | 1S-DL-YP-CTC-DSRD-1403-RJN020 | MANAVSTHALI (K):ID | TG-RJN020A-2 | 19504560 | 990 | 320 | 243 | 0.97 | 197 | 85 | 356 | 46 | 191 | 66 | 277 | 143 | 2019-06-12 15:00 | 54.5 | -5.9 | 382 | R | 128 | 69 | 103 | 59 |  |  | 65.4 | 34.6 | 507.4 | 719.4 | 682.4 | 719.4 | 212 | [15 empty] | 719.4 | 0.2 | 0.71 | 0.2
194 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN021 | 1S-DL-YP-CTC-DSRD-1403-RJN021 | NEHRU PARK P/M:PL | TG-RJN021A-1 | 19506517 | 630 | 200 | 238 | 0.97 | 420 | 136 | 562 | 196 | 870 | 88 | 388 | 423 | 2019-06-06 02:30 | 125.4 | 30.2 | 870 | Y | 111 | 104 | 84 | 27 | 0.4 |  | 47.9 | 51.6 |  |  | 1.3 |  | 111.3 | 147.05 | 147.05 | 173 | 592.35 | 556.3 | 287.35 | 531.05 |  | 0.3 | [6 empty] | 704.05 | 15.55 | 0.68 | 0.67
195 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN021 | 1S-DL-YP-CTC-DSRD-1403-RJN021 | NEHRU PARK P/M:PL | TG-RJN021A-2 | 19500415 | 630 | 200 | 243 | 0.96 | 470 | 174 | 739 | 141 | 589 | 155 | 644 | 131 | 2019-06-03 | 115.5 | 46 | 796 | R | 118 | 91 | 91 | 27 |  | 10.3 | 67.1 | 22.7 |  | 0.3 |  |  | 31 | 242.4 | 242.4 | 118.3 | 679.34 | 476.24 | 444.3 | 601.04 | 9 | [7 empty] | 719.34 | 0.26 | 0.66 | 0.75
196 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN022 | 1S-DL-YP-CTC-DSRD-1403-RJN022 | RAMNATH VIZ:K | TG-RJN022A-1 | 19500407 | 990 | 320 | 242 | 0.97 | 673 | 189 | 767 | 208 | 849 | 276 | 1137 | 336 | 2019-06-12 | 198 | 28.7 | 1253 | B | 87 | 88 | 125 | 38 |  | 1 | 85.3 | 13.8 | 7.3 | 2 |  |  | 408 | 395.3 | 395.3 | 258 | 304.3 | 322.3 | 621 | 462 |  |  | 16.3 | [5 empty] | 720 | 0 | 0.65 | 0.68
197 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN022 | 1S-DL-YP-CTC-DSRD-1403-RJN022 | RAMNATH VIZ:K | TG-RJN022A-2 | 19504386 | 630 | 200 | 237 | 0.97 | 386 | 131 | 585 | 156 | 702 | 99 | 439 | 228 | 2019-06-11 00:30 | 86.5 | 18.9 | 702 | Y | 100 | 109 | 91 | 18 |  |  | 5.6 | 94.4 | 17.3 | 11 | 25.3 | 15.3 | 447 | 393 | 393 | 454 | 255.3 | 316 | 163.3 | 250.3 | [8 empty] | 720 | 0 | 0.6 | 0.61
198 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN023 | 1S-DL-YP-CTC-DSRD-1403-RJN023 | NPL MULTI STORIES:ID | TG-RJN023A-1 | 19503308 | 630 | 200 | 241 | 0.98 | 508 | 193 | 836 | 141 | 604 | 173 | 738 | 201 | 2019-06-11 22:30 | 65.3 | 12.4 | 899 | R | 115 | 87 | 97 | 28 |  | 1 | 52.6 | 46.4 | 3.3 | 17 | 12 | 6.3 | 224.41 | 406.11 | 406.11 | 327.41 | 435.28 | 296.28 | 372.28 | 383.58 | 56 |  | 4 | 1.3 |  |  |  |  | 719.39 | 0.21 | 0.55 | 0.81
199 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN024 | 1S-DL-YP-CTC-DSRD-1403-RJN024 | DDA SHANKAR RD.:ID | TG-RJN024A-1 | 19504502 | 630 | 200 | 239 | 0.98 | 502 | 159 | 688 | 179 | 780 | 163 | 709 | 84 | 2019-06-03 15:00 | 124.2 | 13.3 | 825 | Y | 88 | 121 | 91 | 33 |  | 0.5 | 49.7 | 49.8 | 6.3 |  | 1 |  | 306.28 | 40 | 40 | 161.3 | 406.41 | 661.39 | 463.15 | 558.09 |  | 18 | [6 empty] | 719.39 | 0.21 | 0.61 | 0.8
200 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN024 | 1S-DL-YP-CTC-DSRD-1403-RJN024 | DDA SHANKAR RD.:ID | TG-RJN024A-2 | 19500408 | 990 | 320 | 238 | 0.98 | 700 | 177 | 750 | 354 | 1506 | 169 | 724 | 770 | 2019-06-12 15:00 | 199.5 | 47.8 | 1555 | Y | 80 | 146 | 74 | 72 |  |  | 3 | 97 | 0.3 |  | 1.3 |  | 335.57 | 3.3 | 3.3 | 86.3 | 382.59 | 450.57 | 262.37 | 632.56 |  | 236.59 |  |  |  | 28 |  |  | 719.26 | 0.34 | 0.72 | 0.71
201 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN025 | 1S-DL-YP-CTC-DSRD-1403-RJN025 | J. BLOCK (K) N. R. NGR.:K | TG-RJN025A-1 | 19500308 | 990 | 320 | 235 | 0.97 | 618 | 175 | 761 | 233 | 1028 | 209 | 922 | 232 | 2019-06-12 | 130.3 | 29.4 | 1028 | Y | 95 | 98 | 107 | 12 |  | 0.5 | 45.6 | 53.9 | 1 | 1 |  | 0.3 | 345.08 | 338.38 | 338.38 | 287.38 | 373.2 | 379.5 | 495.2 | 431.2 | [8 empty] | 719.28 | 0.32 | 0.67 | 0.62
202 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN025 | 1S-DL-YP-CTC-DSRD-1403-RJN025 | J. BLOCK (K) N. R. NGR.:K | TG-RJN025A-2 | 19504774 | 990 | 320 | 236 | 0.98 | 529 | 176 | 758 | 175 | 760 | 177 | 769 | 10 | 2019-06-12 | 114.8 | 30.9 | 799 | R | 94 | 100 | 107 | 13 |  |  | 7.6 | 92.4 | 22 | 6.3 |  | 0.3 | 534.11 | 512.39 | 512.39 | 510.09 | 163.28 | 200.3 | 280.43 | 209 | [8 empty] | 719.39 | 0.21 | 0.67 | 0.53
203 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN025 | 1S-DL-YP-CTC-DSRD-1403-RJN025 | J. BLOCK (K) N. R. NGR.:K | TG-RJN025A-3 | 19505317 | 630 | 200 | 242.6254 | 0.98217 | 932.0919 | 323.7348 | 1427.0245 | 319.4 | 1311.5427 | 288.9571 | 1357.307 | 100.7247 | 2019-06-14 23:00 | [15 empty] | 139.5 |  |  |  | 546.5 |  |  |  | 33.5 |  |  |  | 0 |  |  |  | 0.5 | 720 |  | 0.18055 | 1.4795
204 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN026 | 1S-DL-YP-CTC-DSRD-1403-RJN026 | MORELAND | TG-RJN026A-1 | 19503380 | 630 | 200 | 241 | 0.97 | 336 | 106 | 457 | 91 | 387 | 139 | 608 | 195 | 2019-06-01 16:30 | 80 | 19.8 | 649 | B | 101 | 84 | 115 | 31 |  | 8.1 | 91.6 | 0.3 | 3 | 30.3 | 0.3 | 1.3 | 544.11 | 653.09 | 653.09 | 565.39 | 172.28 | 36 | 342.3 | 152.3 | [8 empty] | 719.39 | 0.21 | 0.66 | 0.53
205 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN027 | 1S-DL-YP-CTC-DSRD-1403-RJN027 | ANDH MAHAVIDYALAYA:PL | TG-RJN027A-1 | 19503367 | 630 | 200 | 234 | 0.97 | 369 | 123 | 539 | 143 | 635 | 103 | 455 | 156 | 2019-06-29 16:00 | 81.9 | 31.7 | 697 | B | 84 | 101 | 114 | 30 |  | 0.2 | 23.1 | 76.7 | 28 | 4.3 |  |  | 510.16 | 352.41 | 352.41 | 351.56 | 181.17 | 362.22 | 506.33 | 367.37 | [8 empty] | 719.33 | 0.27 | 0.69 | 0.59
206 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN027 | 1S-DL-YP-CTC-DSRD-1403-RJN027 | ANDH MAHAVIDYALAYA:PL | TG-RJN027A-2 | 19502791 | 630 | 200 | 233 | 0.98 | 310 | 103 | 454 | 110 | 488 | 97 | 433 | 48 | 2019-06-02 22:00 | 63.9 | 17.5 | 575 | R | 111 | 91 | 98 | 20 |  |  | 0.1 | 99.9 | 9 | 16 | 22 | 9 | 384.58 | 644.28 | 644.28 | 555.28 | 326 | 59.3 | 153.3 | 155.3 | [8 empty] | 719.58 | 0.02 | 0.69 | 0.49
207 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN028 | 1S-DL-YP-CTC-DSRD-1403-RJN028 | COMM. CENTRE.N. R. N:K | TG-RJN028A-1 | 19503307 | 990 | 320 | 238 | 0.97 | 636 | 185 | 787 | 242 | 1047 | 209 | 894 | 226 | 2019-06-02 23:30 | 149.4 | 42 | 1103 | Y | 93 | 107 | 101 | 14 |  |  | 31.2 | 68.8 |  | 1.3 |  |  | 368.47 | 246.23 | 246.23 | 283.47 | 351 | 471.54 | 443.3 | 436 | [8 empty] | 719.47 | 0.13 | 0.67 | 0.64
208 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN066 | 1S-DL-YP-CTC-DSRD-1403-RJN066 | MES ( ARMY WIRELESS) :PM | TG-RJN066A-1 | 19503306 | 400 | 120 | 241 | 0.97 | 206 | 64 | 273 | 52 | 218 | 90 | 389 | 151 | 2019-06-27 17:00 | 52.7 | 16.8 | 398 | B | 92 | 102 | 106 | 14 | 0.6 | 5.1 | 45.6 | 48.7 | 4.36 | 3.3 | 5.3 | 3 | 613.53 | 545.03 | 545.03 | 581.33 | 97.5 | 167.46 | 235.16 | 131.46 | [8 empty] | 716.19 | 3.41 | 0.68 | 0.52
209 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN067 | 1S-DL-YP-CTC-DSRD-1403-RJN067 | ST LT NO. 4 (POLICE POST):PM | TG-RJN067A-1 | 19505306 | 100 | 40 | 238 | 0.85 | 44 | 15 | 62 | 11 | 45 | 18 | 76 | 27 | 2019-06-27 19:30 | 36 | -0.2 | 76 | B | 103 | 76 | 121 | 45 |  | 0.2 | 30.2 | 69.6 | 397.4 | 555.1 | 397.4 | 397.4 | 304.56 | 151.1 | 151.1 | 304.56 | 4.14 | 0.3 | 95.44 | 4.14 | [8 empty] | 706.5 | 13.1 | 0.29 | 0.44
210 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN069 | 1S-DL-YP-CTC-DSRD-1403-RJN069 | ST LT NO. 2 (WATER TANK):PM | TG-RJN069A-1 | 19506748 | 100 | 40 | 243 | 0.83 | 81 | 20 | 82 | 33 | 139 | 28 | 118 | 51 | 2019-06-27 19:30 | 61.6 | -2.4 | 139 | Y | 68 | 114 | 117 | 49 |  | 0.7 | 45.2 | 54.1 | 406.48 | 406.18 | 407.51 | 407.18 | 294.51 | 3.56 | 3.56 | 58.26 | 5.12 | 293.55 | 298.25 | 240.55 |  | 2.42 | 0.12 | 0.12 |  |  |  |  | 706.51 | 13.09 | 0.29 | 0.81
211 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN070 | 1S-DL-YP-CTC-DSRD-1403-RJN070 | ST LT NO. 1 (BAPU ASHARAM ASHRAM):PM | TG-RJN070A-1 | 19505387 | 100 | 40 | 245 | 0.96 | 28 | 2 | 7 | 21 | 91 | 5 | 22 | 77 | 2019-06-23 16:00 | 13.9 | 0.2 | 91 | Y | 59 | 78 | 163 | 104 | 0.3 | 1.1 | 7 | 91.5 | 716.18 | 680.18 | 683.06 | 713.48 |  | 31 | 31 | 2.3 |  | 5 | [10 empty] | 716.18 | 3.42 | 0.2 | 0.28
212 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN081 | 1S-DL-YP-CTC-DSRD-1403-RJN081 | HANDIWALA ORN : K | TG-RJN081A-1 | 19503379 | 990 | 320 | 241 | 0.97 | 1021 | 350 | 1459 | 355 | 1475 | 316 | 1322 | 147 | 2019-06-03 02:00 | 197.2 | -43.4 | 1520 | Y | 101 | 99 | 101 | 2 |  |  | 5.8 | 94.2 | 2.3 | 1.3 | 1.3 | 1.3 | 101.32 | 96.25 | 96.25 | 73.35 | 547.56 | 569.08 | 625.5 | 594.53 | 57.44 | 43.09 | 27.57 | 41.57 | 2.4 | 2.1 |  | 0.27 | 712.22 | 7.38 | 0.54 | 1.03
213 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN081 | 1S-DL-YP-CTC-DSRD-1403-RJN081 | HANDIWALA ORN : K | TG-RJN081A-2 | 19504310 | 630 | 200 | 241 | 0.97 | 595 | 187 | 801 | 172 | 735 | 236 | 1022 | 260 | 2019-06-02 00:30 | 130.6 | 41.4 | 1022 | B | 83 | 105 | 112 | 29 |  | 0.6 | 62.1 | 37.3 | 0.3 |  |  |  | 170.48 | 41.28 | 41.28 | 55.58 | 544.02 | 571.22 | 542.22 | 611.52 | 3 | 103.3 | 141.3 | 50.3 |  | 2 | 7 |  | 718.2 | 1.4 | 0.64 | 0.94
214 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN081 | 1S-DL-YP-CTC-DSRD-1403-RJN081 | HANDIWALA ORN : K | TG-RJN081A-3 | 19505206 | 630 | 200 | 241 | 0.97 | 736 | 301 | 1363 | 106 | 431 | 329 | 1537 | 1030 | 2019-06-06 03:00 | 276.2 | 32.8 | 1537 | B | 118 | 69 | 113 | 49 | 0.4 | 0.1 | 36.6 | 63 |  | 19.28 |  |  | 58.07 | 397.21 | 397.21 | 125.13 | 475.42 | 277.05 | 536.55 | 500.36 | 100.3 |  | 94.22 | 67.52 | 59.35 |  | 10.13 | 0.13 | 693.54 | 26.06 | 0.47 | 1.17
215 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN083 | 1S-DL-YP-CTC-DSRD-1403-RJN083 | BOOSTER PUMP | TG-RJN083A-1 | 19506015 | 630 | 120 | 238 | 0.97 | 315 | 88 | 363 | 110 | 467 | 117 | 489 | 116 | 2019-06-27 04:30 | 116.6 | 19.6 | 729 | B | 74 | 116 | 110 | 42 | 0.9 | 34.9 | 52.5 | 11.6 | 326.25 | 35.22 | 22.52 | 47.51 | 387.45 | 528.03 | 528.03 | 642.19 | 3.3 | 154.15 | 81.3 | 27.3 | [8 empty] | 717.4 | 2.2 | 0.57 | 0.5
216 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN084 | 1S-DL-YP-CTC-DSRD-1403-RJN084 | GULASHAN JOLLY 7-B PUSHA ROAD:PKG | TG-RJN084A-1 | 19506703 | 990 | 320 | 245 | 0.94 | 208 | 66 | 263 | 76 | 300 | 66 | 263 | 37 | 2019-06-14 15:00 | 204.5 | -12.8 | 303 | Y | 104 | 107 | 88 | 19 |  |  | 1.9 | 98.1 | 703.23 | 698.23 | 705.23 | 704.53 | 3 | 8 | 8 | 1.3 | [12 empty] | 706.23 | 13.37 | 0.35 | 0.21
217 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN085 | 1S-DL-YP-CTC-DSRD-1403-RJN085 | POLICE STATION NEW RAJINDER NAGAR | TG-RJN085A-1 | 19505872 | 400 | 120 | 246 | 0.97 | 189 | 49 | 205 | 43 | 178 | 97 | 395 | 205 | 2019-06-01 22:00 | 50.6 | 10.3 | 403 | B | 84 | 66 | 150 | 84 | 0.7 | 0.6 | 75.8 | 22.8 | 268.3 | 520.3 | 3 | 107 | 451 | 199.3 | 199.3 | 602.3 | 0.3 |  | 327.3 | 10.3 | [8 empty] | 720 | 0 | 0.56 | 0.47
218 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN092 | 1S-DL-YP-CTC-DSRD-1403-RJN092 | PUMPOSE ROAD:PL | TG-RJN092A-1 | 19505087 | 990 | 320 | 245 | 0.96 | 692 | 218 | 904 | 241 | 1003 | 233 | 979 | 90 | 2019-06-01 22:30 | 204.6 | 52.3 | 1003 | Y | 92 | 103 | 105 | 13 |  |  | 46.4 | 53.6 | 1.3 |  |  |  | 266 | 164 | 164 | 183 | 452.3 | 556 | 576.3 | 537 | [8 empty] | 720 | 0 | 0.67 | 0.7
219 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN092 | 1S-DL-YP-CTC-DSRD-1403-RJN092 | PUMPOSE ROAD:PL | TG-RJN092A-2 | 19506098 | 630 | 200 | 246 | 0.97 | 346 | 97 | 390 | 123 | 498 | 126 | 512 | 115 | 2019-06-15 15:00 | 109 | 9.2 | 810 | B | 93 | 87 | 120 | 33 | 0.4 |  | 20.7 | 78.9 | 373.3 | 425.3 | 175.3 | 321.3 | 244.3 | 187 | 187 | 281.3 | 78.3 | 84 | 114 | 93.3 |  |  | 0.3 | [5 empty] | 696.3 | 23.3 | 0.44 | 0.55
220 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN100 | 1S-DL-YP-CTC-DSRD-1403-RJN100 | 25 B PUSA ROAD | TG-RJN100A-1 | 19506097 | 990 | 320 | 244 | 0.99 | 614 | 200 | 818 | 225 | 926 | 188 | 777 | 133 | 2019-06-06 13:00 | 75.2 | -47 | 962 | Y | 96 | 107 | 97 | 11 |  |  | 0.6 | 99.4 | 203.3 | 170 | 189 | 188 | 256.06 | 238.44 | 238.44 | 259.44 | 245.29 | 296.21 | 221.29 | 257.21 | [8 empty] | 705.05 | 14.55 | 0.53 | 0.62