## Loading Condition > 80%
MIS Report of Distribution Transformer - Jun19
Jun19 1140 SHANKAR ROAD (Loading Condition > 80% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW032 | 1S-DL-YP-CTC-DSRD-1404-CPW032 | JOSHI ROAD KIOSK:K | TG-CPW032A-1 | 19506293 | 990 | 320 | 245 | 0.98 | 870 | 287 | 1191 | 257 | 1079 | 326 | 1377 | 261 | 2019-06-03 | 216.3 | 8.6 | 1518 | B | 105 | 94 | 101 | 11 | 40.1 | 0.8 | 34.1 | 24.9 |  | 1.3 |  |  | 36.3 | 136.58 | 136.58 | 60 | 609.44 | 572.16 | 635.44 | 636.44 | 72.3 | 9 | 28.3 | 23 | 1 |  | 3 |  | 719.44 | 0.16 | 0.64 | 0.88
2 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW035 | 1S-DL-YP-CTC-DSRD-1404-CPW035 | AJMAL KHAN KIOSK | TG-CPW035A-2 | 19505173 | 400 | 120 | 241 | 0.96 | 314 | 155 | 685 | 80 | 354 | 78 | 342 | 337 | 2019-06-03 14:30 | 85.4 | 14 | 685 | R | 121 | 89 | 89 | 32 | 0.1 | 0.1 | 33.1 | 66.7 | 9 | 180 | 69.3 | 25 | 400.57 | 291.57 | 291.57 | 426.57 | 204 | 224.26 | 208.56 | 244.26 | 76.56 |  |  |  | 5.3 |  |  |  | 696.23 | 23.37 | 0.48 | 0.78
3 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW037 | 1S-DL-YP-CTC-DSRD-1404-CPW037 | 53 BLOCK RAMJAS ROAD:K | TG-CPW037A-1 | 19500315 | 990 | 320 | 244 | 0.97 | 923 | 248 | 1003 | 268 | 1103 | 407 | 1664 | 617 | 2019-06-03 02:00 | 242.9 | 67.7 | 1703 | B | 97 | 97 | 106 | 9 | 32.3 | 11.8 | 49.3 | 6.6 | 0.3 |  |  |  | 137.16 | 130.19 | 130.19 | 91.46 | 566.43 | 575.17 | 545.59 | 610.5 | 7 | 5.53 | 56.3 | 8.53 |  |  | 11.53 |  | 711.29 | 8.31 | 0.57 | 0.93
4 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW002 | 1S-DL-YP-CTC-DSRD-1401-KKW002 | MASJID WALA K. BAGH.:PL | TG-KKW002A-1 | 19506653 | 990 | 320 | 246 | 0.97 | 995 | 328 | 1340 | 318 | 1305 | 349 | 1433 | 114 | 2019-06-15 16:00 | 266.6 | 22.7 | 1894 | B | 107 | 91 | 102 | 16 | 0.3 |  | 0.2 | 99.5 | 39 | 248.59 | 140.54 | 110.59 | 399.2 | 200.21 | 200.21 | 335.21 | 121.03 | 135.55 | 90.45 | 110.15 | 133.02 | 109.1 | 142.2 | 137.2 | 2 |  | 15 | 0.3 | 694.25 | 25.35 | 0.43 | 1.01
5 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW003 | 1S-DL-YP-CTC-DSRD-1401-KKW003 | ELAHI BUX:PL | TG-KKW003A-1 | 19503286 | 990 | 320 | 245 | 0.96 | 831 | 271 | 1169 | 287 | 1235 | 273 | 1177 | 62 | 2019-06-29 15:30 | 206.8 | 38.3 | 1275 | Y | 94 | 108 | 98 | 14 |  |  |  | 100 | 2.41 | 0.41 | 4.11 | 0.41 | 233.17 | 173.42 | 173.42 | 221.17 | 162.06 | 190.23 | 171.43 | 171.36 | 2.3 | 35.48 | 8.23 | 7 |  |  |  |  | 400.34 | 31.26 | 0.54 | 0.84
6 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW004 | 1S-DL-YP-CTC-DSRD-1401-KKW004 | BIRLA FLATS K. BAGH:PL | TG-KKW004A-2 | 19500429 | 990 | 320 | 245 | 0.97 | 838 | 247 | 1028 | 296 | 1234 | 294 | 1218 | 199 | 2019-06-15 15:30 | 203.9 | 14.7 | 1359 | B | 82 | 102 | 115 | 33 |  |  | 0.1 | 99.9 | 253.24 | 84.3 | 30.3 | 90.3 | 233.05 | 382.29 | 382.29 | 375.59 | 230.5 | 194.2 | 142.11 | 226.5 |  | 56 | 130.46 | 24 |  |  |  |  | 717.19 | 2.41 | 0.47 | 0.85
7 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW004 | 1S-DL-YP-CTC-DSRD-1401-KKW004 | BIRLA FLATS K. BAGH:PL | TG-KKW004A-1 | 19504500 | 990 | 320 | 239 | 0.97 | 842 | 238 | 1027 | 282 | 1225 | 323 | 1404 | 326 | 2019-06-29 16:30 | 185.5 | 7.4 | 1404 | B | 88 | 94 | 118 | 30 |  |  | 1.3 | 98.7 | 17 | 30.3 | 0.3 | 1.3 | 433.25 | 407.55 | 407.55 | 405.37 | 266.25 | 261.55 | 483.24 | 301.43 | 0.3 | 17 | 48 | 8.3 |  |  |  |  | 717.2 | 2.4 | 0.52 | 0.85
8 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW010 | 1S-DL-YP-CTC-DSRD-1401-KKW010 | POLICE QTR. K. BAGH:PL | TG-KKW010A-1 | 19500312 | 990 | 320 | 240 | 0.97 | 743 | 216 | 941 | 244 | 1065 | 283 | 1226 | 248 | 2019-06-11 16:30 | 196.5 | -14 | 1247 | B | 92 | 97 | 111 | 19 |  | 0.1 | 29.8 | 70.1 | 426.17 | 418.47 | 416.47 | 419.47 | 66 | 66.3 | 66.3 | 61 | 225.42 | 232.42 | 209.12 | 237.12 |  |  | 34 | [5 empty] | 717.59 | 2.01 | 0.37 | 0.75
9 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW013 | 1S-DL-YP-CTC-DSRD-1401-KKW013 | PO NO. 1 K. BAGH:PL | TG-KKW013A-2 | 19505447 | 990 | 320 | 248 | 0.97 | 817 | 258 | 1091 | 300 | 1278 | 259 | 1089 | 188 | 2019-06-12 14:00 | 228.8 | -1 | 1420 | Y | 109 | 100 | 91 | 18 | 0.3 | 0.1 | 10.7 | 88.8 | 401.59 | 414.29 | 436.29 | 416.59 | 86.11 | 75.41 | 75.41 | 72.41 | 180.01 | 195.17 | 212.17 | 207.47 | 34.11 | 16.25 | 0.25 | 4.55 |  | 0.3 |  |  | 702.22 | 17.38 | 0.36 | 0.83
10 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW017 | 1S-DL-YP-CTC-DSRD-1401-KKW017 | PO NO. 5 K. BAGH:PG | TG-KKW017A-1 | 19503298 | 990 | 320 | 240 | 0.99 | 888 | 310 | 1352 | 301 | 1308 | 276 | 1196 | 139 | 2019-06-29 13:00 | 111.1 | 1.5 | 1465 | R | 107 | 99 | 94 | 13 |  |  | 13.1 | 86.9 | 433.22 | 434.52 | 434.22 | 435.22 | 30 | 31 | 31 | 30.3 | 114.57 | 193.57 | 214.57 | 170.27 | 140.3 | 59 | 29 | 82.3 |  |  |  |  | 718.49 | 1.11 | 0.34 | 0.9
11 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW018 | 1S-DL-YP-CTC-DSRD-1401-KKW018 | H S ROAD BASEMENT:ID | TG-KKW018A-2 | 19500417 | 990 | 320 | 249 | 0.98 | 808 | 279 | 1105 | 260 | 1016 | 269 | 1063 | 77 | 2019-06-30 14:30 | 171.5 | 2.9 | 1256 | R | 101 | 104 | 95 | 9 | 0.1 | 1.3 | 41.7 | 56.9 | 433.46 | 431.16 | 434.16 | 433.46 | 39.24 | 39.24 | 39.24 | 36.54 | 179.45 | 245.12 | 242.15 | 243.12 | 65.27 | 2.3 | 6 | 4.3 |  |  |  |  | 718.22 | 1.38 | 0.35 | 0.82
12 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN030 | 1S-DL-YP-CTC-DSRD-1403-RJN030 | SP.MUKERJI MKT. FAIZ RD. P/M NO. 2:PL | TG-RJN030A-2 | 19505972 | 400 | 120 | 243 | 0.98 | 393 | 76 | 311 | 112 | 458 | 206 | 881 | 513 | 2019-06-02 02:00 | 108.8 | 8 | 888 | B | 89 | 97 | 115 | 26 | 2.5 | 1.1 | 48.1 | 48.3 |  | 1.3 | 1 | 1 | 207.07 | 102.59 | 102.59 | 49.57 | 483.48 | 571.15 | 603.59 | 634 | 23.26 | 27.37 | 70.22 | 29.24 |  | 11 | 15.3 |  | 714.21 | 5.39 | 0.57 | 0.98
13 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN041 | 1S-DL-YP-CTC-DSRD-1403-RJN041 | JHANDENWALAN NO. 1:ID | TG-RJN041A-1 | 19500386 | 990 | 320 | 239 | 0.98 | 812 | 244 | 1049 | 250 | 1063 | 318 | 1367 | 311 | 2019-06-14 13:00 | 176.6 | -10.3 | 1447 | B | 90 | 95 | 115 | 25 |  |  | 26.9 | 73.1 | 333.45 | 367.45 | 325.15 | 343.15 | 168.3 | 117 | 117 | 135.3 | 214.12 | 231.12 | 190.01 | 235.42 |  | 0.3 | 66.12 | 2 |  |  |  |  | 716.27 | 3.33 | 0.4 | 0.82
14 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW007 | 1S-DL-YP-CTC-DSRD-1401-KKW007 | SHASTRI PARK (INDOOR):ID | TG-KKW007A-1 | 19503317 | 990 | 320 | 243 | 0.97 | 825 | 239 | 1019 | 300 | 1284 | 286 | 1216 | 239 | 2019-06-14 13:30 | 223 | 12.5 | 1325 | Y | 90 | 104 | 106 | 16 |  |  | 0.8 | 99.2 | 337 | 325 | 295.3 | 323.3 | 159.3 | 101.3 | 101.3 | 129.3 | 223.3 | 232 | 222.3 | 242 |  | 61.3 | 65 | 25 |  |  |  |  | 720 | 0 | 0.43 | 0.83
15 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW008 | 1S-DL-YP-CTC-DSRD-1401-KKW008 | JESSA RAM HOSPITAL PACKAGE S/STN | TG-KKW008A-3 | 19505210 | 630 | 200 | 245 | 0.96 | 731 | 255 | 1060 | 235 | 987 | 241 | 1015 | 64 | 2019-06-08 17:30 | 180.6 | 42.8 | 1197 | Y | 102 | 95 | 103 | 8 | 0.3 | 0.1 | 10.3 | 89.4 |  |  |  |  | 222 | 320 | 320 | 271 | 254 | 165.3 | 277 | 203 | 208.3 | 207.3 | 199 | 221 | 12 | 3.3 | 21.3 | 1.3 | 696.3 | 23.3 | 0.51 | 1.16
16 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW020 | 1S-DL-YP-CTC-DSRD-1401-KKW020 | 39, BEEDEN PURA (W):PL | TG-KKW020A-2 | 19505869 | 630 | 200 | 245 | 0.96 | 513 | 158 | 678 | 183 | 782 | 172 | 734 | 90 | 2019-06-29 15:30 | 144 | 27.2 | 1012 | R | 87 | 111 | 102 | 24 | 0.2 | 0.1 | 0.3 | 99.5 | 226.01 | 8.01 | 28.01 | 30.31 | 239.3 | 428.16 | 428.16 | 420.46 | 239.43 | 226.57 | 244.27 | 252.27 |  | 42.3 | 9.3 | 2 | 0.3 |  |  |  | 705.44 | 14.16 | 0.49 | 0.81
17 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW025 | 1S-DL-YP-CTC-DSRD-1401-KKW025 | 8 C WEA KAROL BAGH JASSA RAM | TG-KKW025A-1 | 19506095 | 990 | 320 | 245 | 0.98 | 1011 | 346 | 1482 | 309 | 1320 | 356 | 1521 | 185 | 2019-06-11 14:00 | 234.9 | -41.3 | 1521 | B | 101 | 97 | 102 | 5 | 0.3 |  | 0.8 | 98.9 | 64.29 | 62.33 | 43.29 | 49.59 | 236.48 | 250.44 | 250.44 | 242.48 | 306.53 | 321.49 | 341.17 | 320.05 | 91.03 | 71.33 | 92.43 | 91.47 | 7.26 |  | 4.52 | 2 | 706.39 | 13.21 | 0.49 | 1.02
18 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW025 | 1S-DL-YP-CTC-DSRD-1401-KKW025 | 8 C WEA KAROL BAGH JASSA RAM | TG-KKW025A-2 | 19506378 | 400 | 120 | 240 | 0.97 | 404 | 131 | 553 | 145 | 618 | 128 | 536 | 75 | 2019-06-24 16:00 | 107 | 3.5 | 712 | Y | 89 | 102 | 109 | 20 | 0.4 | 1.4 | 59.4 | 38.9 | 195.04 | 146 | 43.3 | 160 | 131.55 | 126.05 | 126.05 | 113.05 | 326.31 | 357.57 | 363.01 | 358.57 | 53.26 | 69.24 | 71.28 | 73.24 |  | 7.3 | 12.56 | 1.3 | 706.56 | 13.04 | 0.45 | 1.01
19 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW028 | 1S-DL-YP-CTC-DSRD-1401-KKW028 | H.S.RD. KHATTAWAL K. BAGH:PL | TG-KKW028A-1 | 19505272 | 990 | 320 | 237 | 0.96 | 959 | 287 | 1205 | 390 | 1653 | 282 | 1188 | 457 | 2019-06-01 | 264.6 | 97.3 | 1653 | Y | 103 | 100 | 97 | 6 | 51.2 | 2.7 | 20.8 | 25.3 |  |  |  |  | 6.3 | 8 | 8 | 6.3 | 538.36 | 509.36 | 584.36 | 552.06 | 144.3 | 175 | 102.3 | 136.3 | 5.3 | 2.3 | 0.3 |  | 695.06 | 24.54 | 0.71 | 0.97
20 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW028 | 1S-DL-YP-CTC-DSRD-1401-KKW028 | H.S.RD. KHATTAWAL K. BAGH:PL | TG-KKW028A-2 | 19505496 | 990 | 320 | 248 | 0.96 | 914 | 296 | 1235 | 352 | 1473 | 265 | 1109 | 320 | 2019-06-29 16:00 | 271 | 80.6 | 1534 | R | 100 | 109 | 91 | 18 | 3.8 | 0.1 | 2.4 | 93.7 |  |  |  |  | 35 | 15 | 15 | 29 | 601.05 | 581.35 | 644.16 | 624.35 | 81 | 116.3 | 5.3 | 65 | 1.3 | 5.3 |  |  | 718.35 | 1.25 | 0.67 | 0.92
21 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW029 | 1S-DL-YP-CTC-DSRD-1401-KKW029 | PYAUWALA H. S. ROAD:PM | TG-KKW029A-1 | 19505483 | 400 | 120 | 248 | 0.95 | 301 | 92 | 375 | 115 | 469 | 93 | 377 | 93 | 2019-06-01 22:30 | 106.9 | 17.3 | 509 | Y | 80 | 115 | 104 | 35 |  | 0.1 | 25.8 | 74.2 | 121 |  |  |  | 81.53 | 15 | 15 | 36 | 502.05 | 638.28 | 651.28 | 668.58 |  | 51.3 | 8 | [5 empty] | 704.58 | 15.02 | 0.72 | 0.75
22 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW031 | 1S-DL-YP-CTC-DSRD-1401-KKW031 | 13 BLK WEA K. BAGH:PACKAGE S/STN | TG-KKW031A-2 | 19504549 | 990 | 320 | 246 | 0.98 | 862 | 287 | 1217 | 316 | 1331 | 259 | 1093 | 206 | 2019-06-26 14:00 | 148.7 | -4.4 | 1331 | Y | 100 | 107 | 93 | 14 |  |  | 3.8 | 96.2 | 425.24 | 411.24 | 422.24 | 420.54 | 43 | 54 | 54 | 48.3 | 199.54 | 112.52 | 245.44 | 198.24 | 50.5 | 140.52 | 3 | 51.2 |  |  |  |  | 719.08 | 0.52 | 0.37 | 0.87
23 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW032 | 1S-DL-YP-CTC-DSRD-1401-KKW032 | 5WEA K BAGH KIOSK:PACKAGE S/STN | TG-KKW032A-2 | 19504614 | 990 | 320 | 236 | 0.97 | 893 | 279 | 1135 | 314 | 1293 | 300 | 1228 | 137 | 2019-06-14 13:00 | 225.2 | 19.1 | 1384 | Y | 94 | 112 | 94 | 18 |  | 0.6 | 25.1 | 74.3 | 133.56 | 43 | 110 | 79.3 | 278.3 | 331.56 | 331.56 | 321.56 | 305.35 | 263.35 | 298.35 | 311.05 | 1 | 80.3 | 2.3 | 6.3 |  |  |  |  | 719.01 | 0.59 | 0.47 | 0.9
24 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW037 | 1S-DL-YP-CTC-DSRD-1401-KKW037 | 26 BEEDEN PURA P.L RD.:PL | TG-KKW037A-1 | 19504238 | 990 | 320 | 239 | 0.97 | 967 | 356 | 1465 | 272 | 1155 | 339 | 1443 | 300 | 2019-06-12 16:00 | 231.1 | 68.4 | 1542 | B | 107 | 90 | 103 | 17 | 75.8 | 23.9 | 0.2 | 0.1 |  |  |  |  | 21 | 80 | 80 | 36.3 | 546.27 | 637.19 | 563.31 | 605.19 | 146.52 | 1.54 | 123.42 | 77.24 | 4.54 |  | 4 |  | 719.13 | 0.47 | 0.63 | 0.98
25 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW039 | 1S-DL-YP-CTC-DSRD-1401-KKW039 | 40 REGER PURA P/M:PL | TG-KKW039A-1 | 19506093 | 990 | 320 | 238 | 0.96 | 950 | 295 | 1301 | 231 | 968 | 423 | 1966 | 880 | 2019-06-06 02:30 | 302.4 | 104 | 1966 | B | 110 | 99 | 91 | 19 | 0.2 | 0.1 |  | 99.7 |  |  |  |  | 6.3 | 19 | 19 | 13.3 | 497.27 | 613.18 | 615.48 | 599.18 | 178.51 | 61.3 | 38.3 | 81 | 11 |  | 0.3 |  | 693.48 | 26.12 | 0.67 | 0.96
26 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW046 | 1S-DL-YP-CTC-DSRD-1401-KKW046 | PUSA RD. CAMP CENTRE:ID | TG-KKW046A-1 | 19503332 | 990 | 320 | 242 | 0.96 | 875 | 267 | 1101 | 289 | 1190 | 319 | 1330 | 200 | 2019-06-30 00:30 | 199.5 | 55.9 | 1350 | Y | 88 | 101 | 111 | 23 |  |  | 26.2 | 73.8 | 0.3 | 0.3 |  |  | 171.29 | 88.25 | 88.25 | 69 | 521.33 | 555.07 | 625.02 | 605.32 | 2 | 51.3 | 54.3 | 21 |  |  |  |  | 695.32 | 0.28 | 0.62 | 0.88
27 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW046 | 1S-DL-YP-CTC-DSRD-1401-KKW046 | PUSA RD. CAMP CENTRE:ID | TG-KKW046A-4 | 19505842 | 990 | 320 | 243 | 0.98 | 1023 | 353 | 1495 | 327 | 1380 | 343 | 1445 | 100 | 2019-06-30 15:00 | 327 | 32 | 1781 | R | 100 | 101 | 99 | 2 | 0.4 |  | 0.4 | 99.2 |  |  |  |  | 21.37 | 10.07 | 10.07 | 17.37 | 550 | 598.3 | 531.54 | 564.3 | 131 | 98.3 | 135.06 | 124 | 5 | 0.3 | 8 | 1.3 | 707.37 | 12.23 | 0.63 | 1.03
28 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW059 | 1S-DL-YP-CTC-DSRD-1401-KKW059 | BAPU BHAWAN S/ST.:PL | TG-KKW059A-1 | 19504541 | 990 | 320 | 233 | 0.97 | 852 | 306 | 1337 | 279 | 1206 | 267 | 1123 | 187 | 2019-06-30 00:30 | 172.2 | 77.3 | 1337 | R | 102 | 96 | 102 | 6 | 99.8 | 0.2 | [6 empty] | 40 | 58 | 58 | 42 | 668.31 | 656.31 | 652.31 | 670.01 | 10.3 | 4.3 | 30.3 | 7 |  |  |  |  | 719.01 | 0.59 | 0.65 | 0.86
29 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW067 | 1S-DL-YP-CTC-DSRD-1401-KKW067 | 5 BLOCK WEA KAROL BAGH KIOSK | TG-KKW067A-1 | 19503314 | 990 | 320 | 245 | 0.97 | 929 | 287 | 1250 | 289 | 1255 | 353 | 1534 | 281 | 2019-06-11 15:00 | 212 | -31.6 | 1554 | B | 89 | 97 | 114 | 25 |  |  | 3.2 | 96.8 | 253.3 | 251.3 | 246 | 249.3 | 42.3 | 43 | 43 | 39 | 173.35 | 115.05 | 73.35 | 107.05 | 22 | 82 | 122 | 96 |  |  | 22 |  | 695.35 | 0.25 | 0.39 | 0.94
30 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW067 | 1S-DL-YP-CTC-DSRD-1401-KKW067 | 5 BLOCK WEA KAROL BAGH KIOSK | TG-KKW067A-2 | 19505495 | 990 | 320 | 245 | 0.97 | 1094 | 527 | 2312 | 304 | 1252 | 264 | 1050 | 1173 | 2019-06-12 19:00 | 340.5 | 77.1 | 2312 | R | 100 | 101 | 98 | 3 | 0.2 |  | 2.1 | 97.7 |  |  |  |  | 124 | 114.3 | 114.3 | 93.3 | 448.36 | 464.36 | 578.36 | 501.36 | 143 | 132.3 | 67.3 | 124 | 4 | 8 |  | 0.3 | 719.36 | 0.24 | 0.52 | 1.11
31 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | EPN003 | 1S-DL-YP-CTC-DSRD-1402-EPN003 | 21 BLK. O. R. NAGAR:K | TG-EPN003A-1 | 19503328 | 990 | 320 | 236 | 0.97 | 923 | 295 | 1240 | 318 | 1335 | 310 | 1295 | 83 | 2019-06-30 01:00 | 178.8 | 51.5 | 1383 | Y | 95 | 102 | 103 | 8 |  |  | 9.2 | 90.8 |  |  |  |  | 134.3 | 87.3 | 87.3 | 84.3 | 561.3 | 590 | 598.3 | 597.3 | 24 | 42.3 | 53.3 | 38 |  |  |  |  | 720 | 0 | 0.59 | 0.93
32 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | EPN003 | 1S-DL-YP-CTC-DSRD-1402-EPN003 | 21 BLK. O. R. NAGAR:K | TG-EPN003A-3 | 19504344 | 990 | 320 | 239 | 0.98 | 913 | 327 | 1493 | 306 | 1402 | 280 | 1270 | 194 | 2019-06-10 13:00 | 212 | 30.2 | 1493 | R | 114 | 103 | 84 | 30 |  | 0.1 | 3.1 | 96.8 | 1.15 | 1.15 | 1.15 | 1.15 | 30 | 62 | 62 | 69.3 | 586.11 | 629.51 | 484.4 | 622.51 | 100.05 | 25.25 | 2 | 24.55 | 1 |  |  |  | 718.31 | 1.29 | 0.6 | 0.92
33 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN006 | 1S-DL-YP-CTC-DSRD-1403-RJN006 | TIKONA PARK BAZAR MARG:PL | TG-RJN006A-1 | 19503361 | 990 | 320 | 242 | 0.97 | 917 | 365 | 1577 | 256 | 1089 | 296 | 1261 | 429 | 2019-06-30 23:30 | 165.6 | 47.8 | 1577 | R | 96 | 97 | 108 | 12 |  |  | 11.9 | 88.1 |  |  |  |  | 166.05 | 111.25 | 111.25 | 100.44 | 521.52 | 590.56 | 557.59 | 585.37 | 29.24 | 16 | 75.54 | 32 | 1 |  | 9.3 |  | 718.21 | 1.39 | 0.59 | 0.93
34 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN011 | 1S-DL-YP-CTC-DSRD-1403-RJN011 | SALWAN SCHOOL OLD:PL | TG-RJN011A-1 | 19506581 | 990 | 320 | 244 | 0.95 | 982 | 321 | 1367 | 320 | 1357 | 341 | 1445 | 83 | 2019-06-01 12:30 | 291.8 | 39 | 1445 | B | 96 | 105 | 99 | 9 | 0.1 |  | 1.4 | 98.5 | 133.3 | 22.3 | 92 | 84 | 268 | 351.3 | 351.3 | 299.3 | 236.17 | 218.3 | 257.47 | 234.17 | 66.21 | 111.38 | 66.3 | 86.21 |  |  | 0.51 |  | 704.08 | 15.52 | 0.46 | 0.99
35 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN012 | 1S-DL-YP-CTC-DSRD-1403-RJN012 | SALWAN SCHOOL NEW:K | TG-RJN012A-1 | 19503377 | 990 | 320 | 236 | 0.98 | 931 | 273 | 1149 | 337 | 1426 | 322 | 1370 | 253 | 2019-06-30 | 167.1 | 23.6 | 1587 | Y | 95 | 109 | 95 | 14 |  |  | 1.3 | 98.7 | 1 | 0.3 | 2.3 | 0.3 | 232.33 | 119.46 | 119.46 | 193.46 | 474.28 | 551.45 | 440.15 | 505.45 | 8 | 42 | 15 | 16 |  | 2 |  |  | 716.01 | 3.59 | 0.52 | 0.94
36 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN019 | 1S-DL-YP-CTC-DSRD-1403-RJN019 | SRD BUILDING OFFICE:ID | TG-RJN019A-1 | 19503282 | 990 | 320 | 238 | 0.97 | 872 | 310 | 1318 | 247 | 1046 | 314 | 1340 | 284 | 2019-06-29 23:30 | 182.5 | 61.8 | 1432 | B | 101 | 85 | 114 | 29 |  |  | 26.3 | 73.7 |  |  |  |  | 71.3 | 185 | 185 | 61 | 621.25 | 533.55 | 615.55 | 646.55 | 26 |  | 84 | 11 |  |  | 1.3 |  | 718.55 | 1.05 | 0.63 | 0.88
37 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN023 | 1S-DL-YP-CTC-DSRD-1403-RJN023 | NPL MULTI STORIES:ID | TG-RJN023A-1 | 19503308 | 630 | 200 | 241 | 0.98 | 508 | 193 | 836 | 141 | 604 | 173 | 738 | 201 | 2019-06-11 22:30 | 65.3 | 12.4 | 899 | R | 115 | 87 | 97 | 28 |  | 1 | 52.6 | 46.4 | 3.3 | 17 | 12 | 6.3 | 224.41 | 406.11 | 406.11 | 327.41 | 435.28 | 296.28 | 372.28 | 383.58 | 56 |  | 4 | 1.3 |  |  |  |  | 719.39 | 0.21 | 0.55 | 0.81
38 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN024 | 1S-DL-YP-CTC-DSRD-1403-RJN024 | DDA SHANKAR RD.:ID | TG-RJN024A-2 | 19500408 | 990 | 320 | 238 | 0.98 | 700 | 177 | 750 | 354 | 1506 | 169 | 724 | 770 | 2019-06-12 15:00 | 199.5 | 47.8 | 1555 | Y | 80 | 146 | 74 | 72 |  |  | 3 | 97 | 0.3 |  | 1.3 |  | 335.57 | 3.3 | 3.3 | 86.3 | 382.59 | 450.57 | 262.37 | 632.56 |  | 236.59 |  |  |  | 28 |  |  | 719.26 | 0.34 | 0.72 | 0.71
39 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN081 | 1S-DL-YP-CTC-DSRD-1403-RJN081 | HANDIWALA ORN : K | TG-RJN081A-1 | 19503379 | 990 | 320 | 241 | 0.97 | 1021 | 350 | 1459 | 355 | 1475 | 316 | 1322 | 147 | 2019-06-03 02:00 | 197.2 | -43.4 | 1520 | Y | 101 | 99 | 101 | 2 |  |  | 5.8 | 94.2 | 2.3 | 1.3 | 1.3 | 1.3 | 101.32 | 96.25 | 96.25 | 73.35 | 547.56 | 569.08 | 625.5 | 594.53 | 57.44 | 43.09 | 27.57 | 41.57 | 2.4 | 2.1 |  | 0.27 | 712.22 | 7.38 | 0.54 | 1.03
40 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN081 | 1S-DL-YP-CTC-DSRD-1403-RJN081 | HANDIWALA ORN : K | TG-RJN081A-2 | 19504310 | 630 | 200 | 241 | 0.97 | 595 | 187 | 801 | 172 | 735 | 236 | 1022 | 260 | 2019-06-02 00:30 | 130.6 | 41.4 | 1022 | B | 83 | 105 | 112 | 29 |  | 0.6 | 62.1 | 37.3 | 0.3 |  |  |  | 170.48 | 41.28 | 41.28 | 55.58 | 544.02 | 571.22 | 542.22 | 611.52 | 3 | 103.3 | 141.3 | 50.3 |  | 2 | 7 |  | 718.2 | 1.4 | 0.64 | 0.94

## Loading Condition > 100%
MIS Report of Distribution Transformer - Jun19
Jun19 1140 SHANKAR ROAD (Loading Condition > 100% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW001 | 1S-DL-YP-CTC-DSRD-1401-KKW001 | NANAK HOTEL K. BAGH:PL | TG-KKW001A-1 | 19503278 | 990 | 320 | 239 | 0.98 | 1029 | 380 | 1675 | 319 | 1409 | 330 | 1452 | 248 | 2019-06-04 16:00 | 170 | 0.7 | 1725 | R | 117 | 90 | 93 | 27 |  |  | 2 | 98 | 142.3 | 372 | 272.52 | 311 | 282.23 | 65.23 | 65.23 | 121.23 | 98.3 | 160 | 201.57 | 142 | 96.27 | 96.57 | 45.3 | 114.57 | 74.3 |  | 0.3 | 5 | 694.2 | 1.4 | 0.38 | 1.04
2 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | KKW018 | 1S-DL-YP-CTC-DSRD-1401-KKW018 | H S ROAD BASEMENT:ID | TG-KKW018A-3 | 19500418 | 990 | 320 | 249 | 0.97 | 988 | 322 | 1341 | 294 | 1221 | 372 | 1543 | 282 | 2019-06-15 15:30 | 239.9 | -6.6 | 1559 | B | 98 | 92 | 110 | 18 |  |  | 1.9 | 98.1 | 432.24 | 436.24 | 428.24 | 433.24 | 39.3 | 35 | 35 | 35.3 | 112 | 170.3 | 52.3 | 93.3 | 134.3 | 77.3 | 131.3 | 157 | 1 |  | 76 |  | 719.24 | 0.36 | 0.34 | 1
3 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW046 | 1S-DL-YP-CTC-DSRD-1401-KKW046 | PUSA RD. CAMP CENTRE:ID | TG-KKW046A-2 | 19503315 | 990 | 320 | 235 | 0.98 | 957 | 279 | 1198 | 338 | 1472 | 340 | 1457 | 267 | 2019-06-11 23:30 | 152.4 | 63.3 | 1747 | B | 85 | 102 | 113 | 28 |  | 1.4 | 43.7 | 54.8 |  |  |  |  | 101.33 | 22.04 | 22.04 | 21.04 | 573.17 | 534.55 | 442 | 554.16 | 36.19 | 152.4 | 206.09 | 135.49 |  | 1.3 | 54 |  | 711.09 | 8.51 | 0.66 | 0.97
4 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW049 | 1S-DL-YP-CTC-DSRD-1401-KKW049 | R. K. DASS-1 K. BAGH:K | TG-KKW049A-1 | 19504998 | 990 | 320 | 253 | 0.95 | 1175 | 393 | 1574 | 393 | 1574 | 389 | 1535 | 39 | 2019-06-30 00:30 | 380.5 | 131.7 | 1654 | R | 106 | 98 | 96 | 10 |  | 2.5 | 64.7 | 32.8 | [5 empty] | 0.3 | 0.3 |  | 381 | 458.3 | 471 | 441.3 | 240.3 | 217 | 183 | 213.3 | 98.3 | 44 | 65 | 65 | 720 | 0 | 0.65 | 1.19
5 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN006 | 1S-DL-YP-CTC-DSRD-1403-RJN006 | TIKONA PARK BAZAR MARG:PL | TG-RJN006A-3 | 19505136 | 630 | 200 | 243 | 0.97 | 594 | 106 | 435 | 288 | 1255 | 199 | 862 | 710 | 2019-06-06 03:00 | 222 | 21 | 1255 | Y | 92 | 93 | 115 | 23 | 0.9 | 50.8 | 15.2 | 33.2 | 0.49 | 3.12 | 1.12 | 1.12 | 202.51 | 218.57 | 218.57 | 154.57 | 486.41 | 463.42 | 531.36 | 515.48 | 4 | 8.3 | 50.24 | 22.54 | 0.3 | 0.3 | 29.3 |  | 694.51 | 25.09 | 0.55 | 0.94
6 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN007 | 1S-DL-YP-CTC-DSRD-1403-RJN007 | BAZAR MARG (K):K | TG-RJN007A-2 | 19505084 | 630 | 200 | 236 | 0.97 | 702 | 253 | 1099 | 208 | 889 | 241 | 1032 | 186 | 2019-06-30 00:30 | 129.3 | 38.6 | 1224 | R | 111 | 88 | 101 | 23 |  | 0.3 | 41 | 58.7 |  |  |  |  | 23.58 | 106.28 | 106.28 | 36.28 | 471.3 | 554 | 528.3 | 541.3 | 135 | 34.3 | 108 | 105 | 65.3 | 1 | 15.3 | 13 | 695.58 | 0.02 | 0.57 | 1.11
7 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN013 | 1S-DL-YP-CTC-DSRD-1403-RJN013 | SETHI PETROL PUMP:ID | TG-RJN013A-2 | 19504685 | 990 | 320 | 242 | 0.97 | 1161 | 355 | 1483 | 309 | 1276 | 497 | 2094 | 736 | 2019-06-30 01:00 | 219.3 | 79.5 | 2098 | B | 96 | 90 | 114 | 24 |  | 0.1 | 32.3 | 67.6 |  |  |  |  | 40.28 | 43.58 | 43.58 | 27.28 | 550.5 | 609.49 | 439.08 | 547.5 | 115.19 | 61.59 | 183.51 | 122.29 | 9.09 |  | 79.19 | 17.59 | 715.46 | 4.14 | 0.56 | 1.17
8 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN081 | 1S-DL-YP-CTC-DSRD-1403-RJN081 | HANDIWALA ORN : K | TG-RJN081A-3 | 19505206 | 630 | 200 | 241 | 0.97 | 736 | 301 | 1363 | 106 | 431 | 329 | 1537 | 1030 | 2019-06-06 03:00 | 276.2 | 32.8 | 1537 | B | 118 | 69 | 113 | 49 | 0.4 | 0.1 | 36.6 | 63 |  | 19.28 |  |  | 58.07 | 397.21 | 397.21 | 125.13 | 475.42 | 277.05 | 536.55 | 500.36 | 100.3 |  | 94.22 | 67.52 | 59.35 |  | 10.13 | 0.13 | 693.54 | 26.06 | 0.47 | 1.17