## Underload DTs
MIS Report of Distribution Transformer - Jun19
Jun19 1140 SHANKAR ROAD (Underload DTs)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | CPW047 | 1S-DL-YP-CTC-DSRD-1404-CPW047 | CPWD HOSTEL:ID | TG-CPW047A-1 | 19500420 | 400 | 120 | 247 | 0.98 | 43 | 9 | 38 | 16 | 68 | 18 | 74 | 33 | 2019-06-11 23:00 | 9.7 | 0.3 | 91 | Y | 54 | 150 | 96 | 96 |  |  | 7.6 | 92.4 | 720 | 720 | 720 | 720 | [16 empty] | 720 | 0 | 0.44 | 0.11
2 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN033 | 1S-DL-YP-CTC-DSRD-1403-RJN033 | F. FACTORY G BLOCK:ID | TG-RJN033A-1 | 19500692 | 990 | 300 | 246 | 0.95 | 58 | 12 | 47 | 20 | 78 | 26 | 104 | 50 | 2019-06-17 14:30 | 23.5 | 0.7 | 115 | B | 21 | 106 | 173 | 152 |  |  | 1.6 | 98.4 | 718.21 | 718.21 | 718.21 | 718.21 | [16 empty] | 718.21 | 1.39 | 0.18 | 0.06
3 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN034 | 1S-DL-YP-CTC-DSRD-1403-RJN034 | F. FACTORY E BLOCK:ID | TG-RJN034A-1 | 19502919 | 990 | 300 | 246 | 0.95 | 14 | 5 | 19 | 5 | 19 | 4 | 16 | 3 | 2019-06-17 16:30 | 0.7 | -0.7 | 22 | Y | 124 | 122 | 54 | 70 |  |  | 2.5 | 97.5 | 718.24 | 718.24 | 718.24 | 718.24 | [16 empty] | 718.24 | 1.36 | 0.23 | 0.01
4 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN034 | 1S-DL-YP-CTC-DSRD-1403-RJN034 | F. FACTORY E BLOCK:ID | TG-RJN034A-2 | 19503587 | 990 | 300 | 247 | 0.93 | 26 | 11 | 47 | 13 | 54 | 1 | 6 | 45 | 2019-06-12 14:00 | 8.3 | 0.7 | 55 | Y | 140 | 129 | 31 | 109 |  |  | 34.6 | 65.4 | 717.54 | 717.54 | 717.54 | 717.54 | [16 empty] | 717.54 | 2.06 | 0.2 | 0.03
5 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN036 | 1S-DL-YP-CTC-DSRD-1403-RJN036 | F. FACTORY A BLOCK:ID | TG-RJN036A-2 | 19503559 | 990 | 300 | 247 | 0.98 | 147 | 47 | 209 | 42 | 186 | 57 | 252 | 59 | 2019-06-11 15:30 | 25.5 | -0.7 | 252 | B | 94 | 88 | 118 | 30 |  |  | 4.9 | 95.1 | 690.27 | 690.27 | 690.27 | 690.27 | [16 empty] | 690.27 | 5.33 | 0.27 | 0.15
6 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | CHHAPARWALAN | 1140 | RJN093 | 1S-DL-YP-CTC-DSRD-1403-RJN093 | Ashoka Pahari | TG-RJN093A-1 | 19506386 | 990 | 300 | 243 | 0.96 | 172 | 53 | 214 | 59 | 251 | 60 | 257 | 40 | 2019-06-13 23:30 | 43.2 | 8.4 | 300 | R | 80 | 98 | 122 | 42 | 100 |  |  |  | 706.41 | 707.11 | 707.11 | 707.11 | 0.3 | [15 empty] | 707.11 | 12.49 | 0.57 | 0.17
7 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | EPN001 | 1S-DL-YP-CTC-DSRD-1402-EPN001 | LINK ROAD PACKAGE S/STN | TG-EPN001A-2 | 19505493 | 990 | 320 | 244 | 0.97 | 163 | 54 | 221 | 60 | 248 | 49 | 200 | 41 | 2019-06-26 11:30 | 49 | 1 | 439 | B | 71 | 111 | 118 | 47 | 0.2 | 0.1 | 8 | 91.8 | 693.29 | 692.19 | 692.29 | 693.29 |  | 1.1 | 1.1 | [13 empty] | 693.29 | 26.31 | 0.37 | 0.16
8 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW005 | 1S-DL-YP-CTC-DSRD-1401-KKW005 | SATBHRAWA :PACKAGE S/STN | TG-KKW005A-1 | 19500011 | 990 | 320 | 250 | 0.96 | 165 | 55 | 219 | 49 | 193 | 60 | 235 | 37 | 2019-06-28 17:00 | 50.8 | 2.2 | 240 | R | 100 | 90 | 111 | 21 |  |  | 8.9 | 91.1 | 718.33 | 718.33 | 718.33 | 718.33 | [16 empty] | 718.33 | 1.27 | 0.46 | 0.17
9 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW008 | 1S-DL-YP-CTC-DSRD-1401-KKW008 | JESSA RAM HOSPITAL PACKAGE S/STN | TG-KKW008A-2 | 19503322 | 990 | 320 | 246 | 0.98 | 156 | 37 | 155 | 53 | 223 | 66 | 276 | 105 | 2019-06-29 16:00 | 25.8 | 2.2 | 279 | B | 67 | 105 | 128 | 61 |  |  | 1.9 | 98.1 | 695.51 | 695.51 | 695.21 | 695.51 | [16 empty] | 695.51 | 0.09 | 0.59 | 0.16
10 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW008 | 1S-DL-YP-CTC-DSRD-1401-KKW008 | JESSA RAM HOSPITAL PACKAGE S/STN | TG-KKW008A-1 | 19503352 | 990 | 320 | 245 | 0.97 | 160 | 78 | 322 | 55 | 227 | 27 | 110 | 184 | 2019-06-14 18:00 | 43.4 | 2.9 | 322 | R | 149 | 107 | 44 | 105 |  |  | 1.4 | 98.6 | 642 | 696 | 696 | 696 | 54 | [15 empty] | 696 | 0 | 0.45 | 0.16
11 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW040 | 1S-DL-YP-CTC-DSRD-1401-KKW040 | KHALSA COLLEGE S/ST:K | TG-KKW040A-2 | 19506710 | 630 | 200 | 244 | 0.95 | 144 | 52 | 226 | 47 | 203 | 45 | 194 | 28 | 2019-06-10 11:30 | 47 | 4.2 | 263 | Y | 154 | 79 | 67 | 87 | 0.3 |  | 0.6 | 99.1 | 631.09 | 666.09 | 700.39 | 683.09 | 75.3 | 40.3 | 40.3 | 23.3 | [12 empty] | 706.39 | 13.21 | 0.34 | 0.23
12 | 2019-06-02 | 2019-06-30 23:30 | SHANKAR ROAD | PUSA ROAD | 1140 | KKW055 | 1S-DL-YP-CTC-DSRD-1401-KKW055 | 7A WEA (MOTHER DAIRY)PACKAGE S/STN | TG-KKW055A-1 | 19503354 | 990 | 320 | 244 | 0.98 | 127 | 52 | 226 | 8 | 33 | 67 | 288 | 231 | 2019-06-06 | 24.3 | 2.9 | 298 | B | 156 | 13 | 130 | 143 |  |  | 54.2 | 45.8 | 695.15 | 695.15 | 690.45 | 695.15 | [16 empty] | 695.15 | 0.45 | 0.59 | 0.13
13 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN012 | 1S-DL-YP-CTC-DSRD-1403-RJN012 | SALWAN SCHOOL NEW:K | TG-RJN012A-2 | 19504309 | 990 | 320 | 238 | 0.97 | 224 | 88 | 360 | 95 | 393 | 41 | 166 | 213 | 2019-06-30 02:00 | 46.4 | 11 | 431 | Y | 113 | 122 | 65 | 57 |  | 0.1 | 15.1 | 84.8 | 674.24 | 590.24 | 718.05 | 713.22 | 43.41 | 127.41 | 127.41 | 4.43 | [12 empty] | 718.05 | 1.55 | 0.57 | 0.23
14 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN017 | 1S-DL-YP-CTC-DSRD-1403-RJN017 | NPL QTR. OUTSIDE P/M:PL | TG-RJN017A-2 | 19504385 | 400 | 120 | 239 | 0.98 | 82 | 25 | 105 | 30 | 126 | 27 | 111 | 18 | 2019-06-11 23:00 | 15.5 | 1.9 | 133 | R | 108 | 102 | 91 | 17 |  |  | 64.8 | 35.2 | 706.03 | 704.03 | 716.33 | 717.33 | 12.3 | 14.3 | 14.3 | 1 | [12 empty] | 718.33 | 1.27 | 0.52 | 0.21
15 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN018 | 1S-DL-YP-CTC-DSRD-1403-RJN018 | NPL COLONY INSIDE:ID | TG-RJN018A-1 | 19503336 | 400 | 120 | 245 | 0.98 | 45 | 13 | 54 | 21 | 85 | 10 | 42 | 39 | 2019-06-29 23:30 | 9.4 | 0.3 | 86 | Y | 87 | 146 | 67 | 79 |  |  | 0.3 | 99.7 | 718.08 | 718.08 | 718.08 | 718.08 | [16 empty] | 718.08 | 1.52 | 0.41 | 0.11
16 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN018 | 1S-DL-YP-CTC-DSRD-1403-RJN018 | NPL COLONY INSIDE:ID | TG-RJN018A-2 | 19503386 | 400 | 120 | 245 | 0.99 | 29 | 10 | 41 | 6 | 24 | 14 | 57 | 28 | 2019-06-14 23:30 | 3.6 | -0.6 | 60 | B | 68 | 92 | 140 | 72 |  |  | 1.5 | 98.5 | 718.13 | 718.13 | 718.13 | 718.13 | [16 empty] | 718.13 | 1.47 | 0.4 | 0.07
17 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN019 | 1S-DL-YP-CTC-DSRD-1403-RJN019 | SRD BUILDING OFFICE:ID | TG-RJN019A-2 | 19503296 | 990 | 320 | 244 | 0.96 | 266 | 97 | 420 | 80 | 345 | 89 | 373 | 65 | 2019-06-12 15:00 | 70.7 | -3.7 | 420 | R | 103 | 97 | 100 | 6 | 17.8 | 82.2 | 0.1 |  | 590.28 | 711.49 | 661.19 | 662.19 | 129.21 | 8 | 8 | 57.3 | [12 empty] | 719.49 | 0.11 | 0.43 | 0.27
18 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN020 | 1S-DL-YP-CTC-DSRD-1403-RJN020 | MANAVSTHALI (K):ID | TG-RJN020A-2 | 19504560 | 990 | 320 | 243 | 0.97 | 197 | 85 | 356 | 46 | 191 | 66 | 277 | 143 | 2019-06-12 15:00 | 54.5 | -5.9 | 382 | R | 128 | 69 | 103 | 59 |  |  | 65.4 | 34.6 | 507.4 | 719.4 | 682.4 | 719.4 | 212 | [15 empty] | 719.4 | 0.2 | 0.71 | 0.2
19 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN070 | 1S-DL-YP-CTC-DSRD-1403-RJN070 | ST LT NO. 1 (BAPU ASHARAM ASHRAM):PM | TG-RJN070A-1 | 19505387 | 100 | 40 | 245 | 0.96 | 28 | 2 | 7 | 21 | 91 | 5 | 22 | 77 | 2019-06-23 16:00 | 13.9 | 0.2 | 91 | Y | 59 | 78 | 163 | 104 | 0.3 | 1.1 | 7 | 91.5 | 716.18 | 680.18 | 683.06 | 713.48 |  | 31 | 31 | 2.3 |  | 5 | [10 empty] | 716.18 | 3.42 | 0.2 | 0.28
20 | 2019-06-01 | 2019-06-30 23:30 | SHANKAR ROAD | R BLOCK NEW RAJENDER NAGAR | 1140 | RJN084 | 1S-DL-YP-CTC-DSRD-1403-RJN084 | GULASHAN JOLLY 7-B PUSHA ROAD:PKG | TG-RJN084A-1 | 19506703 | 990 | 320 | 245 | 0.94 | 208 | 66 | 263 | 76 | 300 | 66 | 263 | 37 | 2019-06-14 15:00 | 204.5 | -12.8 | 303 | Y | 104 | 107 | 88 | 19 |  |  | 1.9 | 98.1 | 703.23 | 698.23 | 705.23 | 704.53 | 3 | 8 | 8 | 1.3 | [12 empty] | 706.23 | 13.37 | 0.35 | 0.21