## Loading Condition > 80%
MIS Report of Distribution Transformer - Jun19
Jun19 1141 PATEL NAGAR (Loading Condition > 80% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | KIKARWALAN | 1141 | PNR003 | 1S-DL-YP-CTC-DPNR-1451-PNR003 | H.S. RD.P/M BAPA NGR:PL | TG-PNR003A-2 | 19504414 | 990 | 320 | 240 | 0.96 | 1042 | 329 | 1372 | 328 | 1367 | 385 | 1630 | 261 | 2019-06-30 | 334.9 | 96.4 | 1630 | B | 96 | 102 | 103 | 7 |  |  | 42.2 | 57.8 |  |  |  |  | 6.3 | 1 | 1 | 3 | 605.42 | 558.33 | 546.44 | 580.44 | 100.3 | 153.53 | 149.1 | 129.04 | 1.14 | 0.3 | 16.02 | 1.08 | 713.56 | 6.04 | 0.65 | 1.05
2 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | KIKARWALAN | 1141 | PNR003 | 1S-DL-YP-CTC-DPNR-1451-PNR003 | H.S. RD.P/M BAPA NGR:PL | TG-PNR003A-1 | 19506516 | 990 | 320 | 241 | 0.96 | 917 | 280 | 1158 | 319 | 1317 | 318 | 1333 | 168 | 2019-06-30 | 290.6 | 92.5 | 1531 | R | 91 | 102 | 107 | 16 | 0.3 |  | 46.3 | 53.5 |  |  |  |  | 11.3 | 8 | 8 | 6.3 | 676.02 | 578.54 | 525.41 | 612.49 | 9.23 | 110.01 | 163.14 | 77.36 |  |  | 3.3 |  | 696.55 | 23.05 | 0.71 | 0.93
3 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | KIKARWALAN | 1141 | PNR005 | 1S-DL-YP-CTC-DPNR-1451-PNR005 | 17 B DEV NGR. K. BAGH:PL | TG-PNR005A-1 | 19504744 | 990 | 320 | 245 | 0.96 | 865 | 266 | 1099 | 326 | 1347 | 273 | 1116 | 240 | 2019-06-29 23:00 | 175.2 | 97.2 | 1347 | Y | 98 | 106 | 95 | 11 |  |  | 4.3 | 95.7 |  |  |  |  | 32 | 21.3 | 21.3 | 25 | 687.03 | 655.33 | 662.04 | 687.03 | 0.3 | 42.3 | 2.3 | 7.3 |  |  |  |  | 719.33 | 0.27 | 0.62 | 0.87
4 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | KIKARWALAN | 1141 | PNR006 | 1S-DL-YP-CTC-DPNR-1451-PNR006 | 11 B DEV NGR. A.S RD.:PL | TG-PNR006A-2 | 19503773 | 990 | 320 | 251 | 0.96 | 885 | 282 | 1143 | 343 | 1391 | 260 | 1041 | 312 | 2019-06-30 00:30 | 297.3 | 80.2 | 1391 | Y | 95 | 115 | 90 | 25 |  | 0.1 | 36.9 | 62.9 |  |  |  |  | 156.21 | 22 | 22 | 81.3 | 550.45 | 600.36 | 511.5 | 609.36 | 12.3 | 93 | 3.3 | 28.3 |  | 4 |  |  | 719.36 | 0.24 | 0.59 | 0.89
5 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | KIKARWALAN | 1141 | PNR007 | 1S-DL-YP-CTC-DPNR-1451-PNR007 | 13-B DEV NAGAR K. BAGH:PL | TG-PNR007A-1 | 19504424 | 990 | 320 | 230 | 0.98 | 807 | 248 | 1083 | 322 | 1426 | 237 | 1036 | 369 | 2019-06-29 23:30 | 137.6 | 54.5 | 1426 | Y | 94 | 116 | 90 | 26 |  |  | 19.6 | 80.4 | 0.3 |  |  |  | 136.51 | 29 | 29 | 83.55 | 580.52 | 632.43 | 539.28 | 632.48 |  | 56.3 |  | 1.3 |  |  |  |  | 718.13 | 1.47 | 0.64 | 0.82
6 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | KIKARWALAN | 1141 | PNR008 | 1S-DL-YP-CTC-DPNR-1451-PNR008 | 14-B MCD QTR. P.L. RD.:PL | TG-PNR008A-2 | 19505037 | 990 | 320 | 246 | 0.96 | 833 | 263 | 1087 | 259 | 1069 | 310 | 1289 | 212 | 2019-06-12 | 196.5 | 81 | 1333 | B | 98 | 95 | 106 | 11 |  |  |  | 100 |  |  |  |  | 80.3 | 132.09 | 132.09 | 62.3 | 631.13 | 579.04 | 633.5 | 644.43 | 3 | 3.3 | 47.21 | 7.3 |  |  |  |  | 714.43 | 5.17 | 0.65 | 0.84
7 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | KIKARWALAN | 1141 | PNR008 | 1S-DL-YP-CTC-DPNR-1451-PNR008 | 14-B MCD QTR. P.L. RD.:PL | TG-PNR008A-1 | 19505956 | 990 | 320 | 233 | 0.97 | 1112 | 382 | 1645 | 343 | 1483 | 386 | 1670 | 176 | 2019-06-03 02:00 | 224.3 | 78.1 | 1941 | B | 99 | 98 | 103 | 5 | 0.2 | 0.3 | 10.2 | 89.3 |  |  |  |  | 36.3 | 31.3 | 31.3 | 27 | 552.41 | 591.41 | 546.41 | 568.41 | 96.25 | 69.13 | 91.43 | 87.43 | 11.28 | 4.4 | 24.1 | 13.4 | 697.04 | 22.56 | 0.56 | 1.12
8 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | KIKARWALAN | 1141 | PNR010 | 1S-DL-YP-CTC-DPNR-1451-PNR010 | MILITARY ROAD (K):PL | TG-PNR010A-1 | 19504865 | 990 | 320 | 244 | 0.97 | 862 | 250 | 981 | 311 | 1220 | 301 | 1186 | 224 | 2019-06-01 21:30 | 269.4 | 66.2 | 1358 | Y | 87 | 110 | 103 | 23 |  |  | 1 | 99 |  |  |  |  | 213 | 34 | 34 | 67.3 | 506.23 | 593.23 | 643.53 | 633.53 |  | 92 | 28 | 18 |  |  |  |  | 719.23 | 0.37 | 0.62 | 0.87
9 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | KIKARWALAN | 1141 | PNR010 | 1S-DL-YP-CTC-DPNR-1451-PNR010 | MILITARY ROAD (K):PL | TG-PNR010A-2 | 19505039 | 990 | 320 | 245 | 0.96 | 876 | 335 | 1372 | 289 | 1189 | 253 | 1034 | 293 | 2019-06-02 00:30 | 231.8 | 69.9 | 1372 | R | 115 | 97 | 87 | 28 |  |  | 6.3 | 93.7 |  |  |  |  | 9 | 108 | 108 | 65 | 656.23 | 608.05 | 463.3 | 650.05 | 51.41 | 1.59 |  | 2.59 | 1 |  |  |  | 718.04 | 1.56 | 0.58 | 0.89
10 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | KIKARWALAN | 1141 | PNR013 | 1S-DL-YP-CTC-DPNR-1451-PNR013 | TANK RD .BOOSTER PUMP:PL | TG-PNR013A-1 | 19500291 | 990 | 320 | 250 | 0.96 | 1016 | 327 | 1353 | 341 | 1407 | 347 | 1426 | 65 | 2019-06-02 16:00 | 365.8 | 62.6 | 1461 | Y | 94 | 107 | 99 | 13 |  | 0.1 | 26.8 | 73.1 |  |  |  |  | 80.26 | 27.57 | 27.57 | 48.26 | 510.53 | 472.07 | 489.53 | 492.53 | 125.08 | 191.23 | 171.38 | 173.38 | 0.3 | 25.3 | 5 | 2 | 716.57 | 3.03 | 0.62 | 1.03
11 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | KIKARWALAN | 1141 | PNR013 | 1S-DL-YP-CTC-DPNR-1451-PNR013 | TANK RD .BOOSTER PUMP:PL | TG-PNR013A-2 | 19505172 | 990 | 320 | 238 | 0.98 | 948 | 315 | 1381 | 280 | 1223 | 353 | 1562 | 294 | 2019-06-02 15:30 | 177.9 | 14.1 | 1562 | B | 105 | 91 | 105 | 14 | 0.3 | 0.3 | 32.5 | 66.9 | 81 | 139 | 111.3 | 103 | 309.24 | 264.2 | 264.2 | 293.55 | 238.06 | 284.56 | 191.09 | 259.35 | 65.16 | 5.3 | 99.16 | 37.16 |  |  | 4 |  | 693.46 | 26.14 | 0.45 | 0.96
12 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | KIKARWALAN | 1141 | PNR013 | 1S-DL-YP-CTC-DPNR-1451-PNR013 | TANK RD .BOOSTER PUMP:PL | TG-PNR013A-3 | 19505343 | 990 | 320 | 248 | 0.98 | 851 | 278 | 1146 | 284 | 1174 | 289 | 1203 | 50 | 2019-06-12 16:00 | 179.2 | 1.9 | 1568 | B | 103 | 88 | 109 | 21 | 0.1 |  | 6.5 | 93.3 | 364.54 | 433.24 | 345.24 | 393.54 | 99.56 | 46.56 | 46.56 | 74.56 | 179.15 | 208.57 | 173.39 | 193.28 | 57 | 11.48 | 66.06 | 38.47 |  |  | 0.3 |  | 701.05 | 18.55 | 0.37 | 0.86
13 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | KIKARWALAN | 1141 | PNR016 | 1S-DL-YP-CTC-DPNR-1451-PNR016 | REGER PURA ZONAL OFF INDOOR S/ST:ID | TG-PNR016A-2 | 19503212 | 990 | 320 | 233 | 0.97 | 875 | 329 | 1491 | 264 | 1201 | 282 | 1286 | 258 | 2019-06-12 14:30 | 171.5 | 57.4 | 1491 | R | 104 | 101 | 95 | 9 |  | 0.1 | 43.2 | 56.7 |  |  | 0.3 |  | 106.24 | 110.54 | 110.54 | 128.54 | 566.53 | 594.18 | 505.48 | 570.48 | 44.55 | 13 | 25.3 | 18.3 |  |  |  |  | 718.12 | 1.48 | 0.62 | 0.88
14 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | KIKARWALAN | 1141 | PNR016 | 1S-DL-YP-CTC-DPNR-1451-PNR016 | REGER PURA ZONAL OFF INDOOR S/ST:ID | TG-PNR016A-1 | 19504459 | 630 | 200 | 232 | 0.97 | 548 | 225 | 1021 | 143 | 651 | 179 | 799 | 323 | 2019-06-12 16:00 | 137.5 | 42.8 | 1033 | R | 114 | 87 | 100 | 27 |  | 9.2 | 77.2 | 13.6 |  |  | 1 |  | 21.3 | 120.33 | 120.33 | 45 | 539.04 | 597.39 | 639.24 | 649.42 | 150.08 |  | 28 | 23.3 | 7.3 |  |  |  | 718.12 | 1.48 | 0.68 | 0.87
15 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | KIKARWALAN | 1141 | PNR125 | 1S-DL-YP-CTC-DPNR-1451-PNR125 | MILITARY ROAD S/ST. NO. 3:PM | TG-PNR125A-1 | 19506708 | 630 | 200 | 242 | 0.96 | 575 | 194 | 805 | 204 | 844 | 177 | 730 | 100 | 2019-06-02 01:30 | 185.4 | 32.4 | 1156 | R | 104 | 103 | 93 | 11 | 0.1 | 0.1 | 7.1 | 92.7 |  |  |  |  | 9 | 4 | 4 | 7.3 | 495.3 | 523.3 | 620 | 560.3 | 196 | 174.3 | 55 | 134 | 1.3 |  |  |  | 702 | 18 | 0.74 | 0.91
16 | 2019-06-01 | 2019-06-10 23:30 | PATEL NAGAR | KIKARWALAN | 1141 | PNR157 | 1S-DL-YP-CTC-DPNR-1451-PNR157 | 10-B, RAJENDRAPLACE | TG-PNR157A-1 | 19503741 | 990 | 320 | 235 | 0.98 | 791 | 299 | 1298 | 246 | 1054 | 246 | 1059 | 241 | 2019-06-10 16:00 | 125.9 | 44.9 | 1312 | R | 105 | 89 | 107 | 18 |  | 0.6 | 52.7 | 46.6 |  | 1 |  |  | 55 | 126.3 | 126.3 | 58.3 | 165 | 105.06 | 198.36 | 174.06 | 12.36 | [7 empty] | 232.36 | 7.24 | 0.62 | 0.8
17 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR019 | 1S-DL-YP-CTC-DPNR-1451-PNR019 | FARID PURI NO.1 | TG-PNR019A-1 | 19506651 | 400 | 120 | 242 | 0.95 | 401 | 133 | 559 | 138 | 575 | 130 | 544 | 27 | 2019-06-29 17:30 | 205.8 | 11.3 | 827 | B | 101 | 100 | 99 | 2 | 0.1 | 0.1 | 15.6 | 84.3 | 8.18 | 4.36 | 8.18 | 8.18 | 66.3 | 100.12 | 100.12 | 69.3 | 594.39 | 564.39 | 570.09 | 592.09 | 39.53 | 39.23 | 37.53 | 39.53 | 1 | 1.3 | 1.3 | 0.3 | 710.2 | 9.4 | 0.54 | 1
18 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR020 | 1S-DL-YP-CTC-DPNR-1451-PNR020 | FARID PURI P/M NO. 2:PL | TG-PNR020A-1 | 19503407 | 990 | 320 | 237 | 0.97 | 1158 | 376 | 1697 | 436 | 1997 | 346 | 1574 | 377 | 2019-06-02 05:30 | 437.2 | 2.9 | 1997 | Y | 106 | 107 | 87 | 20 | 0.1 |  | 10.4 | 89.5 | 0.35 | 0.35 | 1.05 | 0.35 | 84.17 | 72.08 | 72.08 | 115.28 | 577.38 | 600.26 | 427.36 | 564.27 | 48.21 | 36.21 | 9.21 | 31.51 | 2 | 3.21 | 0.3 | 0.3 | 712.51 | 7.09 | 0.45 | 1.17
19 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR029 | 1S-DL-YP-CTC-DPNR-1451-PNR029 | 10 BLOCK E. P. NAGAR (K):PL | TG-PNR029A-2 | 19506571 | 990 | 320 | 235 | 0.98 | 1030 | 379 | 1751 | 243 | 1072 | 408 | 1837 | 726 | 2019-06-29 12:00 | 313.3 | 21.8 | 1837 | B | 107 | 93 | 100 | 14 | 0.5 |  | 18.3 | 81.2 |  | 2.3 |  |  | 92.3 | 198.3 | 198.3 | 155 | 516.09 | 486.39 | 456.39 | 485.09 | 96 | 20.3 | 71.3 | 67.3 | 3.3 |  | 1 | 0.3 | 708.09 | 11.51 | 0.53 | 1.04
20 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR032 | 1S-DL-YP-CTC-DPNR-1451-PNR032 | 22 BLOCK W.P. NAGAR:PL | TG-PNR032A-2 | 19504944 | 990 | 320 | 240 | 0.97 | 845 | 254 | 1095 | 274 | 1169 | 317 | 1367 | 244 | 2019-06-26 | 198 | 44.2 | 1367 | B | 96 | 87 | 117 | 30 | 0.1 | 1.8 | 83.9 | 14.3 | 1 | 11 |  |  | 293 | 346.3 | 346.3 | 227 | 419.43 | 361 | 611 | 489.3 | 5.3 | 0.43 | 35.13 | 2.43 |  |  |  |  | 719.13 | 0.47 | 0.57 | 0.85
21 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR032 | 1S-DL-YP-CTC-DPNR-1451-PNR032 | 22 BLOCK W.P. NAGAR:PL | TG-PNR032A-1 | 19506441 | 990 | 320 | 245 | 0.97 | 864 | 314 | 1301 | 275 | 1130 | 275 | 1132 | 170 | 2019-06-26 00:30 | 209.6 | 46.4 | 1325 | Y | 108 | 98 | 95 | 13 | 0.1 | 0.4 | 23 | 76.6 |  |  | 0.3 |  | 103.3 | 172.01 | 172.01 | 139.31 | 557.13 | 526.12 | 497.42 | 555.12 | 51.3 | 14 | 13.3 | 17.3 |  |  |  |  | 712.13 | 7.47 | 0.59 | 0.87
22 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR043 | 1S-DL-YP-CTC-DPNR-1451-PNR043 | BALJIT NGR. BARAT GHAR:PL | TG-PNR043A-2 | 19502619 | 990 | 320 | 237 | 0.97 | 869 | 290 | 1199 | 336 | 1401 | 242 | 996 | 350 | 2019-06-16 01:30 | 260.5 | 58.1 | 1505 | Y | 97 | 116 | 87 | 29 |  | 0.1 | 34.3 | 65.6 | 33.3 |  |  |  | 108 | 41 | 41 | 114 | 538.56 | 571.52 | 476.56 | 586.24 | 38.58 | 105.32 |  | 19 |  | 1 |  |  | 719.24 | 0.36 | 0.61 | 0.88
23 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR051 | 1S-DL-YP-CTC-DPNR-1451-PNR051 | DAV MULTAN:PL | TG-PNR051A-1 | 19502782 | 990 | 320 | 238 | 0.97 | 857 | 274 | 1175 | 309 | 1323 | 274 | 1175 | 148 | 2019-06-03 17:00 | 172.2 | 69.9 | 1345 | R | 107 | 94 | 98 | 13 |  |  | 7.4 | 92.6 |  |  |  |  | 25 | 70.21 | 70.21 | 40.3 | 636.24 | 638.08 | 638.24 | 665.24 | 52.27 | 5.22 | 10.57 | 7.57 |  |  |  |  | 713.51 | 6.09 | 0.67 | 0.87
24 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR051 | 1S-DL-YP-CTC-DPNR-1451-PNR051 | DAV MULTAN:PL | TG-PNR051A-2 | 19502859 | 990 | 320 | 245 | 0.97 | 960 | 310 | 1337 | 341 | 1480 | 308 | 1335 | 144 | 2019-06-01 12:00 | 233.3 | 8.1 | 1480 | Y | 93 | 103 | 105 | 12 |  | 0.1 | 9.1 | 90.8 | 20.27 | 12.27 | 11.57 | 11.57 | 387.31 | 354.28 | 354.28 | 369.56 | 290.57 | 283.49 | 298.19 | 288.53 | 9.33 | 57.17 | 65.15 | 37.42 |  | 0.27 | 0.3 |  | 708.28 | 11.32 | 0.47 | 0.97
25 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR051 | 1S-DL-YP-CTC-DPNR-1451-PNR051 | DAV MULTAN:PL | TG-PNR051A-3 | 19506440 | 630 | 200 | 244 | 0.97 | 620 | 236 | 1020 | 207 | 891 | 177 | 766 | 220 | 2019-06-10 14:30 | 140 | 42.2 | 1020 | R | 113 | 86 | 101 | 27 | 0.1 |  | 62.4 | 37.4 | 5 | 5.3 | 5 | 5 | 14.3 | 120.58 | 120.58 | 35 | 462.54 | 548.41 | 578.36 | 581.06 | 205.12 | 32.27 | 89 | 86.3 | 20 |  |  |  | 707.36 | 12.24 | 0.64 | 0.98
26 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR056 | 1S-DL-YP-CTC-DPNR-1451-PNR056 | F&G BLOCK W.P. NAGAR:PL | TG-PNR056A-1 | 19506652 | 990 | 320 | 233 | 0.97 | 948 | 312 | 1311 | 305 | 1272 | 331 | 1403 | 117 | 2019-06-03 02:00 | 276.5 | 53.1 | 1494 | B | 95 | 96 | 109 | 14 | 0.3 | 4.6 | 88.6 | 6.5 |  |  |  |  | 114.3 | 100 | 100 | 72 | 537 | 549 | 544.3 | 562.3 | 61.3 | 63.3 | 118 | 78.3 |  | 0.3 | 4 |  | 713 | 7 | 0.62 | 0.96
27 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR057 | 1S-DL-YP-CTC-DPNR-1451-PNR057 | S- BLOCK W.P. NAGAR:PL | TG-PNR057A-3 | 19505748 | 630 | 200 | 232 | 0.97 | 512 | 225 | 1041 | 148 | 673 | 139 | 629 | 391 | 2019-06-29 23:00 | 179.4 | 29.4 | 1108 | R | 123 | 91 | 86 | 37 | 0.2 | 0.2 | 3 | 96.6 | 0.3 | 5.3 | 7.3 | 0.3 | 157.57 | 401.31 | 401.31 | 354.46 | 467.45 | 305.05 | 284.09 | 354.2 | 78.54 | 0.3 |  | 3 | 7.3 |  |  |  | 712.36 | 7.24 | 0.55 | 0.81
28 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR057 | 1S-DL-YP-CTC-DPNR-1451-PNR057 | S- BLOCK W.P. NAGAR:PL | TG-PNR057A-2 | 19506245 | 990 | 320 | 238 | 0.97 | 1019 | 423 | 1853 | 375 | 1717 | 221 | 966 | 828 | 2019-06-04 15:30 | 320.6 | 81 | 1853 | R | 100 | 90 | 110 | 20 | 0.3 |  | 2 | 97.7 |  |  |  |  | 60.45 | 173.38 | 173.38 | 64.27 | 620.2 | 516.02 | 598.44 | 605.43 | 30.3 | 21.55 | 80.51 | 41.25 | 0.3 | 0.3 | 1.3 | 0.3 | 712.05 | 7.55 | 0.54 | 1.03
29 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR059 | 1S-DL-YP-CTC-DPNR-1451-PNR059 | BALJIT NGR. NO. 1 (DOGWALA):PL | TG-PNR059A-2 | 19506478 | 630 | 200 | 243 | 0.97 | 724 | 235 | 971 | 230 | 961 | 258 | 1081 | 115 | 2019-06-11 23:30 | 259.2 | 36.6 | 1171 | B | 100 | 97 | 104 | 7 | 0.2 | 2.6 | 6.6 | 90.6 | 3.58 | 3.58 | 3.58 | 3.58 | 191.2 | 224.15 | 224.15 | 181.21 | 468.54 | 430.08 | 463.58 | 463.55 | 36.38 | 30.21 | 55.17 | 54.01 | 5.18 | 17.26 | 8.06 | 2.53 | 706.08 | 13.52 | 0.44 | 1.15
30 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR059 | 1S-DL-YP-CTC-DPNR-1451-PNR059 | BALJIT NGR. NO. 1 (DOGWALA):PL | TG-PNR059A-1 | 19506705 | 990 | 320 | 243 | 0.96 | 960 | 283 | 1221 | 316 | 1372 | 360 | 1571 | 304 | 2019-06-28 23:00 | 284.2 | 65.3 | 1571 | B | 95 | 106 | 99 | 11 | 0.1 | 0.1 | 4.1 | 95.6 |  |  |  |  | 211.59 | 97.56 | 97.56 | 168.31 | 469.15 | 540.52 | 454.14 | 492.51 | 25.47 | 67.53 | 51.12 | 45.39 |  | 0.2 | 2.3 |  | 707.01 | 12.59 | 0.54 | 0.97
31 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR063 | 1S-DL-YP-CTC-DPNR-1451-PNR063 | Z-BLOCK, W.P. NAGAR:PL | TG-PNR063A-1 | 19502755 | 990 | 320 | 238 | 0.96 | 875 | 314 | 1311 | 281 | 1171 | 280 | 1172 | 139 | 2019-06-30 20:00 | 216.4 | 71.4 | 1372 | R | 109 | 94 | 97 | 15 |  |  | 9.1 | 90.9 |  | 0.3 |  |  | 54.3 | 156.16 | 156.16 | 118.26 | 585.37 | 552.5 | 487.41 | 565.41 | 79.29 | 10 | 50 | 35.29 |  |  |  |  | 719.36 | 0.24 | 0.64 | 0.88
32 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR064 | 1S-DL-YP-CTC-DPNR-1451-PNR064 | D-BLOCK, W.P. NAGAR P/M:PM | TG-PNR064A-1 | 19500297 | 630 | 200 | 236 | 0.96 | 609 | 198 | 838 | 193 | 810 | 218 | 923 | 102 | 2019-06-02 03:00 | 144 | 20.7 | 1009 | B | 90 | 102 | 108 | 18 |  |  | 7.4 | 92.6 | 1 | 0.3 | 0.3 | 1 | 176.49 | 88.54 | 88.54 | 89.27 | 522.39 | 565.4 | 538.07 | 566.37 | 19 | 64.24 | 107.54 | 62.24 |  |  | 8.3 |  | 719.28 | 0.32 | 0.57 | 0.97
33 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR067 | 1S-DL-YP-CTC-DPNR-1451-PNR067 | 30 BLOCK WEST PATEL NAGAR:PL | TG-PNR067A-2 | 19504734 | 630 | 200 | 239 | 0.97 | 536 | 205 | 899 | 160 | 704 | 171 | 753 | 176 | 2019-06-02 23:30 | 115.5 | 34 | 938 | R | 112 | 91 | 98 | 21 |  |  | 0.4 | 99.6 |  | 1.3 |  |  | 160.02 | 372.07 | 372.07 | 265.44 | 507.37 | 342.32 | 451.37 | 446.55 | 48.3 | 0.3 | 1.3 | 4 | 0.3 |  |  |  | 716.39 | 3.21 | 0.56 | 0.85
34 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR094 | 1S-DL-YP-CTC-DPNR-1451-PNR094 | 29 BLOCK W.P. NAGAR:PL | TG-PNR094A-2 | 19504444 | 990 | 320 | 238 | 0.97 | 949 | 297 | 1243 | 299 | 1253 | 354 | 1492 | 244 | 2019-06-03 03:00 | 202.4 | 54.5 | 1533 | Y | 98 | 100 | 102 | 4 |  |  | 2.2 | 97.8 |  |  | 3 |  | 249.29 | 224.36 | 224.36 | 221.58 | 438.53 | 457 | 462.23 | 462.25 | 22.51 | 29.18 | 50.27 | 26.5 |  | 0.19 | 1.14 |  | 711.13 | 8.47 | 0.52 | 0.96
35 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR131 | 1S-DL-YP-CTC-DPNR-1451-PNR131 | HOLI CHOWK PATEL NAGAR | TG-PNR131A-1 | 19502792 | 990 | 320 | 237 | 0.97 | 819 | 309 | 1331 | 306 | 1319 | 204 | 869 | 457 | 2019-06-29 23:30 | 173.7 | 42.7 | 1379 | R | 110 | 112 | 79 | 33 |  |  | 9.7 | 90.3 | 0.3 |  | 0.3 | 0.3 | 4 | 4.3 | 4.3 | 6.3 | 629.03 | 653.33 | 596.35 | 705.33 | 86 | 61.3 |  | 7 |  |  |  |  | 719.33 | 0.27 | 0.71 | 0.83
36 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR153 | 1S-DL-YP-CTC-DPNR-1451-PNR153 | ROAD NO-20 BALJEET NAGAR | TG-PNR153A-2 | 19502810 | 990 | 320 | 243 | 0.97 | 994 | 342 | 1439 | 321 | 1346 | 330 | 1374 | 83 | 2019-06-14 06:00 | 440.1 | 50.8 | 1573 | R | 108 | 101 | 91 | 17 |  | 0.4 | 64.3 | 35.3 |  |  |  |  | 125.14 | 163.05 | 163.05 | 158.35 | 462.35 | 460.28 | 439.36 | 473.44 | 112.25 | 89.37 | 29.29 | 80.21 | 12.56 |  | 0.3 | 0.3 | 713.1 | 6.5 | 0.54 | 1
37 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | SARAI ROHILLA | 1141 | PNR100 | 1S-DL-YP-CTC-DPNR-1451-PNR100 | K. PAHR G. NO. 9:PL | TG-PNR100A-1 | 19506285 | 990 | 320 | 248 | 0.98 | 1015 | 321 | 1389 | 334 | 1447 | 360 | 1550 | 142 | 2019-06-26 12:30 | 198.4 | -169 | 1550 | B | 101 | 99 | 100 | 2 |  |  | 13.4 | 86.6 | 157.17 | 188.17 | 202.17 | 176.47 | 236.38 | 207.38 | 207.38 | 216.38 | 210.33 | 207.33 | 188.33 | 204.03 | 105.07 | 105.37 | 125.37 | 111.37 |  | 0.3 | 0.3 | 0.3 | 709.35 | 10.25 | 0.43 | 1.02
38 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | SARAI ROHILLA | 1141 | PNR101 | 1S-DL-YP-CTC-DPNR-1451-PNR101 | S/STN NO.15 GALI NO.8 KALA PAHAR | TG-PNR101A-2 | 19505749 | 990 | 320 | 242 | 0.97 | 990 | 320 | 1398 | 327 | 1434 | 343 | 1501 | 90 | 2019-06-15 14:00 | 183.7 | -116.8 | 1501 | B | 102 | 99 | 99 | 3 |  |  | 4.2 | 95.8 | 126.26 | 205.56 | 201.56 | 178.26 | 259.22 | 186.52 | 186.52 | 210.52 | 162.02 | 165.32 | 168.02 | 165.32 | 161.06 | 149.06 | 151.06 | 153.36 |  | 1.3 | 2 | 0.3 | 708.56 | 11.04 | 0.46 | 1
39 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | SARAI ROHILLA | 1141 | PNR102 | 1S-DL-YP-CTC-DPNR-1451-PNR102 | NAGARWALA GHATTI RD.:PL | TG-PNR102A-1 | 19505845 | 990 | 320 | 238 | 0.97 | 1035 | 359 | 1508 | 353 | 1471 | 323 | 1346 | 147 | 2019-06-30 17:00 | 336 | 57.3 | 1707 | Y | 103 | 104 | 93 | 11 |  | 0.1 | 9.1 | 90.8 |  |  |  |  | 5 | 3.3 | 3.3 | 4.3 | 481.36 | 454.39 | 563.36 | 498.09 | 203.38 | 220.35 | 126.23 | 197.2 | 13.15 | 24.45 |  | 3.3 | 703.29 | 16.31 | 0.67 | 1.05
40 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | SARAI ROHILLA | 1141 | PNR104 | 1S-DL-YP-CTC-DPNR-1451-PNR104 | ZONAL OFF. K. PAHAR:PL | TG-PNR104A-2 | 19506080 | 990 | 320 | 243 | 0.93 | 836 | 283 | 1165 | 291 | 1192 | 262 | 1073 | 108 | 2019-06-19 16:30 | 62.4 | -193.9 | 1253 | Y | 104 | 103 | 93 | 11 |  |  | 11.3 | 88.7 | 149.54 | 162.24 | 227.54 | 175.24 | 248.3 | 228 | 228 | 227.3 | 283.13 | 280.43 | 297.3 | 300.43 | 32.3 | 43 | 0.3 | 10.3 |  |  |  |  | 714.07 | 5.53 | 0.49 | 0.84
41 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | SARAI ROHILLA | 1141 | PNR107 | 1S-DL-YP-CTC-DPNR-1451-PNR107 | BANGALI DHABA K. PAHAR:PL | TG-PNR107A-1 | 19502628 | 990 | 320 | 251 | 0.98 | 905 | 286 | 1139 | 302 | 1207 | 317 | 1266 | 110 | 2019-06-26 16:00 | 213.4 | -40.5 | 1266 | B | 96 | 97 | 107 | 11 |  |  | 1 | 99 | 324.3 | 336 | 275 | 319 | 97 | 83 | 83 | 99.3 | 277 | 245.3 | 223.3 | 241 | 21.3 | 55.3 | 92.3 | 60.3 |  |  |  |  | 720 | 0 | 0.43 | 0.91
42 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | SARAI ROHILLA | 1141 | PNR113 | 1S-DL-YP-CTC-DPNR-1451-PNR113 | SARAI ROHILLA:PL | TG-PNR113A-1 | 19503210 | 990 | 320 | 237 | 0.97 | 911 | 321 | 1348 | 259 | 1080 | 331 | 1397 | 295 | 2019-06-30 03:00 | 259.8 | 58.9 | 1397 | B | 108 | 93 | 99 | 15 |  | 0.1 | 53 | 46.9 |  |  |  |  | 10 | 42.19 | 42.19 | 14.3 | 585.52 | 639.03 | 602.52 | 628.52 | 123 | 37.3 | 90 | 75.3 |  |  | 0.3 |  | 718.52 | 1.08 | 0.67 | 0.92
43 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | SARAI ROHILLA | 1141 | PNR120 | 1S-DL-YP-CTC-DPNR-1451-PNR120 | SOHAN SINGH K.PAHAR:PL | TG-PNR120A-3 | 19503574 | 630 | 200 | 247 | 0.99 | 569 | 179 | 757 | 205 | 867 | 185 | 788 | 98 | 2019-06-28 15:30 | 131.1 | -40.9 | 867 | Y | 98 | 104 | 98 | 6 |  |  | 0.1 | 99.9 | 19 | 20.51 | 16.3 | 18 | 358.54 | 351.03 | 351.03 | 361.54 | 314.3 | 244 | 303 | 290.3 | 27 | 103.3 | 28.3 | 49 |  |  |  |  | 719.24 | 0.36 | 0.51 | 0.9
44 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | SARAI ROHILLA | 1141 | PNR120 | 1S-DL-YP-CTC-DPNR-1451-PNR120 | SOHAN SINGH K.PAHAR:PL | TG-PNR120A-1 | 19506568 | 630 | 200 | 249 | 0.9 | 599 | 198 | 792 | 197 | 791 | 203 | 823 | 32 | 2019-06-04 11:00 | 106.8 | -143.6 | 862 | B | 98 | 98 | 104 | 6 |  | 1.7 | 73.9 | 24.3 | 144.54 | 195.54 | 201.54 | 182.54 | 256 | 200.3 | 200.3 | 217 | 249.3 | 258.3 | 192 | 230 | 54 | 49.3 | 113.3 | 74.3 |  |  |  |  | 704.24 | 15.36 | 0.45 | 0.95
45 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | SARAI ROHILLA | 1141 | PNR127 | 1S-DL-YP-CTC-DPNR-1451-PNR127 | MILITARY RD. P/M S/ST:PL | TG-PNR127A-2 | 19504393 | 990 | 320 | 257 | 0.96 | 998 | 308 | 1213 | 280 | 1091 | 410 | 1620 | 480 | 2019-06-30 02:30 | 288.5 | -270.8 | 1620 | B | 96 | 83 | 121 | 38 |  | 0.1 | 63.3 | 36.7 | 2.5 | 7.2 | 2.5 | 2.5 | 182.5 | 303.49 | 303.49 | 151.5 | 513.15 | 393.28 | 563.28 | 531.15 | 13.48 | 8.06 | 110.07 | 26.18 |  |  | 10.18 | 0.3 | 712.43 | 7.17 | 0.52 | 1.01
46 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | SARAI ROHILLA | 1141 | PNR129 | 1S-DL-YP-CTC-DPNR-1451-PNR129 | GALI-4 POST OFFICE ANAND PARBAT | TG-PNR129A-1 | 19502933 | 990 | 320 | 253 | 0.99 | 793 | 224 | 910 | 276 | 1123 | 293 | 1189 | 253 | 2019-06-14 15:30 | 166.3 | -78 | 1239 | B | 94 | 102 | 104 | 10 |  |  | 1.4 | 98.6 | 80.3 | 86.24 | 151.24 | 107.24 | 346.54 | 316.3 | 316.3 | 297 | 291.1 | 301.4 | 298.1 | 313.4 |  | 14 | 31.3 | 0.3 |  |  |  |  | 718.34 | 1.26 | 0.5 | 0.8
47 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | SARAI ROHILLA | 1141 | PNR130 | 1S-DL-YP-CTC-DPNR-1451-PNR130 | TAULUI WALA PATEL NAGAR | TG-PNR130A-1 | 19506739 | 990 | 320 | 245 | 0.99 | 865 | 269 | 1091 | 289 | 1168 | 308 | 1257 | 144 | 2019-06-25 16:00 | 185 | -46.1 | 1281 | B | 96 | 95 | 109 | 14 |  |  | 60.9 | 39.1 | 3 | 3.3 |  | 1 | 367 | 369 | 369 | 362 | 322.3 | 317 | 326 | 312 | 15.3 | 18.3 | 79 | 33 |  |  |  |  | 708 | 12 | 0.56 | 0.87
48 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | SARAI ROHILLA | 1141 | PNR139 | 1S-DL-YP-CTC-DPNR-1451-PNR139 | POST OFFICE P/M GALI NO-2 | TG-PNR139A-1 | 19502809 | 400 | 120 | 243 | 0.84 | 335 | 120 | 524 | 111 | 477 | 103 | 442 | 71 | 2019-06-26 16:00 | 11.6 | -107.9 | 541 | R | 102 | 105 | 93 | 12 | 0.8 | 9.5 | 54.5 | 35.2 | 241.04 | 63 | 262.34 | 183.34 | 180.3 | 347.04 | 347.04 | 238.3 | 232.24 | 294.48 | 284.18 | 282.18 | 63.54 | 13 | 0.3 | 13.3 |  |  |  |  | 717.52 | 2.08 | 0.48 | 0.84
49 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | SARAI ROHILLA | 1141 | PNR149 | 1S-DL-YP-CTC-DPNR-1451-PNR149 | HR. ROAD ANAND PARVAT | TG-PNR149A-2 | 19505394 | 400 | 120 | 243 | 0.99 | 352 | 121 | 502 | 105 | 435 | 126 | 525 | 82 | 2019-06-22 16:00 | 106.1 | -7.7 | 620 | R | 103 | 86 | 111 | 25 |  |  | 14 | 86 | 0.3 | 4.3 | 0.3 | 0.3 | 64.26 | 273.26 | 273.26 | 101.26 | 622.18 | 419.18 | 595.18 | 583.48 | 15.3 | 6 | 60 | 17.3 | 0.3 |  |  |  | 703.14 | 16.46 | 0.62 | 0.88
50 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | SARAI ROHILLA | 1141 | PNR165 | 1S-DL-YP-CTC-DPNR-1451-PNR165 | Booster Pump Nai basti( Rajiv Vatika ) | TG-PNR165A-1 | 19504825 | 990 | 320 | 240 | 0.96 | 827 | 278 | 1149 | 317 | 1298 | 232 | 951 | 302 | 2019-06-11 23:30 | 275.3 | 36.8 | 1416 | Y | 103 | 111 | 87 | 24 |  | 0.1 | 68.2 | 31.8 | 0.3 | 0.3 | 1 | 1 | 65.3 | 39 | 39 | 66 | 641.24 | 576.24 | 533.54 | 642.24 | 12 | 103 |  | 10 |  | 0.3 |  |  | 719.24 | 0.36 | 0.66 | 0.84

## Loading Condition > 100%
MIS Report of Distribution Transformer - Jun19
Jun19 1141 PATEL NAGAR (Loading Condition > 100% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | KIKARWALAN | 1141 | PNR012 | 1S-DL-YP-CTC-DPNR-1451-PNR012 | TANK RD. KHATTA S/ST.:PL | TG-PNR012A-1 | 19500318 | 990 | 320 | 235 | 0.98 | 1201 | 429 | 1867 | 441 | 1947 | 330 | 1440 | 472 | 2019-06-02 15:00 | 134.7 | 26.5 | 1980 | Y | 102 | 110 | 89 | 21 |  | 0.7 | 29.5 | 69.8 | 30.3 | 21.3 | 102 | 40 | 403.34 | 402.03 | 402.03 | 396.25 | 134.59 | 102.21 | 151.13 | 131.08 | 64.11 | 87.2 | 103.01 | 80.05 | 79.25 | 99.25 | 2 | 65.01 | 712.39 | 7.21 | 0.4 | 1.21
2 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | KIKARWALAN | 1141 | PNR015 | 1S-DL-YP-CTC-DPNR-1451-PNR015 | KRISHNA TIRATH DEV NAGAR | TG-PNR015A-1 | 19502800 | 990 | 320 | 246 | 0.98 | 990 | 294 | 1243 | 338 | 1439 | 358 | 1521 | 247 | 2019-06-02 14:00 | 149.4 | 5.9 | 1589 | B | 87 | 103 | 111 | 24 |  |  | 2.4 | 97.6 | 444.17 | 439.47 | 430.47 | 437.17 | 38.16 | 38.16 | 38.16 | 41.16 | 171.29 | 75.33 | 51.03 | 80.03 | 60.44 | 153.1 | 121.1 | 156.1 |  | 8 | 67 |  | 714.46 | 5.14 | 0.36 | 1
3 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | KIKARWALAN | 1141 | PNR155 | 1S-DL-YP-CTC-DPNR-1451-PNR155 | VIJAY CHOWK | TG-PNR155A-1 | 19500300 | 990 | 300 | 238 | 0.97 | 931 | 240 | 994 | 379 | 1600 | 313 | 1319 | 525 | 2019-06-01 22:00 | 265.7 | 11 | 1668 | Y | 88 | 110 | 103 | 22 |  | 5.5 | 86.9 | 7.7 | 0.3 | 145.36 |  |  | 155.15 | 42.3 | 42.3 | 125.06 | 555.43 | 344.08 | 647.24 | 545.22 |  | 140.57 | 28.3 | 41 |  | 38.17 |  |  | 711.28 | 8.32 | 0.59 | 0.94
4 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR021 | 1S-DL-YP-CTC-DPNR-1451-PNR021 | RAJASTHANI COLONY P/M-1:PM | TG-PNR021A-2 | 19506527 | 400 | 120 | 243 | 0.96 | 441 | 144 | 590 | 132 | 544 | 165 | 690 | 129 | 2019-06-13 05:30 | 246.1 | 27.1 | 705 | B | 100 | 88 | 112 | 24 | 0.1 | 0.7 | 31.9 | 67.4 | 0.3 | 0.3 | 0.3 | 0.3 | 76 | 178 | 178 | 52.3 | 588.52 | 496.22 | 607.52 | 617.22 | 28 | 37 | 41.3 | 22 | 20.3 | 2 | 38.3 | 21.3 | 713.52 | 6.08 | 0.51 | 1.1
5 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR043 | 1S-DL-YP-CTC-DPNR-1451-PNR043 | BALJIT NGR. BARAT GHAR:PL | TG-PNR043A-1 | 19505121 | 990 | 320 | 238 | 0.97 | 1120 | 334 | 1414 | 442 | 1920 | 345 | 1480 | 476 | 2019-06-02 01:30 | 314.6 | 69.4 | 1920 | Y | 97 | 106 | 97 | 9 | 0.1 | 0.3 | 18.5 | 81.1 |  |  |  |  | 30.3 | 17.3 | 17.3 | 23.3 | 529.48 | 454.52 | 536.52 | 518.22 | 125.06 | 162.3 | 118.52 | 128.02 | 17.3 | 68.02 | 21.1 | 33 | 702.54 | 17.06 | 0.59 | 1.13
6 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR044 | 1S-DL-YP-CTC-DPNR-1451-PNR044 | BALJIT NAGAR AGGARWAL SWEET P/M:PM | TG-PNR044A-1 | 19506244 | 400 | 120 | 237 | 0.97 | 434 | 134 | 612 | 129 | 588 | 172 | 792 | 193 | 2019-06-10 02:00 | 137.5 | 25.4 | 965 | B | 83 | 88 | 129 | 46 | 0.7 | 0.5 | 11.1 | 87.7 | 1 | 1 | 1 | 1 | 295.3 | 176.3 | 176.3 | 82.3 | 389.55 | 509.55 | 465.54 | 526.52 | 15.3 | 15 | 118.28 | 86.33 | 0.3 |  | 109.33 | 5.3 | 702.25 | 17.35 | 0.53 | 1.09
7 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR047 | 1S-DL-YP-CTC-DPNR-1451-PNR047 | SHADI PUR DTC DEPOT:PL | TG-PNR047A-2 | 19506556 | 630 | 200 | 251 | 0.97 | 791 | 242 | 960 | 213 | 845 | 336 | 1359 | 468 | 2019-06-02 23:30 | 186.8 | 40.2 | 1371 | B | 91 | 90 | 119 | 29 | 1.3 | 0.9 | 25.6 | 72.2 |  |  |  |  | 172 | 117 | 117 | 75 | 450.16 | 530.13 | 464.16 | 509.46 | 71.27 | 47 | 111 | 95.57 | 1.3 | 1 | 90.57 | 14.3 | 695.13 | 24.47 | 0.47 | 1.26
8 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR048 | 1S-DL-YP-CTC-DPNR-1451-PNR048 | BALJIT NAGAR SCHOOLWALA TR.1:PM | TG-PNR048A-2 | 19506082 | 990 | 320 | 242 | 0.96 | 1288 | 464 | 2073 | 420 | 1848 | 405 | 1795 | 256 | 2019-06-02 01:00 | 599.7 | 21.4 | 2234 | Y | 99 | 96 | 105 | 9 | 0.2 | 0.1 | 6.8 | 92.9 | 95.3 | 0.3 | 0.3 | 0.3 | 47.58 | 102 | 102 | 61.3 | 330.08 | 431.47 | 476.38 | 454.36 | 109.28 | 101.15 | 139.58 | 109.28 | 107.47 | 55.19 | 62.15 | 64.47 | 690.51 | 29.09 | 0.51 | 1.3
9 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR048 | 1S-DL-YP-CTC-DPNR-1451-PNR048 | BALJIT NAGAR SCHOOLWALA TR.1:PM | TG-PNR048A-1 | 19506083 | 990 | 320 | 243 | 0.97 | 1425 | 555 | 2381 | 420 | 1791 | 450 | 1789 | 591 | 2019-06-05 06:00 | 622.4 | 81 | 2381 | R | 100 | 105 | 96 | 9 | 100 |  |  |  | 0.3 | 0.3 | 0.3 | 0.3 | 64.3 | 40 | 40 | 41 | 513.27 | 520.27 | 561.27 | 537.27 | 99.55 | 113.5 | 87.17 | 102.18 | 35.2 | 38.55 | 29.58 | 32.27 | 713.42 | 6.18 | 0.44 | 1.44
10 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR049 | 1S-DL-YP-CTC-DPNR-1451-PNR049 | BALJIT NAGAR JANTA PARK:PL | TG-PNR049A-1 | 19502781 | 990 | 320 | 243 | 0.96 | 1054 | 354 | 1459 | 339 | 1396 | 361 | 1488 | 82 | 2019-06-30 05:00 | 444.5 | 72.1 | 1662 | R | 110 | 96 | 94 | 16 |  |  | 12.1 | 87.9 |  |  |  |  | 12.57 | 65.05 | 65.05 | 29.07 | 495 | 526.52 | 563.06 | 532.5 | 148.59 | 122.21 | 94.51 | 143.53 | 58.22 | 1 | 6 | 9.28 | 715.18 | 4.42 | 0.59 | 1.07
11 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR054 | 1S-DL-YP-CTC-DPNR-1451-PNR054 | POLICE STN. W.P.NAGAR:PL | TG-PNR054A-1 | 19502603 | 990 | 320 | 243 | 0.97 | 1191 | 373 | 1526 | 378 | 1548 | 440 | 1803 | 267 | 2019-06-02 01:00 | 287 | 78 | 1803 | B | 93 | 100 | 107 | 14 |  |  | 0.6 | 99.4 |  |  |  |  | 26.37 | 4.34 | 4.34 | 7.04 | 571.56 | 548.4 | 426.51 | 527.41 | 104.12 | 138.01 | 208.44 | 155.28 | 9.58 | 21.28 | 71.38 | 22.3 | 712.43 | 7.17 | 0.58 | 1.2
12 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR062 | 1S-DL-YP-CTC-DPNR-1451-PNR062 | NALA (K) W.P. NAGAR:PL | TG-PNR062A-1 | 19502808 | 990 | 320 | 241 | 0.97 | 1113 | 336 | 1451 | 413 | 1823 | 364 | 1576 | 328 | 2019-06-11 00:30 | 279.7 | 57.4 | 1823 | Y | 93 | 104 | 103 | 11 |  | 0.2 | 29.6 | 70.2 |  |  |  |  | 36.53 | 37.14 | 37.14 | 36.44 | 551.55 | 463.34 | 465.04 | 486.34 | 119.5 | 142.3 | 152.4 | 157.1 | 5.58 | 71.18 | 62.08 | 34.08 | 714.36 | 5.24 | 0.59 | 1.12
13 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR066 | 1S-DL-YP-CTC-DPNR-1451-PNR066 | WEST PATEL NAGAR INDOOR:PL | TG-PNR066A-2 | 19501641 | 630 | 200 | 235 | 0.97 | 743 | 243 | 1060 | 253 | 1135 | 247 | 1098 | 65 | 2019-06-12 00:30 | 164.2 | 23.5 | 1246 | Y | 100 | 96 | 104 | 8 | 55.8 | 39.6 | 3.8 | 0.8 | 1 | 1 | 1 | 1 | 3 | 9 | 9 | 3 | 373.01 | 478.02 | 346.34 | 404.3 | 269.59 | 165.28 | 299.56 | 249 | 72.23 | 65.53 | 70.53 | 61.53 | 719.23 | 0.37 | 0.65 | 1.18
14 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR152 | 1S-DL-YP-CTC-DPNR-1451-PNR152 | 25 BLK WEST PATEL NAGAR | TG-PNR152A-1 | 19502853 | 990 | 320 | 239 | 0.97 | 1381 | 416 | 1810 | 491 | 2170 | 474 | 2071 | 322 | 2019-06-11 00:30 | 277.5 | 55.9 | 2173 | Y | 94 | 103 | 103 | 9 |  |  | 13.1 | 86.9 |  |  |  |  | 36.3 | 11 | 11 | 13.3 | 465.24 | 420.54 | 421.54 | 438.54 | 136.3 | 132.3 | 161.3 | 147.3 | 79.48 | 153.48 | 126.48 | 118.18 | 718.12 | 1.48 | 0.54 | 1.39
15 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | PATEL NAGAR | 1141 | PNR153 | 1S-DL-YP-CTC-DPNR-1451-PNR153 | ROAD NO-20 BALJEET NAGAR | TG-PNR153A-1 | 19505847 | 990 | 320 | 242 | 0.96 | 1271 | 401 | 1640 | 449 | 1856 | 421 | 1749 | 187 | 2019-06-13 05:30 | 588.2 | 81.3 | 2031 | Y | 97 | 103 | 100 | 6 |  | 0.2 | 46.8 | 53 |  |  |  |  | 8 | 8.3 | 8.3 | 4 | 509.05 | 482.13 | 512.13 | 500.43 | 140.49 | 121.3 | 140.3 | 136.3 | 49.19 | 95 | 52.3 | 66 | 707.13 | 12.47 | 0.55 | 1.28
16 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | SARAI ROHILLA | 1141 | PNR114 | 1S-DL-YP-CTC-DPNR-1451-PNR114 | KAMAL (K) K.PAHAR:PL | TG-PNR114A-1 | 19504060 | 630 | 200 | 240 | 0.98 | 590 | 264 | 1146 | 156 | 669 | 171 | 730 | 450 | 2019-06-29 16:00 | 137.5 | 12.4 | 1187 | R | 129 | 80 | 91 | 49 |  | 0.1 | 10.2 | 89.7 |  |  | 0.3 |  | 14 | 273.39 | 273.39 | 74.34 | 493.45 | 444.06 | 611.41 | 620.11 | 155.3 | 0.3 | 1 | 23.3 | 55 |  |  |  | 718.15 | 1.45 | 0.6 | 0.94
17 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | SARAI ROHILLA | 1141 | PNR141 | 1S-DL-YP-CTC-DPNR-1451-PNR141 | TIKONA PARK GODODIA ROAD | TG-PNR141A-1 | 19502625 | 990 | 320 | 245 | 0.96 | 1113 | 320 | 1362 | 439 | 1877 | 355 | 1510 | 459 | 2019-06-29 23:00 | 307.6 | 103.8 | 2054 | Y | 95 | 122 | 83 | 39 |  | 1.5 | 11 | 87.5 |  |  |  |  | 1.16 |  |  | 0.46 | 549.38 | 264.25 | 634.43 | 484.27 | 160.16 | 242.59 | 58.41 | 187.57 | 4 | 207.46 | 6 | 42 | 715.1 | 4.5 | 0.65 | 1.12
18 | 2019-06-03 | 2019-06-30 23:30 | PATEL NAGAR | SARAI ROHILLA | 1141 | PNR149 | 1S-DL-YP-CTC-DPNR-1451-PNR149 | HR. ROAD ANAND PARVAT | TG-PNR149A-1 | 19504684 | 630 | 200 | 245 | 0.96 | 651 | 226 | 923 | 214 | 868 | 211 | 863 | 58 | 2019-06-26 16:00 | 52 | -168.4 | 953 | R | 110 | 93 | 97 | 17 |  |  | 23.7 | 76.3 | 94 | 213 | 145 | 143.3 | 228.05 | 127.06 | 127.06 | 189.06 | 105.06 | 189.05 | 176.05 | 149.05 | 191 | 127 | 144.3 | 173.3 | 38.3 | 0.3 | 0.3 | 1.3 | 656.41 | 15.19 | 0.47 | 1.03
19 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | SARAI ROHILLA | 1141 | PNR200 | 1S-DL-YP-CTC-DPNR-1451-PNR200 | NEW TIN MARKET | TG-PNR200A-1 | 19505104 | 630 | 200 | 236 | 0.99 | 714 | 242 | 1065 | 208 | 906 | 264 | 1176 | 235 | 2019-06-01 16:30 | 161.8 | -8.2 | 1176 | B | 106 | 87 | 107 | 20 |  | 1.7 | 63.1 | 35.2 | [5 empty] | 19.3 | 19.3 |  | 359.45 | 435.15 | 322.15 | 378.15 | 125 | 97.3 | 144 | 135.3 | 69.3 | 2 | 88 | 40.3 | 708.02 | 11.58 | 0.62 | 1.13