## Complete Report
MIS Report of Distribution Transformer - Jun19
Jun19 1141 PATEL NAGAR (Complete Report)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | SARAI ROHILLA | 1141 | PNR098 | 1S-DL-YP-CTC-DPNR-1451-PNR098 | DOOGARMAL G. NO. 6/7 A. PBT.:PL | TG-PNR098A-1 | 19502851 | 990 | 320 | 250 | 0.71 | 640 | 206 | 867 | 225 | 938 | 209 | 879 | 65 | 2019-06-29 14:30 | -13.2 | -257.6 | 938 | Y | 99 | 98 | 103 | 5 |  |  | 21.5 | 78.5 | 143 | 308.3 | 192.3 | 233.3 | 364 | 158 | 158 | 248.3 | 210.3 | 251 | 245.3 | 235.3 | [8 empty] | 717.3 | 2.3 | 0.48 | 0.65
2 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | SARAI ROHILLA | 1141 | PNR119 | 1S-DL-YP-CTC-DPNR-1451-PNR119 | GALI NO.5 K.PAHAR:PL | TG-PNR119A-1 | 19502595 | 990 | 320 | 243 | 0.84 | 314 | 115 | 482 | 99 | 413 | 100 | 416 | 68 | 2019-06-15 16:00 | 18.4 | -96.4 | 484 | R | 105 | 96 | 100 | 9 |  |  | 4.9 | 95.1 | 423.23 | 448.23 | 428.23 | 430.53 | 296 | 271 | 271 | 288.3 | [12 empty] | 719.23 | 0.37 | 0.52 | 0.32
3 | 2019-06-01 | 2019-06-30 23:30 | PATEL NAGAR | SARAI ROHILLA | 1141 | PNR139 | 1S-DL-YP-CTC-DPNR-1451-PNR139 | POST OFFICE P/M GALI NO-2 | TG-PNR139A-1 | 19502809 | 400 | 120 | 243 | 0.84 | 335 | 120 | 524 | 111 | 477 | 103 | 442 | 71 | 2019-06-26 16:00 | 11.6 | -107.9 | 541 | R | 102 | 105 | 93 | 12 | 0.8 | 9.5 | 54.5 | 35.2 | 241.04 | 63 | 262.34 | 183.34 | 180.3 | 347.04 | 347.04 | 238.3 | 232.24 | 294.48 | 284.18 | 282.18 | 63.54 | 13 | 0.3 | 13.3 |  |  |  |  | 717.52 | 2.08 | 0.48 | 0.84