## Complete Report
MIS Report of Distribution Transformer - Jun19
Jun19 1210 KARKARDOOMA (Complete Report)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI002 | 1S-DL-YP-ETC-DJLM-2203-JHI002 | ESI HOSPITAL:ID | TG-JHI002A-1 | 19505836 | 400 | 120 | 241 | 0.99 | 81 | 2 | 10 | 18 | 76 | 61 | 265 | 229 | 2019-06-16 03:30 | 27 | 0.4 | 265 | B | 17 | 123 | 160 | 143 | 0.1 | 0.6 | 62.4 | 37 | 718.19 | 714.49 | 575.19 | 717.49 |  | 3.3 | 3.3 | 0.3 |  |  | 0.3 | [9 empty] | 718.19 | 1.41 | 0.43 | 0.2
2 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI007 | 1S-DL-YP-ETC-DJLM-2203-JHI007 | B BLOCK VIVEK VIHAR PH-1(MTD):ID | TG-JHI007A-1 | 19501645 | 990 | 320 | 239 | 0.98 | 739 | 240 | 1040 | 237 | 1026 | 262 | 1156 | 123 | 2019-06-12 | 164.1 | 51.5 | 1218 | B | 101 | 96 | 103 | 7 |  | 4.1 | 43.6 | 52.3 |  |  |  |  | 68 | 93.3 | 93.3 | 71.3 | 651.1 | 626.1 | 642.27 | 648.1 | 0.3 |  | 3.3 | [5 empty] | 719.4 | 0.2 | 0.71 | 0.75
3 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI007 | 1S-DL-YP-ETC-DJLM-2203-JHI007 | B BLOCK VIVEK VIHAR PH-1(MTD):ID | TG-JHI007A-2 | 19505581 | 990 | 320 | 242 | 0.99 | 541 | 112 | 477 | 120 | 485 | 309 | 1376 | 895 | 2019-06-16 03:30 | 137.3 | -21.8 | 1376 | B | 95 | 92 | 113 | 21 | 0.1 | 1.1 | 41.4 | 57.4 | 20.3 | 17 | 7 | 10 | 576.41 | 617.41 | 617.41 | 551.11 | 106 | 68.3 | 273.3 | 142 |  |  | 0.3 | [5 empty] | 703.11 | 16.49 | 0.62 | 0.55
4 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI038 | 1S-DL-YP-ETC-DJLM-2203-JHI038 | D-BLK VIVEK VIHAR PLM:PL | TG-JHI038A-1 | 19501553 | 990 | 320 | 239 | 0.98 | 565 | 232 | 1005 | 172 | 749 | 162 | 703 | 282 | 2019-06-11 23:30 | 102.3 | 39.7 | 1005 | R | 117 | 91 | 93 | 26 |  |  | 7.9 | 92.1 |  | 6.3 | 2 |  | 232.37 | 535.57 | 535.57 | 432.26 | 481.27 | 171.37 | 204.38 | 281.38 | [8 empty] | 714.04 | 5.56 | 0.67 | 0.57
5 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI038 | 1S-DL-YP-ETC-DJLM-2203-JHI038 | D-BLK VIVEK VIHAR PLM:PL | TG-JHI038A-2 | 19505944 | 630 | 200 | 245 | 0.97 | 546 | 91 | 376 | 306 | 1357 | 150 | 601 | 890 | 2019-06-16 03:30 | 197 | 31.8 | 1357 | Y | 88 | 94 | 118 | 30 | 0.1 |  | 9.2 | 90.6 |  |  |  |  | 284.36 | 283.21 | 283.21 | 190.59 | 416.56 | 417.41 | 520.38 | 510.03 |  |  | 83.3 | 0.3 |  | 0.3 |  |  | 701.32 | 18.28 | 0.55 | 0.87
6 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI039 | 1S-DL-YP-ETC-DJLM-2203-JHI039 | PRATAP KHAND:ID | TG-JHI039A-1 | 19506635 | 630 | 200 | 246 | 0.96 | 374 | 104 | 439 | 126 | 530 | 144 | 604 | 144 | 2019-06-12 | 107.2 | 29.6 | 664 | Y | 92 | 106 | 103 | 14 | 0.1 | 0.1 | 10.5 | 89.2 | 38.28 | 15 | 6 | 11.3 | 480.13 | 371.41 | 371.41 | 434.11 | 183.3 | 315.3 | 285.26 | 256.3 | [8 empty] | 702.11 | 17.49 | 0.63 | 0.59
7 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI039 | 1S-DL-YP-ETC-DJLM-2203-JHI039 | PRATAP KHAND:ID | TG-JHI039A-2 | 19505839 | 400 | 120 | 246 | 0.95 | 276 | 73 | 290 | 154 | 673 | 50 | 208 | 430 | 2019-06-16 03:30 | 94.2 | 20.8 | 673 | Y | 101 | 94 | 105 | 11 | 0.1 | 0.4 | 35.5 | 64 | 59.47 | 29.3 | 3.3 | 5.3 | 373.58 | 512.1 | 512.1 | 493.1 | 267.55 | 160 | 231.3 | 203.3 | 0.3 |  |  |  |  | 0.3 |  |  | 702.1 | 17.5 | 0.52 | 0.69
8 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI039 | 1S-DL-YP-ETC-DJLM-2203-JHI039 | PRATAP KHAND:ID | TG-JHI039A-3 | 19506493 | 630 | 200 | 246 | 0.96 | 496 | 183 | 754 | 176 | 728 | 137 | 567 | 175 | 2019-06-30 00:30 | 135 | 41.4 | 811 | R | 111 | 95 | 94 | 17 |  | 0.1 | 21.1 | 78.8 |  | 2 |  |  | 205.45 | 312.15 | 312.15 | 259.45 | 459 | 385.3 | 408.4 | 442 | 37 | 2 | [6 empty] | 701.45 | 18.15 | 0.59 | 0.79
9 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI040 | 1S-DL-YP-ETC-DJLM-2203-JHI040 | POLICE STATION VIVEK VIHAR:ID | TG-JHI040A-1 | 19501612 | 630 | 200 | 241 | 0.98 | 119 | 35 | 149 | 29 | 127 | 56 | 242 | 105 | 2019-06-02 22:30 | 18.9 | 2.3 | 244 | B | 88 | 80 | 132 | 52 |  | 0.1 | 17.9 | 82 | 719.15 | 719.15 | 628.15 | 719.15 | [16 empty] | 719.15 | 0.45 | 0.6 | 0.19
10 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI041 | 1S-DL-YP-ETC-DJLM-2203-JHI041 | 928 QTR. VIVEK VHR-1(MOTHER DAIRY):ID) | TG-JHI041A-1 | 19502872 | 630 | 200 | 240 | 0.97 | 340 | 105 | 461 | 95 | 412 | 140 | 615 | 184 | 2019-06-30 23:30 | 63 | 18.9 | 645 | B | 97 | 88 | 115 | 27 |  |  | 4.9 | 95.1 | 135.27 | 198.27 | 91.29 | 119.27 | 495.51 | 492.5 | 492.5 | 484.21 | 88.29 | 28.3 | 207.52 | 115.59 | [8 empty] | 719.47 | 0.13 | 0.54 | 0.54
11 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI042 | 1S-DL-YP-ETC-DJLM-2203-JHI042 | 928 QTR. VIVEK VHR-2(SHIV MANDIR):ID | TG-JHI042A-1 | 19503596 | 630 | 200 | 239 | 0.97 | 434 | 192 | 833 | 127 | 551 | 114 | 492 | 315 | 2019-06-12 00:30 | 79.6 | 16.1 | 833 | R | 133 | 84 | 83 | 50 |  |  | 6.7 | 93.3 | 0.3 | 69.38 | 65.55 | 9 | 226.28 | 507.18 | 507.18 | 460.26 | 476.54 | 140.56 | 139.28 | 248.26 | 14 | [7 empty] | 717.52 | 2.08 | 0.54 | 0.69
12 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI042 | 1S-DL-YP-ETC-DJLM-2203-JHI042 | 928 QTR. VIVEK VHR-2(SHIV MANDIR):ID | TG-JHI042A-2 | 19501611 | 630 | 200 | 238 | 0.97 | 494 | 185 | 801 | 168 | 726 | 141 | 608 | 168 | 2019-06-12 00:30 | 104.4 | 31.7 | 804 | R | 112 | 102 | 87 | 25 |  |  | 10.2 | 89.8 | 4.3 | 6.3 | 24 | 7.3 | 269.3 | 347.58 | 347.58 | 367.28 | 423.52 | 362.24 | 242.25 | 342.54 | 20 | 1 | [6 empty] | 717.52 | 2.08 | 0.54 | 0.78
13 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI047 | 1S-DL-YP-ETC-DJLM-2203-JHI047 | BATRA S/STN JLM COL.:K | TG-JHI047A-1 | 19506733 | 990 | 320 | 246 | 0.97 | 636 | 322 | 1398 | 167 | 665 | 147 | 615 | 760 | 2019-06-16 03:00 | 207 | 36.8 | 1398 | R | 95 | 114 | 91 | 23 | 0.2 | 0.6 | 14.8 | 84.4 | 26 | 21.23 | 108.23 | 29.53 | 529.11 | 419.18 | 419.18 | 490.18 | 138.51 | 251.51 | 143.21 | 174.21 | 0.3 | 2 | [6 empty] | 694.32 | 25.28 | 0.52 | 0.64
14 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI047 | 1S-DL-YP-ETC-DJLM-2203-JHI047 | BATRA S/STN JLM COL.:K | TG-JHI047A-2 | 19503691 | 990 | 320 | 245 | 0.97 | 646 | 182 | 736 | 277 | 1117 | 187 | 756 | 372 | 2019-06-03 01:30 | 142 | 48.6 | 1189 | Y | 84 | 125 | 91 | 41 |  | 0.4 | 26.6 | 73 | 6 |  | 5.3 | 0.3 | 568.4 | 204.48 | 204.48 | 406.4 | 139.28 | 498.24 | 211.28 | 306.58 |  | 10.56 | [6 empty] | 714.08 | 5.52 | 0.6 | 0.65
15 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI047 | 1S-DL-YP-ETC-DJLM-2203-JHI047 | BATRA S/STN JLM COL.:K | TG-JHI047A-3 | 19505367 | 630 | 200 | 243 | 0.96 | 287 | 115 | 494 | 83 | 356 | 89 | 380 | 128 | 2019-06-11 | 73 | 21 | 508 | Y | 108 | 97 | 94 | 14 | 31.5 | 0.1 | 13.7 | 54.6 | 149.57 | 232.24 | 207.13 | 193.25 | 467.48 | 465.39 | 465.39 | 488.08 | 87.18 | 7 | 16.18 | 23.3 | [8 empty] | 716.01 | 3.59 | 0.55 | 0.46
16 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI061 | 1S-DL-YP-ETC-DJLM-2203-JHI061 | C-BLK VIVEK VIHAR(PARK WALA):PG | TG-JHI061A-1 | 19503696 | 990 | 320 | 241 | 0.97 | 502 | 182 | 749 | 117 | 479 | 203 | 828 | 318 | 2019-06-13 23:30 | 100.8 | 25 | 950 | B | 107 | 72 | 121 | 49 |  | 0.1 | 18 | 81.9 | 52.3 | 384.16 | 42.28 | 103.26 | 568.59 | 331.13 | 331.13 | 533.03 | 94 |  | 203.56 | 79 | [8 empty] | 715.29 | 4.31 | 0.56 | 0.51
17 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI061 | 1S-DL-YP-ETC-DJLM-2203-JHI061 | C-BLK VIVEK VIHAR(PARK WALA):PG | TG-JHI061A-2 | 19504197 | 630 | 200 | 245 | 0.97 | 572 | 196 | 823 | 203 | 851 | 173 | 716 | 123 | 2019-06-29 23:00 | 118.2 | 26.2 | 859 | R | 97 | 106 | 97 | 9 |  |  | 13.5 | 86.5 | 1.3 | 9 | 5.3 | 3 | 307.56 | 236.26 | 236.26 | 290.26 | 393.37 | 452.37 | 357.37 | 408.37 | 14 | 19 | 25.3 | 15 |  |  |  |  | 717.03 | 2.57 | 0.52 | 0.91
18 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI062 | 1S-DL-YP-ETC-DJLM-2203-JHI062 | JANTA QTR. VIVEK VIHAR:PL | TG-JHI062A-1 | 19501614 | 630 | 200 | 241 | 0.97 | 584 | 202 | 915 | 172 | 779 | 211 | 963 | 165 | 2019-06-30 23:30 | 121.4 | 36.8 | 1065 | B | 108 | 74 | 118 | 44 | 0.1 |  | 5.4 | 94.6 |  | 4.3 |  |  | 67.58 | 397.39 | 397.39 | 113.11 | 547.15 | 277 | 524.15 | 528.58 | 64.56 | 2.3 | 112.26 | 39.3 | 1.3 |  | 16 |  | 684.35 | 35.25 | 0.58 | 0.93
19 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI062 | 1S-DL-YP-ETC-DJLM-2203-JHI062 | JANTA QTR. VIVEK VIHAR:PL | TG-JHI062A-2 | 19505586 | 630 | 200 | 246 | 0.98 | 312 | 64 | 265 | 88 | 365 | 160 | 676 | 370 | 2019-06-12 | 82.2 | 17 | 676 | B | 75 | 96 | 128 | 53 | 0.1 | 0.3 | 24.3 | 75.3 | 349.31 | 133.58 | 34.3 | 113.58 | 349 | 515.33 | 515.33 | 507.38 | 1.3 | 50.3 | 219.25 | 78.25 | [8 empty] | 700.01 | 19.59 | 0.56 | 0.49
20 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI063 | 1S-DL-YP-ETC-DJLM-2203-JHI063 | MAHILA COLLEGE VIVEK VIHAR:PL | TG-JHI063A-1 | 19503019 | 990 | 320 | 239 | 0.93 | 713 | 230 | 949 | 234 | 975 | 249 | 1044 | 85 | 2019-06-03 03:30 | 167.8 | 53.7 | 1044 | B | 102 | 91 | 108 | 17 |  |  | 22 | 78 | 6.2 | 23.12 | 8.59 | 10.49 | 455.58 | 539.13 | 539.13 | 475.29 | 254.16 | 154.09 | 304.16 | 230.16 | [8 empty] | 716.34 | 3.26 | 0.5 | 0.72
21 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI063 | 1S-DL-YP-ETC-DJLM-2203-JHI063 | MAHILA COLLEGE VIVEK VIHAR:PL | TG-JHI063A-2 | 19505797 | 630 | 200 | 245 | 0.97 | 557 | 169 | 717 | 158 | 676 | 230 | 989 | 294 | 2019-06-30 23:30 | 119.2 | 29.8 | 989 | B | 90 | 93 | 116 | 26 | 0.3 | 0.1 | 41.4 | 58.2 | 5 |  |  |  | 321.44 | 258.33 | 258.33 | 232.44 | 361.04 | 432.43 | 451.32 | 436.34 | 4.58 | 2 | 95.56 | 23.58 | 0.3 |  | 6.3 |  | 693.16 | 26.44 | 0.55 | 0.88
22 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI064 | 1S-DL-YP-ETC-DJLM-2203-JHI064 | SHIVA KHAND:PL | TG-JHI064A-1 | 19501632 | 630 | 200 | 244 | 0.97 | 545 | 178 | 744 | 145 | 605 | 222 | 946 | 296 | 2019-06-30 | 103.5 | 35.9 | 954 | B | 97 | 87 | 115 | 28 |  | 0.9 | 33.2 | 65.9 | 1.3 | 10.3 | 1 | 0.3 | 281.55 | 361.55 | 361.55 | 268.55 | 432.53 | 346.53 | 447.54 | 441.53 | 3 |  | 83.59 | 8 |  |  | 3 |  | 719.18 | 0.42 | 0.55 | 0.86
23 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI064 | 1S-DL-YP-ETC-DJLM-2203-JHI064 | SHIVA KHAND:PL | TG-JHI064A-2 | 19501038 | 400 | 120 | 238 | 0.96 | 212 | 76 | 338 | 76 | 338 | 60 | 265 | 73 | 2019-06-11 | 53.3 | 12.1 | 354 | R | 106 | 105 | 89 | 17 |  |  | 34.1 | 65.9 | 77.57 | 62.59 | 168.36 | 74.14 | 443 | 456.28 | 456.28 | 476.13 | 197.59 | 199.29 | 97.29 | 168.29 | [8 empty] | 718.56 | 1.04 | 0.59 | 0.53
24 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI069 | 1S-DL-YP-ETC-DJLM-2203-JHI069 | D-BLK VIVEK VIHAR:ID | TG-JHI069A-1 | 19505310 | 990 | 320 | 240 | 0.99 | 496 | 147 | 612 | 161 | 680 | 188 | 786 | 152 | 2019-06-02 23:30 | 124.2 | -3.2 | 1008 | Y | 85 | 93 | 122 | 37 | 0.1 | 0.6 | 17.1 | 82.1 | 210.52 | 176.09 | 40 | 106.23 | 486.16 | 509.29 | 509.29 | 561.15 | 4.3 | 16 | 177.48 | 34 | [8 empty] | 701.38 | 18.22 | 0.54 | 0.5
25 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI069 | 1S-DL-YP-ETC-DJLM-2203-JHI069 | D-BLK VIVEK VIHAR:ID | TG-JHI069A-2 | 19501541 | 990 | 320 | 233 | 0.98 | 525 | 161 | 682 | 190 | 809 | 174 | 744 | 110 | 2019-06-13 23:00 | 101.6 | 33.9 | 915 | Y | 92 | 111 | 97 | 19 |  | 0.1 | 46.5 | 53.4 | 0.3 |  | 2 |  | 551.01 | 277.53 | 277.53 | 419.47 | 163.48 | 437.26 | 261.31 | 295.32 | [8 empty] | 715.19 | 4.41 | 0.73 | 0.53
26 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI069 | 1S-DL-YP-ETC-DJLM-2203-JHI069 | D-BLK VIVEK VIHAR:ID | TG-JHI069A-3 | 19505455 | 630 | 200 | 244 | 0.97 | 407 | 136 | 600 | 83 | 363 | 188 | 854 | 425 | 2019-06-30 23:00 | 108.2 | 25.6 | 854 | B | 123 | 81 | 96 | 42 | 0.2 | 0.1 | 11.7 | 87.9 |  | 1.3 | 5.3 |  | 124 | 614.55 | 614.55 | 329.3 | 576.43 | 85.18 | 313.43 | 372.13 | 1 |  | 0.3 | [5 empty] | 701.43 | 18.17 | 0.64 | 0.65
27 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI070 | 1S-DL-YP-ETC-DJLM-2203-JHI070 | ABUDANA VIVEK VIHAR:PL | TG-JHI070A-1 | 19501619 | 990 | 320 | 241 | 0.97 | 593 | 217 | 891 | 218 | 919 | 158 | 658 | 249 | 2019-06-14 | 131 | 37.5 | 971 | R | 103 | 113 | 84 | 29 | 8.6 | 83.5 | 7.6 | 0.2 | 2.12 | 0.3 | 10.43 | 1.12 | 438.21 | 325.33 | 325.33 | 479.51 | 274.39 | 389.09 | 48.39 | 234.09 | [8 empty] | 717.12 | 2.48 | 0.62 | 0.6
28 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI070 | 1S-DL-YP-ETC-DJLM-2203-JHI070 | ABUDANA VIVEK VIHAR:PL | TG-JHI070A-2 | 19504307 | 630 | 200 | 245 | 0.98 | 406 | 128 | 542 | 140 | 595 | 138 | 587 | 49 | 2019-06-12 | 69.5 | 12 | 628 | B | 99 | 99 | 102 | 3 |  |  | 1 | 99 | 2 | 4.3 | 2.3 | 1.3 | 428.51 | 444.12 | 444.12 | 425.42 | 286.3 | 268.39 | 320 | 290.09 | [8 empty] | 717.21 | 2.39 | 0.61 | 0.64
29 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI071 | 1S-DL-YP-ETC-DJLM-2203-JHI071 | VIVEK VIHAR SUPER BAZAR:PL | TG-JHI071A-1 | 19506230 | 990 | 320 | 233 | 0.99 | 777 | 201 | 910 | 193 | 870 | 384 | 1807 | 917 | 2019-06-30 22:30 | 231.7 | 13.1 | 1807 | B | 87 | 95 | 118 | 31 | 0.6 | 1.7 | 53.2 | 44.5 | 10 | 8 | 0.3 | 1.3 | 411.26 | 355.56 | 355.56 | 309.56 | 280.06 | 337.06 | 509.06 | 390.06 |  |  | 33 |  |  | 0.3 | 1 |  | 701.32 | 18.28 | 0.57 | 0.79
30 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI072 | 1S-DL-YP-ETC-DJLM-2203-JHI072 | A-BLK DSIDC JLM COLONY:ID | TG-JHI072A-1 | 19504212 | 400 | 120 | 246 | 0.97 | 219 | 91 | 382 | 78 | 333 | 50 | 211 | 153 | 2019-06-11 00:30 | 54.4 | 14.4 | 426 | R | 128 | 99 | 73 | 55 |  |  | 10.5 | 89.5 | 7.3 | 54 | 211.15 | 34 | 356.24 | 516.48 | 516.48 | 542.18 | 355.24 | 148.3 | 0.3 | 143 | [8 empty] | 719.18 | 0.42 | 0.59 | 0.55
31 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI073 | 1S-DL-YP-ETC-DJLM-2203-JHI073 | B-BLK DSIDC JLM COLONY:ID | TG-JHI073A-1 | 19505798 | 400 | 120 | 240 | 0.97 | 228 | 51 | 218 | 94 | 410 | 84 | 362 | 172 | 2019-06-12 | 44.9 | 12.2 | 420 | Y | 76 | 120 | 104 | 44 | 0.1 | 0.6 | 33.9 | 65.4 | 227.15 | 27.3 | 113.45 | 65 | 484.54 | 432.14 | 432.14 | 507.09 | 7.3 | 259.55 | 195.3 | 147.3 | [8 empty] | 719.39 | 0.21 | 0.55 | 0.57
32 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI074 | 1S-DL-YP-ETC-DJLM-2203-JHI074 | C-BLK DSIDC JLM COLONY:ID | TG-JHI074A-1 | 19505838 | 400 | 120 | 244 | 0.97 | 402 | 144 | 601 | 120 | 496 | 138 | 574 | 94 | 2019-06-02 00:30 | 93.4 | 18.2 | 685 | R | 110 | 94 | 97 | 16 | 0.1 | 0.1 | 8.6 | 91.2 |  |  |  |  | 30.58 | 125.22 | 125.22 | 67.28 | 556.51 | 551.27 | 510.37 | 567.21 | 107 | 41 | 71.3 | 82.3 | 23 |  | 1.3 | 0.3 | 717.49 | 2.11 | 0.57 | 1
33 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI074 | 1S-DL-YP-ETC-DJLM-2203-JHI074 | C-BLK DSIDC JLM COLONY:ID | TG-JHI074A-2 | 19506228 | 400 | 120 | 246 | 0.97 | 191 | 41 | 167 | 82 | 337 | 68 | 277 | 150 | 2019-06-03 | 40.4 | 8.9 | 365 | Y | 78 | 125 | 97 | 47 | 0.1 |  | 4.6 | 95.3 | 426.07 | 159.42 | 287.28 | 277.07 | 289.13 | 389.1 | 389.1 | 386.43 | 2.3 | 168.58 | 29 | 54 | [8 empty] | 717.5 | 2.1 | 0.51 | 0.48
34 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI075 | 1S-DL-YP-ETC-DJLM-2203-JHI075 | D-BLK DSIDC JLM COLONY:ID | TG-JHI075A-1 | 19501597 | 400 | 120 | 247 | 0.92 | 93 | 31 | 126 | 27 | 109 | 35 | 144 | 30 | 2019-06-15 16:00 | 47.5 | -0.3 | 168 | R | 117 | 68 | 116 | 49 |  |  | 65.9 | 34.1 | 657.1 | 713.38 | 679.08 | 705.38 | 60.58 | 4.3 | 4.3 | 12.3 | [12 empty] | 718.08 | 1.52 | 0.41 | 0.23
35 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI076 | 1S-DL-YP-ETC-DJLM-2203-JHI076 | E-BLK DSIDC JLM COLONY:ID | TG-JHI076A-1 | 19504700 | 630 | 200 | 240 | 0.98 | 286 | 125 | 557 | 83 | 367 | 77 | 338 | 206 | 2019-06-27 | 46 | 9.7 | 565 | R | 123 | 90 | 87 | 36 |  | 0.3 | 80.8 | 18.9 | 116.58 | 376.44 | 346.1 | 268.15 | 492.11 | 335.25 | 335.25 | 441.54 | 110.3 | 7.3 |  | 9.3 | [8 empty] | 719.39 | 0.21 | 0.52 | 0.45
36 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI076 | 1S-DL-YP-ETC-DJLM-2203-JHI076 | E-BLK DSIDC JLM COLONY:ID | TG-JHI076A-2 | 19506227 | 400 | 120 | 247 | 0.98 | 167 | 50 | 216 | 32 | 139 | 85 | 365 | 199 | 2019-06-10 23:30 | 28.7 | -16.1 | 365 | B | 100 | 71 | 129 | 58 | 0.1 | 0.2 | 5.7 | 94 | 222.45 | 433.1 | 75 | 215.45 | 322.55 | 118.3 | 118.3 | 333.55 | 6 |  | 90 | 2 | [8 empty] | 551.4 | 0.2 | 0.55 | 0.42
37 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI078 | 1S-DL-YP-ETC-DJLM-2203-JHI078 | GOBIND KHAND:PG | TG-JHI078A-1 | 19503614 | 990 | 320 | 240 | 0.97 | 670 | 240 | 1050 | 187 | 809 | 243 | 1066 | 249 | 2019-06-11 00:30 | 130.3 | 42 | 1115 | B | 103 | 86 | 111 | 25 |  | 0.1 | 9.4 | 90.6 | 33.28 | 45.23 | 11.28 | 21.55 | 425.41 | 520.11 | 520.11 | 456.14 | 259.55 | 153.3 | 340.55 | 240.55 | [8 empty] | 719.04 | 0.56 | 0.55 | 0.68
38 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI079 | 1S-DL-YP-ETC-DJLM-2203-JHI079 | ROAD NO.56 VIVEK VIHAR:PM | TG-JHI079A-1 | 19506732 | 100 | 40 | 245 | 0.89 | 50 | 17 | 71 | 20 | 83 | 13 | 52 | 27 | 2019-06-18 12:00 | 32.7 | 0.2 | 87 | R | 110 | 105 | 85 | 25 |  | 0.4 | 41.2 | 58.3 | 52.09 | 16.37 | 93.07 | 56.07 | 385.23 | 518.25 | 518.25 | 543.55 | 263.3 | 166 | 20 | 101 | [8 empty] | 701.02 | 18.58 | 0.67 | 0.5
39 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI087 | 1S-DL-YP-ETC-DJLM-2203-JHI087 | PRATAP KHAND EXTN:PL | TG-JHI087A-1 | 19504160 | 630 | 200 | 240 | 0.97 | 443 | 189 | 865 | 132 | 600 | 122 | 555 | 291 | 2019-06-30 23:30 | 90.6 | 32.2 | 865 | R | 124 | 87 | 88 | 37 |  | 0.1 | 58.8 | 41.1 |  | 17.3 | 19 | 2 | 230.1 | 472.04 | 472.04 | 379.37 | 463.23 | 229.59 | 239 | 337.56 | 26 | [7 empty] | 719.33 | 0.27 | 0.58 | 0.7
40 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI088 | 1S-DL-YP-ETC-DJLM-2203-JHI088 | E-BLK JHILMIL COLONY:ID | TG-JHI088A-1 | 19504400 | 630 | 200 | 239 | 0.97 | 356 | 107 | 453 | 125 | 538 | 124 | 531 | 82 | 2019-06-29 23:30 | 73.6 | 20.2 | 589 | B | 88 | 98 | 114 | 26 |  | 0.2 | 78.2 | 21.6 | 169.15 | 50.3 | 16.3 | 46.28 | 422.24 | 527.39 | 527.39 | 510.41 | 128 | 141.3 | 258.3 | 162.3 | [8 empty] | 719.39 | 0.21 | 0.57 | 0.56
41 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI088 | 1S-DL-YP-ETC-DJLM-2203-JHI088 | E-BLK JHILMIL COLONY:ID | TG-JHI088A-2 | 19503615 | 990 | 320 | 246 | 0.96 | 673 | 194 | 798 | 235 | 984 | 243 | 1004 | 197 | 2019-06-30 00:30 | 156 | 61.1 | 1042 | Y | 90 | 104 | 106 | 16 | 0.1 | 1 | 96.9 | 2.1 |  |  |  |  | 365.14 | 248.45 | 248.45 | 289.45 | 354.25 | 470.54 | 498.24 | 429.54 | [8 empty] | 719.39 | 0.21 | 0.65 | 0.68
42 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI099 | 1S-DL-YP-ETC-DJLM-2203-JHI099 | SEWYAM SEWA SANSTHAN VIVEK VIHAR | TG-JHI099A-1 | 19504220 | 990 | 320 | 246 | 0.97 | 745 | 275 | 1215 | 193 | 845 | 276 | 1212 | 368 | 2019-06-30 23:30 | 137.6 | 53 | 1215 | R | 104 | 86 | 110 | 24 |  | 2.4 | 91.7 | 5.9 | 4.3 | 15.3 | 0.3 | 3 | 360.41 | 463.33 | 463.33 | 372.11 | 345.17 | 237.25 | 428.08 | 341.17 | 6 |  | 8 | [5 empty] | 716.28 | 3.32 | 0.56 | 0.75
43 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI100 | 1S-DL-YP-ETC-DJLM-2203-JHI100 | MTNL QTR. VIVEK VHR-1:ID | TG-JHI100A-1 | 19501615 | 630 | 200 | 240 | 0.98 | 85 | 31 | 129 | 17 | 71 | 37 | 153 | 73 | 2019-06-03 | 12 | 2.8 | 157 | B | 109 | 68 | 123 | 55 |  |  | 1.3 | 98.7 | 717.02 | 717.02 | 717.02 | 717.02 | [16 empty] | 717.02 | 2.58 | 0.52 | 0.13
44 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI100 | 1S-DL-YP-ETC-DJLM-2203-JHI100 | MTNL QTR. VIVEK VHR-1:ID | TG-JHI100A-2 | 19506494 | 630 | 200 | 242 | 0.97 | 81 | 30 | 129 | 23 | 97 | 28 | 113 | 27 | 2019-06-29 23:00 | 24.6 | 3.8 | 140 | R | 116 | 88 | 96 | 28 | 100 |  |  |  | 717.02 | 717.02 | 717.02 | 717.02 | [16 empty] | 717.02 | 2.58 | 0.48 | 0.13
45 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI101 | 1S-DL-YP-ETC-DJLM-2203-JHI101 | MTNL QTR. VIVEK VHR-2:ID | TG-JHI101A-1 | 19503448 | 630 | 200 | 245 | 0.96 | 270 | 148 | 617 | 66 | 275 | 55 | 227 | 368 | 2019-06-05 23:30 | 63 | 17 | 669 | R | 162 | 73 | 65 | 97 |  | 0.1 | 34.6 | 65.3 | 31 | 504.58 | 541.33 | 276.28 | 401.28 | 212.05 | 212.05 | 423.05 | 284.35 |  | 9.3 | 17.3 | [8 empty] | 717.03 | 2.57 | 0.56 | 0.43
46 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI101 | 1S-DL-YP-ETC-DJLM-2203-JHI101 | MTNL QTR. VIVEK VHR-2:ID | TG-JHI101A-2 | 19505837 | 630 | 200 | 242 | 0.97 | 99 | 41 | 174 | 29 | 123 | 30 | 126 | 50 | 2019-06-02 23:00 | 24 | 4.4 | 183 | Y | 105 | 97 | 98 | 8 | 0.1 | 0.1 | 6.1 | 93.7 | 700.32 | 700.32 | 700.32 | 700.32 | [16 empty] | 700.32 | 19.28 | 0.51 | 0.16
47 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI102 | 1S-DL-YP-ETC-DJLM-2203-JHI102 | A-BLK VIVEK VIHAR NURSERY WALA:PM | TG-JHI102A-1 | 19505475 | 990 | 320 | 247 | 0.97 | 705 | 373 | 1642 | 171 | 683 | 161 | 675 | 963 | 2019-06-16 03:00 | 289.9 | 26.6 | 1642 | R | 102 | 95 | 103 | 8 | 0.1 | 0.3 | 17.8 | 81.8 | 15 | 77.28 | 18 | 20.3 | 450.42 | 399.47 | 399.47 | 453.15 | 236.3 | 225.27 | 250.27 | 228.57 |  |  |  |  | 0.3 |  |  |  | 702.42 | 17.18 | 0.51 | 0.71
48 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI102 | 1S-DL-YP-ETC-DJLM-2203-JHI102 | A-BLK VIVEK VIHAR NURSERY WALA:PM | TG-JHI102A-2 | 19506229 | 400 | 120 | 248 | 0.98 | 171 | 57 | 230 | 55 | 222 | 59 | 238 | 15 | 2019-06-03 00:30 | 55.7 | 3.5 | 390 | Y | 102 | 111 | 87 | 24 | 0.1 |  | 8.7 | 91.2 | 256.15 | 148.58 | 401.45 | 254.45 | 427.56 | 533.43 | 533.43 | 442.26 | 18.3 | 20 | 13.3 | 5.3 | [8 empty] | 702.41 | 17.19 | 0.55 | 0.43
49 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI126 | 1S-DL-YP-ETC-DJLM-2203-JHI126 | A-BLK VIVEK VIHAR PH-2 | TG-JHI126A-1 | 19505009 | 990 | 320 | 245 | 0.97 | 811 | 265 | 1115 | 279 | 1170 | 266 | 1130 | 49 | 2019-06-29 23:30 | 157.5 | 51.5 | 1263 | B | 90 | 99 | 111 | 21 |  | 0.1 | 37.9 | 62 |  |  |  |  | 226.42 | 134.59 | 134.59 | 111.46 | 491.54 | 583.37 | 626.2 | 606.5 | 1 | 1 | 33.3 | 1 |  |  |  |  | 719.36 | 0.24 | 0.62 | 0.82
50 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI126 | 1S-DL-YP-ETC-DJLM-2203-JHI126 | A-BLK VIVEK VIHAR PH-2 | TG-JHI126A-2 | 19505428 | 400 | 120 | 244.0402 | 0.97472 | 298.0303 | 115.7397 | 483.8618 | 105.5294 | 435.4781 | 76.7612 | 319.0406 | 146.739 | 2019-06-13 23:00 | [15 empty] | 2.5 |  |  |  | 318 |  |  |  | 398.5 |  |  |  | 0 |  |  |  | 0 | 719 |  | 0.58964 | 0.74508
51 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI135 | 1S-DL-YP-ETC-DJLM-2203-JHI135 | I.T.I. STAFF QUATERS | TG-JHI135A-1 | 19504050 | 400 | 120 | 249 | 0.99 | 46 | 9 | 37 | 20 | 85 | 17 | 72 | 43 | 2019-06-11 23:30 | 7.5 | 1.1 | 94 | Y | 70 | 123 | 107 | 53 | 0.7 | 1.3 | 16.6 | 81.4 | 719.41 | 719.41 | 719.41 | 719.41 | [16 empty] | 719.41 | 0.19 | 0.54 | 0.12
52 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI135 | 1S-DL-YP-ETC-DJLM-2203-JHI135 | I.T.I. STAFF QUATERS | TG-JHI135A-2 | 19504196 | 400 | 120 | 248 | 0.99 | 35 | 10 | 41 | 8 | 34 | 17 | 69 | 32 | 2019-06-02 23:00 | 4.1 | 0.3 | 70 | B | 88 | 63 | 149 | 86 |  |  | 71 | 29 | 719.41 | 719.41 | 719.41 | 719.41 | [16 empty] | 719.41 | 0.19 | 0.47 | 0.09
53 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI145 | 1S-DL-YP-ETC-DJLM-2203-JHI145 | D-Block Vivek Vihar Nalla PSS | TG-JHI145A-1 | 19506259 | 990 | 320 | 246 | 0.97 | 513 | 110 | 456 | 124 | 492 | 279 | 1216 | 743 | 2019-06-16 03:00 | 171.2 | 37.8 | 1216 | B | 93 | 101 | 106 | 13 | 0.1 | 0.2 | 6.8 | 92.8 | 20 | 3.31 | 7.01 | 5.01 | 588.51 | 554.5 | 554.5 | 569.5 | 94 | 144.3 | 202 | 128 |  |  | 0.3 | [5 empty] | 702.51 | 17.09 | 0.66 | 0.52
54 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | VNG002 | 1S-DL-YP-ETC-DJLM-2201-VNG002 | YOJNA VIHAR C-BLOCK:ID | TG-VNG002A-1 | 19504191 | 990 | 320 | 246 | 0.97 | 920 | 287 | 1237 | 327 | 1408 | 305 | 1317 | 148 | 2019-06-11 23:00 | 186.9 | 58.9 | 1408 | Y | 91 | 99 | 110 | 19 |  |  | 19.8 | 80.2 |  |  |  |  | 131.45 | 108.58 | 108.58 | 67.28 | 570.13 | 536 | 626.28 | 606 | 17.3 | 74.3 | 70 | 46 |  |  |  |  | 719.28 | 0.32 | 0.61 | 0.93
55 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | VNG003 | 1S-DL-YP-ETC-DJLM-2201-VNG003 | SAVITA VIHAR:ID | TG-VNG003A-1 | 19506236 | 990 | 320 | 246 | 0.96 | 332 | 95 | 382 | 70 | 293 | 167 | 727 | 397 | 2019-06-16 03:00 | 128.3 | 17.9 | 727 | B | 112 | 100 | 88 | 24 | 0.1 | 0.2 | 5.5 | 94.1 | 317.56 | 382.49 | 495.43 | 382.17 | 386.23 | 321.3 | 321.3 | 322.02 |  |  | 0.3 | [9 empty] | 704.19 | 15.41 | 0.6 | 0.34
56 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | VNG003 | 1S-DL-YP-ETC-DJLM-2201-VNG003 | SAVITA VIHAR:ID | TG-VNG003A-2 | 19504746 | 990 | 320 | 245 | 0.97 | 618 | 165 | 687 | 209 | 870 | 245 | 1018 | 288 | 2019-06-11 16:00 | 138.4 | 48.6 | 1068 | B | 87 | 103 | 109 | 22 |  |  | 2.6 | 97.4 | 11.3 | 2 | 4.3 | 1 | 575.19 | 404.16 | 404.16 | 431.53 | 131 | 311.33 | 380.56 | 284.56 | [8 empty] | 717.49 | 2.11 | 0.61 | 0.62
57 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | VNG004 | 1S-DL-YP-ETC-DJLM-2201-VNG004 | VIGYAN VIHAR:ID | TG-VNG004A-1 | 19502999 | 990 | 320 | 246 | 0.98 | 309 | 110 | 459 | 86 | 359 | 113 | 479 | 112 | 2019-06-29 23:30 | 72.1 | 8.8 | 520 | R | 107 | 92 | 102 | 15 |  |  | 0.6 | 99.4 | 261.28 | 434.24 | 326.26 | 321.58 | 458.26 | 285.3 | 285.3 | 397.56 | [12 empty] | 719.54 | 0.06 | 0.66 | 0.31
58 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | VNG004 | 1S-DL-YP-ETC-DJLM-2201-VNG004 | VIGYAN VIHAR:ID | TG-VNG004A-2 | 19501506 | 990 | 320 | 245 | 0.97 | 733 | 285 | 1221 | 195 | 840 | 253 | 1073 | 332 | 2019-06-30 23:30 | 132.5 | 45.6 | 1268 | R | 118 | 84 | 99 | 34 |  | 0.1 | 31.8 | 68.1 |  | 10.3 |  |  | 124.58 | 452.26 | 452.26 | 288.26 | 583.26 | 256.58 | 405.58 | 431.28 | 11.3 | [7 empty] | 719.54 | 0.06 | 0.6 | 0.74
59 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | VNG039 | 1S-DL-YP-ETC-DJLM-2201-VNG039 | YOJANA VIHAR:ID | TG-VNG039A-1 | 19505943 | 990 | 320 | 240 | 0.97 | 722 | 137 | 586 | 190 | 778 | 395 | 1798 | 1128 | 2019-06-16 03:30 | 241.3 | 42.6 | 1798 | B | 86 | 111 | 104 | 25 | 0.1 | 0.4 | 9.9 | 89.6 | 7 |  | 1 |  | 473.32 | 267.01 | 267.01 | 351.25 | 223.25 | 429.26 | 374.56 | 352.32 |  | 7.3 |  |  |  |  | 0.3 |  | 703.57 | 16.03 | 0.57 | 0.73
60 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | VNG039 | 1S-DL-YP-ETC-DJLM-2201-VNG039 | YOJANA VIHAR:ID | TG-VNG039A-2 | 19506752 | 990 | 320 | 242 | 0.98 | 453 | 92 | 394 | 110 | 446 | 251 | 1115 | 696 | 2019-06-16 03:00 | 136.3 | 14.7 | 1115 | B | 88 | 102 | 110 | 22 | 0.1 | 0.2 | 17.7 | 82 | 303.25 | 144.57 | 82.58 | 145.55 | 400.32 | 538 | 538 | 549.02 |  | 21 | 50.3 | 9 | [8 empty] | 703.57 | 16.03 | 0.56 | 0.46
61 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | VNG047 | 1S-DL-YP-ETC-DJLM-2201-VNG047 | SURAJ MAL VIHAR D-BLOCK:ID | TG-VNG047A-1 | 19501643 | 990 | 320 | 237 | 0.98 | 692 | 205 | 882 | 278 | 1204 | 209 | 902 | 313 | 2019-06-11 23:00 | 117.8 | 7.4 | 1204 | Y | 96 | 107 | 98 | 11 |  |  | 0.8 | 99.2 | 3.3 | 3 | 15 | 2 | 412.26 | 307.52 | 307.52 | 373.26 | 303.01 | 406.05 | 319.02 | 343.31 |  | 2 | [6 empty] | 718.57 | 1.03 | 0.59 | 0.7
62 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | VNG047 | 1S-DL-YP-ETC-DJLM-2201-VNG047 | SURAJ MAL VIHAR D-BLOCK:ID | TG-VNG047A-2 | 19505953 | 990 | 320 | 246 | 0.98 | 493 | 171 | 749 | 130 | 562 | 192 | 834 | 241 | 2019-06-11 | 107.2 | 26.9 | 834 | B | 104 | 77 | 119 | 42 | 0.1 | 0.2 | 43.2 | 56.5 | 7 | 120.3 | 3.3 | 10.3 | 540.55 | 586.54 | 586.54 | 591.58 | 161.29 | 2 | 332.56 | 106.56 | [8 empty] | 709.24 | 10.36 | 0.66 | 0.5
63 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | VNG048 | 1S-DL-YP-ETC-DJLM-2201-VNG048 | SURAJ MAL VIHAR C-BLOCK:ID | TG-VNG048A-1 | 19502894 | 990 | 320 | 251 | 0.96 | 866 | 314 | 1255 | 282 | 1126 | 270 | 1077 | 159 | 2019-06-03 02:00 | 211.2 | 67 | 1377 | R | 107 | 101 | 92 | 15 |  |  | 1.7 | 98.3 | 2.3 | 2.3 | 2.3 | 2.3 | 93 | 126.58 | 126.58 | 119.58 | 574.26 | 569.58 | 542.56 | 585.56 | 49.58 | 20.28 | 0.3 | 11.3 |  |  |  |  | 719.54 | 0.06 | 0.59 | 0.87
64 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | VNG048 | 1S-DL-YP-ETC-DJLM-2201-VNG048 | SURAJ MAL VIHAR C-BLOCK:ID | TG-VNG048A-2 | 19502893 | 990 | 200 | 245 | 0.97 | 745 | 270 | 1140 | 276 | 1176 | 199 | 844 | 316 | 2019-06-13 22:00 | 158.7 | 33.6 | 1243 | R | 109 | 98 | 93 | 16 |  |  | 19.9 | 80.1 |  | 3 | 6 |  | 225.42 | 314.42 | 314.42 | 300.12 | 485 | 401 | 340 | 419.3 | 9 | 1 | [6 empty] | 719.42 | 0.18 | 0.6 | 0.75
65 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | VNG048 | 1S-DL-YP-ETC-DJLM-2201-VNG048 | SURAJ MAL VIHAR C-BLOCK:ID | TG-VNG048A-3 | 19504546 | 630 | 200 | 245 | 0.97 | 510 | 123 | 524 | 210 | 914 | 176 | 750 | 339 | 2019-06-08 23:30 | 119.1 | 25.3 | 1012 | Y | 77 | 128 | 95 | 51 | 1 | 12.6 | 82.8 | 3.5 | 12 |  | 6 |  | 473.26 | 64 | 64 | 264.26 | 234.3 | 555.26 | 391 | 454 |  | 96.3 | 3.3 | 1.3 |  | 4 |  |  | 719.56 | 0.04 | 0.58 | 0.81
66 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | VNG069 | 1S-DL-YP-ETC-DJLM-2201-VNG069 | PETROL PUMP OPP.VIVEK VIHAR P.S:PM | TG-VNG069A-1 | 19503609 | 400 | 120 | 243 | 0.89 | 120 | 37 | 153 | 46 | 189 | 37 | 150 | 37 | 2019-06-13 19:30 | 12.4 | -44.4 | 195 | Y | 93 | 113 | 94 | 20 |  |  | 79.4 | 20.6 | 227 | 143.3 | 157 | 146.3 | 492.53 | 576.23 | 576.23 | 573.23 | [12 empty] | 719.53 | 0.07 | 0.73 | 0.3
67 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | VNG104 | 1S-DL-YP-ETC-DJLM-2201-VNG104 | YOJANA VIHAR B-BLOCK:ID | TG-VNG104A-1 | 19503000 | 990 | 320 | 241 | 0.97 | 385 | 155 | 658 | 119 | 497 | 111 | 467 | 178 | 2019-06-29 23:00 | 77.3 | 19.1 | 713 | R | 114 | 94 | 92 | 22 |  |  | 40 | 60 | 128.3 | 218.28 | 233.25 | 144 | 524.1 | 501.12 | 501.12 | 575.4 | 67 | [11 empty] | 719.4 | 0.2 | 0.63 | 0.39
68 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | VNG104 | 1S-DL-YP-ETC-DJLM-2201-VNG104 | YOJANA VIHAR B-BLOCK:ID | TG-VNG104A-2 | 19503016 | 400 | 120 | 238 | 0.97 | 348 | 85 | 365 | 115 | 497 | 148 | 647 | 244 | 2019-06-16 00:30 | 72.9 | 15.2 | 650 | B | 81 | 100 | 120 | 39 |  | 17.6 | 66.3 | 16.1 | 8 |  |  |  | 356.15 | 186.45 | 186.45 | 183.15 | 355.25 | 500.55 | 445.42 | 515.25 |  | 32 | 138 | 21 |  |  | 18.3 |  | 719.4 | 0.2 | 0.59 | 0.87
69 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | VNG115 | 1S-DL-YP-ETC-DJLM-2201-VNG115 | SURAJ MAL VIHAR B-BLOCK:PG | TG-VNG115A-1 | 19501029 | 990 | 320 | 241 | 0.94 | 1038 | 337 | 1442 | 366 | 1554 | 336 | 1435 | 115 | 2019-06-01 00:30 | 442.3 | -174.4 | 1664 | Y | 106 | 106 | 87 | 19 | 5.4 | 5.7 | 6.9 | 82 | 0.3 | 0.3 | 0.3 | 0.3 | 58.3 | 56 | 56 | 70.31 | 511.12 | 513.11 | 533.36 | 540.1 | 116.25 | 112.15 | 16.03 | 100.33 | 27.05 | 31.46 | 0.28 | 1.58 | 714.42 | 5.18 | 0.56 | 1.05
70 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | VNG172 | 1S-DL-YP-ETC-DJLM-2201-VNG172 | A-Blk Yojana Vihar Pkg | TG-VNG172A-1 | 19501013 | 990 | 320 | 252 | 0.96 | 616 | 191 | 798 | 189 | 789 | 236 | 983 | 190 | 2019-06-10 23:30 | 153.8 | 49.3 | 999 | B | 97 | 86 | 116 | 30 |  |  | 33.7 | 66.3 | 3 | 18 |  |  | 394.15 | 509.38 | 509.38 | 378.15 | 322.23 | 192 | 517.45 | 341.23 | [8 empty] | 719.38 | 0.22 | 0.64 | 0.62
71 | 2019-06-04 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | JHI043 | 1S-DL-YP-ETC-DJLM-2203-JHI043 | KASTURBA NGR.COMPLAINT CENTRE:ID | TG-JHI043A-1 | 19503707 | 990 | 320 | 240 | 0.98 | 612 | 186 | 816 | 254 | 1121 | 172 | 752 | 341 | 2019-06-26 23:00 | 121.4 | -8.1 | 1121 | Y | 94 | 129 | 76 | 53 |  |  | 9.4 | 90.6 | 64.42 | 0.3 | 167.42 | 25.42 | 452.23 | 297.35 | 297.35 | 467.53 | 130.3 | 349.3 | 28.3 | 154 | [8 empty] | 647.35 | 0.25 | 0.54 | 0.62
72 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG005 | 1S-DL-YP-ETC-DJLM-2201-VNG005 | SHAHDRA CITY:K | TG-VNG005A-1 | 19506064 | 630 | 200 | 243 | 0.96 | 392 | 106 | 452 | 104 | 444 | 182 | 781 | 333 | 2019-06-30 23:00 | 136.6 | 37 | 781 | B | 86 | 104 | 110 | 24 | 0.1 | 0.2 | 35.6 | 64.1 | 2.3 | 1.3 |  |  | 584.44 | 337.44 | 337.44 | 392.44 | 121 | 369 | 437 | 315.3 |  |  | 1.3 | [5 empty] | 708.14 | 11.46 | 0.63 | 0.62
73 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG005 | 1S-DL-YP-ETC-DJLM-2201-VNG005 | SHAHDRA CITY:K | TG-VNG005A-2 | 19504090 | 990 | 320 | 244 | 0.97 | 443 | 148 | 589 | 174 | 697 | 120 | 477 | 191 | 2019-06-13 18:30 | 131 | 33.9 | 743 | Y | 115 | 102 | 83 | 32 |  |  | 17.2 | 82.8 | 2 | 18.08 | 57.38 | 11 | 454.46 | 504.24 | 504.24 | 639.46 | 262.24 | 196.38 | 0.3 | 68.24 | [8 empty] | 719.1 | 0.5 | 0.72 | 0.45
74 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG005 | 1S-DL-YP-ETC-DJLM-2201-VNG005 | SHAHDRA CITY:K | TG-VNG005A-3 | 19502912 | 990 | 320 | 239 | 0.97 | 270 | 89 | 380 | 106 | 451 | 76 | 318 | 115 | 2019-06-15 00:30 | 61.1 | -1.5 | 504 | Y | 101 | 110 | 89 | 21 | 0.1 |  | 55.8 | 44.1 | 414.54 | 356.04 | 476.24 | 412.26 | 103.47 | 162.37 | 162.37 | 106.15 | [12 empty] | 518.41 | 33.19 | 0.48 | 0.27
75 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG006 | 1S-DL-YP-ETC-DJLM-2201-VNG006 | DCP OFFICE:K | TG-VNG006A-1 | 19504180 | 990 | 320 | 239 | 0.98 | 607 | 186 | 801 | 199 | 857 | 222 | 961 | 141 | 2019-06-10 16:00 | 117.8 | 17.7 | 1079 | B | 81 | 102 | 117 | 36 |  |  |  | 100 | 25.3 |  |  |  | 572.47 | 312.47 | 312.47 | 349.47 | 121.3 | 407 | 525.47 | 370 | [8 empty] | 719.47 | 0.13 | 0.66 | 0.61
76 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG006 | 1S-DL-YP-ETC-DJLM-2201-VNG006 | DCP OFFICE:K | TG-VNG006A-2 | 19501310 | 990 | 320 | 246 | 0.99 | 306 | 98 | 405 | 72 | 297 | 136 | 564 | 233 | 2019-06-12 14:30 | 65.5 | -31.6 | 564 | B | 80 | 93 | 128 | 48 |  |  |  | 100 | 566.08 | 509.08 | 249.08 | 408.08 | 153.3 | 210.3 | 210.3 | 311.3 |  |  | 2 | [9 empty] | 719.38 | 0.22 | 0.61 | 0.31
77 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG006 | 1S-DL-YP-ETC-DJLM-2201-VNG006 | DCP OFFICE:K | TG-VNG006A-3 | 19505449 | 630 | 200 | 246 | 0.96 | 152 | 33 | 135 | 71 | 292 | 48 | 198 | 137 | 2019-06-11 23:30 | 42 | 9.8 | 300 | Y | 62 | 112 | 127 | 65 |  |  | 5.1 | 94.9 | 701.23 | 457.53 | 272 | 584.23 |  | 243.3 | 243.3 | 117 | [12 empty] | 701.23 | 18.37 | 0.69 | 0.24
78 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG007 | 1S-DL-YP-ETC-DJLM-2201-VNG007 | RAMA BLOCK(BABU RAM SCHOOL):K | TG-VNG007A-1 | 19501463 | 630 | 200 | 243 | 0.97 | 459 | 189 | 799 | 140 | 584 | 129 | 541 | 239 | 2019-06-11 23:00 | 95.2 | 22.1 | 883 | R | 123 | 83 | 93 | 40 |  |  | 28.2 | 71.8 |  | 13 | 2 |  | 102 | 440.45 | 440.45 | 264.16 | 574.15 | 265.3 | 406.23 | 454.59 | 43 | [7 empty] | 719.15 | 0.45 | 0.62 | 0.73
79 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG007 | 1S-DL-YP-ETC-DJLM-2201-VNG007 | RAMA BLOCK(BABU RAM SCHOOL):K | TG-VNG007A-2 | 19503651 | 990 | 320 | 244 | 0.97 | 928 | 353 | 1476 | 258 | 1072 | 317 | 1318 | 352 | 2019-06-12 | 175.9 | 55.2 | 1593 | R | 110 | 88 | 101 | 22 |  |  | 3.5 | 96.5 |  |  |  |  | 67 | 178 | 178 | 88.01 | 535.53 | 541.23 | 585.22 | 585.22 | 104 |  | 50.3 | 46 | 12.3 |  |  |  | 719.23 | 0.37 | 0.58 | 0.94
80 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG008 | 1S-DL-YP-ETC-DJLM-2201-VNG008 | SARVARIA MARKET:K | TG-VNG008A-1 | 19506624 | 990 | 320 | 246 | 0.97 | 161 | 95 | 413 | 28 | 123 | 39 | 168 | 270 | 2019-06-08 23:00 | 43.5 | 4.2 | 413 | R | 165 | 59 | 76 | 106 | 0.1 | 0.1 | 3 | 96.7 | 539.05 | 706.04 | 706.04 | 706.04 | 166.59 | [15 empty] | 706.04 | 13.56 | 0.62 | 0.16
81 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG008 | 1S-DL-YP-ETC-DJLM-2201-VNG008 | SARVARIA MARKET:K | TG-VNG008A-2 | 19502923 | 990 | 320 | 240 | 0.96 | 226 | 92 | 403 | 87 | 377 | 47 | 204 | 188 | 2019-06-11 23:30 | 57.4 | 13.2 | 568 | Y | 122 | 113 | 65 | 57 |  |  | 4.1 | 95.9 | 566.19 | 620.57 | 718.49 | 682.49 | 152.3 | 95.52 | 95.52 | 36 |  | 2 | [10 empty] | 718.49 | 1.11 | 0.57 | 0.23
82 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG008 | 1S-DL-YP-ETC-DJLM-2201-VNG008 | SARVARIA MARKET:K | TG-VNG008A-3 | 19502920 | 990 | 320 | 244 | 0.92 | 75 | 21 | 84 | 24 | 95 | 31 | 123 | 35 | 2019-06-16 09:30 | 49.3 | -0.7 | 126 | B | 79 | 94 | 128 | 49 |  |  | 1.1 | 98.9 | 719.35 | 719.35 | 719.35 | 719.35 | [16 empty] | 719.35 | 0.25 | 0.52 | 0.08
83 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG008 | 1S-DL-YP-ETC-DJLM-2201-VNG008 | SARVARIA MARKET:K | TG-VNG008A-4 | 19502917 | 990 | 200 | 245 | 0.98 | 356 | 96 | 400 | 133 | 554 | 127 | 525 | 141 | 2019-06-13 22:30 | 75.9 | 19.3 | 574 | B | 84 | 107 | 110 | 26 |  |  | 0.3 | 99.7 | 393.35 | 180.27 | 99.35 | 196.57 | 325.46 | 536.54 | 536.54 | 522.24 |  | 2 | 1.3 | [9 empty] | 719.21 | 0.39 | 0.65 | 0.36
84 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG009 | 1S-DL-YP-ETC-DJLM-2201-VNG009 | TIKONA PARK JWALA NAGAR:K | TG-VNG009A-1 | 19501196 | 990 | 320 | 239 | 0.98 | 526 | 144 | 590 | 154 | 628 | 228 | 943 | 335 | 2019-06-30 00:30 | 95.7 | 0.7 | 943 | B | 89 | 96 | 115 | 26 |  |  | 3.3 | 96.7 | 96.27 | 66.23 | 19.21 | 37.51 | 596.19 | 593.52 | 593.52 | 615.38 | 24.16 | 56.47 | 150.32 | 63.33 | [8 empty] | 717.02 | 2.58 | 0.56 | 0.53
85 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG009 | 1S-DL-YP-ETC-DJLM-2201-VNG009 | TIKONA PARK JWALA NAGAR:K | TG-VNG009A-2 | 19503571 | 990 | 320 | 251 | 0.97 | 727 | 246 | 1034 | 254 | 1063 | 226 | 937 | 114 | 2019-06-11 23:30 | 134.7 | 5.2 | 1209 | R | 105 | 99 | 96 | 9 |  | 0.1 | 45 | 55 | 1.3 | 9.3 | 7 | 4 | 263.01 | 303.19 | 303.19 | 279.53 | 442.52 | 399.04 | 395.1 | 434 | 10.3 | 6 | [6 empty] | 717.53 | 2.07 | 0.6 | 0.73
86 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG009 | 1S-DL-YP-ETC-DJLM-2201-VNG009 | TIKONA PARK JWALA NAGAR:K | TG-VNG009A-3 | 19501248 | 990 | 320 | 245 | 0.96 | 366 | 102 | 419 | 142 | 587 | 122 | 508 | 146 | 2019-06-11 23:30 | 86.1 | 26.5 | 587 | Y | 88 | 112 | 100 | 24 |  |  | 3.3 | 96.7 | 349.22 | 123.22 | 264.22 | 230.22 | 370.23 | 593.53 | 593.53 | 489.23 |  | 2.3 | 1 | [9 empty] | 719.45 | 0.15 | 0.63 | 0.37
87 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG009 | 1S-DL-YP-ETC-DJLM-2201-VNG009 | TIKONA PARK JWALA NAGAR:K | TG-VNG009A-4 | 19506351 | 630 | 200 | 245 | 0.98 | 261 | 98 | 414 | 80 | 338 | 82 | 347 | 72 | 2019-06-10 23:00 | 56.4 | 1.8 | 504 | R | 106 | 98 | 96 | 10 |  |  | 0.6 | 99.4 | 58.3 | 106.3 | 94.22 | 76.3 | 612.15 | 598.15 | 598.15 | 627.15 | 36 | 2 | 3.3 | 3 | [8 empty] | 706.45 | 13.15 | 0.66 | 0.41
88 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG010 | 1S-DL-YP-ETC-DJLM-2201-VNG010 | ANAJ MANDI:K | TG-VNG010A-1 | 19504171 | 630 | 200 | 244 | 0.97 | 398 | 116 | 487 | 146 | 623 | 136 | 571 | 119 | 2019-06-12 13:30 | 95.7 | 24.4 | 668 | B | 84 | 103 | 112 | 28 |  | 12 | 59.4 | 28.6 | 19 |  |  |  | 470.28 | 313 | 313 | 288.3 | 230.08 | 406.36 | 533.06 | 431.06 | [8 empty] | 719.36 | 0.24 | 0.67 | 0.63
89 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG010 | 1S-DL-YP-ETC-DJLM-2201-VNG010 | ANAJ MANDI:K | TG-VNG010A-2 | 19505882 | 990 | 320 | 245 | 0.98 | 954 | 299 | 1242 | 365 | 1527 | 290 | 1205 | 305 | 2019-06-10 | 232 | 49.3 | 1541 | B | 104 | 100 | 96 | 8 |  | 0.1 | 4.7 | 95.1 |  |  |  |  | 60 | 71.3 | 71.3 | 48.3 | 593.15 | 610.15 | 649.15 | 648.45 | 62.3 | 35 | 12 | 22.3 | 4 | 3 | 0.3 |  | 719.45 | 0.15 | 0.58 | 0.96
90 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG011 | 1S-DL-YP-ETC-DJLM-2201-VNG011 | DELHI GATE:K | TG-VNG011A-1 | 19506806 | 990 | 320 | 240 | 0.98 | 792 | 276 | 1180 | 291 | 1238 | 225 | 950 | 264 | 2019-06-10 23:30 | 224.3 | 62.1 | 1359 | R | 99 | 109 | 92 | 17 |  | 0.9 | 63.1 | 36 |  |  |  |  | 113.27 | 75.27 | 75.27 | 107.27 | 588.27 | 597.57 | 543.57 | 595.57 | 2 | 30.3 |  | 0.3 |  |  |  |  | 703.54 | 16.06 | 0.65 | 0.8
91 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG011 | 1S-DL-YP-ETC-DJLM-2201-VNG011 | DELHI GATE:K | TG-VNG011A-2 | 19504394 | 400 | 120 | 244 | 0.97 | 288 | 104 | 435 | 104 | 434 | 80 | 334 | 101 | 2019-06-11 23:30 | 48.6 | 18.5 | 477 | Y | 116 | 103 | 82 | 34 | 0 |  | 0.1 | 99.9 |  |  | 52.3 |  | 234.13 | 358.36 | 358.36 | 385.06 | 478.14 | 358.51 | 202.48 | 333.21 | 6 | 1 | [6 empty] | 718.27 | 1.33 | 0.57 | 0.72
92 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG013 | 1S-DL-YP-ETC-DJLM-2201-VNG013 | BIHARI COLONY:K | TG-VNG013A-1 | 19503502 | 990 | 320 | 247 | 0.97 | 981 | 378 | 1583 | 248 | 1041 | 355 | 1509 | 509 | 2019-06-11 23:30 | 179.6 | 87.6 | 1583 | R | 112 | 79 | 108 | 33 |  |  | 64.3 | 35.7 |  |  |  |  | 13.19 | 281.58 | 281.58 | 49.18 | 556.39 | 437.29 | 570.28 | 588.09 | 121.59 |  | 106.59 | 82 | 27.3 |  | 12.3 |  | 719.27 | 0.33 | 0.58 | 0.99
93 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG013 | 1S-DL-YP-ETC-DJLM-2201-VNG013 | BIHARI COLONY:K | TG-VNG013A-2 | 19506743 | 990 | 320 | 249 | 0.97 | 855 | 339 | 1410 | 278 | 1149 | 238 | 971 | 383 | 2019-06-30 23:00 | 192.6 | 68.8 | 1410 | R | 116 | 105 | 79 | 37 | 0.4 | 1.1 | 87.9 | 10.6 |  |  |  |  | 79.57 | 115.12 | 115.12 | 157.33 | 556 | 580.45 | 314.29 | 549.54 | 74 | 14.3 |  | 3 | 0.3 |  |  |  | 710.27 | 9.33 | 0.58 | 0.86
94 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG013 | 1S-DL-YP-ETC-DJLM-2201-VNG013 | BIHARI COLONY:K | TG-VNG013A-3 | 19504190 | 990 | 320 | 236 | 0.97 | 1048 | 354 | 1571 | 353 | 1587 | 341 | 1522 | 59 | 2019-06-11 00:30 | 174.4 | 78 | 1590 | B | 98 | 98 | 104 | 6 |  | 0.1 | 17.3 | 82.6 |  |  |  |  | 34.13 | 28 | 28 | 23.3 | 556.15 | 593.58 | 541.58 | 566.28 | 121.59 | 93.59 | 142.29 | 124.59 | 7 | 3.3 | 18.3 | 4.3 | 719.27 | 0.33 | 0.6 | 1.06
95 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG014 | 1S-DL-YP-ETC-DJLM-2201-VNG014 | COMMERCIAL BLOCK:K | TG-VNG014A-1 | 19504838 | 990 | 200 | 243 | 0.97 | 709 | 264 | 1091 | 179 | 735 | 267 | 1111 | 366 | 2019-06-12 | 156.4 | 46.5 | 1194 | R | 104 | 89 | 107 | 18 |  |  | 9.3 | 90.7 |  | 0.3 |  |  | 192.24 | 315.58 | 315.58 | 222.31 | 522.33 | 401.29 | 515.26 | 495.26 | 3 |  | 3.3 | [5 empty] | 717.57 | 2.03 | 0.65 | 0.72
96 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG014 | 1S-DL-YP-ETC-DJLM-2201-VNG014 | COMMERCIAL BLOCK:K | TG-VNG014A-2 | 19504075 | 990 | 320 | 250 | 0.96 | 769 | 267 | 1091 | 215 | 868 | 287 | 1170 | 272 | 2019-06-13 23:30 | 172.2 | 67.7 | 1222 | B | 104 | 89 | 107 | 18 |  | 0.3 | 4.9 | 94.7 |  |  |  |  | 147.3 | 313 | 313 | 183.3 | 569.1 | 406.1 | 576.1 | 535.4 | 2.3 |  | 7.3 | [5 empty] | 719.1 | 0.5 | 0.6 | 0.78
97 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG015 | 1S-DL-YP-ETC-DJLM-2201-VNG015 | SHAMSHAN GHAT:PL | TG-VNG015A-1 | 19504540 | 990 | 320 | 244 | 0.97 | 560 | 152 | 618 | 206 | 837 | 202 | 823 | 213 | 2019-06-29 23:30 | 138.4 | 32.4 | 953 | B | 76 | 105 | 119 | 43 |  |  | 0.3 | 99.7 | 10.1 |  |  |  | 687.44 | 332.4 | 332.4 | 381.4 | 21.3 | 386.44 | 577.14 | 337.44 | [8 empty] | 719.24 | 0.36 | 0.7 | 0.57
98 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG015 | 1S-DL-YP-ETC-DJLM-2201-VNG015 | SHAMSHAN GHAT:PL | TG-VNG015A-2 | 19504538 | 630 | 200 | 239 | 0.97 | 256 | 43 | 180 | 120 | 502 | 93 | 383 | 282 | 2019-06-01 | 51.5 | 8.7 | 518 | Y | 58 | 138 | 103 | 80 |  |  | 6.9 | 93.1 | 687.24 | 220.12 | 378.4 | 422.24 | 32 | 380.12 | 380.12 | 296 |  | 119 | 2 | 1 | [8 empty] | 719.24 | 0.36 | 0.49 | 0.41
99 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG016 | 1S-DL-YP-ETC-DJLM-2201-VNG016 | RAMLEELA GROUND JWALA NAGAR:PL | TG-VNG016A-1 | 19505775 | 990 | 320 | 244 | 0.97 | 810 | 372 | 1607 | 216 | 928 | 222 | 1013 | 641 | 2019-06-03 00:30 | 243.8 | 47.7 | 1607 | R | 113 | 100 | 87 | 26 | 55.7 | 24.2 | 5.1 | 15.1 |  |  |  |  | 56.12 | 211.27 | 211.27 | 175.59 | 631.21 | 506.06 | 375.46 | 541.04 | 28.3 |  |  | 0.3 | 1.3 |  |  |  | 717.33 | 2.27 | 0.58 | 0.82
100 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG016 | 1S-DL-YP-ETC-DJLM-2201-VNG016 | RAMLEELA GROUND JWALA NAGAR:PL | TG-VNG016A-2 | 19501198 | 990 | 320 | 242 | 0.97 | 654 | 163 | 705 | 211 | 905 | 280 | 1207 | 437 | 2019-06-12 00:30 | 148.7 | 50 | 1235 | B | 76 | 97 | 127 | 51 |  | 1.9 | 30.5 | 67.6 | 2.1 |  |  |  | 605.2 | 330.35 | 330.35 | 286.05 | 110.16 | 387.11 | 642.31 | 431.41 |  |  | 8.48 | [5 empty] | 717.46 | 2.14 | 0.65 | 0.66
101 | 2019-06-13 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG017 | 1S-DL-YP-ETC-DJLM-2201-VNG017 | MUKESH NAGAR:PL | TG-VNG017A-1 | 19506922 | 990 | 320 | 255 | 0.96 | 978 | 320 | 1371 | 361 | 1581 | 298 | 1289 | 261 | 2019-06-30 23:30 | 284.5 | 99.2 | 1581 | Y | 103 | 98 | 99 | 5 | 0.1 | 0.9 | 14.7 | 84.3 |  |  |  |  | 21.24 | 29.24 | 29.24 | 20.54 | 326.31 | 340.01 | 351.55 | 341.31 | 51.3 | 35 | 34 | 44 | 7 | 2 |  |  | 406.25 | 25.35 | 0.59 | 0.99
102 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG017 | 1S-DL-YP-ETC-DJLM-2201-VNG017 | MUKESH NAGAR:PL | TG-VNG017A-2 | 19504777 | 990 | 320 | 239 | 0.97 | 683 | 239 | 1014 | 180 | 766 | 265 | 1120 | 315 | 2019-06-02 23:30 | 149.4 | 33.9 | 1219 | B | 97 | 83 | 120 | 37 |  |  | 0.4 | 99.6 | 0.39 | 2.09 | 0.39 | 0.39 | 334.05 | 480.3 | 480.3 | 261.51 | 382.25 | 234.3 | 619.56 | 454.39 |  |  | 5.3 | [5 empty] | 717.09 | 2.51 | 0.64 | 0.69
103 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG018 | 1S-DL-YP-ETC-DJLM-2201-VNG018 | TEL MILL:PL | TG-VNG018A-1 | 19505883 | 990 | 320 | 245 | 0.97 | 969 | 443 | 1887 | 255 | 1072 | 271 | 1131 | 788 | 2019-06-09 | 232.6 | 44.2 | 1887 | R | 118 | 85 | 97 | 33 |  | 0.3 | 8.4 | 91.3 |  |  |  |  | 81.22 | 263.22 | 263.22 | 147.52 | 511.23 | 456.23 | 537.23 | 533.23 | 93 |  | 34.3 | 38.3 | 34 |  | 0.3 |  | 719.45 | 0.15 | 0.54 | 0.98
104 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG020 | 1S-DL-YP-ETC-DJLM-2201-VNG020 | TASH FACTORY:PL | TG-VNG020A-1 | 19505531 | 990 | 320 | 238 | 0.97 | 531 | 158 | 701 | 184 | 813 | 189 | 834 | 124 | 2019-06-11 01:30 | 308.2 | 4.8 | 834 | B | 88 | 108 | 104 | 20 |  |  | 0.6 | 99.4 | 170.54 | 88.27 | 97.57 | 116.54 | 493.29 | 498.56 | 498.56 | 516.59 | 39 | 116 | 89.3 | 69.3 | [8 empty] | 703.23 | 16.37 | 0.55 | 0.54
105 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG020 | 1S-DL-YP-ETC-DJLM-2201-VNG020 | TASH FACTORY:PL | TG-VNG020A-2 | 19501465 | 990 | 320 | 233 | 0.99 | 318 | 109 | 472 | 101 | 433 | 108 | 464 | 35 | 2019-06-27 16:00 | 50.8 | -23.6 | 472 | R | 100 | 94 | 107 | 13 |  |  | 2.2 | 97.8 | 533.25 | 554.55 | 491.55 | 523.25 | 186.27 | 164.57 | 164.57 | 196.27 | [12 empty] | 719.52 | 0.08 | 0.46 | 0.32
106 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG021 | 1S-DL-YP-ETC-DJLM-2201-VNG021 | GALI NO-5 V.NGR:PL | TG-VNG021A-1 | 19504076 | 990 | 320 | 238 | 0.98 | 711 | 240 | 1040 | 256 | 1102 | 215 | 927 | 154 | 2019-06-10 03:00 | 127.3 | 36.8 | 1164 | Y | 108 | 106 | 86 | 22 |  |  | 15 | 85 | 1.3 |  | 7 | 0.3 | 256.28 | 270.58 | 270.58 | 324.55 | 461.56 | 448.56 | 244.59 | 394.29 | [8 empty] | 719.54 | 0.06 | 0.6 | 0.72
107 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG022 | 1S-DL-YP-ETC-DJLM-2201-VNG022 | 4-POLE PANDAV ROAD:PL | TG-VNG022A-1 | 19505267 | 990 | 320 | 238 | 0.98 | 855 | 232 | 1014 | 292 | 1283 | 331 | 1457 | 386 | 2019-06-10 23:30 | 147.2 | 59.5 | 1457 | B | 90 | 96 | 114 | 24 |  | 0.1 | 19.1 | 80.8 |  |  |  |  | 188.35 | 124.36 | 124.36 | 85.06 | 513.36 | 569.05 | 593.11 | 604.05 |  | 8.3 | 74 | 13 |  |  | 0.3 |  | 702.11 | 17.49 | 0.62 | 0.86
108 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG024 | 1S-DL-YP-ETC-DJLM-2201-VNG024 | GALI NO-16 VISHWAS NAGAR:PL | TG-VNG024A-1 | 19506850 | 990 | 320 | 250 | 0.98 | 243 | 72 | 293 | 94 | 383 | 77 | 314 | 81 | 2019-06-15 16:00 | 67.5 | -3.5 | 443 | R | 88 | 130 | 82 | 48 |  | 0.1 | 1.1 | 98.7 | 688.46 | 564.29 | 680.47 | 664.17 | 31 | 155.17 | 155.17 | 55.29 | [12 empty] | 719.46 | 0.14 | 0.53 | 0.25
109 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG024 | 1S-DL-YP-ETC-DJLM-2201-VNG024 | GALI NO-16 VISHWAS NAGAR:PL | TG-VNG024A-2 | 19506689 | 990 | 320 | 237 | 0.97 | 215 | 64 | 279 | 72 | 309 | 80 | 344 | 56 | 2019-06-10 22:30 | 47.7 | 13.4 | 423 | B | 78 | 107 | 115 | 37 | 0.1 | 0.2 | 0.6 | 99.1 | 695.16 | 592.46 | 539.46 | 674.46 | 1 | 103.3 | 103.3 | 21.3 | [12 empty] | 696.16 | 23.44 | 0.69 | 0.22
110 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG025 | 1S-DL-YP-ETC-DJLM-2201-VNG025 | MAHAVIR BLOCK:PL | TG-VNG025A-1 | 19505298 | 400 | 120 | 250 | 0.96 | 388 | 109 | 437 | 172 | 698 | 107 | 428 | 265 | 2019-06-02 23:30 | 96.7 | 29.9 | 727 | Y | 88 | 104 | 108 | 20 |  | 0.6 | 47.5 | 51.9 |  | 1 |  |  | 220.13 | 134 | 134 | 124 | 476.52 | 514.05 | 582.08 | 546.35 | 3.3 | 36 | 58.44 | 30 |  | 15.3 |  |  | 700.35 | 19.25 | 0.55 | 0.97
111 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG025 | 1S-DL-YP-ETC-DJLM-2201-VNG025 | MAHAVIR BLOCK:PL | TG-VNG025A-2 | 19506616 | 400 | 200 | 242 | 0.96 | 307 | 109 | 447 | 94 | 393 | 105 | 432 | 48 | 2019-06-12 00:30 | 66 | 17.6 | 464 | R | 101 | 97 | 102 | 5 | 1.1 | 79.7 | 18.3 | 0.9 | 1 | 2.3 | 1.3 |  | 305.13 | 381.14 | 381.14 | 340.43 | 392.21 | 316.5 | 363.07 | 359.51 | 2 |  | 2 | [5 empty] | 700.34 | 19.26 | 0.56 | 0.77
112 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG026 | 1S-DL-YP-ETC-DJLM-2201-VNG026 | DALAI MOHALLA:PL | TG-VNG026A-1 | 19504081 | 990 | 320 | 243 | 0.99 | 792 | 224 | 936 | 268 | 1127 | 300 | 1248 | 272 | 2019-06-12 14:30 | 86.1 | -35.3 | 1258 | B | 93 | 102 | 105 | 12 | 11.8 | 0.2 | 19.3 | 68.6 |  |  |  |  | 55.3 | 29.3 | 29.3 | 27.3 | 544.08 | 569.08 | 566.08 | 571.38 |  | 1 | 11.3 | 0.3 |  |  |  |  | 599.38 | 72.22 | 0.7 | 0.8
113 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG027 | 1S-DL-YP-ETC-DJLM-2201-VNG027 | SHALIMAR PARK:K | TG-VNG027A-1 | 19505963 | 990 | 320 | 244 | 0.97 | 981 | 390 | 1661 | 248 | 1051 | 343 | 1465 | 540 | 2019-06-10 23:30 | 239.4 | 56.3 | 1749 | R | 109 | 84 | 107 | 25 | 0.1 |  | 0.2 | 99.7 |  |  |  |  | 43.3 | 201.02 | 201.02 | 79 | 537.24 | 508.52 | 499.24 | 550.54 | 114 |  | 102.3 | 80 | 15 |  | 28.3 |  | 709.54 | 10.06 | 0.57 | 0.99
114 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG027 | 1S-DL-YP-ETC-DJLM-2201-VNG027 | SHALIMAR PARK:K | TG-VNG027A-2 | 19505354 | 630 | 200 | 239 | 0.98 | 374 | 128 | 559 | 122 | 530 | 124 | 538 | 26 | 2019-06-29 23:00 | 80.6 | 23.4 | 656 | R | 108 | 85 | 107 | 23 |  |  | 2.9 | 97.1 | 6.3 | 17.3 |  | 0.3 | 413.32 | 615.55 | 615.55 | 505.55 | 289.23 | 76 | 293 | 203 | [8 empty] | 709.25 | 10.35 | 0.61 | 0.59
115 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG028 | 1S-DL-YP-ETC-DJLM-2201-VNG028 | MANI RAM MANDIR:PL | TG-VNG028A-1 | 19506740 | 990 | 320 | 244 | 0.97 | 1245 | 368 | 1467 | 360 | 1413 | 517 | 2088 | 649 | 2019-06-27 03:00 | 342.4 | 85.8 | 2088 | B | 101 | 97 | 103 | 6 | 0.6 | 4.3 | 68 | 27.1 | 1.3 | 1.3 | 1.3 | 1.3 | 12.3 | 23 | 23 | 13 | 545.28 | 549.28 | 516.58 | 540.58 | 114.3 | 101.3 | 113 | 113 | 36.33 | 35.03 | 61.03 | 42.03 | 710.31 | 9.29 | 0.53 | 1.26
116 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG028 | 1S-DL-YP-ETC-DJLM-2201-VNG028 | MANI RAM MANDIR:PL | TG-VNG028A-2 | 19504924 | 990 | 320 | 246 | 0.97 | 800 | 221 | 907 | 316 | 1311 | 264 | 1069 | 352 | 2019-06-30 23:30 | 136.2 | 20.6 | 1311 | Y | 92 | 115 | 94 | 23 |  | 4.1 | 95.8 | 0.1 | 26.29 | 4 | 29.51 | 15.3 | 491.04 | 339.33 | 339.33 | 433.33 | 201.3 | 363.3 | 235 | 268 |  | 12 | 2.3 | 2 |  |  |  |  | 719.03 | 0.57 | 0.47 | 0.81
117 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG028 | 1S-DL-YP-ETC-DJLM-2201-VNG028 | MANI RAM MANDIR:PL | TG-VNG028A-3 | 19505681 | 630 | 200 | 242 | 0.97 | 648 | 280 | 1180 | 220 | 896 | 148 | 607 | 496 | 2019-06-12 | 164 | 32.8 | 1180 | R | 90 | 119 | 91 | 29 | 25 | 1.1 | 6 | 67.9 | 1 | 0.3 | 13.41 | 0.3 | 150.02 | 35.59 | 35.59 | 99.32 | 193.3 | 252.03 | 203.3 | 228.3 | 11.3 | 59.3 | 4 | 29.3 | 2.3 | 10.3 | 0.3 | 0.3 | 710.54 | 9.06 | 0.5 | 1.03
118 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG029 | 1S-DL-YP-ETC-DJLM-2201-VNG029 | IDGAH BHOLA NATH NAGAR:PL | TG-VNG029A-1 | 19505511 | 990 | 320 | 240.9735 | 0.97697 | 1160.112 | 457.9477 | 2048.7998 | 309.9058 | 1380.5495 | 392.2585 | 1779.5959 | 582.3518 | 2019-06-10 23:30 | [15 empty] | 2 |  |  |  | 3 |  |  |  | 568.5 |  |  |  | 130.5 |  |  |  | 14.5 | 718.5 |  | 0.58425 | 1.1718
119 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG030 | 1S-DL-YP-ETC-DJLM-2201-VNG030 | TELEWARA:PM | TG-VNG030A-1 | 19504455 | 400 | 120 | 235 | 0.98 | 347 | 120 | 519 | 115 | 497 | 112 | 487 | 29 | 2019-06-12 | 56.6 | 21 | 560 | R | 108 | 96 | 97 | 12 |  |  | 1.5 | 98.5 | 0.3 | 1 | 0.3 | 0.3 | 34.3 | 146.24 | 146.24 | 66.3 | 647.36 | 545.12 | 594.56 | 635.06 | 36.3 | 26.3 | 12.3 | 17 |  |  |  |  | 719.06 | 0.54 | 0.63 | 0.87
120 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG031 | 1S-DL-YP-ETC-DJLM-2201-VNG031 | TEJAB MILL:PL | TG-VNG031A-1 | 19503074 | 990 | 320 | 242 | 0.97 | 942 | 291 | 1285 | 376 | 1667 | 275 | 1213 | 423 | 2019-06-11 00:30 | 184 | 48.6 | 1714 | Y | 95 | 114 | 91 | 23 |  |  | 4.9 | 95.1 | 1 | 0.3 | 1 | 0.3 | 21.01 | 1.01 | 1.01 | 12.31 | 670.07 | 542.18 | 651.44 | 634.02 | 17.09 | 112.49 | 16.02 | 62.14 |  | 52.39 |  |  | 709.17 | 10.43 | 0.64 | 0.95
121 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG031 | 1S-DL-YP-ETC-DJLM-2201-VNG031 | TEJAB MILL:PL | TG-VNG031A-2 | 19504207 | 990 | 320 | 242 | 0.98 | 626 | 228 | 1019 | 192 | 849 | 205 | 917 | 148 | 2019-06-30 23:30 | 129.5 | 9.6 | 1038 | R | 99 | 99 | 102 | 3 |  |  | 4.8 | 95.2 | 0.3 | 14.19 | 1.3 | 0.3 | 383.38 | 320.09 | 320.09 | 333.11 | 324.17 | 373.57 | 394.41 | 374.44 | [8 empty] | 708.25 | 11.35 | 0.64 | 0.63
122 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG031 | 1S-DL-YP-ETC-DJLM-2201-VNG031 | TEJAB MILL:PL | TG-VNG031A-3 | 19506510 | 630 | 200 | 244 | 0.97 | 501 | 184 | 742 | 136 | 546 | 181 | 724 | 188 | 2019-06-30 | 124.8 | 34.2 | 780 | R | 106 | 88 | 107 | 19 |  |  | 4.4 | 95.6 | 0.3 | 0.3 | 0.3 | 0.3 | 25.32 | 89.26 | 89.26 | 27.02 | 271.36 | 214.2 | 279.44 | 276.44 | 6.38 |  | 5 | [5 empty] | 690.24 | 29.36 | 0.65 | 0.79
123 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG032 | 1S-DL-YP-ETC-DJLM-2201-VNG032 | MAHA RAM MOHALLA:PL | TG-VNG032A-1 | 19506260 | 990 | 320 | 241 | 0.97 | 515 | 259 | 1140 | 141 | 611 | 115 | 495 | 595 | 2019-06-26 | 133.4 | 29.4 | 1140 | R | 113 | 107 | 79 | 34 |  | 0.2 | 26.2 | 73.6 | 28.3 | 55.3 | 269.13 | 81.3 | 501.11 | 515.11 | 515.11 | 518.11 | 171.3 | 130.3 | 3 | 101.3 | [8 empty] | 701.11 | 18.49 | 0.56 | 0.52
124 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG032 | 1S-DL-YP-ETC-DJLM-2201-VNG032 | MAHA RAM MOHALLA:PL | TG-VNG032A-2 | 19506688 | 630 | 200 | 244 | 0.96 | 546 | 204 | 830 | 159 | 645 | 183 | 747 | 161 | 2019-06-30 00:30 | 132.4 | 47.4 | 1055 | B | 113 | 83 | 104 | 30 |  | 2.2 | 11.4 | 86.3 |  | 3.25 |  |  | 31.28 | 257.41 | 257.41 | 92.25 | 589.34 | 440.26 | 571.36 | 596.37 | 80.3 |  | 33.56 | 12.3 |  |  | 13 |  | 701.32 | 18.28 | 0.62 | 0.87
125 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG033 | 1S-DL-YP-ETC-DJLM-2201-VNG033 | INDRA PARK:PL | TG-VNG033A-1 | 19504971 | 990 | 320 | 244 | 0.96 | 713 | 172 | 745 | 248 | 1083 | 292 | 1267 | 458 | 2019-06-27 00:30 | 146.5 | 58.1 | 1267 | B | 71 | 108 | 121 | 50 |  |  | 10.6 | 89.4 | 45.22 |  |  |  | 562.5 | 226.44 | 226.44 | 322.14 | 110.24 | 491.52 | 550.37 | 396.22 |  |  | 12.38 | [5 empty] | 718.36 | 1.24 | 0.59 | 0.72
126 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG033 | 1S-DL-YP-ETC-DJLM-2201-VNG033 | INDRA PARK:PL | TG-VNG033A-2 | 19504136 | 990 | 320 | 237 | 0.98 | 666 | 161 | 709 | 252 | 1139 | 253 | 1125 | 423 | 2019-06-27 00:30 | 121.4 | 34.6 | 1233 | Y | 76 | 118 | 106 | 42 | 0.1 | 8.8 | 78.8 | 12.3 | 18.3 |  |  |  | 594.45 | 189.15 | 189.15 | 330.45 | 105.23 | 526.53 | 425.23 | 387.53 |  | 2.3 | [6 empty] | 718.38 | 1.22 | 0.62 | 0.67
127 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG034 | 1S-DL-YP-ETC-DJLM-2201-VNG034 | DCP OFFICE PEELA MANDIR:ID | TG-VNG034A-1 | 19503010 | 990 | 320 | 245 | 0.96 | 405 | 170 | 708 | 96 | 393 | 139 | 574 | 273 | 2019-06-11 01:30 | 93.5 | 39 | 708 | R | 118 | 76 | 106 | 42 |  |  | 6 | 94 | 5.3 | 279 | 34 | 36.3 | 586.23 | 440.53 | 440.53 | 679.23 | 128 |  | 28 | 4 | [8 empty] | 719.53 | 0.07 | 0.68 | 0.41
128 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG036 | 1S-DL-YP-ETC-DJLM-2201-VNG036 | BHOLA NATH NAGAR:K | TG-VNG036A-1 | 19503515 | 990 | 320 | 240 | 0.97 | 809 | 249 | 1051 | 261 | 1116 | 299 | 1249 | 175 | 2019-06-29 23:30 | 148.7 | 39 | 1328 | B | 103 | 95 | 103 | 8 |  | 1.1 | 16.8 | 82.1 | 0.3 | 0.3 | 0.3 | 0.3 | 58 | 161.4 | 161.4 | 104 | 658.34 | 554.54 | 557.04 | 613.04 | 1.3 | 1.3 | 22 | 1 |  |  |  |  | 718.34 | 1.26 | 0.63 | 0.82
129 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG036 | 1S-DL-YP-ETC-DJLM-2201-VNG036 | BHOLA NATH NAGAR:K | TG-VNG036A-2 | 19501600 | 990 | 320 | 239 | 0.97 | 805 | 231 | 941 | 275 | 1142 | 300 | 1243 | 266 | 2019-06-12 | 143.5 | 3.7 | 1399 | B | 90 | 99 | 112 | 22 |  | 5.6 | 87.8 | 6.7 | 0.3 | 0.3 | 0.3 | 0.3 | 292.44 | 268.59 | 268.59 | 202.44 | 426.15 | 435.3 | 557.15 | 514.45 |  | 14.3 | 39.3 | 1.3 |  |  |  |  | 719.29 | 0.31 | 0.59 | 0.81
130 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG036 | 1S-DL-YP-ETC-DJLM-2201-VNG036 | BHOLA NATH NAGAR:K | TG-VNG036A-3 | 19506687 | 630 | 200 | 247 | 0.97 | 665 | 210 | 887 | 169 | 710 | 285 | 1238 | 465 | 2019-06-10 01:30 | 200.6 | 42.2 | 1238 | B | 103 | 97 | 100 | 6 | 0.6 | 0.5 | 11.4 | 87.5 | 1 | 1 | 1 | 1 | 120.42 | 126.16 | 126.16 | 129.41 | 524.46 | 563.41 | 474 | 532.47 | 55.04 | 11.47 | 53 | 38.59 | 1.12 |  | 6.16 | 0.17 | 702.44 | 17.16 | 0.5 | 1.06
131 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG037 | 1S-DL-YP-ETC-DJLM-2201-VNG037 | PATHAN PURA:PL | TG-VNG037A-1 | 19505282 | 990 | 320 | 246 | 0.97 | 1165 | 364 | 1656 | 500 | 2284 | 300 | 1321 | 847 | 2019-06-09 23:30 | 430.1 | 55 | 2284 | Y | 96 | 123 | 81 | 42 | 4.3 | 2.1 | 77.8 | 15.9 |  |  | 2.3 |  | 120.54 | 17 | 17 | 93.54 | 563.48 | 505.12 | 447.3 | 553.18 | 11 | 131.3 | 1 | 48.3 | 0.3 | 42.3 |  | 0.3 | 696.12 | 23.48 | 0.48 | 1.18
132 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG038 | 1S-DL-YP-ETC-DJLM-2201-VNG038 | AGGARWAL BHAWAN:PM | TG-VNG038A-1 | 19501636 | 630 | 200 | 240 | 0.98 | 511 | 179 | 744 | 176 | 732 | 156 | 656 | 83 | 2019-06-11 23:30 | 79.1 | 20.7 | 788 | R | 106 | 99 | 96 | 10 |  |  | 12.4 | 87.6 | 0.3 | 0.3 | 3 | 0.3 | 186.11 | 254.11 | 254.11 | 236.11 | 522 | 464 | 411.3 | 482.3 | 11 | 1 | 0.3 | 0.3 |  |  |  |  | 719.41 | 0.19 | 0.58 | 0.81
133 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG038 | 1S-DL-YP-ETC-DJLM-2201-VNG038 | AGGARWAL BHAWAN:PM | TG-VNG038A-2 | 19506027 | 630 | 200 | 247 | 0.96 | 478 | 156 | 688 | 126 | 555 | 196 | 888 | 291 | 2019-06-09 23:00 | 188.4 | 25.2 | 888 | B | 96 | 82 | 122 | 40 | 0.2 | 0.8 | 65.1 | 33.9 | 42 | 118.41 | 14.3 | 24 | 527.41 | 538 | 538 | 525.11 | 150 | 63 | 324 | 170.3 |  |  | 0.3 | [5 empty] | 719.41 | 0.19 | 0.44 | 0.76
134 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG059 | 1S-DL-YP-ETC-DJLM-2201-VNG059 | 28/29 BLOCK VISHWAS NAGAR | TG-VNG059A-1 | 19504619 | 990 | 320 | 245 | 0.97 | 538 | 194 | 775 | 148 | 589 | 197 | 783 | 190 | 2019-06-15 23:00 | 117.8 | 44.9 | 865 | R | 105 | 80 | 115 | 35 |  |  | 0.3 | 99.7 | 4 | 55.3 |  | 0.3 | 463.28 | 621.58 | 621.58 | 524.58 | 252.3 | 42.3 | 366.58 | 194.3 | [8 empty] | 719.58 | 0.02 | 0.65 | 0.54
135 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG059 | 1S-DL-YP-ETC-DJLM-2201-VNG059 | 28/29 BLOCK VISHWAS NAGAR | TG-VNG059A-2 | 19504199 | 990 | 320 | 247 | 0.98 | 238 | 79 | 325 | 87 | 360 | 73 | 297 | 55 | 2019-06-28 15:00 | 53.7 | -7.4 | 362 | Y | 103 | 114 | 83 | 31 |  | 0.1 | 14.7 | 85.3 | 691.52 | 646.22 | 715.52 | 698.22 | 28 | 73.3 | 73.3 | 21.3 | [12 empty] | 719.52 | 0.08 | 0.61 | 0.24
136 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG060 | 1S-DL-YP-ETC-DJLM-2201-VNG060 | NEHRU GALI:PL | TG-VNG060A-1 | 19504588 | 990 | 320 | 246 | 0.98 | 153 | 48 | 209 | 41 | 178 | 64 | 275 | 86 | 2019-06-11 | 56.7 | 0.7 | 277 | B | 114 | 71 | 115 | 44 |  |  |  | 100 | 719.54 | 719.54 | 719.54 | 719.54 | [16 empty] | 719.54 | 0.06 | 0.48 | 0.15
137 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG061 | 1S-DL-YP-ETC-DJLM-2201-VNG061 | SHIVAM ENCLAVE-1:ID | TG-VNG061A-1 | 19501259 | 630 | 200 | 246 | 0.96 | 409 | 147 | 649 | 134 | 588 | 127 | 559 | 80 | 2019-06-10 23:30 | 93.4 | 18.9 | 685 | R | 110 | 94 | 97 | 16 |  |  | 19.5 | 80.5 | 55 | 86 | 62.01 | 54 | 399.51 | 445.14 | 445.14 | 439.21 | 263.53 | 187.3 | 195.23 | 225.23 | [8 empty] | 718.44 | 1.16 | 0.53 | 0.65
138 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG062 | 1S-DL-YP-ETC-DJLM-2201-VNG062 | SHIVAM ENCLAVE-2:ID | TG-VNG062A-1 | 19501298 | 400 | 120 | 248 | 0.97 | 79 | 39 | 167 | 10 | 41 | 31 | 130 | 112 | 2019-06-11 23:30 | 15.2 | 2.5 | 191 | R | 147 | 31 | 122 | 116 |  |  | 17.6 | 82.4 | 561.23 | 719.52 | 672.52 | 719.52 | 158.29 | [15 empty] | 719.52 | 0.08 | 0.5 | 0.2
139 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG062 | 1S-DL-YP-ETC-DJLM-2201-VNG062 | SHIVAM ENCLAVE-2:ID | TG-VNG062A-2 | 19501315 | 630 | 200 | 247 | 0.95 | 237 | 69 | 282 | 81 | 332 | 87 | 351 | 62 | 2019-06-29 23:30 | 63.9 | 13.8 | 368 | B | 93 | 94 | 113 | 20 | 38.5 | 61.5 |  |  | 416.27 | 430.22 | 161.58 | 315.58 | 303.25 | 289.3 | 289.3 | 403.54 |  |  | 4.3 | [9 empty] | 719.52 | 0.08 | 0.57 | 0.38
140 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG064 | 1S-DL-YP-ETC-DJLM-2201-VNG064 | HALKANA KUNA NO-1:K | TG-VNG064A-1 | 19504605 | 630 | 200 | 235 | 0.97 | 540 | 155 | 683 | 167 | 732 | 218 | 966 | 263 | 2019-06-29 23:00 | 113.2 | 41.4 | 966 | B | 93 | 93 | 114 | 21 |  |  | 11.1 | 88.9 |  |  |  |  | 9 | 21.3 | 21.3 | 9 | 708.22 | 677.28 | 582.23 | 702.22 | 0.3 | 18.54 | 133.59 | 6.3 |  |  | 0.3 |  | 717.52 | 2.08 | 0.72 | 0.86
141 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG064 | 1S-DL-YP-ETC-DJLM-2201-VNG064 | HALKANA KUNA NO-1:K | TG-VNG064A-2 | 19504069 | 990 | 320 | 245 | 0.96 | 481 | 167 | 672 | 152 | 614 | 162 | 651 | 51 | 2019-06-30 | 145 | 40.5 | 718 | R | 103 | 88 | 109 | 21 |  |  | 0.3 | 99.7 | 4.16 | 14.46 |  | 1.46 | 546.11 | 651.11 | 651.11 | 592.41 | 169 | 53.3 | 239.47 | 125 | [8 empty] | 719.27 | 0.33 | 0.71 | 0.49
142 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG064 | 1S-DL-YP-ETC-DJLM-2201-VNG064 | HALKANA KUNA NO-1:K | TG-VNG064A-3 | 19504070 | 990 | 320 | 250 | 0.98 | 679 | 233 | 963 | 207 | 868 | 240 | 992 | 113 | 2019-06-29 23:00 | 119.2 | -30.9 | 1033 | B | 97 | 99 | 104 | 7 |  | 0.2 | 49.8 | 50 | 2 | 2.3 | 1.3 | 1.3 | 264.26 | 258.24 | 258.24 | 228.26 | 452.14 | 457.46 | 527.12 | 488.44 | [8 empty] | 718.4 | 1.2 | 0.66 | 0.69
143 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG064 | 1S-DL-YP-ETC-DJLM-2201-VNG064 | HALKANA KUNA NO-1:K | TG-VNG064A-4 | 19506251 | 630 | 200 | 245 | 0.97 | 795 | 54 | 221 | 335 | 1630 | 405 | 1773 | 1485 | 2019-06-29 15:00 | 252.6 | 17.2 | 1773 | B | 68 | 92 | 140 | 72 | 0.2 | 1.6 | 77 | 21.1 | 236.14 | 56.31 | 2 | 25.37 | 464.08 | 578.51 | 578.51 | 557.45 |  | 64 | 416.21 | 116.3 |  | 0.3 | 4 |  |  | 0.3 | 0.3 | 0.3 | 700.22 | 19.38 | 0.26 | 1.26
144 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG065 | 1S-DL-YP-ETC-DJLM-2201-VNG065 | HALKANA KUAN NO-II:PL | TG-VNG065A-1 | 19504347 | 990 | 320 | 247 | 0.99 | 451 | 145 | 609 | 171 | 721 | 135 | 568 | 137 | 2019-06-10 15:00 | 61.1 | -82.4 | 721 | Y | 94 | 117 | 90 | 27 |  |  | 9 | 91 | 263.53 | 36.29 | 286.53 | 160.23 | 439.26 | 623.5 | 623.5 | 542.56 | 16 | 59 | 3 | 16 | [8 empty] | 719.19 | 0.41 | 0.58 | 0.46
145 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG065 | 1S-DL-YP-ETC-DJLM-2201-VNG065 | HALKANA KUAN NO-II:PL | TG-VNG065A-2 | 19503598 | 990 | 320 | 248 | 0.97 | 432 | 133 | 535 | 158 | 641 | 140 | 561 | 96 | 2019-06-29 23:30 | 75.1 | 22.8 | 673 | Y | 90 | 104 | 106 | 16 |  |  | 11.5 | 88.5 | 219.31 | 168.03 | 57.37 | 142.33 | 498.47 | 462.45 | 462.45 | 563.15 | 1 | 88.3 | 25.3 | 13.3 | [8 empty] | 719.18 | 0.42 | 0.6 | 0.44
146 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG066 | 1S-DL-YP-ETC-DJLM-2201-VNG066 | NEHRU GALI (NALLAHA SIDE):PL | TG-VNG066A-1 | 19506562 | 630 | 200 | 235 | 0.85 | 23 | 8 | 34 | 1 | 4 | 13 | 55 | 44 | 2019-06-12 18:30 | 11.8 | -0.2 | 65 | R | 82 | 47 | 170 | 123 |  |  | 38.4 | 61.6 | 705.03 | 705.03 | 705.03 | 705.03 | [16 empty] | 705.03 | 14.57 | 0.34 | 0.04
147 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG066 | 1S-DL-YP-ETC-DJLM-2201-VNG066 | NEHRU GALI (NALLAHA SIDE):PL | TG-VNG066A-2 | 19506564 | 630 | 200 | 248 | 0.93 | 28 | 5 | 19 | 8 | 33 | 15 | 62 | 38 | 2019-06-17 18:00 | 12.2 | 0.8 | 79 | Y | 55 | 194 | 51 | 143 |  | 0.1 | 1.8 | 98.1 | 705.03 | 705.03 | 705.03 | 705.03 | [16 empty] | 705.03 | 14.57 | 0.56 | 0.05
148 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG067 | 1S-DL-YP-ETC-DJLM-2201-VNG067 | 18 QTR VISWAS NAGAR:PL | TG-VNG067A-1 | 19504231 | 990 | 320 | 248 | 0.97 | 157 | 52 | 214 | 38 | 158 | 66 | 272 | 99 | 2019-06-29 16:00 | 46.4 | 11 | 313 | B | 107 | 78 | 115 | 37 |  |  | 15.6 | 84.4 | 719.21 | 719.51 | 710.51 | 719.51 | 0.3 | [15 empty] | 719.51 | 0.09 | 0.64 | 0.16
149 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG068 | 1S-DL-YP-ETC-DJLM-2201-VNG068 | PATEL GALI NALA:PL | TG-VNG068A-1 | 19504118 | 630 | 200 | 249 | 0.96 | 72 | 30 | 116 | 26 | 101 | 16 | 62 | 48 | 2019-06-06 | 22.5 | 0.5 | 120 | Y | 123 | 111 | 66 | 57 |  | 0.6 | 69.8 | 29.5 | 719.22 | 719.22 | 719.22 | 719.22 | [16 empty] | 719.22 | 0.38 | 0.53 | 0.11
150 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG068 | 1S-DL-YP-ETC-DJLM-2201-VNG068 | PATEL GALI NALA:PL | TG-VNG068A-2 | 19504059 | 990 | 320 | 248 | 0.97 | 122 | 45 | 186 | 25 | 102 | 53 | 217 | 103 | 2019-06-10 23:00 | 35.3 | 2.9 | 234 | B | 104 | 55 | 141 | 86 |  |  | 10.1 | 89.9 | 719.24 | 719.24 | 719.24 | 719.24 | [16 empty] | 719.24 | 0.36 | 0.6 | 0.12
151 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG077 | 1S-DL-YP-ETC-DJLM-2201-VNG077 | SHASTRI GALI (BAGILCHI):PL | TG-VNG077A-1 | 19504159 | 990 | 320 | 241 | 0.98 | 106 | 53 | 221 | 22 | 91 | 31 | 129 | 116 | 2019-06-30 14:30 | 21.3 | 0.7 | 225 | R | 137 | 68 | 95 | 69 |  | 0.1 | 24.9 | 75.1 | 719.19 | 719.19 | 719.19 | 719.19 | [16 empty] | 719.19 | 0.41 | 0.65 | 0.11
152 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG082 | 1S-DL-YP-ETC-DJLM-2201-VNG082 | SHASTRI GALI (NALA):PL | TG-VNG082A-1 | 19504739 | 630 | 200 | 241 | 0.97 | 110 | 54 | 228 | 25 | 105 | 32 | 133 | 112 | 2019-06-02 23:30 | 24.8 | 3.2 | 260 | R | 154 | 66 | 80 | 88 |  |  | 15.6 | 84.4 | 561.52 | 719.22 | 719.22 | 719.22 | 157.3 | [15 empty] | 719.22 | 0.38 | 0.59 | 0.18
153 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG083 | 1S-DL-YP-ETC-DJLM-2201-VNG083 | KARAM GALI:PL | TG-VNG083A-1 | 19502910 | 990 | 320 | 247 | 0.96 | 84 | 18 | 75 | 12 | 51 | 54 | 227 | 165 | 2019-06-08 16:30 | 29.4 | 2.9 | 227 | B | 68 | 55 | 177 | 122 |  |  | 7.8 | 92.2 | 719.54 | 719.54 | 719.54 | 719.54 | [16 empty] | 719.54 | 0.06 | 0.63 | 0.08
154 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG084 | 1S-DL-YP-ETC-DJLM-2201-VNG084 | RAM GALI (NALA):PL | TG-VNG084A-1 | 19503499 | 990 | 320 | 241 | 0.97 | 89 | 48 | 203 | 18 | 77 | 22 | 94 | 119 | 2019-06-09 22:00 | 25 | -0.7 | 205 | R | 134 | 82 | 85 | 52 |  |  | 16 | 84 | 719.33 | 719.33 | 719.33 | 719.33 | [16 empty] | 719.33 | 0.27 | 0.63 | 0.09
155 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG085 | 1S-DL-YP-ETC-DJLM-2201-VNG085 | RAM GALI 60ROAD:PL | TG-VNG085A-1 | 19506352 | 990 | 320 | 247 | 0.97 | 190 | 45 | 182 | 54 | 215 | 91 | 363 | 167 | 2019-06-30 | 53.1 | 9 | 403 | B | 72 | 92 | 136 | 64 |  | 0.1 | 0.1 | 99.8 | 701.24 | 701.24 | 599.54 | 701.24 | [16 empty] | 701.24 | 18.36 | 0.61 | 0.19
156 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG086 | 1S-DL-YP-ETC-DJLM-2201-VNG086 | YUDHISHTER GALI:PL | TG-VNG086A-1 | 19503610 | 990 | 320 | 246 | 0.97 | 161 | 88 | 360 | 44 | 177 | 30 | 121 | 217 | 2019-06-12 15:30 | 37.5 | 11 | 375 | R | 162 | 72 | 65 | 97 |  |  | 30.1 | 69.9 | 495.54 | 719.54 | 719.54 | 719.54 | 224 | [15 empty] | 719.54 | 0.06 | 0.69 | 0.16
157 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG087 | 1S-DL-YP-ETC-DJLM-2201-VNG087 | YUDHISHTER GALI(NALA):PL | TG-VNG087A-1 | 19501237 | 990 | 320 | 240 | 0.97 | 207 | 66 | 296 | 59 | 262 | 83 | 368 | 94 | 2019-06-10 23:30 | 55.9 | 11.8 | 395 | B | 101 | 71 | 127 | 56 |  |  | 19.4 | 80.6 | 718.03 | 719.33 | 463.33 | 709.03 | 1.3 |  |  | 10.3 | [12 empty] | 719.33 | 0.27 | 0.7 | 0.21
158 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG088 | 1S-DL-YP-ETC-DJLM-2201-VNG088 | GALI NO.6 NALA VISWAS NAGAR:PL | TG-VNG088A-1 | 19504778 | 990 | 320 | 248 | 0.98 | 558 | 216 | 863 | 244 | 986 | 98 | 396 | 539 | 2019-06-29 23:30 | 114.8 | 28.7 | 1089 | Y | 112 | 130 | 58 | 72 |  |  | 10.6 | 89.4 | 1.3 | 0.3 | 390.39 | 13.3 | 436.39 | 307.09 | 307.09 | 544.09 | 281.3 | 412 |  | 162 | [8 empty] | 719.39 | 0.21 | 0.6 | 0.56
159 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG089 | 1S-DL-YP-ETC-DJLM-2201-VNG089 | GALI NO-8 VISHWAS NAGAR:PL | TG-VNG089A-1 | 19506258 | 630 | 200 | 249 | 0.98 | 159 | 49 | 198 | 64 | 264 | 46 | 182 | 75 | 2019-06-11 23:30 | 43.2 | -4.4 | 279 | Y | 99 | 116 | 86 | 30 | 13.7 | 14.7 | 33.2 | 38.5 | 611.16 | 508.16 | 685.46 | 604.46 | 102 | 205 | 205 | 108.3 | [12 empty] | 713.16 | 6.44 | 0.59 | 0.25
160 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG089 | 1S-DL-YP-ETC-DJLM-2201-VNG089 | GALI NO-8 VISHWAS NAGAR:PL | TG-VNG089A-2 | 19505774 | 990 | 320 | 256 | 0.97 | 242 | 90 | 367 | 41 | 167 | 112 | 456 | 256 | 2019-06-01 23:30 | 62.7 | 8.3 | 467 | B | 120 | 56 | 124 | 68 |  |  | 3.5 | 96.5 | 534.07 | 713.07 | 481.07 | 631.37 | 179 |  |  | 81.3 | [12 empty] | 713.07 | 6.53 | 0.58 | 0.24
161 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG090 | 1S-DL-YP-ETC-DJLM-2201-VNG090 | GALI NO-10 VISHWAS NAGAR:PL | TG-VNG090A-1 | 19500425 | 990 | 200 | 241 | 0.97 | 268 | 89 | 373 | 108 | 461 | 71 | 302 | 138 | 2019-06-13 22:30 | 61.2 | 23 | 523 | Y | 90 | 123 | 87 | 36 |  |  | 3.7 | 96.3 | 552.09 | 130.49 | 627.24 | 398.13 | 167 | 588.2 | 588.2 | 320.56 | [12 empty] | 719.09 | 0.51 | 0.72 | 0.27
162 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG090 | 1S-DL-YP-ETC-DJLM-2201-VNG090 | GALI NO-10 VISHWAS NAGAR:PL | TG-VNG090A-2 | 19505959 | 990 | 320 | 236 | 0.98 | 920 | 233 | 1014 | 272 | 1197 | 415 | 1887 | 797 | 2019-06-30 23:30 | 252.2 | 35.8 | 1887 | B | 89 | 100 | 110 | 21 | 0.8 | 2.1 | 54.7 | 42.4 |  |  | 0.3 |  | 44.3 | 19 | 19 | 17 | 655.1 | 626.4 | 557.4 | 637.4 | 0.3 | 54.3 | 115.3 | 45.3 |  |  | 16 |  | 700.1 | 19.5 | 0.66 | 0.93
163 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG091 | 1S-DL-YP-ETC-DJLM-2201-VNG091 | BHIKAM SINGH COLONY SCHOOL WALA:PL | TG-VNG091A-1 | 19501963 | 990 | 320 | 246 | 0.98 | 522 | 209 | 879 | 186 | 779 | 127 | 529 | 312 | 2019-06-02 14:00 | 125.9 | 7.4 | 879 | R | 118 | 108 | 75 | 43 |  |  | 0.9 | 99.1 |  |  | 5.3 |  | 57.3 | 179.32 | 179.32 | 312.32 | 661.38 | 539.36 | 8 | 406.36 | [8 empty] | 719.08 | 0.52 | 0.77 | 0.53
164 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG091 | 1S-DL-YP-ETC-DJLM-2201-VNG091 | BHIKAM SINGH COLONY SCHOOL WALA:PL | TG-VNG091A-2 | 19504883 | 990 | 320 | 240 | 0.97 | 526 | 113 | 457 | 214 | 869 | 199 | 808 | 385 | 2019-06-30 | 122.2 | 42.7 | 944 | Y | 76 | 115 | 109 | 39 |  |  | 14.4 | 85.6 | 14.3 |  |  |  | 703.48 | 346.18 | 346.18 | 557.48 |  | 372 | 309.23 | 160.3 | [8 empty] | 718.18 | 1.42 | 0.68 | 0.53
165 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG093 | 1S-DL-YP-ETC-DJLM-2201-VNG093 | NAKUL GALI:PL | TG-VNG093A-1 | 19505067 | 990 | 320 | 247 | 0.96 | 169 | 70 | 283 | 68 | 278 | 31 | 120 | 160 | 2019-06-29 23:30 | 44.2 | 8.8 | 291 | Y | 122 | 123 | 55 | 68 | 91.1 | 8.9 |  |  | 718.04 | 713.04 | 719.34 | 719.34 | 1.3 | 6.3 | 6.3 | [13 empty] | 719.34 | 0.26 | 0.58 | 0.17
166 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG097 | 1S-DL-YP-ETC-DJLM-2201-VNG097 | 18' QTR P/M VISHNU GALI:PM | TG-VNG097A-1 | 19504234 | 990 | 320 | 247 | 0.97 | 161 | 57 | 233 | 38 | 156 | 67 | 275 | 104 | 2019-06-11 22:30 | 37.5 | 6.6 | 297 | B | 111 | 66 | 124 | 58 |  |  | 6.5 | 93.5 | 719.55 | 719.55 | 716.25 | 719.55 | [16 empty] | 719.55 | 0.05 | 0.64 | 0.16
167 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG101 | 1S-DL-YP-ETC-DJLM-2201-VNG101 | BHIKAM SINGH COLONY P/M:PM | TG-VNG101A-1 | 19503004 | 630 | 200 | 253 | 0.99 | 316 | 81 | 328 | 129 | 528 | 106 | 426 | 173 | 2019-06-29 16:30 | 38.6 | -38.2 | 528 | Y | 77 | 130 | 93 | 53 |  |  | 35.2 | 64.8 | 222 |  | 23 | 11 | 496.27 | 396 | 396 | 677.27 | 1.3 | 323.57 | 25.3 | 31.3 | [8 empty] | 719.57 | 0.03 | 0.61 | 0.5
168 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG102 | 1S-DL-YP-ETC-DJLM-2201-VNG102 | SUBHASH GALI (NALA):PL | TG-VNG102A-1 | 19506439 | 990 | 320 | 245 | 0.96 | 105 | 40 | 172 | 41 | 177 | 23 | 97 | 78 | 2019-06-29 23:00 | 26.9 | 4.5 | 200 | B | 106 | 108 | 86 | 22 | 0.1 |  | 1.7 | 98.2 | 717.1 | 717.1 | 717.1 | 717.1 | [16 empty] | 717.1 | 2.5 | 0.58 | 0.11
169 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG105 | 1S-DL-YP-ETC-DJLM-2201-VNG105 | KARKARI MORE:K | TG-VNG105A-1 | 19504837 | 990 | 320 | 246 | 0.97 | 259 | 102 | 418 | 114 | 464 | 42 | 172 | 272 | 2019-06-06 14:30 | 55.2 | 13.2 | 475 | Y | 115 | 126 | 59 | 67 |  |  | 4.4 | 95.6 | 482.52 | 421.28 | 719.51 | 635.22 | 236.59 | 298.23 | 298.23 | 84.29 | [12 empty] | 719.51 | 0.09 | 0.6 | 0.26
170 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG110 | 1S-DL-YP-ETC-DJLM-2201-VNG110 | GALI NO-4-NALA VISHWAS NAGAR:PL | TG-VNG110A-1 | 19505675 | 990 | 320 | 249 | 0.97 | 224 | 64 | 260 | 52 | 210 | 108 | 436 | 205 | 2019-06-11 00:30 | 56.6 | 9 | 480 | B | 89 | 67 | 144 | 77 | 0.1 | 0.2 | 11 | 88.7 | 703.46 | 705.46 | 400.16 | 656.46 | 2 |  |  | 49 | [12 empty] | 705.46 | 14.14 | 0.61 | 0.23
171 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG111 | 1S-DL-YP-ETC-DJLM-2201-VNG111 | BIHARI COLONY EXTN. | TG-VNG111A-1 | 19506872 | 990 | 320 | 241 | 0.97 | 448 | 102 | 419 | 221 | 927 | 125 | 512 | 468 | 2019-06-30 23:00 | 125.1 | 33.6 | 941 | Y | 75 | 138 | 87 | 63 | 0.2 | 7.9 | 89.1 | 2.8 | 130.13 |  | 28.51 | 2.3 | 581.18 | 246.21 | 246.21 | 662.31 |  | 465.1 | 5.3 | 46.3 | [8 empty] | 711.31 | 8.29 | 0.7 | 0.45
172 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG111 | 1S-DL-YP-ETC-DJLM-2201-VNG111 | BIHARI COLONY EXTN. | TG-VNG111A-2 | 19505884 | 630 | 200 | 245 | 0.98 | 562 | 142 | 576 | 200 | 827 | 220 | 910 | 302 | 2019-06-03 | 160.4 | 17.8 | 1071 | Y | 99 | 101 | 100 | 2 | 0.4 | 0.9 | 62.3 | 36.4 |  | 0.3 |  |  | 55.51 | 68.51 | 68.51 | 45.51 | 633.11 | 612.41 | 591.41 | 651.11 | 22.3 | 29 | 40 | 15 | 0.3 | 1 | 2 |  | 712.02 | 7.58 | 0.61 | 0.89
173 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG113 | 1S-DL-YP-ETC-DJLM-2201-VNG113 | BAZAR GALI(NALA):PL | TG-VNG113A-1 | 19504878 | 990 | 320 | 249 | 0.94 | 20 | 17 | 68 | 1 | 6 | 2 | 6 | 62 | 2019-06-30 00:30 | 6.6 | 0.7 | 71 | R | 237 | 47 | 16 | 221 |  |  | 7 | 93 | 719.22 | 719.22 | 719.22 | 719.22 | [16 empty] | 719.22 | 0.38 | 0.52 | 0.02
174 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG113 | 1S-DL-YP-ETC-DJLM-2201-VNG113 | BAZAR GALI(NALA):PL | TG-VNG113A-2 | 19506063 | 400 | 120 | 248 | 0.92 | 62 | 27 | 110 | 31 | 126 | 4 | 16 | 104 | 2019-06-11 22:30 | 32.3 | 1.3 | 136 | R | 123 | 144 | 32 | 112 |  | 0.1 | 3.3 | 96.6 | 683.54 | 701.54 | 704.54 | 704.54 | 21 | 3 | 3 | [13 empty] | 704.54 | 15.06 | 0.53 | 0.16
175 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG132 | 1S-DL-YP-ETC-DJLM-2201-VNG132 | GALI NUMBER - 3 (NALA) VISWAS NGR:PL | TG-VNG132A-1 | 19504413 | 630 | 200 | 248 | 0.96 | 117 | 32 | 132 | 49 | 202 | 37 | 151 | 63 | 2019-06-03 | 29.4 | 6 | 238 | Y | 84 | 136 | 80 | 56 |  |  | 1.1 | 98.9 | 719.45 | 638.15 | 719.45 | 719.45 |  | 81.3 | 81.3 | [13 empty] | 719.45 | 0.15 | 0.57 | 0.19
176 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG158 | 1S-DL-YP-ETC-DJLM-2201-VNG158 | CIVIL HOSPITAL SHAHDARA S/STN | TG-VNG158A-1 | 19501461 | 990 | 320 | 232 | 0.99 | 911 | 341 | 1492 | 295 | 1277 | 275 | 1188 | 270 | 2019-06-30 16:00 | 114.8 | 0.7 | 1526 | R | 112 | 95 | 93 | 19 |  |  | 3.8 | 96.2 | 55.01 | 99.01 | 82.01 | 80.31 | 296.1 | 309.1 | 309.1 | 310.4 | 281.24 | 298.24 | 284.24 | 305.24 | 81.3 | 12.3 | 8 | 22.3 | 5 |  |  |  | 719.05 | 0.55 | 0.47 | 0.92
177 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG170 | 1S-DL-YP-ETC-DJLM-2201-VNG170 | KARAN GALI M.C.D. SCHOOL:PL/M | TG-VNG170A-1 | 19504768 | 630 | 200 | 251 | 0.98 | 297 | 120 | 482 | 79 | 316 | 98 | 394 | 143 | 2019-06-30 | 67.2 | 11.5 | 482 | R | 106 | 89 | 105 | 17 |  |  | 0.6 | 99.4 | 73.3 | 135.08 | 73.3 | 72 | 542.05 | 574.26 | 574.26 | 604.34 | 103.59 | 10 | 92.3 | 43 | [8 empty] | 719.34 | 0.26 | 0.61 | 0.47
178 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG177 | 1S-DL-YP-ETC-DJLM-2201-VNG177 | TELIWARA PARK NEAR GURUDWARA :OD | TG-VNG177A-1 | 19501469 | 630 | 200 | 245 | 0.97 | 509 | 206 | 872 | 118 | 497 | 185 | 762 | 334 | 2019-06-11 23:30 | 115.9 | 32.7 | 953 | R | 119 | 83 | 99 | 36 | 3.6 | 95.1 | 1.3 |  |  | 11 |  |  | 57 | 369.06 | 369.06 | 173.32 | 610.06 | 331.3 | 523.42 | 544.04 | 51.3 | 7.3 | 9 | 1.3 | 0.3 |  |  |  | 719.06 | 0.54 | 0.61 | 0.81
179 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG001 | 1S-DL-YP-ETC-DJLM-2201-VNG001 | CHITRAKOOT CGHS:ID | TG-VNG001A-1 | 19501008 | 990 | 320 | 247 | 0.97 | 98 | 14 | 58 | 54 | 220 | 30 | 125 | 141 | 2019-06-10 23:30 | 28 | 2.2 | 263 | Y | 41 | 185 | 74 | 144 |  |  | 0.1 | 99.9 | 719.58 | 719.58 | 719.58 | 719.58 | [16 empty] | 719.58 | 0.02 | 0.54 | 0.1
180 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG012 | 1S-DL-YP-ETC-DJLM-2201-VNG012 | LSC MKT A-BLK SURAJ MAL VIHAR:ID | TG-VNG012A-1 | 19501049 | 630 | 200 | 236 | 0.97 | 546 | 163 | 697 | 214 | 932 | 169 | 726 | 223 | 2019-06-29 16:30 | 110.9 | 36.8 | 991 | Y | 94 | 122 | 85 | 37 |  | 1.7 | 73.5 | 24.9 |  |  | 0.3 |  | 107 | 13.3 | 13.3 | 78.3 | 608.52 | 544.27 | 515.12 | 635.22 | 2 | 153.55 | 1.3 | 4 |  | 6 |  |  | 717.52 | 2.08 | 0.65 | 0.87
181 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG012 | 1S-DL-YP-ETC-DJLM-2201-VNG012 | LSC MKT A-BLK SURAJ MAL VIHAR:ID | TG-VNG012A-2 | 19501050 | 630 | 200 | 237 | 0.97 | 198 | 53 | 234 | 76 | 339 | 68 | 306 | 93 | 2019-06-08 15:00 | 59.8 | 15.6 | 339 | Y | 88 | 111 | 101 | 23 |  |  | 82.5 | 17.5 | 486.59 | 311.09 | 402.57 | 361.57 | 230.57 | 406.47 | 406.47 | 355.59 | [12 empty] | 717.56 | 2.04 | 0.63 | 0.31
182 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG019 | 1S-DL-YP-ETC-DJLM-2201-VNG019 | ASHOKA NIKETAN:PG | TG-VNG019A-1 | 19504456 | 990 | 320 | 238 | 0.97 | 842 | 330 | 1446 | 267 | 1169 | 246 | 1073 | 335 | 2019-06-11 23:30 | 155.3 | 47.8 | 1492 | R | 117 | 97 | 86 | 31 |  |  | 8.2 | 91.8 | 1.3 | 1.3 | 2.3 | 1.3 | 57.36 | 236.32 | 236.32 | 180.02 | 567.48 | 472.22 | 393.3 | 524.22 | 90.3 | 7 |  | 11.3 |  |  |  |  | 717.24 | 2.36 | 0.59 | 0.85
183 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG023 | 1S-DL-YP-ETC-DJLM-2201-VNG023 | SANJAY AMAR COLONY :PL | TG-VNG023A-1 | 19505881 | 990 | 320 | 240 | 0.96 | 573 | 170 | 690 | 171 | 696 | 232 | 947 | 254 | 2019-06-30 00:30 | 190.4 | 44.5 | 1045 | B | 83 | 91 | 126 | 43 |  |  | 1 | 99 | 1.3 | 1 |  | 0.3 | 551.39 | 453.11 | 453.11 | 295.41 | 159.49 | 258.47 | 660.2 | 416.47 | [8 empty] | 712.58 | 7.02 | 0.72 | 0.58
184 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG035 | 1S-DL-YP-ETC-DJLM-2201-VNG035 | KARKARDOOMA VILLAGE:PM | TG-VNG035A-1 | 19506467 | 990 | 320 | 237 | 0.98 | 958 | 349 | 1466 | 368 | 1551 | 241 | 1012 | 502 | 2019-06-29 23:30 | 281.6 | 54.1 | 1699 | R | 119 | 111 | 70 | 49 | 0.4 | 0.1 | 5 | 94.5 | [7 empty] | 3 | 373.48 | 493.44 | 530.38 | 612.29 | 289.11 | 196.59 |  | 90.14 | 42.44 | 15 |  |  | 705.43 | 14.17 | 0.68 | 0.97
185 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG040 | 1S-DL-YP-ETC-DJLM-2201-VNG040 | ANAND VIHAR B-BLOCK:ID | TG-VNG040A-1 | 19501089 | 990 | 320 | 239 | 0.97 | 539 | 160 | 697 | 165 | 730 | 214 | 938 | 226 | 2019-06-11 23:00 | 108.2 | 30.9 | 938 | B | 90 | 99 | 111 | 21 |  | 12.2 | 87.2 | 0.6 | 49.58 | 68.28 | 17.3 | 26 | 583.56 | 459.58 | 459.58 | 528.56 | 86 | 191.28 | 212.28 | 164.58 | [8 empty] | 719.54 | 0.06 | 0.61 | 0.54
186 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG040 | 1S-DL-YP-ETC-DJLM-2201-VNG040 | ANAND VIHAR B-BLOCK:ID | TG-VNG040A-2 | 19501088 | 990 | 320 | 237 | 0.98 | 598 | 225 | 983 | 184 | 809 | 190 | 828 | 165 | 2019-06-12 | 91.3 | 32.4 | 1034 | R | 108 | 92 | 100 | 16 | 4.5 |  | 13.6 | 81.9 | 26 | 68.48 | 44.43 | 24.3 | 443.59 | 510.41 | 510.41 | 507.59 | 249.28 | 139.58 | 195.58 | 186.58 | [8 empty] | 719.27 | 0.33 | 0.56 | 0.6
187 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG041 | 1S-DL-YP-ETC-DJLM-2201-VNG041 | DAYANAND VIHAR:PG | TG-VNG041A-1 | 19506672 | 990 | 320 | 245 | 0.98 | 588 | 155 | 626 | 214 | 873 | 219 | 892 | 257 | 2019-06-12 00:30 | 153.6 | 24 | 987 | Y | 78 | 110 | 111 | 33 | 0.4 |  | 3.7 | 96 | 121.11 | 11.14 | 6.44 | 17.44 | 531.13 | 417.44 | 417.44 | 488.1 | 52.3 | 275.56 | 271.58 | 199 | [8 empty] | 704.54 | 15.06 | 0.59 | 0.59
188 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG042 | 1S-DL-YP-ETC-DJLM-2201-VNG042 | HANSA APTT. NO-1:ID | TG-VNG042A-1 | 19506065 | 630 | 200 | 248 | 0.97 | 110 | 35 | 148 | 23 | 95 | 53 | 222 | 110 | 2019-06-30 23:30 | 26.4 | 4.6 | 234 | B | 80 | 73 | 147 | 74 |  |  | 0.1 | 99.9 | 719.57 | 719.57 | 628.27 | 719.57 | [16 empty] | 719.57 | 0.03 | 0.51 | 0.18
189 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG042 | 1S-DL-YP-ETC-DJLM-2201-VNG042 | HANSA APTT. NO-1:ID | TG-VNG042A-2 | 19505841 | 630 | 200 | 248 | 0.97 | 114 | 41 | 160 | 30 | 117 | 43 | 172 | 49 | 2019-06-15 00:30 | 62.8 | 3.6 | 187 | B | 102 | 82 | 115 | 33 |  |  | 0.3 | 99.7 | 719.28 | 719.58 | 714.28 | 719.58 | 0.3 | [15 empty] | 719.58 | 0.02 | 0.57 | 0.18
190 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG043 | 1S-DL-YP-ETC-DJLM-2201-VNG043 | HANSA APTT. NO-2:ID | TG-VNG043A-1 | 19506399 | 630 | 200 | 247 | 0.97 | 160 | 62 | 250 | 33 | 134 | 64 | 259 | 121 | 2019-06-12 | 36.2 | 5.8 | 284 | B | 115 | 68 | 117 | 49 |  |  |  | 100 | 567.57 | 696.27 | 542.27 | 627.27 | 128.3 |  |  | 69 | [12 empty] | 696.27 | 23.33 | 0.52 | 0.25
191 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG043 | 1S-DL-YP-ETC-DJLM-2201-VNG043 | HANSA APTT. NO-2:ID | TG-VNG043A-2 | 19501010 | 630 | 200 | 247 | 0.97 | 191 | 63 | 255 | 79 | 323 | 49 | 201 | 106 | 2019-06-11 00:30 | 42.3 | 6.4 | 348 | Y | 96 | 130 | 73 | 57 |  |  | 0.1 | 99.9 | 547.28 | 385.28 | 677.28 | 543.58 | 172.3 | 333 | 333 | 176 |  | 1.3 | [10 empty] | 719.58 | 0.02 | 0.52 | 0.3
192 | 2019-06-02 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG044 | 1S-DL-YP-ETC-DJLM-2201-VNG044 | SHAKTI KIRAN BUILIDING KAKARDOMA GRID:ID | TG-VNG044A-1 | 19502900 | 630 | 200 | 240 | 0.99 | 64 | 26 | 110 | 21 | 89 | 17 | 72 | 34 | 2019-06-27 12:30 | 11.5 | -1.4 | 121 | R | 137 | 99 | 65 | 72 |  | 0.1 | 2.5 | 97.4 | 695.55 | 695.55 | 695.55 | 695.55 | [16 empty] | 695.55 | 0.05 | 0.3 | 0.1
193 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG045 | 1S-DL-YP-ETC-DJLM-2201-VNG045 | JAGRITI ENCLAVE:ID | TG-VNG045A-1 | 19502918 | 990 | 320 | 245 | 0.97 | 484 | 138 | 590 | 157 | 676 | 189 | 807 | 190 | 2019-06-11 23:00 | 94.9 | 34.6 | 807 | B | 90 | 99 | 111 | 21 |  |  | 35.7 | 64.3 | 51 | 65.56 | 42.28 | 34.3 | 666.47 | 597.51 | 597.51 | 639.17 | 2 | 56 | 159.28 | 46 | [8 empty] | 719.47 | 0.13 | 0.6 | 0.49
194 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG045 | 1S-DL-YP-ETC-DJLM-2201-VNG045 | JAGRITI ENCLAVE:ID | TG-VNG045A-2 | 19502925 | 990 | 320 | 244 | 0.97 | 572 | 172 | 738 | 176 | 752 | 225 | 974 | 230 | 2019-06-11 23:00 | 123.6 | 25 | 974 | B | 90 | 99 | 110 | 20 |  |  | 30 | 70 | 2 |  |  |  | 524.2 | 379.29 | 379.29 | 378.57 | 193.28 | 340.19 | 458.21 | 340.51 | [8 empty] | 719.48 | 0.12 | 0.68 | 0.58
195 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG045 | 1S-DL-YP-ETC-DJLM-2201-VNG045 | JAGRITI ENCLAVE:ID | TG-VNG045A-3 | 19504922 | 630 | 200 | 245 | 0.96 | 351 | 119 | 507 | 144 | 612 | 88 | 370 | 210 | 2019-06-03 22:30 | 82.3 | 23.5 | 614 | Y | 101 | 118 | 81 | 37 |  |  | 58.5 | 41.5 | 22.3 | 3 | 93.28 | 13 | 478.25 | 404.55 | 404.55 | 516.55 | 218.58 | 311.58 | 44 | 189.58 | [8 empty] | 719.53 | 0.07 | 0.62 | 0.56
196 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG046 | 1S-DL-YP-ETC-DJLM-2201-VNG046 | SHANTI VIHAR:ID | TG-VNG046A-1 | 19501085 | 630 | 200 | 239 | 0.98 | 236 | 51 | 207 | 94 | 386 | 91 | 378 | 175 | 2019-06-30 00:30 | 40.5 | 5.1 | 448 | B | 74 | 108 | 118 | 44 |  | 0.1 | 12.1 | 87.9 | 603.35 | 367.51 | 297.23 | 443.51 | 116 | 348.44 | 348.44 | 275.44 |  | 3 | 16.3 | [9 empty] | 719.35 | 0.25 | 0.53 | 0.37
197 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG046 | 1S-DL-YP-ETC-DJLM-2201-VNG046 | SHANTI VIHAR:ID | TG-VNG046A-2 | 19501106 | 990 | 320 | 239 | 0.97 | 466 | 196 | 841 | 116 | 500 | 154 | 661 | 296 | 2019-06-28 22:30 | 97.9 | 24.3 | 956 | R | 153 | 107 | 40 | 113 |  | 0.1 | 20.3 | 79.6 | 2.3 | 55.3 | 496.04 | 151.28 | 452.45 | 664 | 664 | 547.02 | 264.15 |  | 19 | 21 | [8 empty] | 719.3 | 0.3 | 0.53 | 0.47
198 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG049 | 1S-DL-YP-ETC-DJLM-2201-VNG049 | GITANJALI APPARTMENT:ID | TG-VNG049A-1 | 19501077 | 990 | 320 | 246 | 0.97 | 214 | 79 | 320 | 78 | 315 | 57 | 231 | 86 | 2019-06-12 01:00 | 50 | 4.4 | 352 | R | 108 | 104 | 88 | 20 |  |  | 0.1 | 99.9 | 674.06 | 690.36 | 719.36 | 713.36 | 45.3 | 29 | 29 | 6 | [12 empty] | 719.36 | 0.24 | 0.53 | 0.22
199 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG049 | 1S-DL-YP-ETC-DJLM-2201-VNG049 | GITANJALI APPARTMENT:ID | TG-VNG049A-2 | 19503013 | 990 | 320 | 246 | 0.98 | 142 | 53 | 227 | 33 | 140 | 57 | 244 | 96 | 2019-06-01 22:30 | 25.8 | -29.4 | 276 | B | 91 | 79 | 130 | 51 |  |  |  | 100 | 719.36 | 719.36 | 718.36 | 719.36 | [16 empty] | 719.36 | 0.24 | 0.57 | 0.14
200 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG050 | 1S-DL-YP-ETC-DJLM-2201-VNG050 | ARYA NAGAR:ID | TG-VNG050A-1 | 19506824 | 990 | 320 | 245 | 0.98 | 699 | 278 | 1188 | 239 | 1013 | 182 | 767 | 366 | 2019-06-30 23:00 | 204.2 | 30.7 | 1261 | Y | 96 | 115 | 89 | 26 | 0.1 | 1.4 | 9.3 | 89.2 |  |  | 1.3 |  | 348.34 | 213 | 213 | 319.35 | 345.58 | 472.02 | 278.3 | 375.27 | 0.3 | 10 | [6 empty] | 695.02 | 24.58 | 0.61 | 0.71
201 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG051 | 1S-DL-YP-ETC-DJLM-2201-VNG051 | ANUPAM APPARTMENT NO-1:ID | TG-VNG051A-1 | 19504925 | 630 | 200 | 236 | 0.97 | 174 | 55 | 244 | 59 | 268 | 60 | 268 | 25 | 2019-06-10 22:30 | 31.3 | 6.4 | 287 | B | 92 | 102 | 106 | 14 |  |  | 3.9 | 96.1 | 671.48 | 587.48 | 549.18 | 603.48 | 48 | 132 | 132 | 116 | [12 empty] | 719.48 | 0.12 | 0.51 | 0.28
202 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG051 | 1S-DL-YP-ETC-DJLM-2201-VNG051 | ANUPAM APPARTMENT NO-1:ID | TG-VNG051A-2 | 19501128 | 990 | 320 | 237 | 0.98 | 155 | 48 | 191 | 58 | 242 | 50 | 205 | 45 | 2019-06-11 23:30 | 26.5 | 3.7 | 281 | Y | 93 | 115 | 92 | 23 | 100 |  |  |  | 719.48 | 719.48 | 719.48 | 719.48 | [16 empty] | 719.48 | 0.12 | 0.51 | 0.16
203 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG052 | 1S-DL-YP-ETC-DJLM-2201-VNG052 | ANUPAM APPTT. NO-2:ID | TG-VNG052A-1 | 19501130 | 990 | 300 | 243 | 0.98 | 176 | 62 | 267 | 58 | 247 | 56 | 237 | 26 | 2019-06-13 21:30 | 33.1 | 4.8 | 297 | R | 107 | 100 | 93 | 14 |  |  | 16.7 | 83.3 | 716.49 | 719.49 | 719.49 | 719.49 | 3 | [15 empty] | 719.49 | 0.11 | 0.52 | 0.18
204 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG052 | 1S-DL-YP-ETC-DJLM-2201-VNG052 | ANUPAM APPTT. NO-2:ID | TG-VNG052A-2 | 19506400 | 630 | 200 | 244 | 0.98 | 169 | 48 | 189 | 53 | 210 | 68 | 274 | 77 | 2019-06-12 00:30 | 30.6 | 4.2 | 281 | B | 83 | 104 | 113 | 30 | 0.1 |  | 16 | 83.9 | 688.48 | 618.48 | 551.48 | 628.48 | 31 | 101 | 101 | 91 | [12 empty] | 719.48 | 0.12 | 0.53 | 0.27
205 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG053 | 1S-DL-YP-ETC-DJLM-2201-VNG053 | ANAND VIHAR C-BLOCK:ID | TG-VNG053A-1 | 19502989 | 990 | 320 | 239 | 0.98 | 367 | 143 | 626 | 124 | 544 | 100 | 435 | 166 | 2019-06-11 23:30 | 58.9 | 4.4 | 640 | R | 119 | 99 | 82 | 37 | 1.9 | 0.5 | 21.7 | 75.9 | 105.28 | 286.14 | 436.24 | 252.14 | 593.49 | 431.33 | 431.33 | 465.33 | 18.3 | [11 empty] | 717.47 | 2.13 | 0.61 | 0.37
206 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG053 | 1S-DL-YP-ETC-DJLM-2201-VNG053 | ANAND VIHAR C-BLOCK:ID | TG-VNG053A-2 | 19502988 | 990 | 320 | 244 | 0.97 | 956 | 325 | 1395 | 346 | 1477 | 285 | 1212 | 235 | 2019-06-11 00:30 | 188.4 | 62.6 | 1553 | Y | 105 | 106 | 89 | 17 |  |  | 37.3 | 62.7 |  |  |  |  | 35.3 | 21.3 | 21.3 | 36.3 | 577.41 | 601.11 | 599.39 | 612.11 | 104 | 91 | 17 | 69 | 0.3 | 4 |  |  | 717.41 | 2.19 | 0.61 | 0.97
207 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG053 | 1S-DL-YP-ETC-DJLM-2201-VNG053 | ANAND VIHAR C-BLOCK:ID | TG-VNG053A-3 | 19504618 | 990 | 320 | 244 | 0.97 | 745 | 364 | 1549 | 190 | 804 | 191 | 804 | 745 | 2019-06-12 | 167.8 | 51.5 | 1574 | R | 130 | 78 | 92 | 52 |  |  | 10.2 | 89.8 |  | 24.58 | 1 |  | 137.28 | 487.22 | 487.22 | 329.15 | 476.39 | 205.47 | 318.18 | 388.52 | 83.3 |  |  |  | 20.3 |  |  |  | 718.07 | 1.53 | 0.59 | 0.75
208 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG054 | 1S-DL-YP-ETC-DJLM-2201-VNG054 | VIVEK APPARTMENT:ID | TG-VNG054A-1 | 19501103 | 990 | 300 | 248 | 0.95 | 109 | 34 | 141 | 50 | 205 | 25 | 102 | 90 | 2019-06-09 23:30 | 31.1 | 4.8 | 216 | Y | 104 | 133 | 63 | 70 |  | 0.1 | 40.5 | 59.5 | 719.4 | 719.4 | 719.4 | 719.4 | [16 empty] | 719.4 | 0.2 | 0.54 | 0.11
209 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG054 | 1S-DL-YP-ETC-DJLM-2201-VNG054 | VIVEK APPARTMENT:ID | TG-VNG054A-2 | 19505840 | 400 | 120 | 248 | 0.97 | 189 | 62 | 257 | 73 | 300 | 54 | 221 | 68 | 2019-06-14 21:30 | 33.8 | 1.9 | 300 | Y | 61 | 122 | 117 | 61 | 0.1 | 0.1 | 9.9 | 89.9 | 719.1 | 709.1 | 705.1 | 719.1 |  | 10 | 10 |  | 0.3 | 0.3 | 0.3 | 0.3 | [8 empty] | 719.4 | 0.2 | 0.19 | 0.47
210 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG055 | 1S-DL-YP-ETC-DJLM-2201-VNG055 | GHRONDA APPARTMENT:ID | TG-VNG055A-1 | 19501082 | 630 | 200 | 246.8286 | 0.96473 | 260.9712 | 94.5521 | 392.6419 | 64.0177 | 265.3364 | 102.4014 | 423.2163 | 145.0302 | 2019-06-29 23:30 | [15 empty] | 367.5 |  |  |  | 351 |  |  |  | 1.5 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.51298 | 0.41424
211 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG055 | 1S-DL-YP-ETC-DJLM-2201-VNG055 | GHRONDA APPARTMENT:ID | TG-VNG055A-2 | 19501105 | 630 | 200 | 247 | 0.97 | 129 | 49 | 207 | 66 | 279 | 14 | 60 | 194 | 2019-06-12 | 22.5 | 4.6 | 280 | Y | 118 | 147 | 35 | 112 |  |  | 3.8 | 96.2 | 697.1 | 599.1 | 719.4 | 719.1 | 22.3 | 120.3 | 120.3 | 0.3 | [12 empty] | 719.4 | 0.2 | 0.46 | 0.21
212 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG056 | 1S-DL-YP-ETC-DJLM-2201-VNG056 | JEEVAN BIMA:ID | TG-VNG056A-1 | 19501043 | 400 | 120 | 243 | 0.97 | 50 | 14 | 57 | 20 | 82 | 16 | 68 | 22 | 2019-06-30 19:30 | 14.1 | 1.4 | 93 | Y | 76 | 129 | 95 | 53 |  | 4.6 | 95.4 |  | 719.57 | 719.57 | 719.57 | 719.57 | [16 empty] | 719.57 | 0.03 | 0.51 | 0.12
213 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG056 | 1S-DL-YP-ETC-DJLM-2201-VNG056 | JEEVAN BIMA:ID | TG-VNG056A-2 | 19501045 | 400 | 120 | 241 | 0.97 | 77 | 37 | 149 | 22 | 92 | 18 | 76 | 66 | 2019-06-11 22:30 | 16 | 1.1 | 149 | R | 129 | 90 | 81 | 48 | 91.6 | 8.4 |  |  | 676.27 | 719.57 | 719.57 | 719.57 | 43.3 | [15 empty] | 719.57 | 0.03 | 0.47 | 0.19
214 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG057 | 1S-DL-YP-ETC-DJLM-2201-VNG057 | LAW APTT.:ID | TG-VNG057A-1 | 19501046 | 400 | 120 | 253 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [7 empty] | 3.9 | 96.1 | 719.36 | 719.36 | 719.36 | 719.36 | [16 empty] | 719.36 | 0.24 |  | 0
215 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG057 | 1S-DL-YP-ETC-DJLM-2201-VNG057 | LAW APTT.:ID | TG-VNG057A-2 | 19506360 | 400 | 120 | 252 | 0.97 | 63 | 9 | 38 | 20 | 82 | 34 | 141 | 89 | 2019-06-02 00:30 | 12.7 | -15.4 | 152 | B | 18 | 125 | 157 | 139 | 0.1 |  |  | 99.9 | 709.36 | 705.36 | 678.06 | 709.36 |  | 4 | 4 | [13 empty] | 709.36 | 10.24 | 0.51 | 0.16
216 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG058 | 1S-DL-YP-ETC-DJLM-2201-VNG058 | BAHUBALI ENCLAVE:ID | TG-VNG058A-1 | 19501122 | 990 | 320 | 240 | 0.97 | 471 | 167 | 723 | 138 | 595 | 166 | 726 | 130 | 2019-06-14 23:30 | 97.9 | 30.2 | 811 | B | 92 | 91 | 117 | 26 |  |  | 27.2 | 72.8 | 56.49 | 67.39 | 1.3 | 15.49 | 619.07 | 601.47 | 601.47 | 633.37 | 43.3 | 50 | 226 | 70 | [8 empty] | 719.26 | 0.34 | 0.66 | 0.48
217 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG063 | 1S-DL-YP-ETC-DJLM-2201-VNG063 | JAGRITI ENCLAVE EXTN.:ID | TG-VNG063A-1 | 19501156 | 990 | 320 | 238 | 0.98 | 794 | 247 | 1094 | 296 | 1314 | 251 | 1119 | 209 | 2019-06-11 23:00 | 137.6 | 33.9 | 1314 | Y | 92 | 107 | 101 | 15 |  |  | 3.6 | 96.4 | 16 | 2.3 | 4 | 4.3 | 400.32 | 289.26 | 289.26 | 334.33 | 300.02 | 420.24 | 397.57 | 377.01 |  | 4.14 |  | 0.3 |  |  |  |  | 716.34 | 3.26 | 0.53 | 0.8
218 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG070 | 1S-DL-YP-ETC-DJLM-2201-VNG070 | AGCR ENCLAVE:ID | TG-VNG070A-1 | 19502985 | 990 | 320 | 250 | 0.99 | 425 | 128 | 510 | 166 | 661 | 131 | 526 | 144 | 2019-06-11 23:00 | 89.1 | 14.7 | 722 | Y | 97 | 114 | 89 | 25 |  |  |  | 100 | 104.3 | 54 | 240 | 99 | 612.15 | 543.45 | 543.45 | 598.45 | 3 | 122 | 4 | 22 | [8 empty] | 719.45 | 0.15 | 0.62 | 0.43
219 | 2019-06-02 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG070 | 1S-DL-YP-ETC-DJLM-2201-VNG070 | AGCR ENCLAVE:ID | TG-VNG070A-2 | 19502991 | 630 | 200 | 248 | 0.97 | 531 | 214 | 861 | 140 | 563 | 177 | 713 | 258 | 2019-06-30 01:00 | 114.5 | 23.5 | 883 | R | 110 | 89 | 101 | 21 |  |  | 1.3 | 98.7 |  | 2.3 | 0.3 |  | 213.51 | 340.3 | 340.3 | 258 | 423.58 | 351.47 | 442.2 | 435.38 | 55.49 |  | 3.57 | 1.09 | 1.09 |  |  |  | 694.47 | 1.13 | 0.55 | 0.84
220 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG070 | 1S-DL-YP-ETC-DJLM-2201-VNG070 | AGCR ENCLAVE:ID | TG-VNG070A-3 | 19504048 | 990 | 320 | 250 | 0.99 | 469 | 171 | 686 | 137 | 549 | 160 | 638 | 120 | 2019-06-30 20:00 | 72.9 | -13.2 | 710 | R | 116 | 94 | 90 | 26 |  | 0.1 | 0.8 | 99.1 | 11 | 81.3 | 194 | 72.3 | 532.48 | 624.53 | 624.53 | 612.53 | 175.35 | 13 | 35 | 34 | [8 empty] | 719.23 | 0.37 | 0.63 | 0.47
221 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG071 | 1S-DL-YP-ETC-DJLM-2201-VNG071 | HARGOVIND ENCLAVE:ID | TG-VNG071A-1 | 19501110 | 990 | 320 | 239 | 0.97 | 830 | 306 | 1354 | 283 | 1256 | 241 | 1063 | 257 | 2019-06-11 00:30 | 178.1 | 33.1 | 1520 | R | 113 | 102 | 85 | 28 |  |  | 0.4 | 99.6 |  | 0.05 | 2.4 | 0.32 | 22.38 | 54.06 | 54.06 | 51.34 | 643.11 | 639.38 | 547.17 | 659.43 | 47.3 | 20 |  | 2 | 0.3 |  |  |  | 713.49 | 6.11 | 0.65 | 0.84
222 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG071 | 1S-DL-YP-ETC-DJLM-2201-VNG071 | HARGOVIND ENCLAVE:ID | TG-VNG071A-2 | 19501074 | 990 | 320 | 244 | 0.97 | 771 | 248 | 1047 | 257 | 1089 | 266 | 1121 | 64 | 2019-06-12 11:30 | 183.3 | 30.9 | 1121 | B | 88 | 99 | 113 | 25 |  |  | 2 | 98 | 4.38 | 2.38 | 0.38 | 3.08 | 400.28 | 236.08 | 236.08 | 202.38 | 306.47 | 473.07 | 638.38 | 506.07 |  |  | 0.14 | [5 empty] | 711.53 | 8.07 | 0.59 | 0.78
223 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG071 | 1S-DL-YP-ETC-DJLM-2201-VNG071 | HARGOVIND ENCLAVE:ID | TG-VNG071A-3 | 19503063 | 630 | 120 | 243 | 0.98 | 720 | 228 | 927 | 268 | 1107 | 224 | 919 | 184 | 2019-06-27 17:00 | 138.8 | 1.7 | 1109 | Y | 98 | 110 | 92 | 18 |  | 0.6 | 56.5 | 42.8 | 0.36 |  | 0.36 | 0.36 | 77.15 | 68.51 | 68.51 | 86.45 | 543.59 | 426 | 502.15 | 515.15 | 85.37 | 185.07 | 52.4 | 97.55 | 5.44 | 33.13 | 5.55 | 12.4 | 713.11 | 6.49 | 0.54 | 1.14
224 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG072 | 1S-DL-YP-ETC-DJLM-2201-VNG072 | KIRAN VIHAR:ID | TG-VNG072A-1 | 19501003 | 990 | 320 | 243 | 0.97 | 651 | 227 | 946 | 187 | 784 | 237 | 996 | 192 | 2019-06-11 23:30 | 139.1 | 42 | 1093 | B | 105 | 86 | 108 | 22 |  |  | 2.7 | 97.3 | 0.3 | 10 |  |  | 302.23 | 486.36 | 486.36 | 349.23 | 416.43 | 223 | 441.41 | 370.13 | [8 empty] | 719.36 | 0.24 | 0.62 | 0.66
225 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG072 | 1S-DL-YP-ETC-DJLM-2201-VNG072 | KIRAN VIHAR:ID | TG-VNG072A-2 | 19501123 | 990 | 320 | 248 | 0.97 | 430 | 144 | 610 | 150 | 628 | 135 | 540 | 81 | 2019-06-30 23:30 | 100.8 | 19.1 | 682 | Y | 101 | 103 | 96 | 7 | 55.4 | 31.7 | 12.9 |  | 150.27 | 200.23 | 143 | 144.57 | 555.39 | 457.43 | 457.43 | 557.39 | 13.3 | 61.3 | 9.3 | 17 | [8 empty] | 719.36 | 0.24 | 0.59 | 0.43
226 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG073 | 1S-DL-YP-ETC-DJLM-2201-VNG073 | DELHI ADMN FLATS:ID | TG-VNG073A-1 | 19501084 | 630 | 200 | 244 | 0.98 | 568 | 211 | 895 | 158 | 669 | 199 | 843 | 205 | 2019-06-30 23:30 | 91.1 | 33.1 | 954 | R | 123 | 76 | 101 | 47 |  |  | 6.1 | 93.9 |  | 0.3 |  |  | 23.3 | 382.42 | 382.42 | 105.3 | 539.56 | 335.14 | 586.25 | 590.26 | 142.3 |  | 28.3 | 22.3 | 12.3 |  |  |  | 718.26 | 1.34 | 0.6 | 0.9
227 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG073 | 1S-DL-YP-ETC-DJLM-2201-VNG073 | DELHI ADMN FLATS:ID | TG-VNG073A-2 | 19501107 | 990 | 320 | 243 | 0.97 | 736 | 221 | 888 | 270 | 1093 | 246 | 985 | 178 | 2019-06-17 07:00 | 214.2 | -47.1 | 1174 | Y | 89 | 112 | 99 | 23 |  | 0.9 | 82 | 17.1 |  |  |  |  | 291.14 | 74.22 | 74.22 | 179.07 | 426.11 | 641.33 | 526.3 | 538.18 |  | 1.3 | [6 empty] | 717.25 | 2.35 | 0.66 | 0.74
228 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG074 | 1S-DL-YP-ETC-DJLM-2201-VNG074 | SHARAD VIHAR:ID | TG-VNG074A-1 | 19501124 | 990 | 320 | 241 | 0.97 | 525 | 193 | 805 | 191 | 790 | 140 | 577 | 221 | 2019-06-30 | 118.5 | 25 | 842 | R | 116 | 99 | 85 | 31 |  |  | 18.7 | 81.3 | 5.49 | 45.39 | 148.57 | 32.09 | 495.07 | 549.47 | 549.47 | 570.47 | 218.3 | 124 | 39.3 | 116.3 | [8 empty] | 719.26 | 0.34 | 0.58 | 0.53
229 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG074 | 1S-DL-YP-ETC-DJLM-2201-VNG074 | SHARAD VIHAR:ID | TG-VNG074A-2 | 19501121 | 990 | 320 | 247 | 0.96 | 366 | 114 | 490 | 105 | 434 | 148 | 623 | 168 | 2019-06-15 | 100.1 | 15.5 | 623 | B | 99 | 90 | 111 | 21 | 2.6 | 84.1 | 8.5 | 4.8 | 327.38 | 384.27 | 238.28 | 327.27 | 391.49 | 335 | 335 | 392 |  |  | 10.3 | [9 empty] | 719.27 | 0.33 | 0.59 | 0.37
230 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG075 | 1S-DL-YP-ETC-DJLM-2201-VNG075 | SAINI ENCLAVE:ID | TG-VNG075A-1 | 19505521 | 990 | 320 | 241 | 0.99 | 752 | 240 | 1007 | 224 | 949 | 288 | 1221 | 248 | 2019-06-11 23:30 | 136 | 29.4 | 1225 | B | 93 | 96 | 111 | 18 | 0.1 | 0.4 | 45.4 | 54.2 |  |  |  |  | 180.04 | 182.33 | 182.33 | 122.34 | 525.48 | 523.19 | 600.48 | 583.18 |  |  | 15 | [5 empty] | 705.52 | 14.08 | 0.64 | 0.76
231 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG075 | 1S-DL-YP-ETC-DJLM-2201-VNG075 | SAINI ENCLAVE:ID | TG-VNG075A-2 | 19503620 | 990 | 320 | 245 | 0.99 | 589 | 173 | 709 | 184 | 751 | 232 | 942 | 216 | 2019-06-15 15:30 | 118.5 | 14 | 951 | B | 90 | 98 | 112 | 22 |  |  | 16.9 | 83.1 | 1 |  | 0.3 |  | 519.59 | 388.3 | 388.3 | 364 | 198.59 | 331.28 | 468.58 | 355.58 | [8 empty] | 719.58 | 0.02 | 0.67 | 0.6
232 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG076 | 1S-DL-YP-ETC-DJLM-2201-VNG076 | SURYA NIKETAN:ID | TG-VNG076A-1 | 19501036 | 990 | 320 | 236 | 0.98 | 754 | 221 | 927 | 300 | 1267 | 233 | 986 | 315 | 2019-06-11 23:30 | 150.1 | 35.3 | 1368 | Y | 95 | 113 | 92 | 21 |  |  | 11.1 | 88.9 |  | 1 |  |  | 275.06 | 172.24 | 172.24 | 256.54 | 442.41 | 503.03 | 347.12 | 460.53 |  | 41.2 | [6 empty] | 717.47 | 2.13 | 0.6 | 0.76
233 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG076 | 1S-DL-YP-ETC-DJLM-2201-VNG076 | SURYA NIKETAN:ID | TG-VNG076A-2 | 19501023 | 990 | 320 | 240 | 0.97 | 1047 | 361 | 1552 | 323 | 1384 | 364 | 1550 | 167 | 2019-06-06 | 203.1 | 42.7 | 1615 | R | 98 | 98 | 104 | 6 |  |  | 18.8 | 81.2 | 0.3 |  |  |  | 62 | 54 | 54 | 34.3 | 544.09 | 553.39 | 564.39 | 566.39 | 104 | 112 | 121 | 114.3 | 9 |  | 14.3 | 4 | 719.39 | 0.21 | 0.59 | 1.06
234 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG076 | 1S-DL-YP-ETC-DJLM-2201-VNG076 | SURYA NIKETAN:ID | TG-VNG076A-3 | 19502911 | 990 | 320 | 236 | 0.98 | 572 | 195 | 812 | 156 | 654 | 221 | 920 | 232 | 2019-06-11 23:30 | 120.7 | 19.1 | 1000 | B | 100 | 90 | 111 | 21 |  | 0.1 | 2 | 97.9 | 40.3 | 71 | 29 | 31.3 | 527.07 | 581.07 | 581.07 | 522.07 | 150.59 | 66.29 | 226 | 164.59 | [8 empty] | 718.36 | 1.24 | 0.56 | 0.58
235 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG078 | 1S-DL-YP-ETC-DJLM-2201-VNG078 | RAM VIHAR:ID | TG-VNG078A-1 | 19505058 | 990 | 320 | 241 | 0.99 | 455 | 144 | 620 | 158 | 689 | 152 | 655 | 59 | 2019-06-12 | 50.8 | -0.7 | 767 | Y | 92 | 106 | 102 | 14 |  |  | 29.3 | 70.7 | 88 | 38 | 31 | 34 | 603.25 | 590.25 | 590.25 | 652.55 | 28 | 91 | 48.3 | 32.3 | [8 empty] | 719.25 | 0.35 | 0.64 | 0.46
236 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG078 | 1S-DL-YP-ETC-DJLM-2201-VNG078 | RAM VIHAR:ID | TG-VNG078A-2 | 19502974 | 990 | 320 | 246 | 0.97 | 483 | 167 | 678 | 172 | 696 | 144 | 582 | 106 | 2019-06-12 01:00 | 119.2 | 31.6 | 758 | Y | 98 | 108 | 95 | 13 |  |  | 4.1 | 95.9 | 40.3 | 17 | 50.3 | 25.3 | 583.58 | 555.28 | 555.28 | 596.28 | 95.3 | 147.3 | 46.3 | 98 | [8 empty] | 719.58 | 0.02 | 0.63 | 0.49
237 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG078 | 1S-DL-YP-ETC-DJLM-2201-VNG078 | RAM VIHAR:ID | TG-VNG078A-3 | 19503470 | 630 | 200 | 246 | 0.98 | 492 | 182 | 751 | 162 | 663 | 147 | 597 | 134 | 2019-06-11 23:30 | 109.9 | 26.2 | 852 | R | 110 | 103 | 87 | 23 |  | 0.1 | 21.5 | 78.4 |  |  |  |  | 122 | 120 | 120 | 158 | 572.58 | 598.28 | 397.59 | 561.58 | 25 | 1.3 | [6 empty] | 719.58 | 0.02 | 0.62 | 0.78
238 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG079 | 1S-DL-YP-ETC-DJLM-2201-VNG079 | SHRESTHA VIHAR:ID | TG-VNG079A-1 | 19502992 | 990 | 320 | 234 | 0.97 | 506 | 176 | 772 | 152 | 665 | 179 | 779 | 111 | 2019-06-11 16:00 | 121.4 | 39.7 | 817 | B | 94 | 103 | 103 | 9 |  |  | 5.6 | 94.4 | 23 | 3.3 | 13 | 6.3 | 605.41 | 558.12 | 558.12 | 571.42 | 91 | 157.59 | 175.59 | 141.29 | [8 empty] | 719.41 | 0.19 | 0.65 | 0.51
239 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG079 | 1S-DL-YP-ETC-DJLM-2201-VNG079 | SHRESTHA VIHAR:ID | TG-VNG079A-2 | 19502995 | 990 | 320 | 240 | 0.98 | 474 | 156 | 679 | 150 | 657 | 168 | 734 | 68 | 2019-06-11 23:30 | 72.1 | 24.3 | 766 | B | 97 | 91 | 112 | 21 |  | 0.1 | 45.3 | 54.6 | 69.28 | 148.45 | 18 | 45.58 | 608.42 | 542.55 | 542.55 | 621.12 | 41.3 | 28 | 107.3 | 52.3 | [8 empty] | 719.4 | 0.2 | 0.6 | 0.48
240 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG080 | 1S-DL-YP-ETC-DJLM-2201-VNG080 | MANAK VIHAR:PG | TG-VNG080A-1 | 19501002 | 990 | 320 | 240 | 0.97 | 611 | 146 | 633 | 196 | 858 | 269 | 1167 | 465 | 2019-06-11 23:30 | 120 | 36.8 | 1261 | B | 68 | 95 | 137 | 69 |  |  | 32.8 | 67.2 | 164.58 | 21 | 0.3 | 6 | 538.43 | 456.11 | 456.11 | 441.41 | 16 | 242.3 | 608.43 | 272 |  |  | 6.3 | [5 empty] | 719.41 | 0.19 | 0.61 | 0.62
241 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG081 | 1S-DL-YP-ETC-DJLM-2201-VNG081 | ANAND VIHAR A-BLOCK:ID | TG-VNG081A-1 | 19501125 | 990 | 320 | 250 | 0.96 | 548 | 164 | 682 | 174 | 733 | 210 | 877 | 175 | 2019-06-11 23:00 | 140.6 | 58.9 | 893 | B | 93 | 98 | 109 | 16 |  |  | 21.5 | 78.5 |  |  |  |  | 473.25 | 420.27 | 420.27 | 390.27 | 246.28 | 299.26 | 470.54 | 329.26 | [8 empty] | 719.53 | 0.07 | 0.71 | 0.55
242 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG081 | 1S-DL-YP-ETC-DJLM-2201-VNG081 | ANAND VIHAR A-BLOCK:ID | TG-VNG081A-2 | 19501090 | 990 | 320 | 243 | 0.97 | 825 | 270 | 1191 | 291 | 1277 | 264 | 1153 | 110 | 2019-06-11 | 170.8 | 70.7 | 1312 | Y | 107 | 98 | 95 | 12 |  |  | 45 | 55 |  |  |  |  | 56 | 107 | 107 | 92.3 | 647.51 | 604.21 | 578.23 | 624.51 | 16 | 8.3 | 1 | 2.3 |  |  |  |  | 719.51 | 0.09 | 0.63 | 0.83
243 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG081 | 1S-DL-YP-ETC-DJLM-2201-VNG081 | ANAND VIHAR A-BLOCK:ID | TG-VNG081A-3 | 19506753 | 630 | 200 | 245 | 0.97 | 356 | 88 | 366 | 89 | 380 | 179 | 811 | 438 | 2019-06-03 00:30 | 132.4 | 21.2 | 925 | B | 83 | 112 | 105 | 29 | 0.4 | 0.4 | 5.7 | 93.5 | 83.3 |  |  |  | 599.22 | 467.54 | 467.54 | 594.52 | 21.3 | 236.28 | 141.29 | 109.3 |  |  | 1 | [5 empty] | 704.22 | 15.38 | 0.59 | 0.56
244 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG092 | 1S-DL-YP-ETC-DJLM-2201-VNG092 | EAST ARJUN NAGAR:K | TG-VNG092A-1 | 19502895 | 990 | 320 | 236 | 0.97 | 723 | 179 | 785 | 235 | 1047 | 309 | 1375 | 512 | 2019-06-30 23:30 | 146.5 | 42.7 | 1375 | B | 83 | 92 | 125 | 42 |  |  | 37.7 | 62.3 | 1 | 3 |  |  | 466.48 | 391.54 | 391.54 | 293.54 | 252 | 324.54 | 561.24 | 425.54 |  |  | 43 | [5 empty] | 719.48 | 0.12 | 0.61 | 0.73
245 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG094 | 1S-DL-YP-ETC-DJLM-2201-VNG094 | SANJAY AMAR COLONY (VEG. MARKET);PL | TG-VNG094A-1 | 19505970 | 990 | 320 | 240 | 0.97 | 510 | 186 | 769 | 162 | 671 | 162 | 669 | 99 | 2019-06-29 23:00 | 169.9 | 52.2 | 786 | R | 106 | 96 | 97 | 10 |  |  | 5.8 | 94.2 |  | 0.3 | 0.3 |  | 377.28 | 530.28 | 530.28 | 481.58 | 336 | 182.3 | 185 | 231.3 | [8 empty] | 713.28 | 6.32 | 0.73 | 0.52
246 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG094 | 1S-DL-YP-ETC-DJLM-2201-VNG094 | SANJAY AMAR COLONY (VEG. MARKET);PL | TG-VNG094A-2 | 19506427 | 630 | 200 | 247 | 0.96 | 345 | 109 | 455 | 111 | 463 | 125 | 524 | 65 | 2019-06-10 22:30 | 229 | 6.8 | 524 | B | 92 | 88 | 120 | 32 |  |  | 0.2 | 99.8 | 553.57 | 560.27 | 399.27 | 528.27 | 157.3 | 151 | 151 | 183 | 1.3 | 1.3 | 1.3 | 1.3 | [8 empty] | 712.57 | 7.03 | 0.3 | 0.55
247 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG095 | 1S-DL-YP-ETC-DJLM-2201-VNG095 | STREET LIGHT CBD:PM | TG-VNG095A-1 | 19504198 | 100 | 40 | 250 | 0.96 | 22 | 4 | 15 | 6 | 23 | 13 | 50 | 32 | 2019-06-18 03:00 | 5.7 | -8.4 | 50 | B | 135 | 24 | 141 | 117 |  |  | 0.9 | 99.1 | 719.48 | 719.48 | 704.18 | 719.18 |  |  |  | 0.3 | [12 empty] | 719.48 | 0.12 | 0.18 | 0.22
248 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG096 | 1S-DL-YP-ETC-DJLM-2201-VNG096 | ST.LIGHT SAI BABA MANDIR:PM | TG-VNG096A-1 | 19505487 | 990 | 320 | 245 | 0.95 | 530 | 140 | 559 | 119 | 493 | 271 | 1165 | 642 | 2019-06-16 03:30 | 199.4 | 67.2 | 1165 | B | 113 | 88 | 99 | 25 | 0.1 | 0.1 | 8 | 91.8 |  | 2 |  |  | 357.19 | 649.41 | 649.41 | 537.41 | 342.52 | 48.3 | 167.3 | 162.3 |  |  | 0.3 | [5 empty] | 700.11 | 19.49 | 0.67 | 0.54
249 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG098 | 1S-DL-YP-ETC-DJLM-2201-VNG098 | MTNL CBD GROUND:ID | TG-VNG098A-1 | 19501119 | 400 | 120 | 244 | 0.98 | 91 | 40 | 170 | 24 | 101 | 27 | 111 | 64 | 2019-06-15 15:00 | 24.8 | -1.9 | 170 | R | 120 | 99 | 81 | 39 |  |  | 0.6 | 99.4 | 580.22 | 719.46 | 717.52 | 716.22 | 139.24 |  |  | 3.24 | [12 empty] | 719.46 | 0.14 | 0.57 | 0.23
250 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG099 | 1S-DL-YP-ETC-DJLM-2201-VNG099 | L.S.C SAINI ENCLAVE:ID | TG-VNG099A-1 | 19501087 | 630 | 200 | 242 | 0.97 | 176 | 36 | 150 | 49 | 205 | 91 | 383 | 211 | 2019-06-12 15:30 | 33.1 | 6.4 | 393 | B | 64 | 81 | 154 | 90 |  |  | 5.8 | 94.2 | 717.57 | 674.57 | 413.3 | 595.48 | 1.3 | 44.3 | 44.3 | 123.39 |  |  | 13 | [9 empty] | 719.27 | 0.33 | 0.42 | 0.28
251 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG099 | 1S-DL-YP-ETC-DJLM-2201-VNG099 | L.S.C SAINI ENCLAVE:ID | TG-VNG099A-2 | 19501086 | 630 | 200 | 237 | 0.97 | 562 | 215 | 925 | 169 | 707 | 179 | 753 | 199 | 2019-06-10 16:00 | 134.3 | 43.7 | 988 | R | 117 | 99 | 85 | 32 | 1.9 | 38.1 | 54.4 | 5.6 |  |  |  |  | 21 | 56.3 | 56.3 | 52 | 522.26 | 629.26 | 590.26 | 640.26 | 172.3 | 33.3 | 4 | 27 | 3.3 |  |  |  | 719.26 | 0.34 | 0.66 | 0.89
252 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG103 | 1S-DL-YP-ETC-DJLM-2201-VNG103 | DAYANAND VIHAR 2:ID | TG-VNG103A-1 | 19501137 | 630 | 200 | 243 | 0.97 | 421 | 139 | 592 | 119 | 504 | 164 | 706 | 175 | 2019-06-29 23:00 | 89.2 | 22.1 | 800 | B | 94 | 78 | 128 | 50 |  | 0.3 | 58.8 | 40.9 | 31.44 | 109.42 | 1.3 | 18.46 | 476.1 | 527.49 | 527.49 | 449.47 | 209.07 | 79.3 | 458.52 | 248.28 |  |  | 11.3 | [5 empty] | 717.01 | 2.59 | 0.56 | 0.67
253 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG103 | 1S-DL-YP-ETC-DJLM-2201-VNG103 | DAYANAND VIHAR 2:ID | TG-VNG103A-2 | 19501081 | 990 | 320 | 244 | 0.97 | 577 | 171 | 718 | 222 | 934 | 184 | 769 | 195 | 2019-06-29 13:30 | 115.6 | 31.6 | 934 | Y | 99 | 103 | 98 | 5 |  |  | 7.9 | 92.1 | 3 | 3 | 14.3 | 3 | 491.07 | 445.37 | 445.37 | 489.07 | 224.12 | 269.42 | 219.38 | 226.12 | [8 empty] | 718.19 | 1.41 | 0.63 | 0.58
254 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG103 | 1S-DL-YP-ETC-DJLM-2201-VNG103 | DAYANAND VIHAR 2:ID | TG-VNG103A-3 | 19505437 | 630 | 200 | 243 | 0.97 | 570 | 186 | 788 | 193 | 816 | 191 | 805 | 25 | 2019-06-29 16:00 | 139.6 | 23.4 | 888 | B | 92 | 96 | 112 | 20 | 0.1 |  | 0.4 | 99.4 | 1 |  |  |  | 246.45 | 238.15 | 238.15 | 178.45 | 456.29 | 456.29 | 608.46 | 516.59 | 2 | 11.3 | 43.28 | 10.3 |  |  |  |  | 706.14 | 13.46 | 0.58 | 0.9
255 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG107 | 1S-DL-YP-ETC-DJLM-2201-VNG107 | LSC RISHABH VIHAR:ID | TG-VNG107A-1 | 19501138 | 990 | 200 | 239 | 0.98 | 385 | 97 | 405 | 144 | 605 | 145 | 618 | 206 | 2019-06-13 22:00 | 76.8 | 25.8 | 673 | B | 77 | 109 | 114 | 37 |  |  | 48.9 | 51.1 | 339.58 | 55.29 | 29 | 86.59 | 380 | 650.29 | 650.29 | 632.59 |  | 14 | 51 | [9 empty] | 719.58 | 0.02 | 0.67 | 0.39
256 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG107 | 1S-DL-YP-ETC-DJLM-2201-VNG107 | LSC RISHABH VIHAR:ID | TG-VNG107A-2 | 19501139 | 990 | 320 | 246 | 0.97 | 539 | 172 | 731 | 133 | 561 | 234 | 996 | 380 | 2019-06-30 23:00 | 136.9 | 41.2 | 996 | B | 102 | 81 | 117 | 36 |  |  | 2.8 | 97.2 |  | 43 |  | 0.3 | 503.58 | 630.28 | 630.28 | 525.58 | 216 | 46.3 | 364 | 193.3 | [8 empty] | 719.58 | 0.02 | 0.66 | 0.54
257 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG109 | 1S-DL-YP-ETC-DJLM-2201-VNG109 | SURAJ MAL VIHAR A-BLOCK:ID | TG-VNG109A-1 | 19502994 | 990 | 320 | 238 | 0.97 | 358 | 107 | 456 | 110 | 469 | 141 | 607 | 145 | 2019-06-01 00:30 | 83.9 | 8.1 | 607 | B | 89 | 96 | 114 | 25 |  |  | 1.3 | 98.7 | 437.48 | 341.15 | 190.2 | 305.49 | 280.14 | 376.47 | 376.47 | 412.13 |  |  | 2.47 | [9 empty] | 718.02 | 1.58 | 0.59 | 0.36
258 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG109 | 1S-DL-YP-ETC-DJLM-2201-VNG109 | SURAJ MAL VIHAR A-BLOCK:ID | TG-VNG109A-2 | 19504391 | 990 | 320 | 231 | 0.98 | 869 | 347 | 1553 | 282 | 1251 | 240 | 1056 | 434 | 2019-06-01 01:00 | 140.6 | 22.1 | 1553 | R | 109 | 102 | 89 | 20 | 0.2 | 0.3 | 16.3 | 83.2 | 1.18 | 0.48 | 1.18 | 0.48 | 121.53 | 186.1 | 186.1 | 183.3 | 548.04 | 516 | 433.26 | 529.4 | 45.13 | 14.15 |  | 3.15 | 0.45 |  |  |  | 717.13 | 2.47 | 0.56 | 0.88
259 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG114 | 1S-DL-YP-ETC-DJLM-2201-VNG114 | JUDGE CLY, KKD COURT:ID | TG-VNG114A-1 | 19506870 | 400 | 120 | 247 | 0.98 | 136 | 43 | 179 | 49 | 207 | 44 | 187 | 25 | 2019-06-01 23:00 | 23.6 | 4.2 | 221 | R | 108 | 97 | 95 | 13 |  |  | 0.5 | 99.5 | 407.3 | 477.23 | 464.3 | 471 | 304.53 | 235 | 235 | 241.23 | [12 empty] | 712.23 | 7.37 | 0.53 | 0.34
260 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG119 | 1S-DL-YP-ETC-DJLM-2201-VNG119 | INSTITUTIONAL AREA:ID | TG-VNG119A-1 | 19504288 | 400 | 120 | 244 | 0.9 | 128 | 35 | 144 | 35 | 144 | 57 | 236 | 92 | 2019-06-13 13:00 | 75.1 | 12.1 | 240 | B | 75 | 89 | 135 | 60 |  |  | 0.3 | 99.7 | 560.07 | 515.37 | 107 | 352.3 | 159.28 | 203.58 | 203.58 | 367.05 |  |  | 10.3 | [9 empty] | 719.35 | 0.25 | 0.63 | 0.32
261 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG122 | 1S-DL-YP-ETC-DJLM-2201-VNG122 | KARKARDOOMA COURT:ID | TG-VNG122A-1 | 19506583 | 630 | 200 | 245 | 0.98 | 416 | 147 | 598 | 151 | 617 | 118 | 477 | 132 | 2019-06-04 13:30 | 78.2 | 0.8 | 636 | Y | 100 | 117 | 83 | 34 | 0.1 | 0.1 | 2.7 | 97.1 | 561.24 | 521.54 | 575.24 | 555.54 | 69.3 | 107.3 | 107.3 | 81.3 | 65.3 | 67 | 40.3 | 59 | [8 empty] | 696.24 | 23.36 | 0.16 | 0.66
262 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG129 | 1S-DL-YP-ETC-DJLM-2201-VNG129 | S/STN NO-2 KARKARDOOMA INST. AREA:ID | TG-VNG129A-1 | 19505382 | 630 | 200 | 247 | 0.98 | 99 | 29 | 120 | 29 | 120 | 40 | 166 | 46 | 2019-06-08 13:30 | 20.4 | 0.2 | 207 | B | 91 | 65 | 144 | 79 |  |  | 0.7 | 99.3 | 712.28 | 712.28 | 707.28 | 712.28 | [16 empty] | 712.28 | 7.32 | 0.37 | 0.16
263 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG129 | 1S-DL-YP-ETC-DJLM-2201-VNG129 | S/STN NO-2 KARKARDOOMA INST. AREA:ID | TG-VNG129A-2 | 19505385 | 630 | 200 | 247 | 0.94 | 105 | 15 | 61 | 8 | 33 | 82 | 330 | 284 | 2019-06-15 17:30 | 41.4 | -2.8 | 330 | B | 123 | 51 | 126 | 75 |  |  | 0.1 | 99.9 | 712.28 | 712.28 | 711.28 | 712.28 | [16 empty] | 712.28 | 7.32 | 0.21 | 0.17
264 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG131 | 1S-DL-YP-ETC-DJLM-2201-VNG131 | MANAK VIHAR (VIGYAN LOK) | TG-VNG131A-1 | 19501109 | 630 | 200 | 245 | 0.97 | 532 | 102 | 411 | 195 | 800 | 234 | 964 | 492 | 2019-06-05 23:30 | 112.2 | 30.4 | 988 | B | 60 | 108 | 132 | 72 | 0.1 | 17.2 | 76 | 6.8 | 42 | 0.3 |  |  | 621.11 | 173.45 | 173.45 | 221.45 | 56.3 | 486.56 | 531.47 | 491.26 |  | 58.3 | 118.56 | 6.3 |  |  | 24 |  | 719.41 | 0.19 | 0.57 | 0.84
265 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG131 | 1S-DL-YP-ETC-DJLM-2201-VNG131 | MANAK VIHAR (VIGYAN LOK) | TG-VNG131A-2 | 19501108 | 990 | 320 | 247 | 0.97 | 221 | 59 | 242 | 100 | 413 | 62 | 254 | 165 | 2019-06-01 23:30 | 46.4 | 10.3 | 435 | Y | 77 | 124 | 99 | 47 |  |  | 1.7 | 98.3 | 719.1 | 523.1 | 713.1 | 700.4 | 0.3 | 196.3 | 196.3 | 19 | [12 empty] | 719.4 | 0.2 | 0.61 | 0.22
266 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG133 | 1S-DL-YP-ETC-DJLM-2201-VNG133 | D BLOCK ANAND VIHAR | TG-VNG133A-1 | 19501012 | 990 | 320 | 242 | 0.98 | 1199 | 468 | 2030 | 353 | 1517 | 378 | 1626 | 469 | 2019-06-11 23:30 | 209.8 | 63.3 | 2030 | R | 104 | 102 | 94 | 10 |  |  | 0.7 | 99.3 |  |  |  |  | 23 | 19 | 19 | 23.3 | 503.3 | 524 | 537.32 | 535.3 | 130.49 | 148.19 | 115.19 | 129.19 | 60.3 | 26.3 | 12.3 | 29.3 | 717.49 | 2.11 | 0.54 | 1.21
267 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG135 | 1S-DL-YP-ETC-DJLM-2201-VNG135 | S/STN.1 LSC KARKARDOOMA NR PETROL PUMP | TG-VNG135A-1 | 19505264 | 630 | 200 | 240 | 0.96 | 180 | 83 | 348 | 43 | 179 | 54 | 227 | 151 | 2019-06-06 17:30 | 62.6 | 3 | 351 | R | 138 | 77 | 85 | 61 | 0.1 | 0.2 | 0.1 | 99.6 | 318.15 | 639.4 | 562.15 | 494.15 | 390.21 | 69.26 | 69.26 | 214.51 | 0.3 | [11 empty] | 709.06 | 10.54 | 0.51 | 0.29
268 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG135 | 1S-DL-YP-ETC-DJLM-2201-VNG135 | S/STN.1 LSC KARKARDOOMA NR PETROL PUMP | TG-VNG135A-2 | 19506469 | 630 | 200 | 239 | 0.97 | 258 | 86 | 373 | 85 | 370 | 87 | 376 | 5 | 2019-06-29 15:30 | 71.8 | -15 | 441 | B | 100 | 102 | 98 | 4 | 0.1 | 0.1 | 9.8 | 89.9 | 392.15 | 369.45 | 385.45 | 363.15 | 313.51 | 335.21 | 335.21 | 343.51 | 2 | 3 | 3 | 1 | [8 empty] | 708.06 | 11.54 | 0.44 | 0.41
269 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG136 | 1S-DL-YP-ETC-DJLM-2201-VNG136 | S/S NUMBER 2, LSC KARKARDOOMA | TG-VNG136A-1 | 19505819 | 630 | 200 | 254 | 0.96 | 39 | 9 | 35 | 15 | 57 | 16 | 62 | 25 | 2019-06-11 17:30 | 15.8 | 0.2 | 91 | Y | 73 | 113 | 114 | 41 |  | 0.1 |  | 99.9 | 709.36 | 709.36 | 709.36 | 709.36 | [16 empty] | 709.36 | 10.24 | 0.32 | 0.06
270 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG136 | 1S-DL-YP-ETC-DJLM-2201-VNG136 | S/S NUMBER 2, LSC KARKARDOOMA | TG-VNG136A-2 | 19501005 | 630 | 200 | 246 | 0.98 | 62 | 12 | 49 | 24 | 103 | 26 | 109 | 57 | 2019-06-10 12:30 | 10.1 | -0.9 | 119 | Y | 67 | 133 | 101 | 66 |  |  | 0.1 | 99.9 | 719.36 | 719.36 | 719.36 | 719.36 | [16 empty] | 719.36 | 0.24 | 0.31 | 0.1
271 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG137 | 1S-DL-YP-ETC-DJLM-2201-VNG137 | 18 KKD COMMERCIAL COMPLEX | TG-VNG137A-1 | 19501538 | 630 | 200 | 246 | 0.89 | 102 | 26 | 105 | 31 | 126 | 45 | 185 | 72 | 2019-06-26 13:00 | 17.9 | -13.3 | 206 | B | 71 | 96 | 133 | 62 |  |  | 2.4 | 97.6 | 719.36 | 719.36 | 674.08 | 719.36 | [16 empty] | 719.36 | 0.24 | 0.3 | 0.16
272 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG137 | 1S-DL-YP-ETC-DJLM-2201-VNG137 | 18 KKD COMMERCIAL COMPLEX | TG-VNG137A-2 | 19506827 | 630 | 200 | 247 | 0.98 | 88 | 21 | 85 | 33 | 136 | 34 | 140 | 53 | 2019-06-30 20:30 | 25.2 | -4 | 148 | Y | 84 | 102 | 115 | 31 | 0.1 |  | 1.1 | 98.9 | 709.06 | 709.06 | 709.06 | 709.06 | [16 empty] | 709.06 | 10.54 | 0.51 | 0.14
273 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG138 | 1S-DL-YP-ETC-DJLM-2201-VNG138 | JJ CLUSTER ANAND VIHAR S/STN | TG-VNG138A-1 | 19505773 | 630 | 200 | 238 | 0.97 | 518 | 147 | 661 | 192 | 872 | 179 | 818 | 190 | 2019-06-30 23:30 | 143.4 | 30 | 885 | Y | 85 | 110 | 104 | 25 |  |  | 8.1 | 91.9 | 1.3 |  | 0.3 |  | 374.17 | 114 | 114 | 241.58 | 325.02 | 585.19 | 465.21 | 457.21 |  | 1.3 | 1.3 | 1.3 |  |  |  |  | 700.49 | 19.11 | 0.57 | 0.82
274 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG139 | 1S-DL-YP-ETC-DJLM-2201-VNG139 | H BLK CBD GROUND I/D | TG-VNG139A-1 | 19503697 | 400 | 120 | 245 | 0.8 | 19 | 18 | 71 | 1 | 3 | 0 | 0 | 69 | 2019-06-03 19:00 | 12.7 | 0.3 | 71 | R | 262 | 38 | 0 | 262 | 0.1 | 0.3 | 42.1 | 57.6 | 571.21 | 571.21 | 571.21 | 571.21 | [16 empty] | 571.21 | 4.39 | 0.34 | 0.05
275 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG140 | 1S-DL-YP-ETC-DJLM-2201-VNG140 | F BLK CBD GROUND I/D | TG-VNG140A-1 | 19504258 | 400 | 120 | 251 | 0.89 | 4 | 0 | 0 | 4 | 14 | 0 | 0 | 14 | 2019-06-02 19:30 | 3.3 | 0.3 | 14 | Y | 0 | 216 | 85 | 216 |  |  | 17.2 | 82.8 | 479.59 | 479.59 | 479.59 | 479.59 | [16 empty] | 479.59 | 0.01 | 0.19 | 0.01
276 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG141 | 1S-DL-YP-ETC-DJLM-2201-VNG141 | B BLK CBD GROUND I/D | TG-VNG141A-1 | 19504282 | 630 | 200 | 243 | 0.93 | 248 | 77 | 324 | 94 | 392 | 77 | 319 | 71 | 2019-06-26 13:30 | 63.9 | -61.2 | 402 | Y | 102 | 105 | 93 | 12 |  | 0.1 | 28.5 | 71.5 | 347.58 | 335.53 | 435.3 | 360.39 | 369.33 | 362.08 | 362.08 | 356.52 |  | 19.3 | [10 empty] | 717.31 | 2.29 | 0.5 | 0.39
277 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG143 | 1S-DL-YP-ETC-DJLM-2201-VNG143 | INSTITUTIONAL AREA S/STN-1 I/D | TG-VNG143A-1 | 19506324 | 630 | 200 | 239 | 0.97 | 161 | 60 | 254 | 45 | 189 | 55 | 232 | 57 | 2019-06-03 12:00 | 46 | 2.8 | 286 | R | 110 | 81 | 109 | 29 |  |  | 1.1 | 98.9 | 677.36 | 676.36 | 679.36 | 683.06 | 34.3 | 35.3 | 35.3 | 29 | [12 empty] | 712.06 | 7.54 | 0.42 | 0.25
278 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG145 | 1S-DL-YP-ETC-DJLM-2201-VNG145 | PLOT NO.14 DDA COMMUNITY CENTER KKD | TG-VNG145A-1 | 19503694 | 990 | 320 | 247 | 0.96 | 154 | 51 | 217 | 53 | 227 | 50 | 213 | 12 | 2019-06-10 12:30 | 42 | 0.7 | 237 | B | 98 | 88 | 114 | 26 |  |  |  | 100 | 719.36 | 719.36 | 719.36 | 719.36 | [16 empty] | 719.36 | 0.24 | 0.32 | 0.16
279 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG146 | 1S-DL-YP-ETC-DJLM-2201-VNG146 | PLOT NO.13 DDA COMMUNITY CENTER KKD | TG-VNG146A-1 | 19505196 | 990 | 300 | 247 | 0.94 | 178 | 61 | 254 | 66 | 274 | 51 | 210 | 56 | 2019-06-14 15:30 | 64.5 | 0.9 | 391 | R | 83 | 117 | 100 | 34 | 0.1 | 0.1 | 0.2 | 99.6 | 708.36 | 702.36 | 709.06 | 709.06 | 0.3 | 6.3 | 6.3 | [13 empty] | 709.06 | 10.54 | 0.39 | 0.18
280 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG147 | 1S-DL-YP-ETC-DJLM-2201-VNG147 | AGCR ENCLAVE:PKG STN | TG-VNG147A-1 | 19501011 | 990 | 320 | 242 | 0.98 | 871 | 266 | 1103 | 344 | 1438 | 261 | 1085 | 345 | 2019-06-11 23:00 | 209 | 44.9 | 1480 | Y | 93 | 110 | 97 | 17 |  |  | 0.8 | 99.2 | 1 | 0.3 | 1 | 1 | 75 | 38 | 38 | 39 | 639.21 | 572.21 | 679.51 | 655.21 | 4.3 | 104.3 | 3.3 | 24.3 |  | 4.3 |  |  | 719.51 | 0.09 | 0.64 | 0.88
281 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG148 | 1S-DL-YP-ETC-DJLM-2201-VNG148 | NAV RACHANA APPTT:ID | TG-VNG148A-1 | 19502382 | 630 | 200 | 252 | 0.97 | 196 | 62 | 245 | 75 | 297 | 58 | 228 | 62 | 2019-06-12 | 45.1 | 8.7 | 308 | Y | 84 | 120 | 96 | 36 |  |  |  | 100 | 661.28 | 458 | 542.28 | 563.28 | 58.3 | 261.58 | 261.58 | 156.3 | [12 empty] | 719.58 | 0.02 | 0.51 | 0.31
282 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG149 | 1S-DL-YP-ETC-DJLM-2201-VNG149 | PLOT NO 15 KARKARDOMA COMM COMP | TG-VNG149A-1 | 19503700 | 990 | 320 | 247 | 0.96 | 171 | 60 | 254 | 45 | 192 | 66 | 283 | 81 | 2019-06-10 14:30 | 24.3 | -33.9 | 283 | B | 101 | 91 | 108 | 17 | 0.1 |  |  | 99.9 | 719.37 | 719.37 | 719.07 | 719.37 | [16 empty] | 719.37 | 0.23 | 0.3 | 0.17
283 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG150 | 1S-DL-YP-ETC-DJLM-2201-VNG150 | PLOT NO 16 KARKARDOMA COMM COMP | TG-VNG150A-1 | 19505566 | 990 | 320 | 247 | 0.96 | 174 | 40 | 165 | 25 | 104 | 109 | 458 | 328 | 2019-06-15 11:00 | 65.3 | -8.3 | 458 | B | 95 | 97 | 108 | 13 | 0.2 | 0.1 |  | 99.7 | 719.36 | 719.36 | 718.36 | 719.36 | [16 empty] | 719.36 | 0.24 | 0.33 | 0.18
284 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG151 | 1S-DL-YP-ETC-DJLM-2201-VNG151 | PLOT NO 17 KARKARDOMA COMM COMP | TG-VNG151A-1 | 19501929 | 990 | 320 | 240 | 0.99 | 127 | 33 | 141 | 42 | 180 | 51 | 219 | 67 | 2019-06-14 14:30 | 19.1 | 0.7 | 219 | B | 90 | 86 | 123 | 37 |  |  | 0.5 | 99.5 | 716.16 | 716.16 | 716.16 | 716.16 | [16 empty] | 716.16 | 3.44 | 0.33 | 0.13
285 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG152 | 1S-DL-YP-ETC-DJLM-2201-VNG152 | KKD INSTITIONAL AREA S/ST-3 | TG-VNG152A-1 | 19505291 | 630 | 200 | 244 | 0.98 | 315 | 108 | 445 | 121 | 499 | 85 | 348 | 132 | 2019-06-14 14:30 | 77.4 | 6.2 | 499 | Y | 98 | 112 | 90 | 22 | 0.1 |  | 0.1 | 99.9 | 108 | 28 | 164.3 | 74 | 573.25 | 606.27 | 606.27 | 617.25 | 30.3 | 77.28 | 14.3 | 20.3 | [8 empty] | 711.55 | 8.05 | 0.55 | 0.5
286 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG152 | 1S-DL-YP-ETC-DJLM-2201-VNG152 | KKD INSTITIONAL AREA S/ST-3 | TG-VNG152A-2 | 19506325 | 630 | 200 | 247 | 0.97 | 68 | 15 | 59 | 34 | 139 | 18 | 74 | 74 | 2019-06-27 16:30 | 19.2 | 2.4 | 156 | Y | 28 | 230 | 42 | 202 |  |  | 0.1 | 99.9 | 711.39 | 711.39 | 711.39 | 711.39 | [16 empty] | 711.39 | 8.21 | 0.41 | 0.11
287 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG153 | 1S-DL-YP-ETC-DJLM-2201-VNG153 | E-BLK CBD GROUND | TG-VNG153A-1 | 19504285 | 400 | 120 | 249 | 0.99 | 47 | 17 | 69 | 19 | 76 | 10 | 41 | 32 | 2019-06-10 13:00 | 6.6 | -0.8 | 86 | Y | 93 | 117 | 91 | 26 |  |  | 0.2 | 99.8 | 718.2 | 718.2 | 718.2 | 718.2 | [16 empty] | 718.2 | 1.4 | 0.34 | 0.12
288 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG159 | 1S-DL-YP-ETC-DJLM-2201-VNG159 | EAST END CLUB | TG-VNG159A-1 | 19501926 | 100 | 40 | 248 | 0.97 | 53 | 26 | 107 | 11 | 46 | 16 | 63 | 54 | 2019-06-10 14:00 | 10.5 | -8.4 | 107 | R | 107 | 59 | 134 | 75 |  | 0.1 | 4.7 | 95.3 | 395 | 648.18 | 236 | 394.3 | 292.18 | 70 | 70 | 321.18 | 32.3 | 1.3 | 42 | 4 | [8 empty] | 719.48 | 0.12 | 0.34 | 0.53
289 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG162 | 1S-DL-YP-ETC-DJLM-2201-VNG162 | KKD Court New S/Stn | TG-VNG162A-1 | 19502938 | 630 | 200 | 244 | 0.98 | 463 | 132 | 532 | 160 | 651 | 171 | 694 | 145 | 2019-06-06 13:30 | 77.7 | -0.5 | 694 | B | 92 | 103 | 105 | 13 |  |  | 2.7 | 97.3 | 567.55 | 556.25 | 562.55 | 560.25 | 91.3 | 95 | 95 | 92.3 | 60.3 | 68.3 | 69.3 | 67 |  |  | 0.3 | [5 empty] | 719.55 | 0.05 | 0.15 | 0.74
290 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG163 | 1S-DL-YP-ETC-DJLM-2201-VNG163 | A - BLK S/STN, CBD GROUND | TG-VNG163A-1 | 19503657 | 630 | 200 | 249 | 0.92 | 286 | 97 | 408 | 94 | 391 | 96 | 403 | 15 | 2019-06-06 09:30 | 52.9 | -66.2 | 425 | R | 107 | 99 | 94 | 13 |  |  | 8.5 | 91.5 | 403.57 | 427.45 | 458 | 419.15 | 250.4 | 266.47 | 266.47 | 258.11 | 61.49 | 21.54 | 23.08 | 39 | [8 empty] | 716.26 | 3.34 | 0.41 | 0.45
291 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG164 | 1S-DL-YP-ETC-DJLM-2201-VNG164 | C- BLK S/STN, CBD GROUND | TG-VNG164A-1 | 19505796 | 400 | 120 | 244 | 0.99 | 22 | 9 | 35 | 13 | 54 | 0 | 0 | 48 | 2019-06-13 13:00 | 9.5 | -1.2 | 60 | Y | 151 | 148 | 1 | 150 |  |  | 9.1 | 90.9 | 710.57 | 710.57 | 710.57 | 710.57 | [16 empty] | 710.57 | 9.03 | 0.46 | 0.06
292 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG167 | 1S-DL-YP-ETC-DJLM-2201-VNG167 | D-Blk S/Stn Cbd Ground, Cbd Ground | TG-VNG167A-1 | 19505978 | 400 | 120 | 251 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-11 11:30 | 0.1 | 0.1 | 0 | Y | 0 | 100 | 100 | 100 |  |  | 23.5 | 76.5 | 708.27 | 708.27 | 708.27 | 708.27 | [16 empty] | 708.27 | 11.33 | 0 | 0
293 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG168 | 1S-DL-YP-ETC-DJLM-2201-VNG168 | G Block S/Stn Cbd, Cbd Ground | TG-VNG168A-1 | 19504681 | 400 | 120 | 251 | 0.97 | 23 | 7 | 27 | 11 | 44 | 5 | 21 | 20 | 2019-06-10 13:30 | 6.1 | -0.3 | 53 | Y | 83 | 207 | 10 | 197 |  | 0.1 | 96.6 | 3.3 | 719.42 | 719.42 | 719.42 | 719.42 | [16 empty] | 719.42 | 0.18 | 0.41 | 0.06
294 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG171 | 1S-DL-YP-ETC-DJLM-2201-VNG171 | Priyadarshni Working Women,Ymca Hostel | TG-VNG171A-1 | 19504683 | 400 | 120 | 245 | 0.89 | 22 | 5 | 22 | 7 | 26 | 10 | 39 | 16 | 2019-06-06 16:30 | 13.5 | 1.1 | 42 | B | 78 | 89 | 133 | 55 |  |  | 1.7 | 98.3 | 719.48 | 719.48 | 719.48 | 719.48 | [16 empty] | 719.48 | 0.12 | 0.51 | 0.05
295 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG176 | 1S-DL-YP-ETC-DJLM-2201-VNG176 | SHAKTI KIRAN BUILIDING CBD-2 GRID:OD | TG-VNG176A-1 | 19504834 | 630 | 200 | 242 | 0.94 | 173 | 54 | 218 | 55 | 220 | 64 | 256 | 37 | 2019-06-14 12:30 | 72.2 | 10.1 | 271 | B | 95 | 91 | 114 | 23 |  |  | 0.8 | 99.2 | 518.3 | 564.59 | 479.3 | 519.3 | 201.28 | 154.59 | 154.59 | 200.28 | [12 empty] | 719.58 | 0.02 | 0.54 | 0.27
296 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG176 | 1S-DL-YP-ETC-DJLM-2201-VNG176 | SHAKTI KIRAN BUILIDING CBD-2 GRID:OD | TG-VNG176A-2 | 19504982 | 630 | 200 | 239 | 0.9 | 306 | 111 | 479 | 94 | 413 | 101 | 440 | 58 | 2019-06-10 09:30 | 125.1 | -0.5 | 479 | R | 108 | 90 | 102 | 18 |  |  | 7 | 93 | 389.58 | 398.58 | 389.58 | 392.28 | 259.57 | 320.27 | 320.27 | 310.57 | 70 | 0.3 | 25.3 | 16.3 | [8 empty] | 719.55 | 0.05 | 0.35 | 0.49
297 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG179 | 1S-DL-YP-ETC-DJLM-2201-VNG179 | HOTEL HOLIDAY INN PKG | TG-VNG179A-1 | 19504521 | 400 | 120 | 249 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [7 empty] | 29.2 | 70.8 | 719.47 | 719.47 | 719.47 | 719.47 | [16 empty] | 719.47 | 0.13 |  | 0
298 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG181 | 1S-DL-YP-ETC-DJLM-2201-VNG181 | Anand Vihar Police Station | TG-VNG181A-1 | 19506387 | 400 | 120 | 247 | 0.99 | 54 | 18 | 74 | 16 | 62 | 20 | 80 | 16 | 2019-06-03 15:30 | 16 | -2.6 | 106 | B | 99 | 85 | 116 | 31 |  |  | 0.1 | 99.9 | 712.53 | 712.53 | 712.53 | 712.53 | [16 empty] | 712.53 | 7.07 | 0.7 | 0.14
299 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG182 | 1S-DL-YP-ETC-DJLM-2201-VNG182 | UTCS STAFF QUARTER | TG-VNG182A-1 | 19505429 | 400 | 120 | 244 | 0.99 | 28 | 12 | 50 | 15 | 62 | 2 | 7 | 50 | 2019-06-03 23:30 | 4.9 | -1.1 | 78 | Y | 99 | 196 | 5 | 191 |  |  | 5.6 | 94.4 | 712.48 | 712.48 | 712.48 | 712.48 | [16 empty] | 712.48 | 7.12 | 0.48 | 0.07
300 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG189 | 1S-DL-YP-ETC-DJLM-2201-VNG189 | EMPLOYMENT EXCHANGE OFFICE S/S | TG-VNG189A-1 | 19506024 | 400 | 120 | 248 | 0.98 | 193 | 66 | 276 | 64 | 264 | 64 | 266 | 11 | 2019-06-06 12:00 | 48.6 | 0.5 | 317 | R | 114 | 75 | 111 | 39 |  |  | 6.5 | 93.5 | 528 | 540.3 | 531.3 | 534.3 | 93 | 171.28 | 171.28 | 131.3 | 92.28 | 1.3 | 112.58 | 47.28 | [8 empty] | 713.28 | 6.32 | 0.26 | 0.48
301 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG200 | 1S-DL-YP-ETC-DJLM-2201-VNG200 | JAGRITI ENCLAVE PHASE-III S/Stn No.1 | TG-VNG200A-1 | 19506747 | 990 | 320 | 247 | 0.96 | 99 | 41 | 167 | 9 | 36 | 49 | 202 | 151 | 2019-06-08 21:00 | 32.6 | 1.3 | 202 | B | 77 | 81 | 142 | 65 | 0.1 | 0.1 | 2 | 97.9 | 699.23 | 699.23 | 699.23 | 699.23 | [16 empty] | 699.23 | 20.37 | 0.22 | 0.1
302 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG201 | 1S-DL-YP-ETC-DJLM-2201-VNG201 | INDER PURI - KKD | TG-VNG201A-1 | 19506696 | 630 | 200 | 247 | 0.97 | 142 | 44 | 180 | 24 | 99 | 74 | 302 | 178 | 2019-06-11 22:00 | 40.6 | 6.8 | 304 | B | 102 | 49 | 150 | 101 | 0.1 | 0.1 | 18 | 81.8 | 626.28 | 706.58 | 216.58 | 658.28 | 80.3 |  |  | 48.3 | [12 empty] | 706.58 | 13.02 | 0.69 | 0.23
303 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG203 | 1S-DL-YP-ETC-DJLM-2201-VNG203 | JAGRITI ENCLAVE PHASE-III S/Stn No.2 | TG-VNG203A-1 | 19506749 | 990 | 320 | 247 | 0.97 | 34 | 22 | 92 | 7 | 30 | 5 | 21 | 67 | 2019-06-28 16:00 | 15 | 0.6 | 92 | R | 98 | 100 | 102 | 4 |  | 0.1 | 6.6 | 93.4 | 700.48 | 700.48 | 700.48 | 700.48 | [16 empty] | 700.48 | 19.12 | 0.57 | 0.03