## Loading Condition > 80%
MIS Report of Distribution Transformer - Jun19
Jun19 1210 KARKARDOOMA (Loading Condition > 80% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI038 | 1S-DL-YP-ETC-DJLM-2203-JHI038 | D-BLK VIVEK VIHAR PLM:PL | TG-JHI038A-2 | 19505944 | 630 | 200 | 245 | 0.97 | 546 | 91 | 376 | 306 | 1357 | 150 | 601 | 890 | 2019-06-16 03:30 | 197 | 31.8 | 1357 | Y | 88 | 94 | 118 | 30 | 0.1 |  | 9.2 | 90.6 |  |  |  |  | 284.36 | 283.21 | 283.21 | 190.59 | 416.56 | 417.41 | 520.38 | 510.03 |  |  | 83.3 | 0.3 |  | 0.3 |  |  | 701.32 | 18.28 | 0.55 | 0.87
2 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI039 | 1S-DL-YP-ETC-DJLM-2203-JHI039 | PRATAP KHAND:ID | TG-JHI039A-3 | 19506493 | 630 | 200 | 246 | 0.96 | 496 | 183 | 754 | 176 | 728 | 137 | 567 | 175 | 2019-06-30 00:30 | 135 | 41.4 | 811 | R | 111 | 95 | 94 | 17 |  | 0.1 | 21.1 | 78.8 |  | 2 |  |  | 205.45 | 312.15 | 312.15 | 259.45 | 459 | 385.3 | 408.4 | 442 | 37 | 2 | [6 empty] | 701.45 | 18.15 | 0.59 | 0.79
3 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI062 | 1S-DL-YP-ETC-DJLM-2203-JHI062 | JANTA QTR. VIVEK VIHAR:PL | TG-JHI062A-1 | 19501614 | 630 | 200 | 241 | 0.97 | 584 | 202 | 915 | 172 | 779 | 211 | 963 | 165 | 2019-06-30 23:30 | 121.4 | 36.8 | 1065 | B | 108 | 74 | 118 | 44 | 0.1 |  | 5.4 | 94.6 |  | 4.3 |  |  | 67.58 | 397.39 | 397.39 | 113.11 | 547.15 | 277 | 524.15 | 528.58 | 64.56 | 2.3 | 112.26 | 39.3 | 1.3 |  | 16 |  | 684.35 | 35.25 | 0.58 | 0.93
4 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI063 | 1S-DL-YP-ETC-DJLM-2203-JHI063 | MAHILA COLLEGE VIVEK VIHAR:PL | TG-JHI063A-2 | 19505797 | 630 | 200 | 245 | 0.97 | 557 | 169 | 717 | 158 | 676 | 230 | 989 | 294 | 2019-06-30 23:30 | 119.2 | 29.8 | 989 | B | 90 | 93 | 116 | 26 | 0.3 | 0.1 | 41.4 | 58.2 | 5 |  |  |  | 321.44 | 258.33 | 258.33 | 232.44 | 361.04 | 432.43 | 451.32 | 436.34 | 4.58 | 2 | 95.56 | 23.58 | 0.3 |  | 6.3 |  | 693.16 | 26.44 | 0.55 | 0.88
5 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI064 | 1S-DL-YP-ETC-DJLM-2203-JHI064 | SHIVA KHAND:PL | TG-JHI064A-1 | 19501632 | 630 | 200 | 244 | 0.97 | 545 | 178 | 744 | 145 | 605 | 222 | 946 | 296 | 2019-06-30 | 103.5 | 35.9 | 954 | B | 97 | 87 | 115 | 28 |  | 0.9 | 33.2 | 65.9 | 1.3 | 10.3 | 1 | 0.3 | 281.55 | 361.55 | 361.55 | 268.55 | 432.53 | 346.53 | 447.54 | 441.53 | 3 |  | 83.59 | 8 |  |  | 3 |  | 719.18 | 0.42 | 0.55 | 0.86
6 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI071 | 1S-DL-YP-ETC-DJLM-2203-JHI071 | VIVEK VIHAR SUPER BAZAR:PL | TG-JHI071A-1 | 19506230 | 990 | 320 | 233 | 0.99 | 777 | 201 | 910 | 193 | 870 | 384 | 1807 | 917 | 2019-06-30 22:30 | 231.7 | 13.1 | 1807 | B | 87 | 95 | 118 | 31 | 0.6 | 1.7 | 53.2 | 44.5 | 10 | 8 | 0.3 | 1.3 | 411.26 | 355.56 | 355.56 | 309.56 | 280.06 | 337.06 | 509.06 | 390.06 |  |  | 33 |  |  | 0.3 | 1 |  | 701.32 | 18.28 | 0.57 | 0.79
7 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI074 | 1S-DL-YP-ETC-DJLM-2203-JHI074 | C-BLK DSIDC JLM COLONY:ID | TG-JHI074A-1 | 19505838 | 400 | 120 | 244 | 0.97 | 402 | 144 | 601 | 120 | 496 | 138 | 574 | 94 | 2019-06-02 00:30 | 93.4 | 18.2 | 685 | R | 110 | 94 | 97 | 16 | 0.1 | 0.1 | 8.6 | 91.2 |  |  |  |  | 30.58 | 125.22 | 125.22 | 67.28 | 556.51 | 551.27 | 510.37 | 567.21 | 107 | 41 | 71.3 | 82.3 | 23 |  | 1.3 | 0.3 | 717.49 | 2.11 | 0.57 | 1
8 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI126 | 1S-DL-YP-ETC-DJLM-2203-JHI126 | A-BLK VIVEK VIHAR PH-2 | TG-JHI126A-1 | 19505009 | 990 | 320 | 245 | 0.97 | 811 | 265 | 1115 | 279 | 1170 | 266 | 1130 | 49 | 2019-06-29 23:30 | 157.5 | 51.5 | 1263 | B | 90 | 99 | 111 | 21 |  | 0.1 | 37.9 | 62 |  |  |  |  | 226.42 | 134.59 | 134.59 | 111.46 | 491.54 | 583.37 | 626.2 | 606.5 | 1 | 1 | 33.3 | 1 |  |  |  |  | 719.36 | 0.24 | 0.62 | 0.82
9 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | VNG002 | 1S-DL-YP-ETC-DJLM-2201-VNG002 | YOJNA VIHAR C-BLOCK:ID | TG-VNG002A-1 | 19504191 | 990 | 320 | 246 | 0.97 | 920 | 287 | 1237 | 327 | 1408 | 305 | 1317 | 148 | 2019-06-11 23:00 | 186.9 | 58.9 | 1408 | Y | 91 | 99 | 110 | 19 |  |  | 19.8 | 80.2 |  |  |  |  | 131.45 | 108.58 | 108.58 | 67.28 | 570.13 | 536 | 626.28 | 606 | 17.3 | 74.3 | 70 | 46 |  |  |  |  | 719.28 | 0.32 | 0.61 | 0.93
10 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | VNG048 | 1S-DL-YP-ETC-DJLM-2201-VNG048 | SURAJ MAL VIHAR C-BLOCK:ID | TG-VNG048A-1 | 19502894 | 990 | 320 | 251 | 0.96 | 866 | 314 | 1255 | 282 | 1126 | 270 | 1077 | 159 | 2019-06-03 02:00 | 211.2 | 67 | 1377 | R | 107 | 101 | 92 | 15 |  |  | 1.7 | 98.3 | 2.3 | 2.3 | 2.3 | 2.3 | 93 | 126.58 | 126.58 | 119.58 | 574.26 | 569.58 | 542.56 | 585.56 | 49.58 | 20.28 | 0.3 | 11.3 |  |  |  |  | 719.54 | 0.06 | 0.59 | 0.87
11 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | VNG048 | 1S-DL-YP-ETC-DJLM-2201-VNG048 | SURAJ MAL VIHAR C-BLOCK:ID | TG-VNG048A-3 | 19504546 | 630 | 200 | 245 | 0.97 | 510 | 123 | 524 | 210 | 914 | 176 | 750 | 339 | 2019-06-08 23:30 | 119.1 | 25.3 | 1012 | Y | 77 | 128 | 95 | 51 | 1 | 12.6 | 82.8 | 3.5 | 12 |  | 6 |  | 473.26 | 64 | 64 | 264.26 | 234.3 | 555.26 | 391 | 454 |  | 96.3 | 3.3 | 1.3 |  | 4 |  |  | 719.56 | 0.04 | 0.58 | 0.81
12 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | VNG104 | 1S-DL-YP-ETC-DJLM-2201-VNG104 | YOJANA VIHAR B-BLOCK:ID | TG-VNG104A-2 | 19503016 | 400 | 120 | 238 | 0.97 | 348 | 85 | 365 | 115 | 497 | 148 | 647 | 244 | 2019-06-16 00:30 | 72.9 | 15.2 | 650 | B | 81 | 100 | 120 | 39 |  | 17.6 | 66.3 | 16.1 | 8 |  |  |  | 356.15 | 186.45 | 186.45 | 183.15 | 355.25 | 500.55 | 445.42 | 515.25 |  | 32 | 138 | 21 |  |  | 18.3 |  | 719.4 | 0.2 | 0.59 | 0.87
13 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG007 | 1S-DL-YP-ETC-DJLM-2201-VNG007 | RAMA BLOCK(BABU RAM SCHOOL):K | TG-VNG007A-1 | 19501463 | 630 | 200 | 243 | 0.97 | 459 | 189 | 799 | 140 | 584 | 129 | 541 | 239 | 2019-06-11 23:00 | 95.2 | 22.1 | 883 | R | 123 | 83 | 93 | 40 |  |  | 28.2 | 71.8 |  | 13 | 2 |  | 102 | 440.45 | 440.45 | 264.16 | 574.15 | 265.3 | 406.23 | 454.59 | 43 | [7 empty] | 719.15 | 0.45 | 0.62 | 0.73
14 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG007 | 1S-DL-YP-ETC-DJLM-2201-VNG007 | RAMA BLOCK(BABU RAM SCHOOL):K | TG-VNG007A-2 | 19503651 | 990 | 320 | 244 | 0.97 | 928 | 353 | 1476 | 258 | 1072 | 317 | 1318 | 352 | 2019-06-12 | 175.9 | 55.2 | 1593 | R | 110 | 88 | 101 | 22 |  |  | 3.5 | 96.5 |  |  |  |  | 67 | 178 | 178 | 88.01 | 535.53 | 541.23 | 585.22 | 585.22 | 104 |  | 50.3 | 46 | 12.3 |  |  |  | 719.23 | 0.37 | 0.58 | 0.94
15 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG010 | 1S-DL-YP-ETC-DJLM-2201-VNG010 | ANAJ MANDI:K | TG-VNG010A-2 | 19505882 | 990 | 320 | 245 | 0.98 | 954 | 299 | 1242 | 365 | 1527 | 290 | 1205 | 305 | 2019-06-10 | 232 | 49.3 | 1541 | B | 104 | 100 | 96 | 8 |  | 0.1 | 4.7 | 95.1 |  |  |  |  | 60 | 71.3 | 71.3 | 48.3 | 593.15 | 610.15 | 649.15 | 648.45 | 62.3 | 35 | 12 | 22.3 | 4 | 3 | 0.3 |  | 719.45 | 0.15 | 0.58 | 0.96
16 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG011 | 1S-DL-YP-ETC-DJLM-2201-VNG011 | DELHI GATE:K | TG-VNG011A-1 | 19506806 | 990 | 320 | 240 | 0.98 | 792 | 276 | 1180 | 291 | 1238 | 225 | 950 | 264 | 2019-06-10 23:30 | 224.3 | 62.1 | 1359 | R | 99 | 109 | 92 | 17 |  | 0.9 | 63.1 | 36 |  |  |  |  | 113.27 | 75.27 | 75.27 | 107.27 | 588.27 | 597.57 | 543.57 | 595.57 | 2 | 30.3 |  | 0.3 |  |  |  |  | 703.54 | 16.06 | 0.65 | 0.8
17 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG013 | 1S-DL-YP-ETC-DJLM-2201-VNG013 | BIHARI COLONY:K | TG-VNG013A-3 | 19504190 | 990 | 320 | 236 | 0.97 | 1048 | 354 | 1571 | 353 | 1587 | 341 | 1522 | 59 | 2019-06-11 00:30 | 174.4 | 78 | 1590 | B | 98 | 98 | 104 | 6 |  | 0.1 | 17.3 | 82.6 |  |  |  |  | 34.13 | 28 | 28 | 23.3 | 556.15 | 593.58 | 541.58 | 566.28 | 121.59 | 93.59 | 142.29 | 124.59 | 7 | 3.3 | 18.3 | 4.3 | 719.27 | 0.33 | 0.6 | 1.06
18 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG013 | 1S-DL-YP-ETC-DJLM-2201-VNG013 | BIHARI COLONY:K | TG-VNG013A-2 | 19506743 | 990 | 320 | 249 | 0.97 | 855 | 339 | 1410 | 278 | 1149 | 238 | 971 | 383 | 2019-06-30 23:00 | 192.6 | 68.8 | 1410 | R | 116 | 105 | 79 | 37 | 0.4 | 1.1 | 87.9 | 10.6 |  |  |  |  | 79.57 | 115.12 | 115.12 | 157.33 | 556 | 580.45 | 314.29 | 549.54 | 74 | 14.3 |  | 3 | 0.3 |  |  |  | 710.27 | 9.33 | 0.58 | 0.86
19 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG013 | 1S-DL-YP-ETC-DJLM-2201-VNG013 | BIHARI COLONY:K | TG-VNG013A-1 | 19503502 | 990 | 320 | 247 | 0.97 | 981 | 378 | 1583 | 248 | 1041 | 355 | 1509 | 509 | 2019-06-11 23:30 | 179.6 | 87.6 | 1583 | R | 112 | 79 | 108 | 33 |  |  | 64.3 | 35.7 |  |  |  |  | 13.19 | 281.58 | 281.58 | 49.18 | 556.39 | 437.29 | 570.28 | 588.09 | 121.59 |  | 106.59 | 82 | 27.3 |  | 12.3 |  | 719.27 | 0.33 | 0.58 | 0.99
20 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG016 | 1S-DL-YP-ETC-DJLM-2201-VNG016 | RAMLEELA GROUND JWALA NAGAR:PL | TG-VNG016A-1 | 19505775 | 990 | 320 | 244 | 0.97 | 810 | 372 | 1607 | 216 | 928 | 222 | 1013 | 641 | 2019-06-03 00:30 | 243.8 | 47.7 | 1607 | R | 113 | 100 | 87 | 26 | 55.7 | 24.2 | 5.1 | 15.1 |  |  |  |  | 56.12 | 211.27 | 211.27 | 175.59 | 631.21 | 506.06 | 375.46 | 541.04 | 28.3 |  |  | 0.3 | 1.3 |  |  |  | 717.33 | 2.27 | 0.58 | 0.82
21 | 2019-06-13 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG017 | 1S-DL-YP-ETC-DJLM-2201-VNG017 | MUKESH NAGAR:PL | TG-VNG017A-1 | 19506922 | 990 | 320 | 255 | 0.96 | 978 | 320 | 1371 | 361 | 1581 | 298 | 1289 | 261 | 2019-06-30 23:30 | 284.5 | 99.2 | 1581 | Y | 103 | 98 | 99 | 5 | 0.1 | 0.9 | 14.7 | 84.3 |  |  |  |  | 21.24 | 29.24 | 29.24 | 20.54 | 326.31 | 340.01 | 351.55 | 341.31 | 51.3 | 35 | 34 | 44 | 7 | 2 |  |  | 406.25 | 25.35 | 0.59 | 0.99
22 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG022 | 1S-DL-YP-ETC-DJLM-2201-VNG022 | 4-POLE PANDAV ROAD:PL | TG-VNG022A-1 | 19505267 | 990 | 320 | 238 | 0.98 | 855 | 232 | 1014 | 292 | 1283 | 331 | 1457 | 386 | 2019-06-10 23:30 | 147.2 | 59.5 | 1457 | B | 90 | 96 | 114 | 24 |  | 0.1 | 19.1 | 80.8 |  |  |  |  | 188.35 | 124.36 | 124.36 | 85.06 | 513.36 | 569.05 | 593.11 | 604.05 |  | 8.3 | 74 | 13 |  |  | 0.3 |  | 702.11 | 17.49 | 0.62 | 0.86
23 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG025 | 1S-DL-YP-ETC-DJLM-2201-VNG025 | MAHAVIR BLOCK:PL | TG-VNG025A-1 | 19505298 | 400 | 120 | 250 | 0.96 | 388 | 109 | 437 | 172 | 698 | 107 | 428 | 265 | 2019-06-02 23:30 | 96.7 | 29.9 | 727 | Y | 88 | 104 | 108 | 20 |  | 0.6 | 47.5 | 51.9 |  | 1 |  |  | 220.13 | 134 | 134 | 124 | 476.52 | 514.05 | 582.08 | 546.35 | 3.3 | 36 | 58.44 | 30 |  | 15.3 |  |  | 700.35 | 19.25 | 0.55 | 0.97
24 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG027 | 1S-DL-YP-ETC-DJLM-2201-VNG027 | SHALIMAR PARK:K | TG-VNG027A-1 | 19505963 | 990 | 320 | 244 | 0.97 | 981 | 390 | 1661 | 248 | 1051 | 343 | 1465 | 540 | 2019-06-10 23:30 | 239.4 | 56.3 | 1749 | R | 109 | 84 | 107 | 25 | 0.1 |  | 0.2 | 99.7 |  |  |  |  | 43.3 | 201.02 | 201.02 | 79 | 537.24 | 508.52 | 499.24 | 550.54 | 114 |  | 102.3 | 80 | 15 |  | 28.3 |  | 709.54 | 10.06 | 0.57 | 0.99
25 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG028 | 1S-DL-YP-ETC-DJLM-2201-VNG028 | MANI RAM MANDIR:PL | TG-VNG028A-3 | 19505681 | 630 | 200 | 242 | 0.97 | 648 | 280 | 1180 | 220 | 896 | 148 | 607 | 496 | 2019-06-12 | 164 | 32.8 | 1180 | R | 90 | 119 | 91 | 29 | 25 | 1.1 | 6 | 67.9 | 1 | 0.3 | 13.41 | 0.3 | 150.02 | 35.59 | 35.59 | 99.32 | 193.3 | 252.03 | 203.3 | 228.3 | 11.3 | 59.3 | 4 | 29.3 | 2.3 | 10.3 | 0.3 | 0.3 | 710.54 | 9.06 | 0.5 | 1.03
26 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG030 | 1S-DL-YP-ETC-DJLM-2201-VNG030 | TELEWARA:PM | TG-VNG030A-1 | 19504455 | 400 | 120 | 235 | 0.98 | 347 | 120 | 519 | 115 | 497 | 112 | 487 | 29 | 2019-06-12 | 56.6 | 21 | 560 | R | 108 | 96 | 97 | 12 |  |  | 1.5 | 98.5 | 0.3 | 1 | 0.3 | 0.3 | 34.3 | 146.24 | 146.24 | 66.3 | 647.36 | 545.12 | 594.56 | 635.06 | 36.3 | 26.3 | 12.3 | 17 |  |  |  |  | 719.06 | 0.54 | 0.63 | 0.87
27 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG032 | 1S-DL-YP-ETC-DJLM-2201-VNG032 | MAHA RAM MOHALLA:PL | TG-VNG032A-2 | 19506688 | 630 | 200 | 244 | 0.96 | 546 | 204 | 830 | 159 | 645 | 183 | 747 | 161 | 2019-06-30 00:30 | 132.4 | 47.4 | 1055 | B | 113 | 83 | 104 | 30 |  | 2.2 | 11.4 | 86.3 |  | 3.25 |  |  | 31.28 | 257.41 | 257.41 | 92.25 | 589.34 | 440.26 | 571.36 | 596.37 | 80.3 |  | 33.56 | 12.3 |  |  | 13 |  | 701.32 | 18.28 | 0.62 | 0.87
28 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG036 | 1S-DL-YP-ETC-DJLM-2201-VNG036 | BHOLA NATH NAGAR:K | TG-VNG036A-2 | 19501600 | 990 | 320 | 239 | 0.97 | 805 | 231 | 941 | 275 | 1142 | 300 | 1243 | 266 | 2019-06-12 | 143.5 | 3.7 | 1399 | B | 90 | 99 | 112 | 22 |  | 5.6 | 87.8 | 6.7 | 0.3 | 0.3 | 0.3 | 0.3 | 292.44 | 268.59 | 268.59 | 202.44 | 426.15 | 435.3 | 557.15 | 514.45 |  | 14.3 | 39.3 | 1.3 |  |  |  |  | 719.29 | 0.31 | 0.59 | 0.81
29 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG036 | 1S-DL-YP-ETC-DJLM-2201-VNG036 | BHOLA NATH NAGAR:K | TG-VNG036A-3 | 19506687 | 630 | 200 | 247 | 0.97 | 665 | 210 | 887 | 169 | 710 | 285 | 1238 | 465 | 2019-06-10 01:30 | 200.6 | 42.2 | 1238 | B | 103 | 97 | 100 | 6 | 0.6 | 0.5 | 11.4 | 87.5 | 1 | 1 | 1 | 1 | 120.42 | 126.16 | 126.16 | 129.41 | 524.46 | 563.41 | 474 | 532.47 | 55.04 | 11.47 | 53 | 38.59 | 1.12 |  | 6.16 | 0.17 | 702.44 | 17.16 | 0.5 | 1.06
30 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG064 | 1S-DL-YP-ETC-DJLM-2201-VNG064 | HALKANA KUNA NO-1:K | TG-VNG064A-1 | 19504605 | 630 | 200 | 235 | 0.97 | 540 | 155 | 683 | 167 | 732 | 218 | 966 | 263 | 2019-06-29 23:00 | 113.2 | 41.4 | 966 | B | 93 | 93 | 114 | 21 |  |  | 11.1 | 88.9 |  |  |  |  | 9 | 21.3 | 21.3 | 9 | 708.22 | 677.28 | 582.23 | 702.22 | 0.3 | 18.54 | 133.59 | 6.3 |  |  | 0.3 |  | 717.52 | 2.08 | 0.72 | 0.86
31 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG090 | 1S-DL-YP-ETC-DJLM-2201-VNG090 | GALI NO-10 VISHWAS NAGAR:PL | TG-VNG090A-2 | 19505959 | 990 | 320 | 236 | 0.98 | 920 | 233 | 1014 | 272 | 1197 | 415 | 1887 | 797 | 2019-06-30 23:30 | 252.2 | 35.8 | 1887 | B | 89 | 100 | 110 | 21 | 0.8 | 2.1 | 54.7 | 42.4 |  |  | 0.3 |  | 44.3 | 19 | 19 | 17 | 655.1 | 626.4 | 557.4 | 637.4 | 0.3 | 54.3 | 115.3 | 45.3 |  |  | 16 |  | 700.1 | 19.5 | 0.66 | 0.93
32 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG111 | 1S-DL-YP-ETC-DJLM-2201-VNG111 | BIHARI COLONY EXTN. | TG-VNG111A-2 | 19505884 | 630 | 200 | 245 | 0.98 | 562 | 142 | 576 | 200 | 827 | 220 | 910 | 302 | 2019-06-03 | 160.4 | 17.8 | 1071 | Y | 99 | 101 | 100 | 2 | 0.4 | 0.9 | 62.3 | 36.4 |  | 0.3 |  |  | 55.51 | 68.51 | 68.51 | 45.51 | 633.11 | 612.41 | 591.41 | 651.11 | 22.3 | 29 | 40 | 15 | 0.3 | 1 | 2 |  | 712.02 | 7.58 | 0.61 | 0.89
33 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG158 | 1S-DL-YP-ETC-DJLM-2201-VNG158 | CIVIL HOSPITAL SHAHDARA S/STN | TG-VNG158A-1 | 19501461 | 990 | 320 | 232 | 0.99 | 911 | 341 | 1492 | 295 | 1277 | 275 | 1188 | 270 | 2019-06-30 16:00 | 114.8 | 0.7 | 1526 | R | 112 | 95 | 93 | 19 |  |  | 3.8 | 96.2 | 55.01 | 99.01 | 82.01 | 80.31 | 296.1 | 309.1 | 309.1 | 310.4 | 281.24 | 298.24 | 284.24 | 305.24 | 81.3 | 12.3 | 8 | 22.3 | 5 |  |  |  | 719.05 | 0.55 | 0.47 | 0.92
34 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG177 | 1S-DL-YP-ETC-DJLM-2201-VNG177 | TELIWARA PARK NEAR GURUDWARA :OD | TG-VNG177A-1 | 19501469 | 630 | 200 | 245 | 0.97 | 509 | 206 | 872 | 118 | 497 | 185 | 762 | 334 | 2019-06-11 23:30 | 115.9 | 32.7 | 953 | R | 119 | 83 | 99 | 36 | 3.6 | 95.1 | 1.3 |  |  | 11 |  |  | 57 | 369.06 | 369.06 | 173.32 | 610.06 | 331.3 | 523.42 | 544.04 | 51.3 | 7.3 | 9 | 1.3 | 0.3 |  |  |  | 719.06 | 0.54 | 0.61 | 0.81
35 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG012 | 1S-DL-YP-ETC-DJLM-2201-VNG012 | LSC MKT A-BLK SURAJ MAL VIHAR:ID | TG-VNG012A-1 | 19501049 | 630 | 200 | 236 | 0.97 | 546 | 163 | 697 | 214 | 932 | 169 | 726 | 223 | 2019-06-29 16:30 | 110.9 | 36.8 | 991 | Y | 94 | 122 | 85 | 37 |  | 1.7 | 73.5 | 24.9 |  |  | 0.3 |  | 107 | 13.3 | 13.3 | 78.3 | 608.52 | 544.27 | 515.12 | 635.22 | 2 | 153.55 | 1.3 | 4 |  | 6 |  |  | 717.52 | 2.08 | 0.65 | 0.87
36 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG019 | 1S-DL-YP-ETC-DJLM-2201-VNG019 | ASHOKA NIKETAN:PG | TG-VNG019A-1 | 19504456 | 990 | 320 | 238 | 0.97 | 842 | 330 | 1446 | 267 | 1169 | 246 | 1073 | 335 | 2019-06-11 23:30 | 155.3 | 47.8 | 1492 | R | 117 | 97 | 86 | 31 |  |  | 8.2 | 91.8 | 1.3 | 1.3 | 2.3 | 1.3 | 57.36 | 236.32 | 236.32 | 180.02 | 567.48 | 472.22 | 393.3 | 524.22 | 90.3 | 7 |  | 11.3 |  |  |  |  | 717.24 | 2.36 | 0.59 | 0.85
37 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG053 | 1S-DL-YP-ETC-DJLM-2201-VNG053 | ANAND VIHAR C-BLOCK:ID | TG-VNG053A-2 | 19502988 | 990 | 320 | 244 | 0.97 | 956 | 325 | 1395 | 346 | 1477 | 285 | 1212 | 235 | 2019-06-11 00:30 | 188.4 | 62.6 | 1553 | Y | 105 | 106 | 89 | 17 |  |  | 37.3 | 62.7 |  |  |  |  | 35.3 | 21.3 | 21.3 | 36.3 | 577.41 | 601.11 | 599.39 | 612.11 | 104 | 91 | 17 | 69 | 0.3 | 4 |  |  | 717.41 | 2.19 | 0.61 | 0.97
38 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG053 | 1S-DL-YP-ETC-DJLM-2201-VNG053 | ANAND VIHAR C-BLOCK:ID | TG-VNG053A-3 | 19504618 | 990 | 320 | 244 | 0.97 | 745 | 364 | 1549 | 190 | 804 | 191 | 804 | 745 | 2019-06-12 | 167.8 | 51.5 | 1574 | R | 130 | 78 | 92 | 52 |  |  | 10.2 | 89.8 |  | 24.58 | 1 |  | 137.28 | 487.22 | 487.22 | 329.15 | 476.39 | 205.47 | 318.18 | 388.52 | 83.3 |  |  |  | 20.3 |  |  |  | 718.07 | 1.53 | 0.59 | 0.75
39 | 2019-06-02 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG070 | 1S-DL-YP-ETC-DJLM-2201-VNG070 | AGCR ENCLAVE:ID | TG-VNG070A-2 | 19502991 | 630 | 200 | 248 | 0.97 | 531 | 214 | 861 | 140 | 563 | 177 | 713 | 258 | 2019-06-30 01:00 | 114.5 | 23.5 | 883 | R | 110 | 89 | 101 | 21 |  |  | 1.3 | 98.7 |  | 2.3 | 0.3 |  | 213.51 | 340.3 | 340.3 | 258 | 423.58 | 351.47 | 442.2 | 435.38 | 55.49 |  | 3.57 | 1.09 | 1.09 |  |  |  | 694.47 | 1.13 | 0.55 | 0.84
40 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG071 | 1S-DL-YP-ETC-DJLM-2201-VNG071 | HARGOVIND ENCLAVE:ID | TG-VNG071A-1 | 19501110 | 990 | 320 | 239 | 0.97 | 830 | 306 | 1354 | 283 | 1256 | 241 | 1063 | 257 | 2019-06-11 00:30 | 178.1 | 33.1 | 1520 | R | 113 | 102 | 85 | 28 |  |  | 0.4 | 99.6 |  | 0.05 | 2.4 | 0.32 | 22.38 | 54.06 | 54.06 | 51.34 | 643.11 | 639.38 | 547.17 | 659.43 | 47.3 | 20 |  | 2 | 0.3 |  |  |  | 713.49 | 6.11 | 0.65 | 0.84
41 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG073 | 1S-DL-YP-ETC-DJLM-2201-VNG073 | DELHI ADMN FLATS:ID | TG-VNG073A-1 | 19501084 | 630 | 200 | 244 | 0.98 | 568 | 211 | 895 | 158 | 669 | 199 | 843 | 205 | 2019-06-30 23:30 | 91.1 | 33.1 | 954 | R | 123 | 76 | 101 | 47 |  |  | 6.1 | 93.9 |  | 0.3 |  |  | 23.3 | 382.42 | 382.42 | 105.3 | 539.56 | 335.14 | 586.25 | 590.26 | 142.3 |  | 28.3 | 22.3 | 12.3 |  |  |  | 718.26 | 1.34 | 0.6 | 0.9
42 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG076 | 1S-DL-YP-ETC-DJLM-2201-VNG076 | SURYA NIKETAN:ID | TG-VNG076A-2 | 19501023 | 990 | 320 | 240 | 0.97 | 1047 | 361 | 1552 | 323 | 1384 | 364 | 1550 | 167 | 2019-06-06 | 203.1 | 42.7 | 1615 | R | 98 | 98 | 104 | 6 |  |  | 18.8 | 81.2 | 0.3 |  |  |  | 62 | 54 | 54 | 34.3 | 544.09 | 553.39 | 564.39 | 566.39 | 104 | 112 | 121 | 114.3 | 9 |  | 14.3 | 4 | 719.39 | 0.21 | 0.59 | 1.06
43 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG076 | 1S-DL-YP-ETC-DJLM-2201-VNG076 | SURYA NIKETAN:ID | TG-VNG076A-1 | 19501036 | 990 | 320 | 236 | 0.98 | 754 | 221 | 927 | 300 | 1267 | 233 | 986 | 315 | 2019-06-11 23:30 | 150.1 | 35.3 | 1368 | Y | 95 | 113 | 92 | 21 |  |  | 11.1 | 88.9 |  | 1 |  |  | 275.06 | 172.24 | 172.24 | 256.54 | 442.41 | 503.03 | 347.12 | 460.53 |  | 41.2 | [6 empty] | 717.47 | 2.13 | 0.6 | 0.76
44 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG092 | 1S-DL-YP-ETC-DJLM-2201-VNG092 | EAST ARJUN NAGAR:K | TG-VNG092A-1 | 19502895 | 990 | 320 | 236 | 0.97 | 723 | 179 | 785 | 235 | 1047 | 309 | 1375 | 512 | 2019-06-30 23:30 | 146.5 | 42.7 | 1375 | B | 83 | 92 | 125 | 42 |  |  | 37.7 | 62.3 | 1 | 3 |  |  | 466.48 | 391.54 | 391.54 | 293.54 | 252 | 324.54 | 561.24 | 425.54 |  |  | 43 | [5 empty] | 719.48 | 0.12 | 0.61 | 0.73
45 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG099 | 1S-DL-YP-ETC-DJLM-2201-VNG099 | L.S.C SAINI ENCLAVE:ID | TG-VNG099A-2 | 19501086 | 630 | 200 | 237 | 0.97 | 562 | 215 | 925 | 169 | 707 | 179 | 753 | 199 | 2019-06-10 16:00 | 134.3 | 43.7 | 988 | R | 117 | 99 | 85 | 32 | 1.9 | 38.1 | 54.4 | 5.6 |  |  |  |  | 21 | 56.3 | 56.3 | 52 | 522.26 | 629.26 | 590.26 | 640.26 | 172.3 | 33.3 | 4 | 27 | 3.3 |  |  |  | 719.26 | 0.34 | 0.66 | 0.89
46 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG103 | 1S-DL-YP-ETC-DJLM-2201-VNG103 | DAYANAND VIHAR 2:ID | TG-VNG103A-3 | 19505437 | 630 | 200 | 243 | 0.97 | 570 | 186 | 788 | 193 | 816 | 191 | 805 | 25 | 2019-06-29 16:00 | 139.6 | 23.4 | 888 | B | 92 | 96 | 112 | 20 | 0.1 |  | 0.4 | 99.4 | 1 |  |  |  | 246.45 | 238.15 | 238.15 | 178.45 | 456.29 | 456.29 | 608.46 | 516.59 | 2 | 11.3 | 43.28 | 10.3 |  |  |  |  | 706.14 | 13.46 | 0.58 | 0.9
47 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG109 | 1S-DL-YP-ETC-DJLM-2201-VNG109 | SURAJ MAL VIHAR A-BLOCK:ID | TG-VNG109A-2 | 19504391 | 990 | 320 | 231 | 0.98 | 869 | 347 | 1553 | 282 | 1251 | 240 | 1056 | 434 | 2019-06-01 01:00 | 140.6 | 22.1 | 1553 | R | 109 | 102 | 89 | 20 | 0.2 | 0.3 | 16.3 | 83.2 | 1.18 | 0.48 | 1.18 | 0.48 | 121.53 | 186.1 | 186.1 | 183.3 | 548.04 | 516 | 433.26 | 529.4 | 45.13 | 14.15 |  | 3.15 | 0.45 |  |  |  | 717.13 | 2.47 | 0.56 | 0.88
48 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG131 | 1S-DL-YP-ETC-DJLM-2201-VNG131 | MANAK VIHAR (VIGYAN LOK) | TG-VNG131A-1 | 19501109 | 630 | 200 | 245 | 0.97 | 532 | 102 | 411 | 195 | 800 | 234 | 964 | 492 | 2019-06-05 23:30 | 112.2 | 30.4 | 988 | B | 60 | 108 | 132 | 72 | 0.1 | 17.2 | 76 | 6.8 | 42 | 0.3 |  |  | 621.11 | 173.45 | 173.45 | 221.45 | 56.3 | 486.56 | 531.47 | 491.26 |  | 58.3 | 118.56 | 6.3 |  |  | 24 |  | 719.41 | 0.19 | 0.57 | 0.84
49 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG147 | 1S-DL-YP-ETC-DJLM-2201-VNG147 | AGCR ENCLAVE:PKG STN | TG-VNG147A-1 | 19501011 | 990 | 320 | 242 | 0.98 | 871 | 266 | 1103 | 344 | 1438 | 261 | 1085 | 345 | 2019-06-11 23:00 | 209 | 44.9 | 1480 | Y | 93 | 110 | 97 | 17 |  |  | 0.8 | 99.2 | 1 | 0.3 | 1 | 1 | 75 | 38 | 38 | 39 | 639.21 | 572.21 | 679.51 | 655.21 | 4.3 | 104.3 | 3.3 | 24.3 |  | 4.3 |  |  | 719.51 | 0.09 | 0.64 | 0.88

## Loading Condition > 100%
MIS Report of Distribution Transformer - Jun19
Jun19 1210 KARKARDOOMA (Loading Condition > 100% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | VNG115 | 1S-DL-YP-ETC-DJLM-2201-VNG115 | SURAJ MAL VIHAR B-BLOCK:PG | TG-VNG115A-1 | 19501029 | 990 | 320 | 241 | 0.94 | 1038 | 337 | 1442 | 366 | 1554 | 336 | 1435 | 115 | 2019-06-01 00:30 | 442.3 | -174.4 | 1664 | Y | 106 | 106 | 87 | 19 | 5.4 | 5.7 | 6.9 | 82 | 0.3 | 0.3 | 0.3 | 0.3 | 58.3 | 56 | 56 | 70.31 | 511.12 | 513.11 | 533.36 | 540.1 | 116.25 | 112.15 | 16.03 | 100.33 | 27.05 | 31.46 | 0.28 | 1.58 | 714.42 | 5.18 | 0.56 | 1.05
2 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG018 | 1S-DL-YP-ETC-DJLM-2201-VNG018 | TEL MILL:PL | TG-VNG018A-1 | 19505883 | 990 | 320 | 245 | 0.97 | 969 | 443 | 1887 | 255 | 1072 | 271 | 1131 | 788 | 2019-06-09 | 232.6 | 44.2 | 1887 | R | 118 | 85 | 97 | 33 |  | 0.3 | 8.4 | 91.3 |  |  |  |  | 81.22 | 263.22 | 263.22 | 147.52 | 511.23 | 456.23 | 537.23 | 533.23 | 93 |  | 34.3 | 38.3 | 34 |  | 0.3 |  | 719.45 | 0.15 | 0.54 | 0.98
3 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG028 | 1S-DL-YP-ETC-DJLM-2201-VNG028 | MANI RAM MANDIR:PL | TG-VNG028A-1 | 19506740 | 990 | 320 | 244 | 0.97 | 1245 | 368 | 1467 | 360 | 1413 | 517 | 2088 | 649 | 2019-06-27 03:00 | 342.4 | 85.8 | 2088 | B | 101 | 97 | 103 | 6 | 0.6 | 4.3 | 68 | 27.1 | 1.3 | 1.3 | 1.3 | 1.3 | 12.3 | 23 | 23 | 13 | 545.28 | 549.28 | 516.58 | 540.58 | 114.3 | 101.3 | 113 | 113 | 36.33 | 35.03 | 61.03 | 42.03 | 710.31 | 9.29 | 0.53 | 1.26
4 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG031 | 1S-DL-YP-ETC-DJLM-2201-VNG031 | TEJAB MILL:PL | TG-VNG031A-1 | 19503074 | 990 | 320 | 242 | 0.97 | 942 | 291 | 1285 | 376 | 1667 | 275 | 1213 | 423 | 2019-06-11 00:30 | 184 | 48.6 | 1714 | Y | 95 | 114 | 91 | 23 |  |  | 4.9 | 95.1 | 1 | 0.3 | 1 | 0.3 | 21.01 | 1.01 | 1.01 | 12.31 | 670.07 | 542.18 | 651.44 | 634.02 | 17.09 | 112.49 | 16.02 | 62.14 |  | 52.39 |  |  | 709.17 | 10.43 | 0.64 | 0.95
5 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG037 | 1S-DL-YP-ETC-DJLM-2201-VNG037 | PATHAN PURA:PL | TG-VNG037A-1 | 19505282 | 990 | 320 | 246 | 0.97 | 1165 | 364 | 1656 | 500 | 2284 | 300 | 1321 | 847 | 2019-06-09 23:30 | 430.1 | 55 | 2284 | Y | 96 | 123 | 81 | 42 | 4.3 | 2.1 | 77.8 | 15.9 |  |  | 2.3 |  | 120.54 | 17 | 17 | 93.54 | 563.48 | 505.12 | 447.3 | 553.18 | 11 | 131.3 | 1 | 48.3 | 0.3 | 42.3 |  | 0.3 | 696.12 | 23.48 | 0.48 | 1.18
6 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG035 | 1S-DL-YP-ETC-DJLM-2201-VNG035 | KARKARDOOMA VILLAGE:PM | TG-VNG035A-1 | 19506467 | 990 | 320 | 237 | 0.98 | 958 | 349 | 1466 | 368 | 1551 | 241 | 1012 | 502 | 2019-06-29 23:30 | 281.6 | 54.1 | 1699 | R | 119 | 111 | 70 | 49 | 0.4 | 0.1 | 5 | 94.5 | [7 empty] | 3 | 373.48 | 493.44 | 530.38 | 612.29 | 289.11 | 196.59 |  | 90.14 | 42.44 | 15 |  |  | 705.43 | 14.17 | 0.68 | 0.97
7 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG071 | 1S-DL-YP-ETC-DJLM-2201-VNG071 | HARGOVIND ENCLAVE:ID | TG-VNG071A-3 | 19503063 | 630 | 120 | 243 | 0.98 | 720 | 228 | 927 | 268 | 1107 | 224 | 919 | 184 | 2019-06-27 17:00 | 138.8 | 1.7 | 1109 | Y | 98 | 110 | 92 | 18 |  | 0.6 | 56.5 | 42.8 | 0.36 |  | 0.36 | 0.36 | 77.15 | 68.51 | 68.51 | 86.45 | 543.59 | 426 | 502.15 | 515.15 | 85.37 | 185.07 | 52.4 | 97.55 | 5.44 | 33.13 | 5.55 | 12.4 | 713.11 | 6.49 | 0.54 | 1.14
8 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG133 | 1S-DL-YP-ETC-DJLM-2201-VNG133 | D BLOCK ANAND VIHAR | TG-VNG133A-1 | 19501012 | 990 | 320 | 242 | 0.98 | 1199 | 468 | 2030 | 353 | 1517 | 378 | 1626 | 469 | 2019-06-11 23:30 | 209.8 | 63.3 | 2030 | R | 104 | 102 | 94 | 10 |  |  | 0.7 | 99.3 |  |  |  |  | 23 | 19 | 19 | 23.3 | 503.3 | 524 | 537.32 | 535.3 | 130.49 | 148.19 | 115.19 | 129.19 | 60.3 | 26.3 | 12.3 | 29.3 | 717.49 | 2.11 | 0.54 | 1.21