## Underload DTs
MIS Report of Distribution Transformer - Jun19
Jun19 1210 KARKARDOOMA (Underload DTs)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI002 | 1S-DL-YP-ETC-DJLM-2203-JHI002 | ESI HOSPITAL:ID | TG-JHI002A-1 | 19505836 | 400 | 120 | 241 | 0.99 | 81 | 2 | 10 | 18 | 76 | 61 | 265 | 229 | 2019-06-16 03:30 | 27 | 0.4 | 265 | B | 17 | 123 | 160 | 143 | 0.1 | 0.6 | 62.4 | 37 | 718.19 | 714.49 | 575.19 | 717.49 |  | 3.3 | 3.3 | 0.3 |  |  | 0.3 | [9 empty] | 718.19 | 1.41 | 0.43 | 0.2
2 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI040 | 1S-DL-YP-ETC-DJLM-2203-JHI040 | POLICE STATION VIVEK VIHAR:ID | TG-JHI040A-1 | 19501612 | 630 | 200 | 241 | 0.98 | 119 | 35 | 149 | 29 | 127 | 56 | 242 | 105 | 2019-06-02 22:30 | 18.9 | 2.3 | 244 | B | 88 | 80 | 132 | 52 |  | 0.1 | 17.9 | 82 | 719.15 | 719.15 | 628.15 | 719.15 | [16 empty] | 719.15 | 0.45 | 0.6 | 0.19
3 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI075 | 1S-DL-YP-ETC-DJLM-2203-JHI075 | D-BLK DSIDC JLM COLONY:ID | TG-JHI075A-1 | 19501597 | 400 | 120 | 247 | 0.92 | 93 | 31 | 126 | 27 | 109 | 35 | 144 | 30 | 2019-06-15 16:00 | 47.5 | -0.3 | 168 | R | 117 | 68 | 116 | 49 |  |  | 65.9 | 34.1 | 657.1 | 713.38 | 679.08 | 705.38 | 60.58 | 4.3 | 4.3 | 12.3 | [12 empty] | 718.08 | 1.52 | 0.41 | 0.23
4 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI100 | 1S-DL-YP-ETC-DJLM-2203-JHI100 | MTNL QTR. VIVEK VHR-1:ID | TG-JHI100A-1 | 19501615 | 630 | 200 | 240 | 0.98 | 85 | 31 | 129 | 17 | 71 | 37 | 153 | 73 | 2019-06-03 | 12 | 2.8 | 157 | B | 109 | 68 | 123 | 55 |  |  | 1.3 | 98.7 | 717.02 | 717.02 | 717.02 | 717.02 | [16 empty] | 717.02 | 2.58 | 0.52 | 0.13
5 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI100 | 1S-DL-YP-ETC-DJLM-2203-JHI100 | MTNL QTR. VIVEK VHR-1:ID | TG-JHI100A-2 | 19506494 | 630 | 200 | 242 | 0.97 | 81 | 30 | 129 | 23 | 97 | 28 | 113 | 27 | 2019-06-29 23:00 | 24.6 | 3.8 | 140 | R | 116 | 88 | 96 | 28 | 100 |  |  |  | 717.02 | 717.02 | 717.02 | 717.02 | [16 empty] | 717.02 | 2.58 | 0.48 | 0.13
6 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI101 | 1S-DL-YP-ETC-DJLM-2203-JHI101 | MTNL QTR. VIVEK VHR-2:ID | TG-JHI101A-2 | 19505837 | 630 | 200 | 242 | 0.97 | 99 | 41 | 174 | 29 | 123 | 30 | 126 | 50 | 2019-06-02 23:00 | 24 | 4.4 | 183 | Y | 105 | 97 | 98 | 8 | 0.1 | 0.1 | 6.1 | 93.7 | 700.32 | 700.32 | 700.32 | 700.32 | [16 empty] | 700.32 | 19.28 | 0.51 | 0.16
7 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI135 | 1S-DL-YP-ETC-DJLM-2203-JHI135 | I.T.I. STAFF QUATERS | TG-JHI135A-1 | 19504050 | 400 | 120 | 249 | 0.99 | 46 | 9 | 37 | 20 | 85 | 17 | 72 | 43 | 2019-06-11 23:30 | 7.5 | 1.1 | 94 | Y | 70 | 123 | 107 | 53 | 0.7 | 1.3 | 16.6 | 81.4 | 719.41 | 719.41 | 719.41 | 719.41 | [16 empty] | 719.41 | 0.19 | 0.54 | 0.12
8 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | B-BLOCK VIVEK VIHAR | 1210 | JHI135 | 1S-DL-YP-ETC-DJLM-2203-JHI135 | I.T.I. STAFF QUATERS | TG-JHI135A-2 | 19504196 | 400 | 120 | 248 | 0.99 | 35 | 10 | 41 | 8 | 34 | 17 | 69 | 32 | 2019-06-02 23:00 | 4.1 | 0.3 | 70 | B | 88 | 63 | 149 | 86 |  |  | 71 | 29 | 719.41 | 719.41 | 719.41 | 719.41 | [16 empty] | 719.41 | 0.19 | 0.47 | 0.09
9 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG008 | 1S-DL-YP-ETC-DJLM-2201-VNG008 | SARVARIA MARKET:K | TG-VNG008A-3 | 19502920 | 990 | 320 | 244 | 0.92 | 75 | 21 | 84 | 24 | 95 | 31 | 123 | 35 | 2019-06-16 09:30 | 49.3 | -0.7 | 126 | B | 79 | 94 | 128 | 49 |  |  | 1.1 | 98.9 | 719.35 | 719.35 | 719.35 | 719.35 | [16 empty] | 719.35 | 0.25 | 0.52 | 0.08
10 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG008 | 1S-DL-YP-ETC-DJLM-2201-VNG008 | SARVARIA MARKET:K | TG-VNG008A-2 | 19502923 | 990 | 320 | 240 | 0.96 | 226 | 92 | 403 | 87 | 377 | 47 | 204 | 188 | 2019-06-11 23:30 | 57.4 | 13.2 | 568 | Y | 122 | 113 | 65 | 57 |  |  | 4.1 | 95.9 | 566.19 | 620.57 | 718.49 | 682.49 | 152.3 | 95.52 | 95.52 | 36 |  | 2 | [10 empty] | 718.49 | 1.11 | 0.57 | 0.23
11 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG008 | 1S-DL-YP-ETC-DJLM-2201-VNG008 | SARVARIA MARKET:K | TG-VNG008A-1 | 19506624 | 990 | 320 | 246 | 0.97 | 161 | 95 | 413 | 28 | 123 | 39 | 168 | 270 | 2019-06-08 23:00 | 43.5 | 4.2 | 413 | R | 165 | 59 | 76 | 106 | 0.1 | 0.1 | 3 | 96.7 | 539.05 | 706.04 | 706.04 | 706.04 | 166.59 | [15 empty] | 706.04 | 13.56 | 0.62 | 0.16
12 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG024 | 1S-DL-YP-ETC-DJLM-2201-VNG024 | GALI NO-16 VISHWAS NAGAR:PL | TG-VNG024A-2 | 19506689 | 990 | 320 | 237 | 0.97 | 215 | 64 | 279 | 72 | 309 | 80 | 344 | 56 | 2019-06-10 22:30 | 47.7 | 13.4 | 423 | B | 78 | 107 | 115 | 37 | 0.1 | 0.2 | 0.6 | 99.1 | 695.16 | 592.46 | 539.46 | 674.46 | 1 | 103.3 | 103.3 | 21.3 | [12 empty] | 696.16 | 23.44 | 0.69 | 0.22
13 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG024 | 1S-DL-YP-ETC-DJLM-2201-VNG024 | GALI NO-16 VISHWAS NAGAR:PL | TG-VNG024A-1 | 19506850 | 990 | 320 | 250 | 0.98 | 243 | 72 | 293 | 94 | 383 | 77 | 314 | 81 | 2019-06-15 16:00 | 67.5 | -3.5 | 443 | R | 88 | 130 | 82 | 48 |  | 0.1 | 1.1 | 98.7 | 688.46 | 564.29 | 680.47 | 664.17 | 31 | 155.17 | 155.17 | 55.29 | [12 empty] | 719.46 | 0.14 | 0.53 | 0.25
14 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG059 | 1S-DL-YP-ETC-DJLM-2201-VNG059 | 28/29 BLOCK VISHWAS NAGAR | TG-VNG059A-2 | 19504199 | 990 | 320 | 247 | 0.98 | 238 | 79 | 325 | 87 | 360 | 73 | 297 | 55 | 2019-06-28 15:00 | 53.7 | -7.4 | 362 | Y | 103 | 114 | 83 | 31 |  | 0.1 | 14.7 | 85.3 | 691.52 | 646.22 | 715.52 | 698.22 | 28 | 73.3 | 73.3 | 21.3 | [12 empty] | 719.52 | 0.08 | 0.61 | 0.24
15 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG060 | 1S-DL-YP-ETC-DJLM-2201-VNG060 | NEHRU GALI:PL | TG-VNG060A-1 | 19504588 | 990 | 320 | 246 | 0.98 | 153 | 48 | 209 | 41 | 178 | 64 | 275 | 86 | 2019-06-11 | 56.7 | 0.7 | 277 | B | 114 | 71 | 115 | 44 |  |  |  | 100 | 719.54 | 719.54 | 719.54 | 719.54 | [16 empty] | 719.54 | 0.06 | 0.48 | 0.15
16 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG062 | 1S-DL-YP-ETC-DJLM-2201-VNG062 | SHIVAM ENCLAVE-2:ID | TG-VNG062A-1 | 19501298 | 400 | 120 | 248 | 0.97 | 79 | 39 | 167 | 10 | 41 | 31 | 130 | 112 | 2019-06-11 23:30 | 15.2 | 2.5 | 191 | R | 147 | 31 | 122 | 116 |  |  | 17.6 | 82.4 | 561.23 | 719.52 | 672.52 | 719.52 | 158.29 | [15 empty] | 719.52 | 0.08 | 0.5 | 0.2
17 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG066 | 1S-DL-YP-ETC-DJLM-2201-VNG066 | NEHRU GALI (NALLAHA SIDE):PL | TG-VNG066A-1 | 19506562 | 630 | 200 | 235 | 0.85 | 23 | 8 | 34 | 1 | 4 | 13 | 55 | 44 | 2019-06-12 18:30 | 11.8 | -0.2 | 65 | R | 82 | 47 | 170 | 123 |  |  | 38.4 | 61.6 | 705.03 | 705.03 | 705.03 | 705.03 | [16 empty] | 705.03 | 14.57 | 0.34 | 0.04
18 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG066 | 1S-DL-YP-ETC-DJLM-2201-VNG066 | NEHRU GALI (NALLAHA SIDE):PL | TG-VNG066A-2 | 19506564 | 630 | 200 | 248 | 0.93 | 28 | 5 | 19 | 8 | 33 | 15 | 62 | 38 | 2019-06-17 18:00 | 12.2 | 0.8 | 79 | Y | 55 | 194 | 51 | 143 |  | 0.1 | 1.8 | 98.1 | 705.03 | 705.03 | 705.03 | 705.03 | [16 empty] | 705.03 | 14.57 | 0.56 | 0.05
19 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG067 | 1S-DL-YP-ETC-DJLM-2201-VNG067 | 18 QTR VISWAS NAGAR:PL | TG-VNG067A-1 | 19504231 | 990 | 320 | 248 | 0.97 | 157 | 52 | 214 | 38 | 158 | 66 | 272 | 99 | 2019-06-29 16:00 | 46.4 | 11 | 313 | B | 107 | 78 | 115 | 37 |  |  | 15.6 | 84.4 | 719.21 | 719.51 | 710.51 | 719.51 | 0.3 | [15 empty] | 719.51 | 0.09 | 0.64 | 0.16
20 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG068 | 1S-DL-YP-ETC-DJLM-2201-VNG068 | PATEL GALI NALA:PL | TG-VNG068A-2 | 19504059 | 990 | 320 | 248 | 0.97 | 122 | 45 | 186 | 25 | 102 | 53 | 217 | 103 | 2019-06-10 23:00 | 35.3 | 2.9 | 234 | B | 104 | 55 | 141 | 86 |  |  | 10.1 | 89.9 | 719.24 | 719.24 | 719.24 | 719.24 | [16 empty] | 719.24 | 0.36 | 0.6 | 0.12
21 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG068 | 1S-DL-YP-ETC-DJLM-2201-VNG068 | PATEL GALI NALA:PL | TG-VNG068A-1 | 19504118 | 630 | 200 | 249 | 0.96 | 72 | 30 | 116 | 26 | 101 | 16 | 62 | 48 | 2019-06-06 | 22.5 | 0.5 | 120 | Y | 123 | 111 | 66 | 57 |  | 0.6 | 69.8 | 29.5 | 719.22 | 719.22 | 719.22 | 719.22 | [16 empty] | 719.22 | 0.38 | 0.53 | 0.11
22 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG077 | 1S-DL-YP-ETC-DJLM-2201-VNG077 | SHASTRI GALI (BAGILCHI):PL | TG-VNG077A-1 | 19504159 | 990 | 320 | 241 | 0.98 | 106 | 53 | 221 | 22 | 91 | 31 | 129 | 116 | 2019-06-30 14:30 | 21.3 | 0.7 | 225 | R | 137 | 68 | 95 | 69 |  | 0.1 | 24.9 | 75.1 | 719.19 | 719.19 | 719.19 | 719.19 | [16 empty] | 719.19 | 0.41 | 0.65 | 0.11
23 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG082 | 1S-DL-YP-ETC-DJLM-2201-VNG082 | SHASTRI GALI (NALA):PL | TG-VNG082A-1 | 19504739 | 630 | 200 | 241 | 0.97 | 110 | 54 | 228 | 25 | 105 | 32 | 133 | 112 | 2019-06-02 23:30 | 24.8 | 3.2 | 260 | R | 154 | 66 | 80 | 88 |  |  | 15.6 | 84.4 | 561.52 | 719.22 | 719.22 | 719.22 | 157.3 | [15 empty] | 719.22 | 0.38 | 0.59 | 0.18
24 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG083 | 1S-DL-YP-ETC-DJLM-2201-VNG083 | KARAM GALI:PL | TG-VNG083A-1 | 19502910 | 990 | 320 | 247 | 0.96 | 84 | 18 | 75 | 12 | 51 | 54 | 227 | 165 | 2019-06-08 16:30 | 29.4 | 2.9 | 227 | B | 68 | 55 | 177 | 122 |  |  | 7.8 | 92.2 | 719.54 | 719.54 | 719.54 | 719.54 | [16 empty] | 719.54 | 0.06 | 0.63 | 0.08
25 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG084 | 1S-DL-YP-ETC-DJLM-2201-VNG084 | RAM GALI (NALA):PL | TG-VNG084A-1 | 19503499 | 990 | 320 | 241 | 0.97 | 89 | 48 | 203 | 18 | 77 | 22 | 94 | 119 | 2019-06-09 22:00 | 25 | -0.7 | 205 | R | 134 | 82 | 85 | 52 |  |  | 16 | 84 | 719.33 | 719.33 | 719.33 | 719.33 | [16 empty] | 719.33 | 0.27 | 0.63 | 0.09
26 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG085 | 1S-DL-YP-ETC-DJLM-2201-VNG085 | RAM GALI 60ROAD:PL | TG-VNG085A-1 | 19506352 | 990 | 320 | 247 | 0.97 | 190 | 45 | 182 | 54 | 215 | 91 | 363 | 167 | 2019-06-30 | 53.1 | 9 | 403 | B | 72 | 92 | 136 | 64 |  | 0.1 | 0.1 | 99.8 | 701.24 | 701.24 | 599.54 | 701.24 | [16 empty] | 701.24 | 18.36 | 0.61 | 0.19
27 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG086 | 1S-DL-YP-ETC-DJLM-2201-VNG086 | YUDHISHTER GALI:PL | TG-VNG086A-1 | 19503610 | 990 | 320 | 246 | 0.97 | 161 | 88 | 360 | 44 | 177 | 30 | 121 | 217 | 2019-06-12 15:30 | 37.5 | 11 | 375 | R | 162 | 72 | 65 | 97 |  |  | 30.1 | 69.9 | 495.54 | 719.54 | 719.54 | 719.54 | 224 | [15 empty] | 719.54 | 0.06 | 0.69 | 0.16
28 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG087 | 1S-DL-YP-ETC-DJLM-2201-VNG087 | YUDHISHTER GALI(NALA):PL | TG-VNG087A-1 | 19501237 | 990 | 320 | 240 | 0.97 | 207 | 66 | 296 | 59 | 262 | 83 | 368 | 94 | 2019-06-10 23:30 | 55.9 | 11.8 | 395 | B | 101 | 71 | 127 | 56 |  |  | 19.4 | 80.6 | 718.03 | 719.33 | 463.33 | 709.03 | 1.3 |  |  | 10.3 | [12 empty] | 719.33 | 0.27 | 0.7 | 0.21
29 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG093 | 1S-DL-YP-ETC-DJLM-2201-VNG093 | NAKUL GALI:PL | TG-VNG093A-1 | 19505067 | 990 | 320 | 247 | 0.96 | 169 | 70 | 283 | 68 | 278 | 31 | 120 | 160 | 2019-06-29 23:30 | 44.2 | 8.8 | 291 | Y | 122 | 123 | 55 | 68 | 91.1 | 8.9 |  |  | 718.04 | 713.04 | 719.34 | 719.34 | 1.3 | 6.3 | 6.3 | [13 empty] | 719.34 | 0.26 | 0.58 | 0.17
30 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG097 | 1S-DL-YP-ETC-DJLM-2201-VNG097 | 18' QTR P/M VISHNU GALI:PM | TG-VNG097A-1 | 19504234 | 990 | 320 | 247 | 0.97 | 161 | 57 | 233 | 38 | 156 | 67 | 275 | 104 | 2019-06-11 22:30 | 37.5 | 6.6 | 297 | B | 111 | 66 | 124 | 58 |  |  | 6.5 | 93.5 | 719.55 | 719.55 | 716.25 | 719.55 | [16 empty] | 719.55 | 0.05 | 0.64 | 0.16
31 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG102 | 1S-DL-YP-ETC-DJLM-2201-VNG102 | SUBHASH GALI (NALA):PL | TG-VNG102A-1 | 19506439 | 990 | 320 | 245 | 0.96 | 105 | 40 | 172 | 41 | 177 | 23 | 97 | 78 | 2019-06-29 23:00 | 26.9 | 4.5 | 200 | B | 106 | 108 | 86 | 22 | 0.1 |  | 1.7 | 98.2 | 717.1 | 717.1 | 717.1 | 717.1 | [16 empty] | 717.1 | 2.5 | 0.58 | 0.11
32 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG110 | 1S-DL-YP-ETC-DJLM-2201-VNG110 | GALI NO-4-NALA VISHWAS NAGAR:PL | TG-VNG110A-1 | 19505675 | 990 | 320 | 249 | 0.97 | 224 | 64 | 260 | 52 | 210 | 108 | 436 | 205 | 2019-06-11 00:30 | 56.6 | 9 | 480 | B | 89 | 67 | 144 | 77 | 0.1 | 0.2 | 11 | 88.7 | 703.46 | 705.46 | 400.16 | 656.46 | 2 |  |  | 49 | [12 empty] | 705.46 | 14.14 | 0.61 | 0.23
33 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG113 | 1S-DL-YP-ETC-DJLM-2201-VNG113 | BAZAR GALI(NALA):PL | TG-VNG113A-1 | 19504878 | 990 | 320 | 249 | 0.94 | 20 | 17 | 68 | 1 | 6 | 2 | 6 | 62 | 2019-06-30 00:30 | 6.6 | 0.7 | 71 | R | 237 | 47 | 16 | 221 |  |  | 7 | 93 | 719.22 | 719.22 | 719.22 | 719.22 | [16 empty] | 719.22 | 0.38 | 0.52 | 0.02
34 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG113 | 1S-DL-YP-ETC-DJLM-2201-VNG113 | BAZAR GALI(NALA):PL | TG-VNG113A-2 | 19506063 | 400 | 120 | 248 | 0.92 | 62 | 27 | 110 | 31 | 126 | 4 | 16 | 104 | 2019-06-11 22:30 | 32.3 | 1.3 | 136 | R | 123 | 144 | 32 | 112 |  | 0.1 | 3.3 | 96.6 | 683.54 | 701.54 | 704.54 | 704.54 | 21 | 3 | 3 | [13 empty] | 704.54 | 15.06 | 0.53 | 0.16
35 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | JWALA NAGAR | 1210 | VNG132 | 1S-DL-YP-ETC-DJLM-2201-VNG132 | GALI NUMBER - 3 (NALA) VISWAS NGR:PL | TG-VNG132A-1 | 19504413 | 630 | 200 | 248 | 0.96 | 117 | 32 | 132 | 49 | 202 | 37 | 151 | 63 | 2019-06-03 | 29.4 | 6 | 238 | Y | 84 | 136 | 80 | 56 |  |  | 1.1 | 98.9 | 719.45 | 638.15 | 719.45 | 719.45 |  | 81.3 | 81.3 | [13 empty] | 719.45 | 0.15 | 0.57 | 0.19
36 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG001 | 1S-DL-YP-ETC-DJLM-2201-VNG001 | CHITRAKOOT CGHS:ID | TG-VNG001A-1 | 19501008 | 990 | 320 | 247 | 0.97 | 98 | 14 | 58 | 54 | 220 | 30 | 125 | 141 | 2019-06-10 23:30 | 28 | 2.2 | 263 | Y | 41 | 185 | 74 | 144 |  |  | 0.1 | 99.9 | 719.58 | 719.58 | 719.58 | 719.58 | [16 empty] | 719.58 | 0.02 | 0.54 | 0.1
37 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG042 | 1S-DL-YP-ETC-DJLM-2201-VNG042 | HANSA APTT. NO-1:ID | TG-VNG042A-2 | 19505841 | 630 | 200 | 248 | 0.97 | 114 | 41 | 160 | 30 | 117 | 43 | 172 | 49 | 2019-06-15 00:30 | 62.8 | 3.6 | 187 | B | 102 | 82 | 115 | 33 |  |  | 0.3 | 99.7 | 719.28 | 719.58 | 714.28 | 719.58 | 0.3 | [15 empty] | 719.58 | 0.02 | 0.57 | 0.18
38 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG042 | 1S-DL-YP-ETC-DJLM-2201-VNG042 | HANSA APTT. NO-1:ID | TG-VNG042A-1 | 19506065 | 630 | 200 | 248 | 0.97 | 110 | 35 | 148 | 23 | 95 | 53 | 222 | 110 | 2019-06-30 23:30 | 26.4 | 4.6 | 234 | B | 80 | 73 | 147 | 74 |  |  | 0.1 | 99.9 | 719.57 | 719.57 | 628.27 | 719.57 | [16 empty] | 719.57 | 0.03 | 0.51 | 0.18
39 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG043 | 1S-DL-YP-ETC-DJLM-2201-VNG043 | HANSA APTT. NO-2:ID | TG-VNG043A-1 | 19506399 | 630 | 200 | 247 | 0.97 | 160 | 62 | 250 | 33 | 134 | 64 | 259 | 121 | 2019-06-12 | 36.2 | 5.8 | 284 | B | 115 | 68 | 117 | 49 |  |  |  | 100 | 567.57 | 696.27 | 542.27 | 627.27 | 128.3 |  |  | 69 | [12 empty] | 696.27 | 23.33 | 0.52 | 0.25
40 | 2019-06-02 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG044 | 1S-DL-YP-ETC-DJLM-2201-VNG044 | SHAKTI KIRAN BUILIDING KAKARDOMA GRID:ID | TG-VNG044A-1 | 19502900 | 630 | 200 | 240 | 0.99 | 64 | 26 | 110 | 21 | 89 | 17 | 72 | 34 | 2019-06-27 12:30 | 11.5 | -1.4 | 121 | R | 137 | 99 | 65 | 72 |  | 0.1 | 2.5 | 97.4 | 695.55 | 695.55 | 695.55 | 695.55 | [16 empty] | 695.55 | 0.05 | 0.3 | 0.1
41 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG049 | 1S-DL-YP-ETC-DJLM-2201-VNG049 | GITANJALI APPARTMENT:ID | TG-VNG049A-1 | 19501077 | 990 | 320 | 246 | 0.97 | 214 | 79 | 320 | 78 | 315 | 57 | 231 | 86 | 2019-06-12 01:00 | 50 | 4.4 | 352 | R | 108 | 104 | 88 | 20 |  |  | 0.1 | 99.9 | 674.06 | 690.36 | 719.36 | 713.36 | 45.3 | 29 | 29 | 6 | [12 empty] | 719.36 | 0.24 | 0.53 | 0.22
42 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG049 | 1S-DL-YP-ETC-DJLM-2201-VNG049 | GITANJALI APPARTMENT:ID | TG-VNG049A-2 | 19503013 | 990 | 320 | 246 | 0.98 | 142 | 53 | 227 | 33 | 140 | 57 | 244 | 96 | 2019-06-01 22:30 | 25.8 | -29.4 | 276 | B | 91 | 79 | 130 | 51 |  |  |  | 100 | 719.36 | 719.36 | 718.36 | 719.36 | [16 empty] | 719.36 | 0.24 | 0.57 | 0.14
43 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG051 | 1S-DL-YP-ETC-DJLM-2201-VNG051 | ANUPAM APPARTMENT NO-1:ID | TG-VNG051A-2 | 19501128 | 990 | 320 | 237 | 0.98 | 155 | 48 | 191 | 58 | 242 | 50 | 205 | 45 | 2019-06-11 23:30 | 26.5 | 3.7 | 281 | Y | 93 | 115 | 92 | 23 | 100 |  |  |  | 719.48 | 719.48 | 719.48 | 719.48 | [16 empty] | 719.48 | 0.12 | 0.51 | 0.16
44 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG052 | 1S-DL-YP-ETC-DJLM-2201-VNG052 | ANUPAM APPTT. NO-2:ID | TG-VNG052A-1 | 19501130 | 990 | 300 | 243 | 0.98 | 176 | 62 | 267 | 58 | 247 | 56 | 237 | 26 | 2019-06-13 21:30 | 33.1 | 4.8 | 297 | R | 107 | 100 | 93 | 14 |  |  | 16.7 | 83.3 | 716.49 | 719.49 | 719.49 | 719.49 | 3 | [15 empty] | 719.49 | 0.11 | 0.52 | 0.18
45 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG054 | 1S-DL-YP-ETC-DJLM-2201-VNG054 | VIVEK APPARTMENT:ID | TG-VNG054A-1 | 19501103 | 990 | 300 | 248 | 0.95 | 109 | 34 | 141 | 50 | 205 | 25 | 102 | 90 | 2019-06-09 23:30 | 31.1 | 4.8 | 216 | Y | 104 | 133 | 63 | 70 |  | 0.1 | 40.5 | 59.5 | 719.4 | 719.4 | 719.4 | 719.4 | [16 empty] | 719.4 | 0.2 | 0.54 | 0.11
46 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG054 | 1S-DL-YP-ETC-DJLM-2201-VNG054 | VIVEK APPARTMENT:ID | TG-VNG054A-2 | 19505840 | 400 | 120 | 248 | 0.97 | 189 | 62 | 257 | 73 | 300 | 54 | 221 | 68 | 2019-06-14 21:30 | 33.8 | 1.9 | 300 | Y | 61 | 122 | 117 | 61 | 0.1 | 0.1 | 9.9 | 89.9 | 719.1 | 709.1 | 705.1 | 719.1 |  | 10 | 10 |  | 0.3 | 0.3 | 0.3 | 0.3 | [8 empty] | 719.4 | 0.2 | 0.19 | 0.47
47 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG055 | 1S-DL-YP-ETC-DJLM-2201-VNG055 | GHRONDA APPARTMENT:ID | TG-VNG055A-2 | 19501105 | 630 | 200 | 247 | 0.97 | 129 | 49 | 207 | 66 | 279 | 14 | 60 | 194 | 2019-06-12 | 22.5 | 4.6 | 280 | Y | 118 | 147 | 35 | 112 |  |  | 3.8 | 96.2 | 697.1 | 599.1 | 719.4 | 719.1 | 22.3 | 120.3 | 120.3 | 0.3 | [12 empty] | 719.4 | 0.2 | 0.46 | 0.21
48 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG056 | 1S-DL-YP-ETC-DJLM-2201-VNG056 | JEEVAN BIMA:ID | TG-VNG056A-1 | 19501043 | 400 | 120 | 243 | 0.97 | 50 | 14 | 57 | 20 | 82 | 16 | 68 | 22 | 2019-06-30 19:30 | 14.1 | 1.4 | 93 | Y | 76 | 129 | 95 | 53 |  | 4.6 | 95.4 |  | 719.57 | 719.57 | 719.57 | 719.57 | [16 empty] | 719.57 | 0.03 | 0.51 | 0.12
49 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG056 | 1S-DL-YP-ETC-DJLM-2201-VNG056 | JEEVAN BIMA:ID | TG-VNG056A-2 | 19501045 | 400 | 120 | 241 | 0.97 | 77 | 37 | 149 | 22 | 92 | 18 | 76 | 66 | 2019-06-11 22:30 | 16 | 1.1 | 149 | R | 129 | 90 | 81 | 48 | 91.6 | 8.4 |  |  | 676.27 | 719.57 | 719.57 | 719.57 | 43.3 | [15 empty] | 719.57 | 0.03 | 0.47 | 0.19
50 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG057 | 1S-DL-YP-ETC-DJLM-2201-VNG057 | LAW APTT.:ID | TG-VNG057A-1 | 19501046 | 400 | 120 | 253 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [7 empty] | 3.9 | 96.1 | 719.36 | 719.36 | 719.36 | 719.36 | [16 empty] | 719.36 | 0.24 |  | 0
51 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG057 | 1S-DL-YP-ETC-DJLM-2201-VNG057 | LAW APTT.:ID | TG-VNG057A-2 | 19506360 | 400 | 120 | 252 | 0.97 | 63 | 9 | 38 | 20 | 82 | 34 | 141 | 89 | 2019-06-02 00:30 | 12.7 | -15.4 | 152 | B | 18 | 125 | 157 | 139 | 0.1 |  |  | 99.9 | 709.36 | 705.36 | 678.06 | 709.36 |  | 4 | 4 | [13 empty] | 709.36 | 10.24 | 0.51 | 0.16
52 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG095 | 1S-DL-YP-ETC-DJLM-2201-VNG095 | STREET LIGHT CBD:PM | TG-VNG095A-1 | 19504198 | 100 | 40 | 250 | 0.96 | 22 | 4 | 15 | 6 | 23 | 13 | 50 | 32 | 2019-06-18 03:00 | 5.7 | -8.4 | 50 | B | 135 | 24 | 141 | 117 |  |  | 0.9 | 99.1 | 719.48 | 719.48 | 704.18 | 719.18 |  |  |  | 0.3 | [12 empty] | 719.48 | 0.12 | 0.18 | 0.22
53 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG098 | 1S-DL-YP-ETC-DJLM-2201-VNG098 | MTNL CBD GROUND:ID | TG-VNG098A-1 | 19501119 | 400 | 120 | 244 | 0.98 | 91 | 40 | 170 | 24 | 101 | 27 | 111 | 64 | 2019-06-15 15:00 | 24.8 | -1.9 | 170 | R | 120 | 99 | 81 | 39 |  |  | 0.6 | 99.4 | 580.22 | 719.46 | 717.52 | 716.22 | 139.24 |  |  | 3.24 | [12 empty] | 719.46 | 0.14 | 0.57 | 0.23
54 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG129 | 1S-DL-YP-ETC-DJLM-2201-VNG129 | S/STN NO-2 KARKARDOOMA INST. AREA:ID | TG-VNG129A-1 | 19505382 | 630 | 200 | 247 | 0.98 | 99 | 29 | 120 | 29 | 120 | 40 | 166 | 46 | 2019-06-08 13:30 | 20.4 | 0.2 | 207 | B | 91 | 65 | 144 | 79 |  |  | 0.7 | 99.3 | 712.28 | 712.28 | 707.28 | 712.28 | [16 empty] | 712.28 | 7.32 | 0.37 | 0.16
55 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG129 | 1S-DL-YP-ETC-DJLM-2201-VNG129 | S/STN NO-2 KARKARDOOMA INST. AREA:ID | TG-VNG129A-2 | 19505385 | 630 | 200 | 247 | 0.94 | 105 | 15 | 61 | 8 | 33 | 82 | 330 | 284 | 2019-06-15 17:30 | 41.4 | -2.8 | 330 | B | 123 | 51 | 126 | 75 |  |  | 0.1 | 99.9 | 712.28 | 712.28 | 711.28 | 712.28 | [16 empty] | 712.28 | 7.32 | 0.21 | 0.17
56 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG131 | 1S-DL-YP-ETC-DJLM-2201-VNG131 | MANAK VIHAR (VIGYAN LOK) | TG-VNG131A-2 | 19501108 | 990 | 320 | 247 | 0.97 | 221 | 59 | 242 | 100 | 413 | 62 | 254 | 165 | 2019-06-01 23:30 | 46.4 | 10.3 | 435 | Y | 77 | 124 | 99 | 47 |  |  | 1.7 | 98.3 | 719.1 | 523.1 | 713.1 | 700.4 | 0.3 | 196.3 | 196.3 | 19 | [12 empty] | 719.4 | 0.2 | 0.61 | 0.22
57 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG136 | 1S-DL-YP-ETC-DJLM-2201-VNG136 | S/S NUMBER 2, LSC KARKARDOOMA | TG-VNG136A-2 | 19501005 | 630 | 200 | 246 | 0.98 | 62 | 12 | 49 | 24 | 103 | 26 | 109 | 57 | 2019-06-10 12:30 | 10.1 | -0.9 | 119 | Y | 67 | 133 | 101 | 66 |  |  | 0.1 | 99.9 | 719.36 | 719.36 | 719.36 | 719.36 | [16 empty] | 719.36 | 0.24 | 0.31 | 0.1
58 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG136 | 1S-DL-YP-ETC-DJLM-2201-VNG136 | S/S NUMBER 2, LSC KARKARDOOMA | TG-VNG136A-1 | 19505819 | 630 | 200 | 254 | 0.96 | 39 | 9 | 35 | 15 | 57 | 16 | 62 | 25 | 2019-06-11 17:30 | 15.8 | 0.2 | 91 | Y | 73 | 113 | 114 | 41 |  | 0.1 |  | 99.9 | 709.36 | 709.36 | 709.36 | 709.36 | [16 empty] | 709.36 | 10.24 | 0.32 | 0.06
59 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG137 | 1S-DL-YP-ETC-DJLM-2201-VNG137 | 18 KKD COMMERCIAL COMPLEX | TG-VNG137A-1 | 19501538 | 630 | 200 | 246 | 0.89 | 102 | 26 | 105 | 31 | 126 | 45 | 185 | 72 | 2019-06-26 13:00 | 17.9 | -13.3 | 206 | B | 71 | 96 | 133 | 62 |  |  | 2.4 | 97.6 | 719.36 | 719.36 | 674.08 | 719.36 | [16 empty] | 719.36 | 0.24 | 0.3 | 0.16
60 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG137 | 1S-DL-YP-ETC-DJLM-2201-VNG137 | 18 KKD COMMERCIAL COMPLEX | TG-VNG137A-2 | 19506827 | 630 | 200 | 247 | 0.98 | 88 | 21 | 85 | 33 | 136 | 34 | 140 | 53 | 2019-06-30 20:30 | 25.2 | -4 | 148 | Y | 84 | 102 | 115 | 31 | 0.1 |  | 1.1 | 98.9 | 709.06 | 709.06 | 709.06 | 709.06 | [16 empty] | 709.06 | 10.54 | 0.51 | 0.14
61 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG139 | 1S-DL-YP-ETC-DJLM-2201-VNG139 | H BLK CBD GROUND I/D | TG-VNG139A-1 | 19503697 | 400 | 120 | 245 | 0.8 | 19 | 18 | 71 | 1 | 3 | 0 | 0 | 69 | 2019-06-03 19:00 | 12.7 | 0.3 | 71 | R | 262 | 38 | 0 | 262 | 0.1 | 0.3 | 42.1 | 57.6 | 571.21 | 571.21 | 571.21 | 571.21 | [16 empty] | 571.21 | 4.39 | 0.34 | 0.05
62 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG140 | 1S-DL-YP-ETC-DJLM-2201-VNG140 | F BLK CBD GROUND I/D | TG-VNG140A-1 | 19504258 | 400 | 120 | 251 | 0.89 | 4 | 0 | 0 | 4 | 14 | 0 | 0 | 14 | 2019-06-02 19:30 | 3.3 | 0.3 | 14 | Y | 0 | 216 | 85 | 216 |  |  | 17.2 | 82.8 | 479.59 | 479.59 | 479.59 | 479.59 | [16 empty] | 479.59 | 0.01 | 0.19 | 0.01
63 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG143 | 1S-DL-YP-ETC-DJLM-2201-VNG143 | INSTITUTIONAL AREA S/STN-1 I/D | TG-VNG143A-1 | 19506324 | 630 | 200 | 239 | 0.97 | 161 | 60 | 254 | 45 | 189 | 55 | 232 | 57 | 2019-06-03 12:00 | 46 | 2.8 | 286 | R | 110 | 81 | 109 | 29 |  |  | 1.1 | 98.9 | 677.36 | 676.36 | 679.36 | 683.06 | 34.3 | 35.3 | 35.3 | 29 | [12 empty] | 712.06 | 7.54 | 0.42 | 0.25
64 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG145 | 1S-DL-YP-ETC-DJLM-2201-VNG145 | PLOT NO.14 DDA COMMUNITY CENTER KKD | TG-VNG145A-1 | 19503694 | 990 | 320 | 247 | 0.96 | 154 | 51 | 217 | 53 | 227 | 50 | 213 | 12 | 2019-06-10 12:30 | 42 | 0.7 | 237 | B | 98 | 88 | 114 | 26 |  |  |  | 100 | 719.36 | 719.36 | 719.36 | 719.36 | [16 empty] | 719.36 | 0.24 | 0.32 | 0.16
65 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG146 | 1S-DL-YP-ETC-DJLM-2201-VNG146 | PLOT NO.13 DDA COMMUNITY CENTER KKD | TG-VNG146A-1 | 19505196 | 990 | 300 | 247 | 0.94 | 178 | 61 | 254 | 66 | 274 | 51 | 210 | 56 | 2019-06-14 15:30 | 64.5 | 0.9 | 391 | R | 83 | 117 | 100 | 34 | 0.1 | 0.1 | 0.2 | 99.6 | 708.36 | 702.36 | 709.06 | 709.06 | 0.3 | 6.3 | 6.3 | [13 empty] | 709.06 | 10.54 | 0.39 | 0.18
66 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG149 | 1S-DL-YP-ETC-DJLM-2201-VNG149 | PLOT NO 15 KARKARDOMA COMM COMP | TG-VNG149A-1 | 19503700 | 990 | 320 | 247 | 0.96 | 171 | 60 | 254 | 45 | 192 | 66 | 283 | 81 | 2019-06-10 14:30 | 24.3 | -33.9 | 283 | B | 101 | 91 | 108 | 17 | 0.1 |  |  | 99.9 | 719.37 | 719.37 | 719.07 | 719.37 | [16 empty] | 719.37 | 0.23 | 0.3 | 0.17
67 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG150 | 1S-DL-YP-ETC-DJLM-2201-VNG150 | PLOT NO 16 KARKARDOMA COMM COMP | TG-VNG150A-1 | 19505566 | 990 | 320 | 247 | 0.96 | 174 | 40 | 165 | 25 | 104 | 109 | 458 | 328 | 2019-06-15 11:00 | 65.3 | -8.3 | 458 | B | 95 | 97 | 108 | 13 | 0.2 | 0.1 |  | 99.7 | 719.36 | 719.36 | 718.36 | 719.36 | [16 empty] | 719.36 | 0.24 | 0.33 | 0.18
68 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG151 | 1S-DL-YP-ETC-DJLM-2201-VNG151 | PLOT NO 17 KARKARDOMA COMM COMP | TG-VNG151A-1 | 19501929 | 990 | 320 | 240 | 0.99 | 127 | 33 | 141 | 42 | 180 | 51 | 219 | 67 | 2019-06-14 14:30 | 19.1 | 0.7 | 219 | B | 90 | 86 | 123 | 37 |  |  | 0.5 | 99.5 | 716.16 | 716.16 | 716.16 | 716.16 | [16 empty] | 716.16 | 3.44 | 0.33 | 0.13
69 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG152 | 1S-DL-YP-ETC-DJLM-2201-VNG152 | KKD INSTITIONAL AREA S/ST-3 | TG-VNG152A-2 | 19506325 | 630 | 200 | 247 | 0.97 | 68 | 15 | 59 | 34 | 139 | 18 | 74 | 74 | 2019-06-27 16:30 | 19.2 | 2.4 | 156 | Y | 28 | 230 | 42 | 202 |  |  | 0.1 | 99.9 | 711.39 | 711.39 | 711.39 | 711.39 | [16 empty] | 711.39 | 8.21 | 0.41 | 0.11
70 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG153 | 1S-DL-YP-ETC-DJLM-2201-VNG153 | E-BLK CBD GROUND | TG-VNG153A-1 | 19504285 | 400 | 120 | 249 | 0.99 | 47 | 17 | 69 | 19 | 76 | 10 | 41 | 32 | 2019-06-10 13:00 | 6.6 | -0.8 | 86 | Y | 93 | 117 | 91 | 26 |  |  | 0.2 | 99.8 | 718.2 | 718.2 | 718.2 | 718.2 | [16 empty] | 718.2 | 1.4 | 0.34 | 0.12
71 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG164 | 1S-DL-YP-ETC-DJLM-2201-VNG164 | C- BLK S/STN, CBD GROUND | TG-VNG164A-1 | 19505796 | 400 | 120 | 244 | 0.99 | 22 | 9 | 35 | 13 | 54 | 0 | 0 | 48 | 2019-06-13 13:00 | 9.5 | -1.2 | 60 | Y | 151 | 148 | 1 | 150 |  |  | 9.1 | 90.9 | 710.57 | 710.57 | 710.57 | 710.57 | [16 empty] | 710.57 | 9.03 | 0.46 | 0.06
72 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG167 | 1S-DL-YP-ETC-DJLM-2201-VNG167 | D-Blk S/Stn Cbd Ground, Cbd Ground | TG-VNG167A-1 | 19505978 | 400 | 120 | 251 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-11 11:30 | 0.1 | 0.1 | 0 | Y | 0 | 100 | 100 | 100 |  |  | 23.5 | 76.5 | 708.27 | 708.27 | 708.27 | 708.27 | [16 empty] | 708.27 | 11.33 | 0 | 0
73 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG168 | 1S-DL-YP-ETC-DJLM-2201-VNG168 | G Block S/Stn Cbd, Cbd Ground | TG-VNG168A-1 | 19504681 | 400 | 120 | 251 | 0.97 | 23 | 7 | 27 | 11 | 44 | 5 | 21 | 20 | 2019-06-10 13:30 | 6.1 | -0.3 | 53 | Y | 83 | 207 | 10 | 197 |  | 0.1 | 96.6 | 3.3 | 719.42 | 719.42 | 719.42 | 719.42 | [16 empty] | 719.42 | 0.18 | 0.41 | 0.06
74 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG171 | 1S-DL-YP-ETC-DJLM-2201-VNG171 | Priyadarshni Working Women,Ymca Hostel | TG-VNG171A-1 | 19504683 | 400 | 120 | 245 | 0.89 | 22 | 5 | 22 | 7 | 26 | 10 | 39 | 16 | 2019-06-06 16:30 | 13.5 | 1.1 | 42 | B | 78 | 89 | 133 | 55 |  |  | 1.7 | 98.3 | 719.48 | 719.48 | 719.48 | 719.48 | [16 empty] | 719.48 | 0.12 | 0.51 | 0.05
75 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG179 | 1S-DL-YP-ETC-DJLM-2201-VNG179 | HOTEL HOLIDAY INN PKG | TG-VNG179A-1 | 19504521 | 400 | 120 | 249 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [7 empty] | 29.2 | 70.8 | 719.47 | 719.47 | 719.47 | 719.47 | [16 empty] | 719.47 | 0.13 |  | 0
76 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG181 | 1S-DL-YP-ETC-DJLM-2201-VNG181 | Anand Vihar Police Station | TG-VNG181A-1 | 19506387 | 400 | 120 | 247 | 0.99 | 54 | 18 | 74 | 16 | 62 | 20 | 80 | 16 | 2019-06-03 15:30 | 16 | -2.6 | 106 | B | 99 | 85 | 116 | 31 |  |  | 0.1 | 99.9 | 712.53 | 712.53 | 712.53 | 712.53 | [16 empty] | 712.53 | 7.07 | 0.7 | 0.14
77 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG182 | 1S-DL-YP-ETC-DJLM-2201-VNG182 | UTCS STAFF QUARTER | TG-VNG182A-1 | 19505429 | 400 | 120 | 244 | 0.99 | 28 | 12 | 50 | 15 | 62 | 2 | 7 | 50 | 2019-06-03 23:30 | 4.9 | -1.1 | 78 | Y | 99 | 196 | 5 | 191 |  |  | 5.6 | 94.4 | 712.48 | 712.48 | 712.48 | 712.48 | [16 empty] | 712.48 | 7.12 | 0.48 | 0.07
78 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG200 | 1S-DL-YP-ETC-DJLM-2201-VNG200 | JAGRITI ENCLAVE PHASE-III S/Stn No.1 | TG-VNG200A-1 | 19506747 | 990 | 320 | 247 | 0.96 | 99 | 41 | 167 | 9 | 36 | 49 | 202 | 151 | 2019-06-08 21:00 | 32.6 | 1.3 | 202 | B | 77 | 81 | 142 | 65 | 0.1 | 0.1 | 2 | 97.9 | 699.23 | 699.23 | 699.23 | 699.23 | [16 empty] | 699.23 | 20.37 | 0.22 | 0.1
79 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG201 | 1S-DL-YP-ETC-DJLM-2201-VNG201 | INDER PURI - KKD | TG-VNG201A-1 | 19506696 | 630 | 200 | 247 | 0.97 | 142 | 44 | 180 | 24 | 99 | 74 | 302 | 178 | 2019-06-11 22:00 | 40.6 | 6.8 | 304 | B | 102 | 49 | 150 | 101 | 0.1 | 0.1 | 18 | 81.8 | 626.28 | 706.58 | 216.58 | 658.28 | 80.3 |  |  | 48.3 | [12 empty] | 706.58 | 13.02 | 0.69 | 0.23
80 | 2019-06-01 | 2019-06-30 23:30 | KARKARDOOMA | SAINI ENCLAVE | 1210 | VNG203 | 1S-DL-YP-ETC-DJLM-2201-VNG203 | JAGRITI ENCLAVE PHASE-III S/Stn No.2 | TG-VNG203A-1 | 19506749 | 990 | 320 | 247 | 0.97 | 34 | 22 | 92 | 7 | 30 | 5 | 21 | 67 | 2019-06-28 16:00 | 15 | 0.6 | 92 | R | 98 | 100 | 102 | 4 |  | 0.1 | 6.6 | 93.4 | 700.48 | 700.48 | 700.48 | 700.48 | [16 empty] | 700.48 | 19.12 | 0.57 | 0.03