## Loading Condition > 80%
MIS Report of Distribution Transformer - Jun19
Jun19 1211 GT ROAD (Loading Condition > 80% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN069 | 1S-DL-YP-ETC-DDGN-2251-DGN069 | A-BLOCK JHILMIL INDILSHAD AREA:ID | TG-DGN069A-4 | 19506858 | 990 | 320 | 248 | 0.96 | 893 | 309 | 1323 | 302 | 1296 | 282 | 1201 | 111 | 2019-06-28 14:30 | 124.2 | -284.5 | 1402 | B | 53 | 124 | 123 | 71 | 59.1 | 0.1 | 2.2 | 38.5 | 432.58 | 10.3 | 21.32 | 122.05 | 119.3 | 355.08 | 355.08 | 323.03 | 116 | 310.2 | 301.51 | 240.2 | 34 | 26.3 | 17.59 | 17 |  |  |  |  | 702.28 | 17.32 | 0.41 | 0.9
2 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN071 | 1S-DL-YP-ETC-DDGN-2251-DGN071 | B-BLK COMPLAINT CENTER JLM IND AREA:ID | TG-DGN071A-1 | 19506356 | 990 | 320 | 253 | 0.99 | 953 | 313 | 1265 | 317 | 1274 | 324 | 1315 | 46 | 2019-06-29 15:00 | 382.1 | -104.6 | 1376 | B | 98 | 98 | 103 | 5 |  |  | 2.1 | 97.9 | 44.3 | 40.3 | 37.3 | 40.3 | 267.3 | 257 | 257 | 258.3 | 337 | 354.3 | 327.3 | 342.3 | 53 | 50 | 89.3 | 60.3 |  |  |  |  | 702 | 18 | 0.5 | 0.96
3 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN072 | 1S-DL-YP-ETC-DDGN-2251-DGN072 | PREM ICE FACTORY:ID | TG-DGN072A-1 | 19506735 | 990 | 320 | 246 | 0.99 | 1024 | 343 | 1409 | 339 | 1397 | 342 | 1412 | 13 | 2019-06-29 15:30 | 212.8 | -54.4 | 1465 | B | 100 | 98 | 102 | 4 |  |  | 11.2 | 88.8 | 16 | 19.3 | 10 | 14.3 | 126 | 118.3 | 118.3 | 124 | 100.42 | 108.12 | 107.42 | 105.12 | 66.13 | 64.43 | 66.43 | 66.13 | 3.3 | 1.3 | 5.3 | 2.3 | 698.42 | 21.18 | 0.52 | 1.03
4 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN073 | 1S-DL-YP-ETC-DDGN-2251-DGN073 | SARDAR ALUMINIUM:ID | TG-DGN073A-1 | 19501448 | 990 | 320 | 254 | 0.91 | 911 | 312 | 1298 | 308 | 1286 | 291 | 1215 | 78 | 2019-06-22 15:00 | 42.7 | -259.8 | 1298 | R | 105 | 101 | 94 | 11 |  |  | 0.2 | 99.8 |  |  | 7.3 |  | 364.07 | 379.37 | 379.37 | 384.37 | 265.25 | 305.52 | 313.52 | 301.52 | 88.27 | 32.3 | 7 | 31.3 |  |  |  |  | 717.59 | 2.01 | 0.52 | 0.92
5 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN077 | 1S-DL-YP-ETC-DDGN-2251-DGN077 | SANSAR:K | TG-DGN077A-3 | 19506621 | 990 | 320 | 253 | 0.98 | 1125 | 383 | 1551 | 367 | 1477 | 375 | 1513 | 64 | 2019-06-26 12:00 | 319.7 | -119 | 1551 | R | 102 | 100 | 98 | 4 |  | 0.1 | 0.6 | 99.3 |  |  |  |  | 92.26 | 93.26 | 93.26 | 95.56 | 428.47 | 451.16 | 439.47 | 438.17 | 171.27 | 153.28 | 153.57 | 164.27 | 12.3 | 7 | 6 | 6.3 | 705.1 | 14.5 | 0.54 | 1.14
6 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN081 | 1S-DL-YP-ETC-DDGN-2251-DGN081 | DILSHAD GDN S/STN-4:ID | TG-DGN081A-3 | 19504435 | 630 | 200 | 249 | 0.99 | 623 | 221 | 903 | 209 | 847 | 193 | 783 | 103 | 2019-06-13 11:30 | 99.4 | -52.9 | 923 | R | 106 | 98 | 96 | 10 |  |  | 3.6 | 96.4 | 2 | 2 | 2 | 2 | 21 | 67 | 67 | 49 | 546.5 | 568.16 | 601.16 | 575.16 | 146.26 | 82 | 47.3 | 93 | 3 |  |  |  | 719.16 | 0.44 | 0.64 | 0.99
7 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN081 | 1S-DL-YP-ETC-DDGN-2251-DGN081 | DILSHAD GDN S/STN-4:ID | TG-DGN081A-4 | 19504966 | 990 | 320 | 245 | 0.99 | 881 | 270 | 1114 | 326 | 1346 | 285 | 1177 | 208 | 2019-06-27 11:00 | 253.9 | -58.9 | 1346 | Y | 87 | 116 | 97 | 29 |  |  | 0.3 | 99.7 | 64.3 | 0.3 | 27.3 | 10 | 345.48 | 211.37 | 211.37 | 314.54 | 307.45 | 439.56 | 368.09 | 388.39 | 0.3 | 66.3 | 3.3 | 5 |  |  |  |  | 718.33 | 1.27 | 0.51 | 0.89
8 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN083 | 1S-DL-YP-ETC-DDGN-2251-DGN083 | R.BLK DILSHAD GARDEN S/S NO-1:ID | TG-DGN083A-2 | 19503033 | 630 | 200 | 237 | 0.99 | 552 | 212 | 877 | 180 | 741 | 160 | 659 | 191 | 2019-06-29 16:00 | 67.6 | -20.7 | 1030 | R | 117 | 87 | 96 | 30 |  |  | 10.6 | 89.4 |  |  |  |  | 28.3 | 265.3 | 265.3 | 86 | 577.19 | 438.31 | 633 | 623.49 | 109.3 | 14.59 |  | 9.11 | 3.41 |  |  |  | 719 | 1 | 0.63 | 0.88
9 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN085 | 1S-DL-YP-ETC-DDGN-2251-DGN085 | A-PKT,DILSHAD GDN:ID | TG-DGN085A-1 | 19501381 | 630 | 200 | 237 | 0.98 | 558 | 193 | 850 | 216 | 954 | 149 | 647 | 271 | 2019-06-11 01:30 | 91.5 | 4.1 | 981 | Y | 96 | 123 | 81 | 42 |  | 0.1 | 51.7 | 48.2 | 37.23 | 0.3 | 37.59 | 9.3 | 381.11 | 177.4 | 177.4 | 377.39 | 288.52 | 468.16 | 213.31 | 325.47 | 10.42 | 67.24 |  | 5.12 |  | 4.18 |  |  | 718.08 | 1.52 | 0.48 | 0.89
10 | 2019-06-13 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN086 | 1S-DL-YP-ETC-DDGN-2251-DGN086 | B-PKT,DILSHAD GDN:ID | TG-DGN086A-2 | 19501384 | 990 | 320 | 237 | 0.98 | 760 | 217 | 915 | 300 | 1267 | 243 | 1026 | 312 | 2019-06-29 23:00 | 128.1 | 49.3 | 1267 | Y | 88 | 116 | 96 | 28 |  |  |  | 100 | 0.3 |  |  |  | 256.55 | 82.49 | 82.49 | 183.36 | 161.16 | 314.22 | 212.06 | 235.05 |  | 21.3 | [6 empty] | 418.41 | 13.19 | 0.58 | 0.77
11 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN088 | 1S-DL-YP-ETC-DDGN-2251-DGN088 | L&H PKT DILSHAD GARDEN:ID | TG-DGN088A-3 | 19504331 | 400 | 120 | 246 | 0.97 | 293 | 102 | 405 | 56 | 223 | 135 | 537 | 273 | 2019-06-15 16:30 | 55.5 | 18.2 | 601 | B | 101 | 69 | 130 | 61 | 4.2 | 1.3 | 21 | 73.5 | 10.3 | 112.47 | 0.3 | 5.3 | 239.32 | 424.37 | 424.37 | 248.02 | 468.42 | 181.2 | 469.41 | 465.12 |  |  | 94 |  |  |  | 3 |  | 718.44 | 1.16 | 0.62 | 0.73
12 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN091 | 1S-DL-YP-ETC-DDGN-2251-DGN091 | O&P PKT DILSHAD GARDEN:ID | TG-DGN091A-2 | 19506560 | 630 | 200 | 245 | 0.97 | 585 | 244 | 1009 | 159 | 647 | 181 | 741 | 325 | 2019-06-02 01:00 | 138.8 | 13.2 | 1027 | R | 115 | 88 | 97 | 27 |  | 0.1 | 29.9 | 69.9 | 0.3 | 1 | 0.3 | 0.3 | 63.3 | 182 | 182 | 111 | 512.52 | 523.22 | 578.52 | 567.52 | 109 | 0.3 | 11.3 | 27.3 | 21 |  |  |  | 706.52 | 13.08 | 0.59 | 0.93
13 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN091 | 1S-DL-YP-ETC-DDGN-2251-DGN091 | O&P PKT DILSHAD GARDEN:ID | TG-DGN091A-1 | 19506580 | 630 | 200 | 244 | 0.96 | 647 | 221 | 911 | 245 | 999 | 181 | 738 | 230 | 2019-06-03 06:00 | 183.6 | 40 | 1293 | Y | 113 | 113 | 74 | 39 | 0.2 |  | 9.6 | 90.2 |  |  | 1 |  | 80 | 105 | 105 | 155.24 | 542.52 | 494.22 | 291.3 | 534.58 | 82 | 93 | 0.3 | 16 | 2 | 14.3 |  | 0.3 | 706.52 | 13.08 | 0.5 | 1.03
14 | 2019-06-02 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN097 | 1S-DL-YP-ETC-DDGN-2251-DGN097 | J&K PKT DILSHAD GARDEN-4 | TG-DGN097A-1 | 19501399 | 630 | 200 | 246 | 0.97 | 453 | 128 | 523 | 228 | 939 | 97 | 397 | 491 | 2019-06-30 00:30 | 75.9 | 17 | 959 | Y | 89 | 149 | 62 | 87 |  |  | 2.2 | 97.8 | 61.57 | 1.3 | 273.47 | 23.57 | 460.2 | 135.24 | 135.24 | 435.2 | 173.11 | 478.04 | 12.3 | 236.11 |  | 78 |  |  |  | 2.3 |  |  | 695.28 | 0.32 | 0.52 | 0.72
15 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN103 | 1S-DL-YP-ETC-DDGN-2251-DGN103 | A BLK TAHIRPUR(JLM IND AREA) S/STN-1:ID | TG-DGN103A-2 | 19501356 | 630 | 200 | 247 | 0.87 | 672 | 230 | 986 | 221 | 953 | 221 | 945 | 38 | 2019-06-21 13:00 | 26.2 | -231.4 | 986 | R | 100 | 99 | 101 | 2 |  |  | 17.2 | 82.8 | 28 | 28.3 | 18.3 | 26.3 | 273.3 | 275.3 | 275.3 | 267 | 309.13 | 328.42 | 362.13 | 329.43 | 103.29 | 85 | 90.29 | 92.59 | 5.3 | 2 | 2 | 3.3 | 719.42 | 0.18 | 0.48 | 1.07
16 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN104 | 1S-DL-YP-ETC-DDGN-2251-DGN104 | A BLK TAHIRPUR(JLM IND AREA) S/STN-3:ID | TG-DGN104A-2 | 19501369 | 630 | 200 | 265 | 0.95 | 577 | 195 | 723 | 199 | 741 | 184 | 683 | 51 | 2019-06-29 16:00 | 103 | -89.2 | 763 | R | 101 | 102 | 97 | 5 |  |  | 0.2 | 99.8 | 278.3 | 265 | 273.3 | 271.3 | 140 | 155.3 | 155.3 | 148.3 | 269.12 | 268.12 | 281.42 | 276.42 | 32 | 31 | 13.3 | 23 |  |  |  |  | 719.42 | 0.18 | 0.42 | 0.92
17 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN104 | 1S-DL-YP-ETC-DDGN-2251-DGN104 | A BLK TAHIRPUR(JLM IND AREA) S/STN-3:ID | TG-DGN104A-1 | 19505489 | 630 | 200 | 249 | 0.97 | 637 | 209 | 893 | 216 | 929 | 212 | 909 | 31 | 2019-06-09 16:30 | 291 | -70 | 929 | Y | 95 | 101 | 103 | 8 |  | 0.1 | 5.1 | 94.8 | 180.04 | 158.39 | 142.09 | 160.39 | 162.27 | 172.25 | 172.25 | 169.25 | 321.56 | 310.56 | 339.23 | 325.26 | 37.3 | 58.57 | 48 | 45.57 |  | 1 | 0.3 | 0.3 | 701.57 | 18.03 | 0.43 | 1.01
18 | 2019-06-10 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN107 | 1S-DL-YP-ETC-DDGN-2251-DGN107 | B BLK OPP SWAHNEY IND.:PL | TG-DGN107A-1 | 19505328 | 990 | 320 | 240 | 0.98 | 876 | 292 | 1266 | 268 | 1161 | 316 | 1366 | 178 | 2019-06-13 17:00 | 265.9 | -85.8 | 1366 | B | 96 | 98 | 106 | 10 |  |  | 1.9 | 98.1 | 127.14 | 89.44 | 74.14 | 97.44 | 160.1 | 188.1 | 188.1 | 175.4 | 184.14 | 195.44 | 186.14 | 194.44 | 8.3 | 6.3 | 28.3 | 12 |  |  |  |  | 480.08 | 23.52 | 0.46 | 0.89
19 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN109 | 1S-DL-YP-ETC-DDGN-2251-DGN109 | B-34 JLM INDUSTRIAL AREA | TG-DGN109A-1 | 19501836 | 990 | 320 | 242 | 0.9 | 1088 | 355 | 1525 | 367 | 1581 | 366 | 1568 | 51 | 2019-06-24 11:30 | 82.4 | -225.2 | 1581 | Y | 99 | 101 | 100 | 2 |  |  | 0.1 | 99.9 | 25 | 57.3 | 45 | 43 | 382 | 347 | 347 | 363 | 154.54 | 126.24 | 137.25 | 137.24 | 151.59 | 168.59 | 163.28 | 163.59 | 6 | 20 | 14 | 12.3 | 719.53 | 0.07 | 0.45 | 1.1
20 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN112 | 1S-DL-YP-ETC-DDGN-2251-DGN112 | DAMODAR PARK,DILSHAD GARDEN:PL | TG-DGN112A-2 | 19502279 | 990 | 320 | 247 | 0.99 | 1045 | 348 | 1518 | 348 | 1523 | 349 | 1521 | 4 | 2019-06-08 11:00 | 170 | -138.4 | 1523 | Y | 103 | 99 | 98 | 5 | 22.8 | 11.1 | 32.5 | 33.6 |  |  | 0.3 |  | 102 | 137 | 137 | 127 | 435.03 | 459.59 | 426.03 | 437.59 | 174.22 | 119.56 | 147.22 | 150.26 | 7.3 | 2 | 3.3 | 3.3 | 718.55 | 1.05 | 0.55 | 1.06
21 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN113 | 1S-DL-YP-ETC-DDGN-2251-DGN113 | DAL MILL,DILSHAD GARDEN:PM | TG-DGN113A-2 | 19503411 | 990 | 200 | 239 | 0.96 | 534 | 203 | 861 | 42 | 179 | 289 | 1227 | 921 | 2019-06-10 00:30 | 133.9 | 6 | 1298 | B | 120 | 11 | 169 | 158 |  |  | 0.1 | 99.9 | 2 | 708.11 | 2 | 2 | 77.46 | 2 | 2 | 331.4 | 630.25 |  | 542.11 | 376.31 |  |  | 161.3 | [5 empty] | 710.11 | 9.49 | 0.76 | 0.54
22 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN116 | 1S-DL-YP-ETC-DDGN-2251-DGN116 | E-BLK NEW SEEMA PURI:PL | TG-DGN116A-1 | 19506588 | 630 | 200 | 238 | 0.97 | 645 | 230 | 1003 | 219 | 949 | 196 | 849 | 135 | 2019-06-25 23:00 | 273 | 13 | 1003 | R | 112 | 95 | 93 | 19 | 0.1 | 0.1 | 15.1 | 84.8 |  |  | 0.3 |  | 5.3 | 24.29 | 24.29 | 12.59 | 606 | 675.22 | 667.01 | 686.22 | 90.21 | 2.29 | 2.29 | 2.59 | 0.59 | 0.3 |  | 0.3 | 702.5 | 17.1 | 0.58 | 1.02
23 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN124 | 1S-DL-YP-ETC-DDGN-2251-DGN124 | G.T ROAD SEEMA PURI BORDER:PM | TG-DGN124A-1 | 19506420 | 630 | 200 | 245 | 0.98 | 637 | 228 | 953 | 205 | 848 | 203 | 844 | 108 | 2019-06-15 15:30 | 267.4 | -87.4 | 966 | R | 107 | 95 | 98 | 12 |  | 1 | 40.8 | 58.3 | 82.3 | 91.27 | 88.57 | 87.27 | 252.14 | 253.47 | 253.47 | 252.47 | 261.24 | 338.34 | 330.57 | 313.26 | 104.31 | 19.44 | 35.21 | 49.22 | 2.53 |  |  | 0.3 | 703.32 | 16.28 | 0.45 | 1.01
24 | 2019-06-10 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN125 | 1S-DL-YP-ETC-DDGN-2251-DGN125 | NEW SEEMAPURI DDA FLAT:ID | TG-DGN125A-1 | 19504891 | 990 | 320 | 238 | 0.97 | 779 | 240 | 1016 | 313 | 1326 | 226 | 945 | 351 | 2019-06-30 | 161.9 | 27.2 | 1410 | Y | 95 | 123 | 82 | 41 |  | 0.1 | 69.3 | 30.6 | 0.3 | 0.3 | 3 | 0.3 | 192.4 | 55.3 | 55.3 | 165.25 | 297.59 | 380.39 | 193.29 | 325.14 |  | 53.3 |  |  |  | 1 |  |  | 491.09 | 12.51 | 0.59 | 0.79
25 | 2019-06-02 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN132 | 1S-DL-YP-ETC-DDGN-2251-DGN132 | E&F PKT. DILSHAD GARDEN:ID | TG-DGN132A-1 | 19501450 | 990 | 320 | 244 | 0.97 | 860 | 338 | 1486 | 288 | 1276 | 233 | 1024 | 401 | 2019-06-10 22:30 | 167.8 | 50 | 1510 | R | 110 | 103 | 87 | 23 | 35.4 | 23.7 | 22 | 18.8 |  | 0.3 | 1.3 |  | 127.54 | 182.17 | 182.17 | 189.17 | 494.08 | 489.15 | 438.45 | 490.45 | 70 | 23 |  | 15 | 3 |  |  |  | 695.02 | 0.58 | 0.59 | 0.87
26 | 2019-06-03 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN133 | 1S-DL-YP-ETC-DDGN-2251-DGN133 | B-BLOCK OLD SEEMAPURI :PL | TG-DGN133A-3 | 19503779 | 630 | 200 | 239 | 0.97 | 386 | 212 | 903 | 119 | 503 | 54 | 226 | 590 | 2019-06-30 00:30 | 86.5 | 26.7 | 940 | R | 164 | 90 | 46 | 118 |  | 0.9 | 60.5 | 38.6 |  | 1 | 331.59 | 1 | 1.3 | 383.28 | 383.28 | 222.55 | 549.44 | 286.08 |  | 446.41 | 117.22 |  |  |  | 2 |  |  |  | 670.36 | 1.24 | 0.7 | 0.61
27 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN135 | 1S-DL-YP-ETC-DDGN-2251-DGN135 | KHERA VILLAGE:PM | TG-DGN135A-1 | 19506547 | 630 | 200 | 247 | 0.96 | 585 | 224 | 935 | 164 | 687 | 197 | 841 | 217 | 2019-06-10 21:30 | 210.6 | 49.2 | 935 | R | 107 | 83 | 110 | 27 | 0.1 | 0.9 | 74.7 | 24.3 |  |  |  |  | 5 | 133.57 | 133.57 | 20 | 540.42 | 570.06 | 510.2 | 593.34 | 156.21 |  | 184.13 | 90.29 | 2 |  |  |  | 704.03 | 15.57 | 0.67 | 0.93
28 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN141 | 1S-DL-YP-ETC-DDGN-2251-DGN141 | B-BLK DILSHAD CLY:PM | TG-DGN141A-2 | 19505287 | 990 | 320 | 237 | 0.98 | 1031 | 321 | 1342 | 352 | 1477 | 359 | 1500 | 148 | 2019-06-30 00:30 | 206.1 | 57.3 | 1604 | B | 92 | 106 | 102 | 14 | 0.1 |  | 6.7 | 93.2 | 1 |  |  |  | 232.25 | 150.57 | 150.57 | 182.55 | 418.56 | 436.11 | 396.43 | 419.43 | 40.1 | 86.13 | 91.43 | 86.23 |  | 19.1 | 14.1 | 3.3 | 692.31 | 27.29 | 0.51 | 1.04
29 | 2019-06-03 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN162 | 1S-DL-YP-ETC-DDGN-2251-DGN162 | F-BLOCK DILSHAD COLONY:ID | TG-DGN162A-3 | 19501791 | 990 | 320 | 248 | 0.97 | 1139 | 340 | 1363 | 432 | 1756 | 367 | 1467 | 353 | 2019-06-30 01:30 | 189.9 | 12.5 | 1756 | Y | 96 | 109 | 95 | 14 |  |  | 59.3 | 40.7 | 0.01 | 0.01 | 2.37 | 0.01 | 147.29 | 72.53 | 72.53 | 143.52 | 476.32 | 494.43 | 391.57 | 452.09 | 39.38 | 84.25 | 65.3 | 66.08 | 0.58 | 12.36 | 4.36 | 2.28 | 664.38 | 7.22 | 0.47 | 1.15
30 | 2019-06-03 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN162 | 1S-DL-YP-ETC-DDGN-2251-DGN162 | F-BLOCK DILSHAD COLONY:ID | TG-DGN162A-1 | 19504839 | 990 | 320 | 242 | 0.97 | 908 | 364 | 1510 | 299 | 1236 | 245 | 1006 | 437 | 2019-06-29 23:30 | 173 | 11.8 | 1553 | R | 116 | 97 | 87 | 29 |  |  | 17.1 | 82.9 | 3 | 5 | 3.3 | 3 | 140.23 | 257.1 | 257.1 | 215.53 | 444.58 | 382.5 | 323.31 | 427.37 | 72.09 | 23.3 |  | 22 | 8 |  |  |  | 668.3 | 3.3 | 0.52 | 0.92
31 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN190 | 1S-DL-YP-ETC-DDGN-2251-DGN190 | NEW POLICE BOTH DILSHAD CLY | TG-DGN190A-1 | 19506003 | 990 | 320 | 247 | 0.97 | 996 | 340 | 1464 | 325 | 1408 | 331 | 1436 | 49 | 2019-06-30 23:30 | 201.6 | 66.9 | 1475 | R | 106 | 97 | 97 | 9 |  | 0.1 | 5.8 | 94.1 |  |  |  |  | 27.57 | 48.27 | 48.27 | 38.57 | 563.49 | 610.49 | 592.52 | 593.49 | 111 | 53 | 61 | 79.3 | 10 | 0.3 | 0.3 | 0.3 | 712.46 | 7.14 | 0.59 | 1.01
32 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN197 | 1S-DL-YP-ETC-DDGN-2251-DGN197 | C- BLK DILSHAD COLONY SSTN NO.-2:PL | TG-DGN197A-1 | 19506596 | 630 | 200 | 249 | 0.98 | 582 | 192 | 768 | 185 | 740 | 205 | 816 | 66 | 2019-06-29 23:30 | 135 | 37 | 893 | B | 90 | 103 | 106 | 16 | 0.1 | 0.1 | 8.8 | 91 |  |  |  |  | 268.53 | 51.57 | 51.57 | 116.54 | 414.52 | 625.48 | 544.51 | 558.51 | 13 | 19 | 49.3 | 21 |  |  | 1 |  | 696.45 | 23.15 | 0.56 | 0.92
33 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN225 | 1S-DL-YP-ETC-DDGN-2251-DGN225 | Oberai compound | TG-DGN225A-1 | 19504360 | 990 | 320 | 246 | 0.98 | 1039 | 352 | 1478 | 352 | 1490 | 335 | 1416 | 70 | 2019-06-01 11:30 | 173.7 | -97.9 | 1490 | Y | 106 | 102 | 92 | 14 |  |  | 1.5 | 98.5 | 107.3 | 154.3 | 197 | 147 | 302.26 | 256.56 | 256.56 | 272.56 | 269.29 | 266.29 | 251.59 | 266.59 | 36 | 37 | 20.3 | 29.3 | 1.3 | 2 | 0.3 | 0.3 | 716.55 | 3.05 | 0.37 | 1.05
34 | 2019-06-04 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN225 | 1S-DL-YP-ETC-DDGN-2251-DGN225 | Oberai compound | TG-DGN225A-2 | 19506760 | 990 | 320 | 239 | 0.97 | 1093 | 367 | 1614 | 365 | 1611 | 361 | 1595 | 17 | 2019-06-20 11:00 | 475.8 | -114.9 | 1872 | Y | 101 | 103 | 96 | 7 | 0.1 | 0.1 | 0.7 | 99.2 | 102.02 | 94.02 | 118.02 | 104.02 | 217.3 | 228.3 | 228.3 | 224.3 | 210.12 | 201.12 | 209.09 | 206.12 | 83.27 | 89.57 | 65.3 | 78.57 | 2 | 1.3 | 0.3 | 1.3 | 615.11 | 32.49 | 0.4 | 1.1
35 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN232 | 1S-DL-YP-ETC-DDGN-2251-DGN232 | DSIDC SUBSTATION NO-2 | TG-DGN232A-2 | 19501354 | 990 | 320 | 236 | 0.93 | 978 | 331 | 1468 | 317 | 1408 | 330 | 1474 | 63 | 2019-06-24 12:00 | 89.1 | -184.7 | 1474 | B | 103 | 94 | 103 | 9 |  |  | 2.8 | 97.2 | 310.3 | 349.59 | 324 | 328 | 101.28 | 76.29 | 76.29 | 89.58 | 184.41 | 209.11 | 190.11 | 191.11 | 120.46 | 82.16 | 113.16 | 108.46 | 0.3 |  |  |  | 717.55 | 2.05 | 0.39 | 0.99
36 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN232 | 1S-DL-YP-ETC-DDGN-2251-DGN232 | DSIDC SUBSTATION NO-2 | TG-DGN232A-4 | 19504958 | 990 | 320 | 248 | 0.97 | 958 | 318 | 1292 | 331 | 1345 | 310 | 1257 | 77 | 2019-06-15 10:30 | 107.5 | -129.5 | 1390 | Y | 101 | 103 | 96 | 7 |  |  | 0.4 | 99.6 | 123.26 | 125.1 | 172.06 | 138.4 | 292.08 | 290.54 | 290.54 | 280.54 | 264.52 | 248.22 | 265.14 | 260.52 | 34.16 | 49.46 | 25.24 | 34.16 |  | 0.3 |  |  | 714.42 | 5.18 | 0.43 | 0.97
37 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN249 | 1S-DL-YP-ETC-DDGN-2251-DGN249 | Police Booth A BLK JLM IA | TG-DGN249A-1 | 19506423 | 990 | 320 | 245 | 0.98 | 956 | 310 | 1320 | 328 | 1393 | 318 | 1354 | 63 | 2019-06-17 14:00 | 262.7 | -33 | 1393 | Y | 99 | 102 | 99 | 3 |  |  | 1.3 | 98.7 | 12.27 | 11.58 | 12.28 | 11.58 | 317.36 | 301.05 | 301.05 | 311.05 | 347.18 | 322.5 | 350.18 | 343.48 | 26.3 | 67.28 | 28.3 | 37 |  | 0.3 |  |  | 703.51 | 16.09 | 0.51 | 0.97
38 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN252 | 1S-DL-YP-ETC-DDGN-2251-DGN252 | RAILWAY LINE IN FRONT OF B-43 JHILMIL | TG-DGN252A-1 | 19506619 | 990 | 320 | 256 | 0.97 | 1135 | 375 | 1531 | 371 | 1519 | 390 | 1604 | 79 | 2019-06-08 18:00 | 336.6 | -63.4 | 1604 | B | 100 | 97 | 103 | 6 |  |  | 0.4 | 99.6 | 16.3 | 26 | 13.3 | 16.3 | 132 | 139.3 | 139.3 | 129 | 388.25 | 389.25 | 380.25 | 386.25 | 160 | 143 | 184.3 | 165.3 | 4.3 | 3.3 | 4.3 | 4 | 701.25 | 18.35 | 0.51 | 1.15
39 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN032 | 1S-DL-YP-ETC-DDGN-2251-DGN032 | J-Block MS Park Package Near Dispensary | TG-DGN032A-1 | 19501019 | 990 | 320 | 242 | 0.97 | 989 | 349 | 1520 | 316 | 1375 | 324 | 1393 | 136 | 2019-06-11 | 200.2 | 59.6 | 1524 | B | 106 | 95 | 99 | 11 |  | 0.6 | 52.3 | 47.1 |  |  |  |  | 53.59 | 153.06 | 153.06 | 89.42 | 538.05 | 493.28 | 542.22 | 530.52 | 114.08 | 68.38 | 86.38 | 94.38 | 9 |  | 0.3 |  | 715.12 | 4.48 | 0.58 | 1
40 | 2019-06-02 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN038 | 1S-DL-YP-ETC-DDGN-2251-DGN038 | MOTI RAM ROAD G.T.ROAD FLYOVER S/STN | TG-DGN038A-2 | 19501708 | 990 | 320 | 242 | 0.97 | 844 | 250 | 1067 | 340 | 1478 | 254 | 1092 | 399 | 2019-06-29 23:30 | 184.7 | 81 | 1478 | Y | 97 | 105 | 98 | 8 |  |  | 7.9 | 92.1 |  |  |  |  | 14.34 | 26.34 | 26.34 | 17.3 | 482.22 | 383.52 | 474.26 | 461.56 | 4 | 88 | 7.3 | 21.3 |  | 2.3 |  |  | 690.03 | 5.57 | 0.7 | 0.85
41 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN039 | 1S-DL-YP-ETC-DDGN-2251-DGN039 | MANSAROVER PARK, MOTHER DAIRY | TG-DGN039A-3 | 19505670 | 630 | 200 | 241 | 0.98 | 467 | 69 | 296 | 150 | 659 | 249 | 1106 | 702 | 2019-06-12 01:00 | 134 | 5.8 | 1239 | B | 60 | 104 | 137 | 77 | 0.3 | 1.7 | 72.2 | 25.8 | 316.13 | 12.02 | 2 | 17.45 | 360.33 | 406.35 | 406.35 | 439.48 | 22.3 | 280.39 | 423.2 | 241.43 |  |  | 50 |  |  |  | 4 |  | 699.16 | 20.44 | 0.51 | 0.74
42 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN039 | 1S-DL-YP-ETC-DDGN-2251-DGN039 | MANSAROVER PARK MOTHER DAIRY | TG-DGN039A-1 | 19506343 | 990 | 320 | 241 | 0.97 | 907 | 343 | 1513 | 315 | 1383 | 250 | 1089 | 376 | 2019-06-10 23:00 | 239 | 59.2 | 1523 | R | 110 | 104 | 85 | 25 | 0.1 | 0.1 | 11.3 | 88.5 | 0.3 | 0.3 | 0.3 | 0.3 | 27.04 | 35.34 | 35.34 | 63.04 | 560.29 | 615.46 | 490.24 | 597.16 | 104.28 | 47.01 |  | 38.01 | 6.2 |  | 0.3 |  | 698.51 | 21.09 | 0.61 | 0.92
43 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN041 | 1S-DL-YP-ETC-DDGN-2251-DGN041 | MOTI RAM UNWALA S/STN | TG-DGN041A-1 | 19505041 | 400 | 120 | 241 | 0.98 | 287 | 80 | 341 | 145 | 624 | 63 | 268 | 325 | 2019-06-30 23:00 | 42.8 | 3.6 | 624 | Y | 91 | 159 | 50 | 109 |  |  | 22.5 | 77.5 | 51.16 |  | 315.33 | 60.35 | 471.36 | 113.12 | 113.12 | 400.08 | 192.2 | 486.01 | 64.59 | 254.29 |  | 104.59 |  |  |  | 11 |  |  | 715.12 | 4.48 | 0.51 | 0.72
44 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN042 | 1S-DL-YP-ETC-DDGN-2251-DGN042 | MOTI RAM PEER WALA S/STN | TG-DGN042A-2 | 19505471 | 630 | 200 | 235 | 0.99 | 592 | 93 | 411 | 286 | 1312 | 212 | 956 | 786 | 2019-06-11 | 147.8 | 5.8 | 1312 | Y | 68 | 114 | 118 | 50 | 0.5 | 1.1 | 29.9 | 68.6 | 9.3 | 0.3 | 0.3 | 0.3 | 406.13 | 54.3 | 54.3 | 89.03 | 282.5 | 508.03 | 519.33 | 579.3 |  | 116.3 | 124.3 | 29.3 |  | 19 | 23 |  | 698.33 | 21.27 | 0.59 | 0.94
45 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN044 | 1S-DL-YP-ETC-DDGN-2251-DGN044 | JAISWAL MARG:PM | TG-DGN044A-1 | 19501798 | 990 | 320 | 243 | 0.97 | 866 | 290 | 1185 | 278 | 1156 | 298 | 1232 | 67 | 2019-06-03 01:00 | 181.8 | 53 | 1390 | B | 97 | 91 | 113 | 22 |  | 4.3 | 94.6 | 1 | 0.3 | 13 |  |  | 328.21 | 375.25 | 375.25 | 287.09 | 375.05 | 326.41 | 508.3 | 422.47 | 11.5 | 0.4 | 40.5 | 5.5 |  |  |  |  | 715.46 | 4.14 | 0.53 | 0.87
46 | 2019-06-20 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN045 | 1S-DL-YP-ETC-DDGN-2251-DGN045 | MANDOLI ROAD:PL | TG-DGN045A-1 | 19501758 | 990 | 320 | 247 | 0.97 | 921 | 346 | 1489 | 257 | 1094 | 319 | 1349 | 347 | 2019-06-30 23:30 | 203.1 | 41.2 | 1489 | R | 110 | 78 | 112 | 34 |  |  | 64.2 | 35.8 | 0.3 | 0.3 |  | 0.3 | 8.41 | 111.49 | 111.49 | 17.11 | 204.08 | 139.19 | 213.19 | 217.38 | 35.49 |  | 35.49 | 16.19 | 2.3 |  |  |  | 251.38 | 12.22 | 0.6 | 0.93
47 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN047 | 1S-DL-YP-ETC-DDGN-2251-DGN047 | BHAGWANPUR KHERA NO-1:PL | TG-DGN047A-1 | 19500681 | 990 | 320 | 239 | 0.97 | 1004 | 318 | 1357 | 322 | 1393 | 364 | 1564 | 191 | 2019-06-09 23:30 | 212.7 | 73.6 | 1564 | B | 97 | 99 | 103 | 6 |  | 0.4 | 59.3 | 40.3 |  |  |  |  | 30.3 | 16.3 | 16.3 | 20 | 602.18 | 661.25 | 575.35 | 621.25 | 81.28 | 40.51 | 101.43 | 76.51 | 4.3 |  | 12.58 | 0.3 | 718.46 | 1.14 | 0.61 | 1.01
48 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN050 | 1S-DL-YP-ETC-DDGN-2251-DGN050 | NEW MODERN SHAHDRA NO I GALI NO 13:PL | TG-DGN050A-1 | 19505901 | 990 | 320 | 240 | 0.97 | 966 | 307 | 1384 | 299 | 1345 | 360 | 1626 | 263 | 2019-06-08 01:30 | 354.9 | 63 | 1718 | B | 94 | 76 | 130 | 54 | 0.3 | 7 | 89.4 | 3.3 |  | 5.51 | 0.3 |  | 144.13 | 340.51 | 340.51 | 89.51 | 541.05 | 358.36 | 532.12 | 586.57 | 20.3 | 0.3 | 138.36 | 29 |  |  | 26.3 |  | 705.48 | 14.12 | 0.55 | 0.98
49 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN052 | 1S-DL-YP-ETC-DDGN-2251-DGN052 | SUBHASH MARG NEW MODERN SHAHDARA:PL | TG-DGN052A-2 | 19505898 | 990 | 320 | 237 | 0.97 | 949 | 266 | 1103 | 328 | 1395 | 355 | 1536 | 382 | 2019-06-11 23:30 | 320.6 | 62.7 | 1826 | B | 82 | 103 | 115 | 33 | 17.5 | 60.5 | 21.3 | 0.6 |  |  |  |  | 339.04 | 148.3 | 148.3 | 173.3 | 362.28 | 498.04 | 489.34 | 485.32 | 1.3 | 55.28 | 98.58 | 44 |  | 1 | 16 |  | 703.02 | 16.58 | 0.54 | 0.96
50 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN074 | 1S-DL-YP-ETC-DDGN-2251-DGN074 | RAJ ENGG.COMPOUND | TG-DGN074A-1 | 19501787 | 990 | 320 | 248 | 0.98 | 1072 | 355 | 1456 | 361 | 1490 | 355 | 1455 | 34 | 2019-06-23 11:00 | 25 | -178.1 | 1490 | Y | 100 | 102 | 99 | 3 |  |  | 0.1 | 99.9 | 2 | 2.3 | 5 | 3.3 | 144.56 | 133.56 | 133.56 | 142.56 | 460.25 | 464.25 | 455.25 | 459.25 | 110.12 | 116.12 | 106.42 | 111.42 | 1.14 | 1.44 | 2.44 | 1.14 | 718.47 | 1.13 | 0.53 | 1.08
51 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN075 | 1S-DL-YP-ETC-DDGN-2251-DGN075 | PAPER PRODUCT | TG-DGN075A-1 | 19505761 | 990 | 320 | 241 | 0.99 | 1026 | 350 | 1525 | 342 | 1487 | 334 | 1446 | 69 | 2019-06-23 11:00 | 442.2 | -29.1 | 1564 | R | 102 | 99 | 99 | 3 |  |  | 3.7 | 96.3 | 58 | 52.3 | 37 | 47 | 301.3 | 324.34 | 324.34 | 320.28 | 280.2 | 280.46 | 296.18 | 288.22 | 61.44 | 44.14 | 32.47 | 46.14 | 1 | 0.3 | 0.3 | 0.3 | 702.34 | 17.26 | 0.44 | 1.04
52 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN105 | 1S-DL-YP-ETC-DDGN-2251-DGN105 | SHAMBU NATH COMP.(F.COL):ID | TG-DGN105A-3 | 19505434 | 990 | 320 | 243 | 0.98 | 1021 | 332 | 1421 | 336 | 1422 | 354 | 1509 | 87 | 2019-06-26 11:00 | 463.4 | -74.9 | 1509 | B | 97 | 99 | 104 | 7 |  |  | 26.8 | 73.2 | 202.45 | 191.45 | 180.45 | 191.15 | 203.14 | 207.14 | 207.14 | 209.44 | 277.4 | 280.1 | 273.47 | 278.1 | 19.46 | 22.16 | 29.09 | 22.46 | 0.3 | 2.3 | 3 | 2 | 703.55 | 16.05 | 0.37 | 1.03
53 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN110 | 1S-DL-YP-ETC-DDGN-2251-DGN110 | VERMA CASTLE:PL | TG-DGN110A-6 | 19501793 | 990 | 320 | 254 | 0.9 | 991 | 329 | 1310 | 327 | 1305 | 335 | 1335 | 27 | 2019-06-17 11:30 | 53.7 | -373.9 | 1366 | R | 99 | 99 | 102 | 3 |  |  | 0.3 | 99.7 | 146.43 | 133.13 | 129.43 | 134.13 | 313.42 | 324.34 | 324.34 | 314.42 | 150.3 | 163.29 | 192.05 | 165.3 | 102.21 | 92 | 100.51 | 98.21 |  |  | 0.3 | 0.3 | 713.16 | 6.44 | 0.41 | 1
54 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN110 | 1S-DL-YP-ETC-DDGN-2251-DGN110 | VERMA CASTLE:PL | TG-DGN110A-1 | 19503035 | 990 | 320 | 247 | 0.91 | 1150 | 370 | 1470 | 374 | 1500 | 406 | 1636 | 153 | 2019-06-01 12:00 | 40.5 | -245.8 | 1636 | B | 98 | 95 | 106 | 11 |  |  | 12.9 | 87.1 | 156.16 | 182.17 | 136.16 | 154.46 | 237.2 | 226.21 | 226.21 | 244.15 | 238.46 | 225.15 | 224.18 | 228.53 | 33.54 | 32.27 | 48.37 | 36.22 | 7.59 | 7.55 | 14.35 | 9.59 | 674.15 | 45.45 | 0.35 | 1.16
55 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN110 | 1S-DL-YP-ETC-DDGN-2251-DGN110 | VERMA CASTLE:PL | TG-DGN110A-5 | 19506053 | 990 | 320 | 245 | 0.96 | 1118 | 376 | 1606 | 369 | 1588 | 373 | 1608 | 19 | 2019-06-23 12:30 | 323.5 | -170.9 | 1608 | B | 99 | 99 | 102 | 3 |  | 0.1 | 4.2 | 95.7 | 52.04 | 57.2 | 34.5 | 47.2 | 277.13 | 280.27 | 280.27 | 273.27 | 230 | 229.3 | 258.03 | 242.3 | 124.57 | 114.27 | 121.19 | 118.27 | 14.21 | 16.51 | 18.26 | 16.51 | 698.35 | 21.25 | 0.45 | 1.13
56 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN111 | 1S-DL-YP-ETC-DDGN-2251-DGN111 | FRIENDS COLONY GALI NO.1 | TG-DGN111A-1 | 19500654 | 990 | 320 | 247 | 0.97 | 883 | 295 | 1206 | 299 | 1220 | 290 | 1179 | 37 | 2019-06-23 12:00 | 36.8 | -156 | 1264 | Y | 100 | 99 | 100 | 1 |  |  | 1.8 | 98.2 | 133.07 | 139.37 | 122.37 | 131.07 | 261.4 | 256.1 | 256.1 | 263.1 | 289.09 | 291.09 | 297.39 | 291.39 | 33.3 | 30.3 | 28 | 31.3 |  |  |  |  | 717.26 | 2.34 | 0.48 | 0.89
57 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN120 | 1S-DL-YP-ETC-DDGN-2251-DGN120 | GALI NO.3 FRIENDS COLONY:PL | TG-DGN120A-1 | 19503629 | 990 | 320 | 247 | 0.92 | 1010 | 339 | 1398 | 341 | 1410 | 330 | 1355 | 50 | 2019-06-24 11:30 | 74.3 | -248.8 | 1419 | Y | 98 | 106 | 97 | 9 |  |  | 0.1 | 99.9 | 45.3 | 36 | 44.3 | 41.3 | 300.11 | 245.41 | 245.41 | 285.41 | 247 | 257.3 | 252.59 | 251.29 | 126.27 | 174.27 | 121.28 | 138.58 | 0.3 | 6 |  | 2 | 719.38 | 0.22 | 0.5 | 1.02
58 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN127 | 1S-DL-YP-ETC-DDGN-2251-DGN127 | GALI NO.1B FRIENDS COLONY:PL | TG-DGN127A-2 | 19504119 | 990 | 320 | 238 | 0.94 | 889 | 283 | 1211 | 317 | 1351 | 290 | 1240 | 128 | 2019-06-27 16:30 | 146.5 | -186.2 | 1370 | Y | 97 | 105 | 98 | 8 |  |  | 4.7 | 95.3 | 152.3 | 140.58 | 165.27 | 148.27 | 283.57 | 290.29 | 290.29 | 287 | 274.49 | 237.5 | 266.49 | 263.2 | 8 | 49.59 | 17 | 20.29 |  |  |  |  | 719.16 | 0.44 | 0.44 | 0.9
59 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN127 | 1S-DL-YP-ETC-DDGN-2251-DGN127 | GALI NO.1B FRIENDS COLONY:PL | TG-DGN127A-3 | 19505853 | 990 | 320 | 242 | 0.94 | 939 | 319 | 1375 | 317 | 1364 | 303 | 1313 | 57 | 2019-06-27 15:30 | 393.6 | -150.7 | 1375 | R | 101 | 101 | 98 | 3 | 0.1 |  | 1 | 98.9 | 173.17 | 176.17 | 177.47 | 174.47 | 247.28 | 243.58 | 243.58 | 249.28 | 257.41 | 253.44 | 258.11 | 256.11 | 33.29 | 37.56 | 23.59 | 31.29 |  |  |  |  | 711.55 | 8.05 | 0.41 | 0.95
60 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN129 | 1S-DL-YP-ETC-DDGN-2251-DGN129 | FRIENDS COLONY GALI NO-5-6 NEAR RLY.LINE:PM | TG-DGN129A-6 | 19506813 | 990 | 320 | 244 | 0.97 | 1099 | 360 | 1558 | 380 | 1644 | 359 | 1560 | 85 | 2019-06-22 11:30 | 238.1 | -123.5 | 1644 | Y | 100 | 103 | 97 | 6 |  |  | 0.5 | 99.5 | 104.3 | 103.3 | 124.3 | 109.3 | 227.29 | 226.29 | 226.29 | 225.29 | 254.06 | 227.1 | 256.23 | 247.36 | 110.28 | 130.28 | 102.11 | 112.58 | 8.59 | 17.55 | 5.29 | 9.59 | 705.32 | 14.28 | 0.44 | 1.11
61 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN131 | 1S-DL-YP-ETC-DDGN-2251-DGN131 | GALI NO.1A FRIENDS COLONY UNDER FLYOVER: PL | TG-DGN131A-1 | 19504318 | 990 | 320 | 249 | 0.87 | 1141 | 384 | 1607 | 370 | 1545 | 387 | 1621 | 70 | 2019-06-19 15:00 | 12.5 | -262.8 | 1621 | B | 101 | 100 | 98 | 3 |  |  | 0.6 | 99.4 | 88 | 87 | 91.3 | 86.3 | 307.29 | 302.59 | 302.59 | 307.59 | 287.14 | 297.14 | 297.14 | 295.14 | 33 | 29.3 | 21 | 26 | 4 | 3 | 4 | 4 | 719.43 | 0.17 | 0.38 | 1.15
62 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN131 | 1S-DL-YP-ETC-DDGN-2251-DGN131 | GALI NO.1A FRIENDS COLONY UNDER FLYOVER: PL | TG-DGN131A-2 | 19504366 | 630 | 200 | 253 | 0.99 | 554 | 174 | 729 | 187 | 788 | 193 | 816 | 76 | 2019-06-12 12:00 | 107.6 | -62.1 | 837 | B | 90 | 101 | 108 | 18 |  |  | 2.6 | 97.4 | 91.3 | 44 | 18.3 | 44.3 | 331.57 | 341.27 | 341.27 | 348.57 | 293.45 | 312.18 | 344.18 | 309.18 | 2.3 | 21.57 | 30.57 | 16.57 |  |  |  |  | 719.42 | 0.18 | 0.5 | 0.88
63 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN178 | 1S-DL-YP-ETC-DDGN-2251-DGN178 | HANSRAJ COMPOUND S/STN | TG-DGN178A-4 | 19505688 | 990 | 320 | 248 | 0.94 | 915 | 294 | 1259 | 316 | 1359 | 304 | 1298 | 87 | 2019-06-07 16:00 | 262.1 | -156.5 | 1359 | Y | 99 | 105 | 96 | 9 |  |  | 19.8 | 80.2 | 61.32 | 68.32 | 113.32 | 70.02 | 360.57 | 344.27 | 344.27 | 350.27 | 276.1 | 250.46 | 263.15 | 266.4 | 7.3 | 42.24 | 14.3 | 19 |  |  |  |  | 706.09 | 13.51 | 0.45 | 0.92
64 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN178 | 1S-DL-YP-ETC-DDGN-2251-DGN178 | HANSRAJ COMPOUND S/STN | TG-DGN178A-1 | 19505895 | 990 | 320 | 242 | 0.89 | 980 | 344 | 1472 | 325 | 1392 | 311 | 1341 | 115 | 2019-06-01 15:00 | 130.9 | -316.8 | 1567 | R | 105 | 98 | 97 | 8 |  | 0.3 | 6 | 93.7 | 4.3 | 24.3 | 53.3 | 18.3 | 345.21 | 350.51 | 350.51 | 354.51 | 294.2 | 307.47 | 287.47 | 298.5 | 60.21 | 22.24 | 25.24 | 33.21 | 1 |  |  |  | 705.32 | 14.28 | 0.47 | 0.99
65 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN198 | 1S-DL-YP-ETC-DDGN-2251-DGN198 | GALI NO-1 METRO PARKING SS-2 | TG-DGN198A-3 | 19504954 | 990 | 320 | 251 | 0.96 | 994 | 334 | 1384 | 327 | 1343 | 333 | 1382 | 40 | 2019-06-27 12:30 | 106 | -195.8 | 1420 | R | 103 | 98 | 100 | 5 |  |  | 2 | 98 | 4.03 | 2.33 | 5.03 | 4.03 | 154.56 | 191.56 | 191.56 | 183.56 | 410.36 | 412.35 | 359.29 | 392.35 | 141.27 | 105.45 | 143.37 | 132.01 | 1.47 |  | 1.14 | 0.14 | 712.49 | 7.11 | 0.56 | 1
66 | 2019-06-19 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN198 | 1S-DL-YP-ETC-DDGN-2251-DGN198 | GALI NO-1 METRO PARKING SS-2 | TG-DGN198A-2 | 19506921 | 990 | 320 | 248 | 0.9 | 1082 | 351 | 1527 | 372 | 1631 | 359 | 1567 | 91 | 2019-06-20 16:00 | 475.5 | -198.1 | 1631 | Y | 98 | 103 | 99 | 5 |  | 0.4 | 18.3 | 81.3 | 67.3 | 72.3 | 74.3 | 72.3 | 68.57 | 62.27 | 62.27 | 63.57 | 84.59 | 71.29 | 77.29 | 78.29 | 50.23 | 60.53 | 53.53 | 55.53 | 3 | 7.3 | 4 | 4 | 274.49 | 13.11 | 0.44 | 1.09
67 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN231 | 1S-DL-YP-ETC-DDGN-2251-DGN231 | GALI NO-1 RAILWAY LINE FRIENDS COLONY | TG-DGN231A-1 | 19504996 | 990 | 320 | 244 | 0.94 | 916 | 294 | 1256 | 306 | 1305 | 316 | 1349 | 80 | 2019-06-20 16:00 | 39 | -192.8 | 1369 | B | 97 | 100 | 103 | 6 |  |  |  | 100 | 56.35 | 53.16 | 56.16 | 55.46 | 339.56 | 333.45 | 333.45 | 332.45 | 262.53 | 244.58 | 215.58 | 239.53 | 52.09 | 79.34 | 116.34 | 83.09 |  |  |  |  | 711.33 | 8.27 | 0.51 | 0.93
68 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN231 | 1S-DL-YP-ETC-DDGN-2251-DGN231 | GALI NO-1 RAILWAY LINE FRIENDS COLONY | TG-DGN231A-2 | 19506054 | 630 | 200 | 243 | 0.9 | 696 | 231 | 989 | 235 | 1006 | 230 | 979 | 23 | 2019-06-07 11:30 | 202.8 | -175.2 | 1039 | Y | 99 | 103 | 98 | 5 |  |  | 3.4 | 96.6 | 12.3 | 14 | 26 | 14.3 | 186.45 | 161.3 | 161.3 | 177 | 378.3 | 383.56 | 377.15 | 380.16 | 120.16 | 132.35 | 119.45 | 125.45 | 7.3 | 13.3 | 5 | 8 | 705.31 | 14.29 | 0.51 | 1.1
69 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN236 | 1S-DL-YP-ETC-DDGN-2251-DGN236 | 1B Friends colony near railway line. | TG-DGN236A-1 | 19505054 | 990 | 320 | 250 | 0.99 | 893 | 307 | 1246 | 301 | 1221 | 285 | 1156 | 81 | 2019-06-24 14:30 | 125.9 | -103.8 | 1289 | R | 102 | 103 | 95 | 8 |  |  | 1.2 | 98.8 | 10.02 | 2.02 | 6.32 | 5.02 | 346.59 | 302.29 | 302.29 | 346.59 | 317.04 | 389.34 | 339.05 | 351.04 | 44.3 | 24.3 | 2.3 | 15.3 |  |  |  |  | 718.35 | 1.25 | 0.53 | 0.9
70 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN255 | 1S-DL-YP-ETC-DDGN-2251-DGN255 | GALI NO. 00 FRIENDS COLONY(THAKUR WALA) | TG-DGN255A-1 | 19506892 | 990 | 320 | 238 | 0.99 | 967 | 329 | 1379 | 317 | 1331 | 321 | 1337 | 46 | 2019-06-24 17:00 | 356.2 | -60.2 | 1379 | R | 103 | 101 | 97 | 6 |  |  | 21.8 | 78.2 | 64.01 | 63.58 | 78.28 | 67.58 | 294.57 | 295.3 | 295.3 | 304 | 309.19 | 316.19 | 295.49 | 306.19 | 34.3 | 27 | 19 | 24.3 |  |  |  |  | 702.47 | 17.13 | 0.46 | 0.98
71 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN002 | 1S-DL-YP-ETC-DDGN-2251-DGN002 | ZAFRABAD CONSTRUCTION OFFICE:ID | TG-DGN002A-2 | 19505261 | 990 | 320 | 241 | 0.97 | 1011 | 311 | 1351 | 291 | 1255 | 410 | 1762 | 467 | 2019-06-03 00:30 | 298.6 | -123.8 | 2048 | B | 128 | 68 | 103 | 60 | 1.4 | 1 | 76 | 21.7 | 55.3 | 444.26 | 421.56 | 318.03 | 381.53 | 140.57 | 140.57 | 213.2 | 255.36 | 120.06 | 170.48 | 159.36 | 17 | 4.3 | 43.3 | 17.3 |  |  | 20.3 | 1.3 | 709.59 | 10.01 | 0.29 | 1.02
72 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN003 | 1S-DL-YP-ETC-DDGN-2251-DGN003 | NAV DURGA MANDIR | TG-DGN003A-1 | 19501845 | 990 | 320 | 246 | 0.98 | 819 | 318 | 1296 | 213 | 868 | 289 | 1181 | 383 | 2019-06-11 23:30 | 138.4 | 11 | 1344 | B | 112 | 82 | 106 | 30 |  |  | 8.1 | 91.9 | 0.3 | 68.46 | 0.3 | 0.3 | 284.24 | 414.23 | 414.23 | 373.47 | 396.4 | 224.51 | 369.46 | 341.43 | 36.26 | 10 | 13.53 | 2 |  |  |  |  | 718 | 2 | 0.52 | 0.83
73 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN003 | 1S-DL-YP-ETC-DDGN-2251-DGN003 | NAV DURGA MANDIR | TG-DGN003A-3 | 19506487 | 630 | 200 | 239 | 0.97 | 511 | 203 | 870 | 138 | 584 | 170 | 721 | 248 | 2019-06-30 23:30 | 208.4 | 32.6 | 1134 | B | 116 | 87 | 97 | 29 | 0.5 | 0.5 | 39.7 | 59.3 | 3.3 | 1.3 |  |  | 206.31 | 407.12 | 407.12 | 301.2 | 411.33 | 293.51 | 384.04 | 400.13 | 78.02 | 0.3 | 2.3 | 1.3 | 3.27 |  | 0.3 |  | 703.03 | 16.57 | 0.56 | 0.81
74 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN004 | 1S-DL-YP-ETC-DDGN-2251-DGN004 | GORAKH PARK NALA (ASHOK WALA) | TG-DGN004A-1 | 19504422 | 630 | 200 | 238 | 0.97 | 550 | 235 | 1064 | 158 | 703 | 157 | 708 | 359 | 2019-06-10 23:30 | 110.4 | 33.6 | 1064 | R | 126 | 86 | 87 | 40 |  |  | 56.5 | 43.5 |  | 7 | 6.3 |  | 70.58 | 337.2 | 337.2 | 215.41 | 541.11 | 374.49 | 378.48 | 496.28 | 95 |  |  | 7 | 12 |  |  |  | 719.09 | 0.51 | 0.55 | 0.87
75 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN009 | 1S-DL-YP-ETC-DDGN-2251-DGN009 | SUBHASH PARK ICE FACTORY | TG-DGN009A-2 | 19506593 | 990 | 200 | 241 | 0.97 | 816 | 200 | 795 | 448 | 1901 | 167 | 682 | 1166 | 2019-06-08 02:30 | 276.8 | 48.8 | 1901 | Y | 92 | 114 | 94 | 22 | 0.1 | 0.2 | 2.2 | 97.5 | 0.3 |  | 0.3 |  | 317.48 | 115.25 | 115.25 | 225.4 | 383.09 | 526.26 | 456.21 | 472.47 |  | 58.36 | 0.3 | 3 |  | 1 |  |  | 701.27 | 18.33 | 0.58 | 0.82
76 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN011 | 1S-DL-YP-ETC-DDGN-2251-DGN011 | H-BLOCK NAVEEN SHAHDARA:PL | TG-DGN011A-3 | 19505334 | 990 | 320 | 246 | 0.97 | 866 | 285 | 1139 | 258 | 1035 | 323 | 1285 | 218 | 2019-06-01 01:00 | 270.7 | 51.2 | 1549 | Y | 103 | 88 | 109 | 21 | 0.5 |  | 20.5 | 79 |  | 4 |  |  | 195.45 | 382.55 | 382.55 | 250.26 | 498.12 | 305.02 | 500.09 | 442.31 | 3.3 | 5 | 37.3 | 4.3 |  | 0.3 |  |  | 697.27 | 22.33 | 0.55 | 0.87
77 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN012 | 1S-DL-YP-ETC-DDGN-2251-DGN012 | MOHAN PARK | TG-DGN012A-1 | 19505755 | 990 | 320 | 239 | 0.97 | 1057 | 294 | 1252 | 387 | 1682 | 377 | 1645 | 412 | 2019-06-09 | 295.7 | 54.7 | 2166 | Y | 104 | 102 | 95 | 9 | 1.2 | 4.5 | 20.2 | 74.1 |  |  |  |  | 44.3 | 85.49 | 85.49 | 77.18 | 545.07 | 486.1 | 468.41 | 504.11 | 82.38 | 108.44 | 74.08 | 113.07 | 28.47 | 20.19 | 19.21 | 6.26 | 701.02 | 18.58 | 0.56 | 1.07
78 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN019 | 1S-DL-YP-ETC-DDGN-2251-DGN019 | KABOOL NAGAR KIOSK | TG-DGN019A-1 | 19506055 | 990 | 320 | 249 | 0.97 | 949 | 268 | 1125 | 256 | 1090 | 425 | 1843 | 736 | 2019-06-02 23:30 | 316.5 | 45.4 | 1843 | B | 101 | 90 | 109 | 19 | 0.7 | 1.5 | 14.3 | 83.5 |  |  |  |  | 28.03 | 105.29 | 105.29 | 37.33 | 661.56 | 576.55 | 565.5 | 629.47 | 10.48 | 16.53 | 80.17 | 33.27 |  | 1.3 | 21.04 |  | 700.47 | 19.13 | 0.61 | 0.96
79 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN020 | 1S-DL-YP-ETC-DDGN-2251-DGN020 | KABOOL NAGAR MOTHER DAIRY:PL | TG-DGN020A-2 | 19506492 | 990 | 320 | 246 | 0.97 | 967 | 359 | 1507 | 296 | 1234 | 311 | 1289 | 250 | 2019-06-12 | 241.6 | 38.4 | 1653 | R | 107 | 91 | 102 | 16 | 0.4 | 0.2 | 24 | 75.5 | 1 | 1 |  | 1 | 118.37 | 200.23 | 200.23 | 123.39 | 451.13 | 466.57 | 554.2 | 501.11 | 106.3 | 35 | 65.3 | 77.3 | 26 |  |  |  | 703.2 | 16.4 | 0.57 | 0.98
80 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN022 | 1S-DL-YP-ETC-DDGN-2251-DGN022 | SHAHI MOHALLA:K | TG-DGN022A-2 | 19501765 | 990 | 320 | 237 | 0.97 | 973 | 367 | 1597 | 307 | 1324 | 299 | 1294 | 289 | 2019-06-30 | 186.2 | 43.4 | 1620 | R | 103 | 104 | 93 | 11 |  |  | 11.1 | 88.9 | 0.17 | 0.17 | 0.17 | 0.17 | 132.54 | 115.33 | 115.33 | 137.3 | 491.22 | 526.13 | 500.26 | 508.46 | 79.09 | 67.39 | 31.3 | 67.39 | 10.3 | 4.3 |  |  | 714.12 | 5.48 | 0.56 | 0.98
81 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN022 | 1S-DL-YP-ETC-DDGN-2251-DGN022 | SHAHI MOHALLA:K | TG-DGN022A-1 | 19504163 | 990 | 320 | 245 | 0.98 | 875 | 321 | 1342 | 343 | 1422 | 212 | 871 | 515 | 2019-06-01 23:30 | 167.1 | 26.5 | 1504 | Y | 107 | 111 | 82 | 29 |  |  | 9.2 | 90.8 | 1.3 | 0.3 | 3 | 0.3 | 102.46 | 64.39 | 64.39 | 121.12 | 529.28 | 539.5 | 463.53 | 553.02 | 78 | 98.45 |  | 38 | 1 | 9 |  |  | 712.44 | 7.16 | 0.62 | 0.88
82 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN023 | 1S-DL-YP-ETC-DDGN-2251-DGN023 | SHIVAJI PARK ARYA SAMAJ MANDIR | TG-DGN023A-1 | 19501792 | 1600 | 500 | 250 | 0.96 | 1612 | 534 | 2155 | 471 | 1903 | 606 | 2441 | 466 | 2019-06-11 00:30 | 378.4 | 70.2 | 2441 | B | 99 | 91 | 110 | 19 |  |  | 0.5 | 99.5 | 0.3 | 0.3 |  | 0.3 | 109.52 | 196.02 | 196.02 | 109.02 | 573.54 | 514.42 | 551.43 | 573.31 | 27.28 | 1 | 91.09 | 28.41 | 0.3 |  | 3.41 | 0.3 | 712.14 | 7.46 | 0.53 | 1.01
83 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN024 | 1S-DL-YP-ETC-DDGN-2251-DGN024 | GORAKH PARK HANUMAN MANDIR PM | TG-DGN024A-1 | 19502520 | 400 | 120 | 243 | 0.97 | 363 | 114 | 472 | 122 | 509 | 127 | 531 | 52 | 2019-06-02 21:00 | 92.2 | 21.8 | 560 | R | 99 | 98 | 104 | 6 |  | 0.2 | 29.2 | 70.5 |  |  |  |  | 138.38 | 165.49 | 165.49 | 134.05 | 519.56 | 480.15 | 507.59 | 527.29 | 60.3 | 73 | 87 | 57.3 |  |  |  |  | 719.04 | 0.56 | 0.63 | 0.91
84 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN025 | 1S-DL-YP-ETC-DDGN-2251-DGN025 | GORAKH PARK KISOK:K | TG-DGN025A-2 | 19505562 | 990 | 320 | 251 | 0.96 | 969 | 358 | 1441 | 325 | 1314 | 285 | 1152 | 251 | 2019-06-12 | 334.7 | 65.9 | 2089 | R | 110 | 99 | 91 | 19 | 0.1 |  | 7.1 | 92.8 |  |  | 0.3 |  | 46.47 | 112.47 | 112.47 | 101.17 | 518.05 | 513.35 | 528.15 | 525.35 | 120.3 | 75.3 | 11 | 79 | 20.3 | 4 |  |  | 705.52 | 14.08 | 0.57 | 0.98
85 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN026 | 1S-DL-YP-ETC-DDGN-2251-DGN026 | BALBIR NAGA NALA GALI NO.14:PL | TG-DGN026A-2 | 19505928 | 990 | 320 | 244 | 0.97 | 764 | 248 | 1058 | 161 | 679 | 356 | 1532 | 740 | 2019-06-12 | 176 | 46.7 | 1532 | B | 102 | 74 | 125 | 51 | 0.3 | 0.7 | 5.2 | 93.8 | 22.3 | 118.3 |  | 8.3 | 384.12 | 473.41 | 473.41 | 412.48 | 305.29 | 125.5 | 439.4 | 296.43 | 5.5 |  | 33.3 |  |  |  | 6.3 |  | 718.01 | 1.59 | 0.51 | 0.77
86 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN028 | 1S-DL-YP-ETC-DDGN-2251-DGN028 | BALBIR NAGAR NALA GALI.4 GORAKH PUR:PL | TG-DGN028A-2 | 19505945 | 630 | 200 | 246 | 0.97 | 605 | 209 | 857 | 160 | 652 | 236 | 968 | 278 | 2019-06-11 00:30 | 224.6 | 30.6 | 1134 | B | 111 | 82 | 107 | 29 | 0.5 | 0.1 | 2.8 | 96.6 |  | 20.29 |  |  | 171.08 | 410.08 | 410.08 | 264.28 | 490.58 | 272.53 | 437.59 | 427.35 | 40.54 | 0.3 | 47.24 | 11.57 | 1 |  | 2.02 |  | 704 | 16 | 0.49 | 0.96
87 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN028 | 1S-DL-YP-ETC-DDGN-2251-DGN028 | BALBIR NAGAR NALA GALI.4 GORAKH PUR:PL | TG-DGN028A-1 | 19506685 | 990 | 320 | 240 | 0.97 | 951 | 247 | 1058 | 356 | 1553 | 349 | 1520 | 480 | 2019-06-29 23:30 | 289.9 | 40 | 1599 | B | 87 | 102 | 111 | 24 | 0.5 | 0.4 | 37.5 | 61.7 | 3.3 | 1 | 1 | 1 | 339.32 | 232.12 | 232.12 | 238.14 | 357.04 | 422.25 | 450.41 | 426.53 | 4.3 | 47.59 | 77.29 | 38.29 |  | 1 | 10 |  | 704.36 | 15.24 | 0.51 | 0.96
88 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN031 | 1S-DL-YP-ETC-DDGN-2251-DGN031 | BALBIR NAGAR SCHOOL:K | TG-DGN031A-2 | 19504165 | 990 | 320 | 249 | 0.97 | 985 | 319 | 1278 | 316 | 1249 | 350 | 1397 | 135 | 2019-06-03 | 186.2 | 50.8 | 1498 | Y | 98 | 101 | 100 | 3 |  | 0.1 | 8.9 | 91 |  | 1.3 |  |  | 193.27 | 189.57 | 189.57 | 188.57 | 455.47 | 428.17 | 437.46 | 444.47 | 69 | 89.3 | 76.3 | 85.3 | 1 | 10 | 6.3 |  | 719.14 | 0.46 | 0.53 | 1
89 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN031 | 1S-DL-YP-ETC-DDGN-2251-DGN031 | BALBIR NAGAR SCHOOL:K | TG-DGN031A-3 | 19506057 | 630 | 200 | 248 | 0.97 | 672 | 199 | 822 | 224 | 943 | 249 | 1064 | 210 | 2019-06-11 22:00 | 217.8 | 38.2 | 1279 | Y | 93 | 100 | 107 | 14 | 0.3 | 1.6 | 39.8 | 58.3 |  |  |  |  | 184 | 149.42 | 149.42 | 135.3 | 485.59 | 477.47 | 487.59 | 492.29 | 35 | 73.3 | 98.3 | 75.3 | 1 | 5 | 18.3 | 2.3 | 705.59 | 14.01 | 0.51 | 1.07
90 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN034 | 1S-DL-YP-ETC-DDGN-2251-DGN034 | LONI ROAD TIKONA PARK:PL | TG-DGN034A-1 | 19506828 | 630 | 200 | 240 | 0.97 | 573 | 236 | 988 | 192 | 785 | 145 | 601 | 336 | 2019-06-03 02:00 | 138 | -119.2 | 1043 | B | 80 | 147 | 73 | 74 | 0.9 | 5.9 | 59.4 | 33.8 | 547.38 | 33.57 | 555.47 | 255.47 | 24.34 | 317.24 | 317.24 | 320.07 | 93.58 | 345.39 | 92.11 | 111.46 | 29.3 | 5.23 | 10.3 | 14.43 | 6.43 |  | 4 |  | 702.23 | 17.37 | 0.31 | 0.91
91 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN053 | 1S-DL-YP-ETC-DDGN-2251-DGN053 | EAST ROHTAS NAGAR:PL | TG-DGN053A-1 | 19501729 | 990 | 320 | 247 | 0.96 | 1084 | 383 | 1567 | 372 | 1535 | 330 | 1350 | 202 | 2019-06-15 | 257.6 | 52.3 | 1571 | R | 106 | 106 | 88 | 18 | 2.1 | 3.7 | 6.8 | 87.3 |  | 1 | 1 |  | 150.57 | 138.28 | 138.28 | 171.57 | 445.46 | 451.12 | 427.44 | 453.13 | 103.27 | 104.47 | 20.3 | 87.47 | 15.33 | 20.16 |  | 2.46 | 715.43 | 4.17 | 0.49 | 1.09

## Loading Condition > 100%
MIS Report of Distribution Transformer - Jun19
Jun19 1211 GT ROAD (Loading Condition > 100% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN069 | 1S-DL-YP-ETC-DDGN-2251-DGN069 | A-BLOCK JHILMIL INDILSHAD AREA:ID | TG-DGN069A-3 | 19506328 | 990 | 320 | 248 | 0.99 | 1088 | 367 | 1571 | 361 | 1542 | 360 | 1532 | 35 | 2019-06-01 11:30 | 246.7 | -577 | 1627 | R | 103 | 93 | 103 | 10 |  |  | 6.6 | 93.4 |  |  |  |  | 8.3 | 37.3 | 37.3 | 11 | 442.03 | 477.4 | 439.41 | 455.11 | 213.52 | 180.15 | 232.13 | 221.13 | 36.29 | 5.29 | 25 | 13.3 | 700.54 | 19.06 | 0.64 | 1.1
2 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN071 | 1S-DL-YP-ETC-DDGN-2251-DGN071 | B-BLK COMPLAINT CENTER JLM IND AREA:ID | TG-DGN071A-3 | 19506610 | 990 | 320 | 248 | 0.96 | 1127 | 380 | 1631 | 378 | 1608 | 369 | 1575 | 48 | 2019-06-22 12:30 | 248 | -220.2 | 1631 | R | 101 | 100 | 99 | 2 |  | 0.1 | 12.2 | 87.7 | 25.3 | 25.3 | 24.3 | 25.3 | 198.3 | 209 | 209 | 204.3 | 237.3 | 229.3 | 227 | 232.3 | 181.3 | 179.3 | 193.3 | 186.3 | 59 | 58.3 | 42.3 | 53 | 702 | 18 | 0.52 | 1.14
3 | 2019-06-03 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN098 | 1S-DL-YP-ETC-DDGN-2251-DGN098 | OLD SEEMAPURI (BUS STOP):ID | TG-DGN098A-1 | 19504962 | 990 | 320 | 244 | 0.97 | 912 | 391 | 1606 | 259 | 1058 | 262 | 1064 | 545 | 2019-06-11 23:30 | 233.3 | 71.4 | 1650 | R | 124 | 91 | 85 | 39 |  |  | 30.8 | 69.2 |  |  |  |  | 0.3 | 14.26 | 14.26 | 5.26 | 326.04 | 650.51 | 628.03 | 585.21 | 256.43 | 3 | 0.3 | 77.3 | 85 |  |  |  | 668.17 | 3.43 | 0.71 | 0.92
4 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN101 | 1S-DL-YP-ETC-DDGN-2251-DGN101 | B-BLK DSIDC SHED JLM IA NO-3:ID | TG-DGN101A-2 | 19501353 | 630 | 200 | 246 | 0.97 | 758 | 247 | 1057 | 260 | 1106 | 251 | 1076 | 42 | 2019-06-29 11:00 | 124.2 | -140.8 | 1106 | Y | 98 | 104 | 98 | 6 |  |  | 2.6 | 97.4 | 20.3 | 13.3 | 24.3 | 18.3 | 281.2 | 242.53 | 242.53 | 271.2 | 272.5 | 278.47 | 267.52 | 268.2 | 123 | 130 | 120.3 | 129 | 18.24 | 50.54 | 27.24 | 28.54 | 716.04 | 3.56 | 0.45 | 1.2
5 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN112 | 1S-DL-YP-ETC-DDGN-2251-DGN112 | DAMODAR PARK,DILSHAD GARDEN:PL | TG-DGN112A-3 | 19505439 | 990 | 320 | 254 | 0.98 | 1327 | 480 | 1954 | 431 | 1738 | 416 | 1696 | 240 | 2019-06-23 11:30 | 458.6 | -190.1 | 1954 | R | 103 | 100 | 97 | 6 | 0.1 | 0.1 | 1.3 | 98.6 | 9.3 | 12 | 17 | 11 | 107 | 125 | 125 | 119 | 290.59 | 279.29 | 280.59 | 286.29 | 91.3 | 89.39 | 107.43 | 97.13 | 196.34 | 189.25 | 165.51 | 181.51 | 695.33 | 24.27 | 0.53 | 1.34
6 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN112 | 1S-DL-YP-ETC-DDGN-2251-DGN112 | DAMODAR PARK,DILSHAD GARDEN:PL | TG-DGN112A-1 | 19506505 | 990 | 320 | 244 | 0.98 | 1313 | 440 | 1846 | 430 | 1805 | 443 | 1861 | 51 | 2019-06-21 16:00 | 219.5 | -178.2 | 1910 | R | 100 | 100 | 100 | 0 | 7.9 | 17.2 | 3.3 | 71.6 | 19.3 | 17 | 19.3 | 18.3 | 185 | 176.3 | 176.3 | 180.3 | 246.24 | 258.54 | 251.54 | 253.54 | 116.57 | 131.26 | 109.29 | 117.57 | 136.34 | 120.35 | 142.32 | 133.34 | 704.25 | 15.35 | 0.48 | 1.33
7 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN114 | 1S-DL-YP-ETC-DDGN-2251-DGN114 | JHULFE BENGAL S/S NO. 2:PL | TG-DGN114A-3 | 19500063 | 990 | 320 | 253 | 0.99 | 1146 | 386 | 1651 | 384 | 1635 | 376 | 1594 | 52 | 2019-06-22 15:30 | 220.1 | -81.7 | 1651 | R | 99 | 103 | 98 | 5 |  |  | 5.1 | 94.9 | 17.57 | 11.57 | 13.57 | 15.27 | 136.3 | 113 | 113 | 130.3 | 335.01 | 360.31 | 347.57 | 347.31 | 168.15 | 172.15 | 163.17 | 170.15 | 32 | 32 | 19.3 | 26 | 712.25 | 7.35 | 0.53 | 1.16
8 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN114 | 1S-DL-YP-ETC-DDGN-2251-DGN114 | JHULFE BENGAL S/S NO. 2:PL | TG-DGN114A-1 | 19506419 | 630 | 200 | 239 | 0.98 | 789 | 250 | 1037 | 279 | 1166 | 261 | 1092 | 112 | 2019-06-28 15:30 | 329.4 | -41.2 | 1188 | R | 95 | 101 | 104 | 9 |  | 0.1 | 17 | 82.9 | 6 | 4.3 | 4.3 | 4.3 | 66.54 | 54.07 | 54.07 | 49.19 | 392.22 | 365.27 | 358.02 | 376.5 | 187.27 | 171.12 | 212.57 | 190.07 | 36.14 | 93.41 | 80.21 | 68.11 | 688.57 | 31.03 | 0.58 | 1.25
9 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN128 | 1S-DL-YP-ETC-DDGN-2251-DGN128 | JULFE BENGAL S/S NO.I | TG-DGN128A-2 | 19505758 | 990 | 320 | 252 | 0.98 | 1181 | 395 | 1698 | 400 | 1708 | 386 | 1661 | 43 | 2019-06-07 12:30 | 488.3 | -130.6 | 1718 | Y | 100 | 105 | 95 | 10 |  | 0.1 | 5.1 | 94.7 | 16.34 | 6.3 | 24.48 | 12.23 | 351 | 308.47 | 308.47 | 352.54 | 144.25 | 182.23 | 149.12 | 150.12 | 150.55 | 142.19 | 144.55 | 148.55 | 25.26 | 48.21 | 10.56 | 23.56 | 688.2 | 31.4 | 0.45 | 1.19
10 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN128 | 1S-DL-YP-ETC-DDGN-2251-DGN128 | JULFE BENGAL S/S NO.I | TG-DGN128A-3 | 19506329 | 630 | 200 | 245 | 0.94 | 906 | 313 | 1340 | 295 | 1255 | 298 | 1291 | 73 | 2019-06-07 17:00 | 343.8 | -123.2 | 1340 | R | 104 | 100 | 96 | 8 |  | 0.2 | 17.5 | 82.2 | 61.3 | 61.3 | 80.3 | 65.3 | 154.52 | 175.02 | 175.02 | 174.02 | 277.35 | 268.55 | 265.14 | 274.55 | 143.15 | 127.45 | 115.15 | 129.15 | 50.48 | 54.48 | 32.18 | 44.18 | 688 | 32 | 0.39 | 1.44
11 | 2019-06-03 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN133 | 1S-DL-YP-ETC-DDGN-2251-DGN133 | B-BLOCK OLD SEEMAPURI :PL | TG-DGN133A-4 | 19504208 | 630 | 200 | 237 | 0.97 | 656 | 240 | 1039 | 172 | 733 | 245 | 1053 | 313 | 2019-06-29 22:30 | 136.6 | 63 | 1084 | B | 108 | 85 | 107 | 23 |  |  | 36.7 | 63.3 | [5 empty] | 10 | 10 |  | 399.01 | 605 | 418.01 | 503.16 | 232.06 | 54.3 | 217.06 | 161.44 | 38.23 |  | 33.23 | 4.3 | 669.3 | 2.3 | 0.69 | 1.04
12 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN134 | 1S-DL-YP-ETC-DDGN-2251-DGN134 | TAHIRPUR SARAI:PM | TG-DGN134A-1 | 19504602 | 400 | 120 | 243 | 0.96 | 445 | 193 | 794 | 122 | 494 | 131 | 532 | 283 | 2019-06-14 02:00 | 121.7 | 33.4 | 809 | R | 118 | 82 | 100 | 36 |  | 0.4 | 23.3 | 76.3 |  |  |  |  | 5.57 | 114.12 | 114.12 | 23.27 | 401.11 | 547.56 | 514.41 | 491.22 | 147.41 | 48.5 | 140.5 | 171.26 | 156.09 |  | 34.3 | 24.43 | 710.58 | 9.02 | 0.61 | 1.11
13 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN228 | 1S-DL-YP-ETC-DDGN-2251-DGN228 | A-BLK DILSHAD COLONY | TG-DGN228A-1 | 19504330 | 990 | 320 | 252 | 0.97 | 1053 | 292 | 1155 | 342 | 1369 | 420 | 1692 | 469 | 2019-06-30 00:30 | 184.7 | 39.7 | 1764 | B | 82 | 103 | 115 | 33 |  | 0.8 | 92 | 7.3 | 2.3 | 0.3 | 0.3 | 0.3 | 288.5 | 137.54 | 137.54 | 157.24 | 415.02 | 462.35 | 466.32 | 457.35 | 13 | 111.23 | 92.53 | 97.53 |  | 7 | 71.3 | 6 | 719.22 | 0.38 | 0.52 | 1.06
14 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN232 | 1S-DL-YP-ETC-DDGN-2251-DGN232 | DSIDC SUBSTATION NO-2 | TG-DGN232A-3 | 19505129 | 990 | 320 | 247 | 0.99 | 1313 | 436 | 1823 | 435 | 1808 | 442 | 1838 | 26 | 2019-06-22 18:00 | 364.8 | -166.4 | 1838 | B | 100 | 98 | 102 | 4 |  |  | 1.1 | 98.9 | 6 | 13.38 | 6.3 | 8.3 | 115.57 | 117.49 | 117.49 | 113.57 | 309.59 | 318.59 | 310.59 | 308.59 | 149.12 | 136.12 | 147.12 | 147.12 | 124.09 | 118.39 | 138.09 | 126.39 | 705.17 | 14.43 | 0.54 | 1.33
15 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN254 | 1S-DL-YP-ETC-DDGN-2251-DGN254 | DAMODAR PARK S/S NO. 2 | TG-DGN254A-2 | 19506876 | 630 | 200 | 249 | 0.92 | 837 | 279 | 1159 | 283 | 1173 | 275 | 1140 | 29 | 2019-06-10 12:30 | 265.6 | -172 | 1214 | Y | 101 | 99 | 100 | 2 |  |  | 0.4 | 99.6 | 21.3 | 18 | 36.3 | 25 | 166 | 177 | 177 | 167.3 | 263.52 | 259.22 | 241.52 | 258.52 | 93.46 | 95.16 | 92.48 | 91.16 | 159.54 | 155.24 | 166.22 | 162.24 | 705.02 | 14.58 | 0.49 | 1.33
16 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN046 | 1S-DL-YP-ETC-DDGN-2251-DGN046 | RAM NAGAR SCHOOL:PL | TG-DGN046A-1 | 19501705 | 990 | 320 | 247 | 0.97 | 1481 | 549 | 2221 | 434 | 1779 | 498 | 2044 | 385 | 2019-06-11 23:30 | 298.1 | 108.2 | 2288 | R | 108 | 90 | 103 | 18 |  | 1.9 | 91.7 | 6.4 | [5 empty] | 10 | 10 | 0.3 | 288.22 | 454.08 | 333.47 | 361.17 | 190.46 | 127.24 | 189.3 | 169.21 | 236.59 | 124.35 | 192.5 | 184.59 | 716.07 | 3.53 | 0.57 | 1.5
17 | 2019-06-20 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN049 | 1S-DL-YP-ETC-DDGN-2251-DGN049 | BHAGWANPUR KHERA NO-3:PL | TG-DGN049A-1 | 19506736 | 990 | 320 | 239 | 0.98 | 1058 | 342 | 1487 | 388 | 1694 | 328 | 1426 | 243 | 2019-06-29 23:30 | 248 | 59.8 | 1906 | R | 104 | 90 | 106 | 16 | 0.2 | 2.9 | 73.7 | 23.1 |  |  |  |  | 3 | 14 | 14 | 1 | 184.49 | 208.49 | 190.49 | 197.19 | 44.3 | 15.3 | 38.3 | 38.3 | 7.3 | 1.3 | 10 | 3 | 239.49 | 24.11 | 0.6 | 1.07
18 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN105 | 1S-DL-YP-ETC-DDGN-2251-DGN105 | SHAMBU NATH COMP.(F.COL):ID | TG-DGN105A-1 | 19505392 | 990 | 320 | 239 | 0.99 | 1187 | 391 | 1784 | 392 | 1792 | 404 | 1842 | 54 | 2019-06-02 14:00 | 483.2 | -76.8 | 1842 | B | 98 | 99 | 103 | 5 |  | 0.1 | 9 | 90.9 | 15.01 | 10.01 | 8.31 | 7.01 | 119.41 | 116.11 | 116.11 | 116.11 | 386.19 | 393.22 | 376.27 | 388.27 | 155.12 | 156.39 | 162.34 | 160.04 | 29.57 | 29.57 | 49.27 | 34.27 | 706.1 | 13.5 | 0.53 | 1.2
19 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN129 | 1S-DL-YP-ETC-DDGN-2251-DGN129 | FRIENDS COLONY GALI NO-5-6 NEAR RLY.LINE:PM | TG-DGN129A-4 | 19505079 | 990 | 320 | 252 | 0.99 | 1131 | 377 | 1525 | 375 | 1505 | 379 | 1526 | 20 | 2019-06-27 15:00 | 94.9 | -161.2 | 1605 | B | 101 | 98 | 101 | 3 |  |  | 0.3 | 99.7 | 20.3 | 45 | 37 | 31.3 | 252.59 | 259.59 | 259.59 | 258.29 | 250.22 | 219.45 | 234.17 | 230.51 | 160.49 | 162.24 | 158.54 | 160.5 | 32.58 | 30.3 | 43.28 | 35.58 | 717.38 | 2.22 | 0.48 | 1.14
20 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN129 | 1S-DL-YP-ETC-DDGN-2251-DGN129 | FRIENDS COLONY GALI NO-5-6 NEAR RLY.LINE:PM | TG-DGN129A-2 | 19506017 | 990 | 320 | 244 | 0.96 | 1201 | 412 | 1798 | 399 | 1728 | 390 | 1703 | 86 | 2019-06-21 12:00 | 280 | -184.6 | 1798 | R | 103 | 99 | 98 | 5 |  | 0.1 | 1.9 | 98.1 | 112.3 | 132.3 | 133.3 | 126.3 | 246.51 | 242.51 | 242.51 | 243.21 | 153.3 | 151.13 | 168.13 | 158.43 | 115.54 | 113.41 | 109.52 | 109.41 | 72.24 | 60.54 | 49.43 | 62.54 | 701.09 | 18.51 | 0.42 | 1.21
21 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN178 | 1S-DL-YP-ETC-DDGN-2251-DGN178 | HANSRAJ COMPOUND S/STN | TG-DGN178A-3 | 19503413 | 630 | 200 | 253 | 0.95 | 701 | 247 | 982 | 239 | 945 | 215 | 852 | 116 | 2019-06-29 12:00 | 47.4 | -163.8 | 982 | R | 103 | 103 | 94 | 9 |  |  | 2.4 | 97.6 | 18.3 | 20.3 | 37.3 | 25 | 342.02 | 350.32 | 350.32 | 354.32 | 166.22 | 144.57 | 190.27 | 156.57 | 154.27 | 163.22 | 121.32 | 161.02 | 33.1 | 35.1 | 3 | 17 | 714.31 | 5.29 | 0.46 | 1.11
22 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN198 | 1S-DL-YP-ETC-DDGN-2251-DGN198 | GALI NO-1 METRO PARKING SS-2 | TG-DGN198A-1 | 19506421 | 990 | 320 | 242 | 0.96 | 1183 | 393 | 1723 | 392 | 1717 | 397 | 1737 | 18 | 2019-06-28 14:30 | 466.6 | -206.1 | 1810 | Y | 98 | 101 | 101 | 3 | 0.3 |  | 2.8 | 96.9 | 22.15 | 19.15 | 21.45 | 20.15 | 178.31 | 153.29 | 153.29 | 169.14 | 297.24 | 310.58 | 284.3 | 293.43 | 145.22 | 139.2 | 137.24 | 143.5 | 53 | 73.3 | 82.26 | 69.3 | 696.32 | 23.28 | 0.52 | 1.19
23 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN001 | 1S-DL-YP-ETC-DDGN-2251-DGN001 | ZAFRABAD AE OFFICE | TG-DGN001A-1 | 19501728 | 990 | 320 | 244 | 0.98 | 925 | 349 | 1428 | 339 | 1403 | 237 | 969 | 447 | 2019-06-30 01:30 | 159 | 31.6 | 1754 | Y | 106 | 121 | 73 | 48 |  | 9.2 | 54.8 | 36.1 |  |  | 2 |  | 75.44 | 44.59 | 44.59 | 85.13 | 544.41 | 488.56 | 355.47 | 599.42 | 93.18 | 141.3 |  | 33.48 | 5 | 43.18 |  |  | 718.43 | 1.17 | 0.6 | 0.93
24 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN003 | 1S-DL-YP-ETC-DDGN-2251-DGN003 | NAV DURGA MANDIR | TG-DGN003A-2 | 19506346 | 990 | 320 | 239 | 0.98 | 1091 | 352 | 1486 | 417 | 1785 | 322 | 1353 | 383 | 2019-06-11 | 302.1 | 69.8 | 2073 | Y | 99 | 108 | 94 | 14 | 0.6 | 0.4 | 12.9 | 86.1 |  |  |  |  | 23.3 | 8.3 | 8.3 | 21.3 | 533.06 | 506.06 | 553.18 | 530.36 | 130.35 | 108.1 | 105.28 | 124.38 | 16.23 | 80.48 | 2 | 26.5 | 703.34 | 16.26 | 0.59 | 1.1
25 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN008 | 1S-DL-YP-ETC-DDGN-2251-DGN008 | SUBHASH PARK CHAND RAM | TG-DGN008A-1 | 19506345 | 990 | 320 | 243 | 0.97 | 1071 | 349 | 1446 | 349 | 1455 | 373 | 1556 | 106 | 2019-06-30 23:30 | 339.2 | 99.8 | 1775 | Y | 98 | 104 | 98 | 6 | 0.1 | 0.7 | 25 | 74.2 | [8 empty] | 509.01 | 445.31 | 513.24 | 492.31 | 197.22 | 203.22 | 152.59 | 191.52 | 6.3 | 64 | 46 | 28.3 | 712.53 | 7.07 | 0.69 | 1.08
26 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN009 | 1S-DL-YP-ETC-DDGN-2251-DGN009 | SUBHASH PARK ICE FACTORY | TG-DGN009A-1 | 19501797 | 990 | 320 | 244 | 0.97 | 961 | 319 | 1305 | 247 | 997 | 395 | 1630 | 548 | 2019-06-12 01:30 | 187.7 | 70.7 | 1662 | B | 104 | 84 | 113 | 29 |  | 1.6 | 42.3 | 56.1 |  |  |  |  | 29.54 | 156.37 | 156.37 | 41.54 | 610.12 | 560.26 | 522.37 | 614.12 | 75.27 |  | 120.3 | 60.57 | 1.3 |  | 42.27 |  | 717.03 | 2.57 | 0.6 | 0.97
27 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN010 | 1S-DL-YP-ETC-DDGN-2251-DGN010 | PANCH SHEEL PARK (JHULE WALA):K | TG-DGN010A-1 | 19501710 | 990 | 320 | 250 | 0.97 | 1071 | 408 | 1650 | 398 | 1585 | 266 | 1060 | 560 | 2019-06-12 | 228.9 | 56.7 | 1812 | Y | 112 | 112 | 76 | 36 | 0.1 | 1 | 13.1 | 85.9 |  |  |  |  | 33 | 55.5 | 55.5 | 83 | 487.57 | 479.41 | 401.15 | 495.27 | 113.3 | 95.26 | 8 | 110.47 | 83.47 | 87.17 |  | 29 | 718.14 | 1.46 | 0.56 | 1.08
28 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN010 | 1S-DL-YP-ETC-DDGN-2251-DGN010 | PANCH SHEEL PARK (JHULE WALA):K | TG-DGN010A-2 | 19505472 | 990 | 320 | 242 | 0.97 | 1195 | 321 | 1387 | 498 | 2201 | 376 | 1611 | 728 | 2019-06-11 01:00 | 317.4 | 62.4 | 2201 | Y | 97 | 104 | 99 | 7 | 0.4 | 1.3 | 30.6 | 67.6 |  |  |  |  | 56.44 | 68.21 | 68.21 | 59.43 | 526.47 | 460.08 | 500.3 | 501.5 | 99.32 | 97.28 | 93.59 | 99.11 | 18.3 | 75.36 | 39.33 | 40.49 | 701.33 | 18.27 | 0.52 | 1.21
29 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN011 | 1S-DL-YP-ETC-DDGN-2251-DGN011 | H-BLOCK NAVEEN SHAHDARA:PL | TG-DGN011A-4 | 19506255 | 630 | 200 | 245 | 0.98 | 666 | 286 | 1238 | 219 | 929 | 161 | 682 | 483 | 2019-06-12 | 162.2 | 18.6 | 1295 | B | 102 | 123 | 75 | 48 | 1.9 | 3.4 | 19.5 | 75.2 | 1.3 | 1.3 | 6.3 | 1.3 | 152.07 | 42.49 | 42.49 | 148.49 | 508.46 | 520.17 | 281.23 | 504.04 | 20.58 | 95.44 | 2.57 | 41.25 | 13.27 | 36.28 | 0.3 | 1 | 696.48 | 23.12 | 0.5 | 1.06
30 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN012 | 1S-DL-YP-ETC-DDGN-2251-DGN012 | MOHAN PARK | TG-DGN012A-2 | 19506546 | 400 | 120 | 245 | 0.96 | 449 | 149 | 623 | 112 | 459 | 189 | 801 | 296 | 2019-06-11 23:30 | 130.1 | 20.3 | 920 | R | 110 | 81 | 109 | 29 | 7 | 20.3 | 59.9 | 12.8 |  |  |  |  | 75.29 | 230.16 | 230.16 | 89.11 | 444.29 | 464.36 | 469.2 | 483.11 | 122.5 | 12.02 | 117.59 | 123.07 | 64.06 |  | 57.32 | 11.25 | 706.54 | 13.06 | 0.53 | 1.12
31 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN014 | 1S-DL-YP-ETC-DDGN-2251-DGN014 | LONI ROAD KHATTEWALA:PL | TG-DGN014A-2 | 19505770 | 630 | 200 | 248 | 0.97 | 622 | 199 | 832 | 133 | 542 | 289 | 1213 | 582 | 2019-06-04 23:30 | 170.8 | 47 | 1280 | B | 110 | 74 | 116 | 42 | 0.8 | 8.6 | 69.9 | 20.7 |  | 2 |  |  | 18.3 | 256.45 | 256.45 | 39 | 549.33 | 460.07 | 488.52 | 577.52 | 141.19 | 0.3 | 142.3 | 102.3 | 10 |  | 75 |  | 719.22 | 0.38 | 0.63 | 0.99
32 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN018 | 1S-DL-YP-ETC-DDGN-2251-DGN018 | R. BLOCK NAVEEN SHAHDARA:PL | TG-DGN018A-2 | 19505754 | 630 | 200 | 246 | 0.98 | 481 | 118 | 487 | 248 | 1048 | 114 | 475 | 568 | 2019-06-12 | 144 | 10.4 | 1062 | Y | 83 | 125 | 92 | 42 | 0.5 | 4.7 | 6 | 88.8 | 14 |  | 2.3 |  | 482.49 | 188.24 | 188.24 | 351.18 | 200.58 | 453.54 | 287.18 | 349.29 | 3 | 12.29 | 1.3 |  |  | 46 |  |  | 700.47 | 19.13 | 0.55 | 0.76
33 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN021 | 1S-DL-YP-ETC-DDGN-2251-DGN021 | KABOOL NAGAR RAIN BASERA:PM | TG-DGN021A-1 | 19506755 | 630 | 200 | 248 | 0.96 | 629 | 102 | 407 | 324 | 1341 | 203 | 833 | 810 | 2019-06-27 01:00 | 196.6 | 42 | 1341 | Y | 63 | 120 | 117 | 57 | 2.3 | 19.9 | 67.7 | 10.1 | 1.31 |  |  |  | 378.34 | 10.14 | 10.14 | 23.24 | 321.28 | 434.45 | 504.42 | 633.51 |  | 225.16 | 159.27 | 44.18 |  | 31.18 | 30.24 |  | 701.33 | 18.27 | 0.61 | 1
34 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN025 | 1S-DL-YP-ETC-DDGN-2251-DGN025 | GORAKH PARK KISOK:K | TG-DGN025A-4 | 19504758 | 630 | 200 | 244 | 0.97 | 683 | 257 | 1080 | 212 | 884 | 213 | 881 | 198 | 2019-06-11 23:30 | 137.5 | 35 | 1136 | R | 116 | 91 | 92 | 25 |  | 1.9 | 45 | 53.1 |  |  |  |  | 65.06 | 236.44 | 236.44 | 137.31 | 455.05 | 401.57 | 432.1 | 461.4 | 135 | 78.3 | 83.3 | 106.3 | 63 | 1 | 4.3 | 12.3 | 718.11 | 1.49 | 0.53 | 1.08
35 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN026 | 1S-DL-YP-ETC-DDGN-2251-DGN026 | BALBIR NAGA NALA GALI NO.14:PL | TG-DGN026A-1 | 19505547 | 990 | 320 | 250 | 0.96 | 1089 | 339 | 1353 | 355 | 1411 | 394 | 1589 | 214 | 2019-06-12 | 301.4 | 83.8 | 2063 | B | 92 | 99 | 109 | 17 | 0.3 | 0.6 | 44.7 | 54.5 |  |  |  |  | 101.3 | 38.3 | 38.3 | 43 | 510.41 | 544.41 | 478.41 | 526.41 | 100.3 | 115.3 | 119 | 118.3 | 7 | 21 | 80 | 31.3 | 719.41 | 0.19 | 0.57 | 1.1
36 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN027 | 1S-DL-YP-ETC-DDGN-2251-DGN027 | BALBIR NAGAR NALA GALI NO. 16:PL | TG-DGN027A-1 | 19505217 | 990 | 320 | 252 | 0.97 | 1179 | 352 | 1509 | 387 | 1639 | 439 | 1929 | 372 | 2019-06-06 22:30 | 469.1 | 72 | 1929 | B | 97 | 91 | 112 | 21 | 0.5 | 14 | 85.1 | 0.3 |  |  |  |  | 87.47 | 131.12 | 131.12 | 66.4 | 470.59 | 460.35 | 470.24 | 481.07 | 107 | 76.29 | 111.3 | 111.59 | 29 | 26.3 | 84.59 | 35 | 694.46 | 25.14 | 0.52 | 1.19
37 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN029 | 1S-DL-YP-ETC-DDGN-2251-DGN029 | BEHAL GALI | TG-DGN029A-1 | 19506361 | 990 | 320 | 244 | 0.98 | 1221 | 332 | 1467 | 501 | 2295 | 387 | 1711 | 736 | 2019-06-06 22:00 | 480.6 | 51.8 | 2304 | B | 99 | 107 | 94 | 13 | 0.6 | 0.1 | 33.8 | 65.6 |  |  |  |  | 33.24 | 24.3 | 24.3 | 26 | 489.16 | 450.4 | 519.06 | 489.4 | 122.26 | 110.26 | 124 | 120.26 | 56 | 115.3 | 25 | 65 | 701.06 | 18.54 | 0.55 | 1.23
38 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN030 | 1S-DL-YP-ETC-DDGN-2251-DGN030 | BALBIR NAGAR EXTN. 60 F ROAD:PM:PL | TG-DGN030A-2 | 19505007 | 630 | 200 | 242 | 0.97 | 840 | 234 | 998 | 302 | 1315 | 304 | 1314 | 316 | 2019-06-29 04:30 | 201.9 | 34 | 1327 | B | 78 | 114 | 108 | 36 | 0 | 0.3 | 14.9 | 84.8 | 0.3 |  |  |  | 339.03 | 39.59 | 39.59 | 120.13 | 349.12 | 505.09 | 461.41 | 486.16 | 20.55 | 122.44 | 98.11 | 98.05 | 1.24 | 43.12 | 52.24 | 6.3 | 711.04 | 8.56 | 0.43 | 1.33
39 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN031 | 1S-DL-YP-ETC-DDGN-2251-DGN031 | BALBIR NAGAR SCHOOL:K | TG-DGN031A-1 | 19506056 | 990 | 320 | 247 | 0.96 | 1328 | 497 | 2051 | 421 | 1750 | 410 | 1696 | 331 | 2019-06-30 | 403.5 | 64.3 | 2542 | B | 108 | 87 | 105 | 21 | 0.8 | 1.9 | 15.6 | 81.7 |  |  |  |  | 5.42 | 84.26 | 84.26 | 18.12 | 447.36 | 479.21 | 451.57 | 480.35 | 119.29 | 106 | 104.5 | 105 | 133 | 36 | 129.3 | 102 | 705.47 | 14.13 | 0.53 | 1.34