## Underload DTs
MIS Report of Distribution Transformer - Jun19
Jun19 1211 GT ROAD (Underload DTs)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN087 | 1S-DL-YP-ETC-DDGN-2251-DGN087 | R-PKT DILSHAD GARDEN:ID | TG-DGN087A-1 | 19501373 | 630 | 200 | 247 | 0.97 | 123 | 49 | 200 | 33 | 133 | 40 | 160 | 58 | 2019-06-12 | 29.9 | 3.7 | 231 | R | 121 | 68 | 111 | 53 |  |  | 5.1 | 94.9 | 613.44 | 718.14 | 714.44 | 718.14 | 104.3 | [15 empty] | 718.14 | 1.46 | 0.54 | 0.19
2 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN126 | 1S-DL-YP-ETC-DDGN-2251-DGN126 | J&K PKT DILSHAD GARDEN-2:ID | TG-DGN126A-2 | 19503582 | 400 | 120 | 248 | 0.97 | 69 | 48 | 195 | 4 | 16 | 18 | 70 | 159 | 2019-06-01 23:30 | 12.7 | 1.7 | 195 | R | 158 | 26 | 116 | 132 | 98.3 | 1 | 0.7 |  | 591.22 | 719.18 | 719.18 | 719.18 | 127.56 | [15 empty] | 719.18 | 0.42 | 0.52 | 0.17
3 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN136 | 1S-DL-YP-ETC-DDGN-2251-DGN136 | HMT COLONY:ID | TG-DGN136A-2 | 19501777 | 630 | 200 | 243 | 0.98 | 122 | 75 | 317 | 24 | 101 | 23 | 91 | 220 | 2019-06-29 23:00 | 20.2 | 3.2 | 317 | R | 174 | 70 | 56 | 118 | 99.9 | 0.1 |  |  | 486.04 | 719.32 | 719.32 | 719.32 | 233.28 | [15 empty] | 719.32 | 0.28 | 0.5 | 0.19
4 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN136 | 1S-DL-YP-ETC-DDGN-2251-DGN136 | HMT COLONY:ID | TG-DGN136A-1 | 19504604 | 630 | 200 | 240 | 0.96 | 52 | 21 | 87 | 10 | 42 | 20 | 82 | 43 | 2019-06-12 | 13.3 | 1.4 | 114 | R | 123 | 61 | 116 | 62 |  |  |  | 100 | 719.32 | 719.32 | 719.32 | 719.32 | [16 empty] | 719.32 | 0.28 | 0.51 | 0.08
5 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN141 | 1S-DL-YP-ETC-DDGN-2251-DGN141 | B-BLK DILSHAD CLY:PM | TG-DGN141A-3 | 19505585 | 630 | 200 | 249 | 0.95 | 146 | 51 | 199 | 53 | 208 | 42 | 163 | 41 | 2019-06-10 06:00 | 111.2 | 4.8 | 214 | Y | 103 | 126 | 72 | 54 |  | 0.6 | 85.4 | 14 | 714.16 | 665.47 | 718.16 | 713.46 | 5.3 | 53.59 | 53.59 | 6 | [12 empty] | 719.46 | 0.14 | 0.45 | 0.23
6 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN152 | 1S-DL-YP-ETC-DDGN-2251-DGN152 | GANPATI ROLLING MILL | TG-DGN152A-1 | 19500034 | 990 | 300 | 248 | 0.94 | 139 | 47 | 185 | 48 | 192 | 44 | 176 | 14 | 2019-06-29 11:00 | 49 | -113.9 | 192 | Y | 98 | 102 | 100 | 4 |  |  | 5.3 | 94.7 | 719.42 | 719.42 | 719.42 | 719.42 | [16 empty] | 719.42 | 0.18 | 0.12 | 0.14
7 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN182 | 1S-DL-YP-ETC-DDGN-2251-DGN182 | DP PM AT SHAMSHAN GHAT OLD SEEMAPURI | TG-DGN182A-1 | 19502668 | 100 | 40 | 247 | 0.95 | 10 | 2 | 9 | 5 | 19 | 3 | 11 | 9 | 2019-06-13 19:30 | 8.8 | 0.5 | 19 | Y | 77 | 119 | 104 | 42 |  |  | 66.4 | 33.6 | 719.28 | 719.28 | 719.28 | 719.28 | [16 empty] | 719.28 | 0.32 | 0.22 | 0.1
8 | 2019-06-03 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN188 | 1S-DL-YP-ETC-DDGN-2251-DGN188 | MEENA BAZAR SSTN NO.-2:PL | TG-DGN188A-1 | 19503540 | 400 | 120 | 248 | 0.91 | 54 | 8 | 33 | 37 | 150 | 9 | 35 | 116 | 2019-06-13 17:30 | 27 | -0.3 | 150 | Y | 51 | 207 | 42 | 165 |  |  | 35.6 | 64.4 | 671.28 | 618.59 | 671.28 | 671.28 |  | 52.29 | 52.29 | [13 empty] | 671.28 | 0.32 | 0.49 | 0.14
9 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN208 | 1S-DL-YP-ETC-DDGN-2251-DGN208 | THANA SEEMAPURI (NEW) | TG-DGN208A-2 | 19504754 | 400 | 120 | 261 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [7 empty] | 0.6 | 99.4 | 719.52 | 719.52 | 719.52 | 719.52 | [16 empty] | 719.52 | 0.08 |  | 0
10 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN208 | 1S-DL-YP-ETC-DDGN-2251-DGN208 | THANA SEEMAPURI (NEW) | TG-DGN208A-1 | 19504759 | 400 | 120 | 241 | 0.98 | 94 | 30 | 127 | 18 | 76 | 46 | 192 | 101 | 2019-06-29 23:00 | 20.4 | 1.7 | 192 | B | 89 | 74 | 137 | 63 |  |  | 0.3 | 99.7 | 703.52 | 718.52 | 312.55 | 676.22 | 16 | 1 | 1 | 43.3 | [12 empty] | 719.52 | 0.08 | 0.66 | 0.24
11 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN221 | 1S-DL-YP-ETC-DDGN-2251-DGN221 | R-BLK DDA Flat laxmi nryn mandir S/Stn-2 | TG-DGN221A-1 | 19504755 | 990 | 320 | 248 | 0.97 | 246 | 75 | 307 | 36 | 145 | 135 | 552 | 356 | 2019-06-29 23:30 | 57.4 | 7.4 | 552 | B | 105 | 43 | 152 | 109 |  |  | 21.8 | 78.2 | 621.47 | 719.47 | 374.48 | 651.17 | 98 |  |  | 68.3 |  |  | 1 | [9 empty] | 719.47 | 0.13 | 0.54 | 0.25
12 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN222 | 1S-DL-YP-ETC-DDGN-2251-DGN222 | P.S. G.T.B Enclave Package S/Stn | TG-DGN222A-1 | 19504795 | 990 | 320 | 252 | 0.98 | 68 | 11 | 44 | 17 | 69 | 39 | 156 | 102 | 2019-06-04 15:00 | 15.5 | 0.7 | 158 | B | 61 | 90 | 148 | 87 |  |  | 1.3 | 98.7 | 719.42 | 719.42 | 719.42 | 719.42 | [16 empty] | 719.42 | 0.18 | 0.51 | 0.07
13 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN057 | 1S-DL-YP-ETC-DDGN-2251-DGN057 | DDA FLAT M.S PARK THANEWALA:ID | TG-DGN057A-1 | 19506365 | 990 | 320 | 240 | 0.97 | 204 | 65 | 270 | 30 | 126 | 108 | 451 | 282 | 2019-06-12 | 44.2 | 10.2 | 451 | B | 99 | 68 | 133 | 65 | 0.1 | 0.2 | 51.2 | 48.5 | 698.09 | 701.23 | 519.03 | 699.23 | 3.14 |  |  | 2 | [12 empty] | 701.23 | 18.37 | 0.61 | 0.21
14 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN186 | 1S-DL-YP-ETC-DDGN-2251-DGN186 | METRO STATION, SHAHDARA:PL | TG-DGN186A-2 | 19502940 | 630 | 200 | 242 | 0.5 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 2019-06-30 19:00 |  |  | 2 | Y | 0 | 300 | 0 | 300 | 0.1 | 0.1 | 26.1 | 73.8 | 718.06 | 718.06 | 718.06 | 718.06 | [16 empty] | 718.06 | 1.54 | 0.31 | 0
15 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN234 | 1S-DL-YP-ETC-DDGN-2251-DGN234 | AHINSA VATIKA HOUSING COMPLEX S/STN.PKG | TG-DGN234A-1 | 19505565 | 990 | 320 | 245 | 0.91 | 25 | 12 | 51 | 3 | 13 | 9 | 37 | 33 | 2019-06-11 01:30 | 23 | -3.5 | 60 | R | 131 | 30 | 139 | 109 | 0.1 | 0.1 | 3.5 | 96.4 | 716.29 | 716.29 | 716.29 | 716.29 | [16 empty] | 716.29 | 3.31 | 0.42 | 0.02
16 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN015 | 1S-DL-YP-ETC-DDGN-2251-DGN015 | SHAHDARA THANA:PM | TG-DGN015A-1 | 19506018 | 400 | 120 | 245 | 0.93 | 175 | 79 | 308 | 78 | 314 | 18 | 72 | 239 | 2019-06-01 11:00 | 28 | 0.5 | 314 | Y | 103 | 73 | 124 | 51 | 0.1 | 0.1 | 4.5 | 95.3 | 698.32 | 701.02 | 700.32 | 701.32 | 3 | 0.3 | 0.3 |  | 0.3 | 0.3 |  | 0.3 | [8 empty] | 702.02 | 17.58 | 0.17 | 0.44
17 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | ZAFFRABAD | 1211 | DGN202 | 1S-DL-YP-ETC-DDGN-2251-DGN202 | Police sation Welcome | TG-DGN202A-1 | 19504908 | 630 | 200 | 236 | 0.99 | 78 | 35 | 147 | 20 | 84 | 23 | 98 | 58 | 2019-06-15 23:00 | 17 | -1.4 | 155 | R | 120 | 103 | 77 | 43 |  |  | 14.7 | 85.3 | 670.35 | 670.35 | 670.35 | 670.35 | [16 empty] | 670.35 | 1.25 | 0.52 | 0.12