## Complete Report
MIS Report of Distribution Transformer - Jun19
Jun19 1211 GT ROAD (Complete Report)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN076 | 1S-DL-YP-ETC-DDGN-2251-DGN076 | SSR MILL:ID | TG-DGN076A-2 | 19505064 | 630 | 200 | 249 | 0.63 | 498 | 162 | 652 | 172 | 687 | 164 | 657 | 33 | 2019-06-30 12:00 | -0.9 | -215.7 | 687 | Y | 96 | 102 | 102 | 6 |  |  | 0.3 | 99.7 | 324.2 | 305.5 | 307.5 | 313.2 | 128.23 | 137.23 | 137.23 | 132.23 | 266.57 | 275.57 | 275.57 | 273.57 |  | 0.3 | [6 empty] | 719.4 | 0.2 | 0.41 | 0.79
2 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN077 | 1S-DL-YP-ETC-DDGN-2251-DGN077 | SANSAR:K | TG-DGN077A-1 | 19500679 | 990 | 320 | 241 | 0.76 | 803 | 269 | 1113 | 273 | 1126 | 262 | 1081 | 40 | 2019-06-28 11:00 | 5.2 | -244.4 | 1139 | Y | 100 | 103 | 96 | 7 |  |  | 0.4 | 99.6 | 77.3 | 68.3 | 83 | 76 | 75 | 83 | 83 | 78 | 119.3 | 119 | 117 | 117.3 | 0.3 | 2 |  | 1 |  |  |  |  | 719.33 | 0.27 | 0.49 | 0.81
3 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | E&F DILSHAD GARDEN | 1211 | DGN122 | 1S-DL-YP-ETC-DDGN-2251-DGN122 | B-BLK DSIDC SHED JLM IA NO-1:ID | TG-DGN122A-2 | 19501374 | 990 | 320 | 243 | 0.84 | 495 | 165 | 683 | 160 | 661 | 169 | 692 | 27 | 2019-06-29 12:30 | 54.5 | -160.4 | 725 | B | 97 | 100 | 102 | 5 |  |  | 18.3 | 81.7 | 393.11 | 394.11 | 375.11 | 382.41 | 268.53 | 260.28 | 260.28 | 262.58 | 57.24 | 64.49 | 99.49 | 73.49 | [8 empty] | 719.28 | 0.32 | 0.47 | 0.5
4 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN110 | 1S-DL-YP-ETC-DDGN-2251-DGN110 | VERMA CASTLE:PL | TG-DGN110A-4 | 19506339 | 630 | 200 | 237.9138 | 0.80146 | 700.3905 | 232.099 | 966.9584 | 243.274 | 1008.6405 | 225.0174 | 926.6077 | 71.0456 | 2019-06-03 10:30 | [15 empty] | 242.5 |  |  |  | 244 |  |  |  | 214.5 |  |  |  | 6.5 |  |  |  | 1 | 708.5 |  | 0.27238 | 1.1117
5 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN127 | 1S-DL-YP-ETC-DDGN-2251-DGN127 | GALI NO.1B FRIENDS COLONY:PL | TG-DGN127A-4 | 19506340 | 630 | 200 | 244 | 0.5 | 448 | 149 | 632 | 144 | 607 | 154 | 646 | 35 | 2019-06-21 15:00 | 259.4 | -97.2 | 646 | B | 100 | 99 | 101 | 2 |  | 0.1 | 1.1 | 98.9 | 313.45 | 314.15 | 316.15 | 314.15 | 276.21 | 296.2 | 296.2 | 283.21 | 120.25 | 99.56 | 122.54 | 112.55 | [8 empty] | 710.31 | 9.29 | 0.34 | 0.71
6 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN129 | 1S-DL-YP-ETC-DDGN-2251-DGN129 | FRIENDS COLONY GALI NO-5-6 NEAR RLY.LINE:PM | TG-DGN129A-1 | 19504943 | 990 | 320 | 253 | 0.74 | 708 | 234 | 981 | 240 | 1006 | 233 | 980 | 26 | 2019-06-13 11:00 | 15.5 | -237 | 1006 | Y | 101 | 101 | 97 | 4 |  |  |  | 100 | 368 | 374.3 | 384.32 | 378.29 | 116.09 | 102.52 | 102.52 | 106.15 | 233.23 | 240.1 | 225.01 | 232.48 | [8 empty] | 717.32 | 2.28 | 0.4 | 0.71
7 | 2019-06-01 | 2019-06-30 23:30 | GT ROAD | GT ROAD SHAHDRA | 1211 | DGN186 | 1S-DL-YP-ETC-DDGN-2251-DGN186 | METRO STATION, SHAHDARA:PL | TG-DGN186A-2 | 19502940 | 630 | 200 | 242 | 0.5 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 2019-06-30 19:00 |  |  | 2 | Y | 0 | 300 | 0 | 300 | 0.1 | 0.1 | 26.1 | 73.8 | 718.06 | 718.06 | 718.06 | 718.06 | [16 empty] | 718.06 | 1.54 | 0.31 | 0