## Complete Report
MIS Report of Distribution Transformer - Jun19
Jun19 1220 KRISHNA NAGAR (Complete Report)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG001 | 1S-DL-YP-ETC-DKRN-2104-JAG001 | ARAM PARK:PL | TG-JAG001A-1 | 19500853 | 990 | 320 | 239 | 0.97 | 1406 | 463 | 1979 | 504 | 2156 | 439 | 1857 | 260 | 2019-06-11 23:00 | 281.9 | 108.2 | 2297 | Y | 100 | 108 | 93 | 15 |  |  | 28.3 | 71.7 |  |  |  |  | 1.3 |  |  | 1.3 | 433.42 | 356.26 | 463.43 | 426.19 | 125.15 | 172.31 | 103.59 | 127.08 | 151.22 | 182.52 | 131.37 | 156.52 | 711.49 | 8.11 | 0.57 | 1.42
2 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG002 | 1S-DL-YP-ETC-DKRN-2104-JAG002 | BEDI MKT:ID | TG-JAG002A-1 | 19506105 | 990 | 320 | 238 | 0.97 | 1022 | 303 | 1265 | 415 | 1772 | 304 | 1279 | 501 | 2019-06-03 02:00 | 279 | 11.2 | 1888 | R | 102 | 103 | 95 | 8 | 0.5 | 4.7 | 28.2 | 66.6 | 0.23 | 0.23 | 0.23 | 0.23 | 40.54 | 90.49 | 90.49 | 76.54 | 595.08 | 517.42 | 541.14 | 550.13 | 55.37 | 45.57 | 21.28 | 63.31 | 0.16 | 37.27 | 6.3 | 1.17 | 692.18 | 27.42 | 0.55 | 1.03
3 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG002 | 1S-DL-YP-ETC-DKRN-2104-JAG002 | BEDI MKT:ID | TG-JAG002A-2 | 19506104 | 1600 | 500 | 243 | 0.97 | 2307 | 457 | 1978 | 874 | 4198 | 976 | 4330 | 2289 | 2019-06-08 23:00 | 710.5 | 44.5 | 4330 | B | 105 | 92 | 103 | 13 | 0.8 | 0.3 | 56.4 | 42.5 | 0.57 | 0.57 | 0.05 | 0.05 | 111.24 | 220.13 | 220.13 | 146.46 | 470.54 | 423 | 464.44 | 457.47 | 101.35 | 49.47 | 88.01 | 86.1 | 11.01 | 1.54 | 15.35 | 5.03 | 695.51 | 24.09 | 0.38 | 1.44
4 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG002 | 1S-DL-YP-ETC-DKRN-2104-JAG002 | BEDI MKT:ID | TG-JAG002A-3 | 19506656 | 990 | 320 | 244 | 0.97 | 1057 | 398 | 1668 | 337 | 1408 | 321 | 1339 | 300 | 2019-06-11 00:30 | 267.5 | 66.6 | 1966 | R | 114 | 97 | 90 | 24 | 0.4 | 0.1 | 16.5 | 83 |  |  |  |  | 69.44 | 169.09 | 169.09 | 143.09 | 453.07 | 446.06 | 435.15 | 453.39 | 113.3 | 68.22 | 32.23 | 87.06 | 51.51 | 4.35 |  | 4.18 | 688.12 | 31.48 | 0.52 | 1.07
5 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG003 | 1S-DL-YP-ETC-DKRN-2104-JAG003 | BALDEV PARK:K | TG-JAG003A-1 | 19505023 | 990 | 320 | 246 | 0.97 | 664 | 192 | 763 | 233 | 926 | 239 | 951 | 177 | 2019-06-30 | 122.9 | 45.6 | 1011 | Y | 90 | 103 | 107 | 17 |  |  | 0.6 | 99.4 | 18 | 10 | 1 | 7 | 501.27 | 421.27 | 421.27 | 454.57 | 198.27 | 286.27 | 329.27 | 255.57 | [8 empty] | 717.54 | 2.06 | 0.57 | 0.67
6 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG003 | 1S-DL-YP-ETC-DKRN-2104-JAG003 | BALDEV PARK:K | TG-JAG003A-2 | 19500831 | 990 | 320 | 231.856 | 0.98153 | 907.8625 | 287.0211 | 1240.4751 | 313.2638 | 1351.2067 | 307.5776 | 1322.7436 | 99.5986 | 2019-06-12 | [15 empty] | 0 |  |  |  | 177.5 |  |  |  | 500 |  |  |  | 41.5 |  |  |  | 0 | 719 |  | 0.56923 | 0.91703
7 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG004 | 1S-DL-YP-ETC-DKRN-2104-JAG004 | BALDEV PARK(PARK WALA):PL | TG-JAG004A-1 | 19504993 | 990 | 320 | 236 | 0.97 | 760 | 182 | 801 | 239 | 1078 | 340 | 1537 | 643 | 2019-06-30 23:30 | 128.8 | 42.7 | 1641 | B | 78 | 90 | 132 | 54 | 0.1 | 43.5 | 56.3 |  | 28.02 | 16 |  | 4.3 | 514.43 | 451.45 | 451.45 | 382.45 | 176 | 251 | 463.2 | 331.3 |  |  | 98.3 |  |  |  | 9 |  | 718.45 | 1.15 | 0.55 | 0.77
8 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG004 | 1S-DL-YP-ETC-DKRN-2104-JAG004 | BALDEV PARK(PARK WALA):PL | TG-JAG004A-2 | 19505834 | 630 | 200 | 244 | 0.97 | 640 | 241 | 1080 | 288 | 1404 | 111 | 502 | 792 | 2019-06-11 01:00 | 218.8 | 27.6 | 1404 | Y | 97 | 125 | 78 | 47 | 0.4 |  | 53.2 | 46.4 | 22.15 |  | 80.15 | 6 | 411.03 | 213.18 | 213.18 | 424.48 | 275 | 472.3 | 168 | 278 | 0.3 | 23 |  |  | 0.3 | 0.3 |  | 0.3 | 709.18 | 10.42 | 0.4 | 1.02
9 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG005 | 1S-DL-YP-ETC-DKRN-2104-JAG005 | BRIJPURI:PL | TG-JAG005A-1 | 19500854 | 990 | 320 | 230.8454 | 0.98313 | 1081.0185 | 413.5829 | 1807.2226 | 350.7725 | 1525.098 | 316.6631 | 1378.1742 | 377.6661 | 2019-06-30 02:00 | [15 empty] | 0 |  |  |  | 7 |  |  |  | 551.5 |  |  |  | 148 |  |  |  | 12.5 | 719 |  | 0.62586 | 1.0919
10 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG006 | 1S-DL-YP-ETC-DKRN-2104-JAG006 | CHANDER NAGAR:ID | TG-JAG006A-1 | 19500790 | 1600 | 500 | 242 | 0.97 | 895 | 265 | 1112 | 350 | 1488 | 280 | 1199 | 341 | 2019-06-01 00:30 | 170.2 | 65.6 | 1555 | Y | 85 | 111 | 104 | 26 |  | 0.8 | 92.2 | 7.1 | 31.49 | 1 | 3 | 4.22 | 614.05 | 428.17 | 428.17 | 528.51 | 72.45 | 289.22 | 214.49 | 185.26 | [8 empty] | 718.39 | 1.21 | 0.63 | 0.56
11 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG006 | 1S-DL-YP-ETC-DKRN-2104-JAG006 | CHANDER NAGAR:ID | TG-JAG006A-2 | 19500787 | 990 | 320 | 236 | 0.97 | 983 | 296 | 1284 | 362 | 1590 | 325 | 1416 | 266 | 2019-06-11 18:30 | 228.2 | 69.9 | 1643 | Y | 96 | 107 | 96 | 11 |  |  | 13.2 | 86.8 |  |  |  |  | 99.3 | 55 | 55 | 83.3 | 547.1 | 530.1 | 495.35 | 532.1 | 71.1 | 114.4 | 91.45 | 102.1 |  | 18 | 1 |  | 717.5 | 2.1 | 0.58 | 0.99
12 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG007 | 1S-DL-YP-ETC-DKRN-2104-JAG007 | CHANDU PARK:K | TG-JAG007A-1 | 19500786 | 990 | 320 | 235.831 | 0.97477 | 735.4908 | 283.8452 | 1213.4802 | 174.7981 | 743.6317 | 276.8476 | 1187.0661 | 457.2141 | 2019-06-11 23:30 | [15 empty] | 0 |  |  |  | 347 |  |  |  | 373 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.58118 | 0.74292
13 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG007 | 1S-DL-YP-ETC-DKRN-2104-JAG007 | CHANDU PARK:K | TG-JAG007A-2 | 19505720 | 630 | 200 | 243 | 0.97 | 415 | 122 | 510 | 183 | 774 | 110 | 459 | 293 | 2019-06-02 01:30 | 154.2 | 21 | 774 | Y | 78 | 121 | 101 | 43 | 0.1 |  | 0.3 | 99.7 | 140 | 3 | 15.3 | 16.3 | 511.58 | 356 | 356 | 502.28 | 67.44 | 360.12 | 213.44 | 200.44 |  | 0.3 | [6 empty] | 719.42 | 0.18 | 0.53 | 0.66
14 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG008 | 1S-DL-YP-ETC-DKRN-2104-JAG008 | GAGAN VIHAR:ID | TG-JAG008A-1 | 19506658 | 990 | 320 | 238 | 0.98 | 699 | 225 | 962 | 234 | 1000 | 240 | 1024 | 55 | 2019-06-03 13:00 | 168.3 | 39.7 | 1058 | B | 96 | 101 | 103 | 7 |  | 0.1 | 0.8 | 99.1 |  |  |  |  | 226.3 | 165.3 | 165.3 | 165.3 | 483.28 | 544.28 | 579.28 | 544.28 | [8 empty] | 709.58 | 10.02 | 0.66 | 0.71
15 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG008 | 1S-DL-YP-ETC-DKRN-2104-JAG008 | GAGAN VIHAR:ID | TG-JAG008A-2 | 19506108 | 990 | 320 | 244 | 0.98 | 889 | 237 | 985 | 391 | 1659 | 262 | 1099 | 624 | 2019-06-12 00:30 | 192 | 48.6 | 1738 | Y | 91 | 110 | 99 | 19 |  | 0.6 | 2.2 | 97.2 |  |  |  |  | 250.13 | 104.4 | 104.4 | 164.3 | 458.51 | 515.24 | 541.04 | 528.34 |  | 78 | 6.3 | 16 |  | 11 | 0.3 |  | 709.04 | 10.56 | 0.57 | 0.9
16 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG008 | 1S-DL-YP-ETC-DKRN-2104-JAG008 | GAGAN VIHAR:ID | TG-JAG008A-3 | 19505113 | 630 | 200 | 244 | 0.97 | 511 | 156 | 672 | 125 | 531 | 230 | 1001 | 417 | 2019-06-03 | 129 | 23.2 | 1001 | B | 102 | 89 | 109 | 20 |  | 0.2 | 0.7 | 99.1 | 6 | 8 | 6 | 4 | 300.17 | 423.44 | 423.44 | 321.16 | 400.57 | 277.3 | 440.27 | 383.28 | 2 |  | 18.3 | 0.3 |  |  | 2.3 |  | 709.14 | 10.46 | 0.54 | 0.81
17 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG009 | 1S-DL-YP-ETC-DKRN-2104-JAG009 | GAGAN VIHAR EXT:ID | TG-JAG009A-1 | 19506647 | 990 | 200 | 244 | 0.97 | 706 | 232 | 1009 | 216 | 931 | 258 | 1112 | 158 | 2019-06-26 23:00 | 130.6 | 15.2 | 1112 | B | 87 | 111 | 101 | 24 |  |  | 0.5 | 99.5 | 183.13 | 2.3 | 37.19 | 27.49 | 389.44 | 466.26 | 466.26 | 517.14 | 132.12 | 236.13 | 171.36 | 160.06 | [8 empty] | 705.09 | 14.51 | 0.47 | 0.71
18 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG009 | 1S-DL-YP-ETC-DKRN-2104-JAG009 | GAGAN VIHAR EXT:ID | TG-JAG009A-2 | 19506155 | 990 | 200 | 248 | 0.97 | 1397 | 464 | 1946 | 416 | 1740 | 517 | 2199 | 398 | 2019-06-11 01:30 | 278.2 | 55.2 | 2199 | B | 104 | 96 | 100 | 8 |  | 0.1 | 6.6 | 93.3 |  |  |  |  | 51.13 | 99.01 | 99.01 | 77.43 | 334.14 | 316.26 | 318.44 | 325.44 | 70.15 | 62.34 | 65.57 | 62.07 | 97.08 | 74.49 | 88.26 | 87.16 | 704.09 | 15.51 | 0.48 | 1.41
19 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG010 | 1S-DL-YP-ETC-DKRN-2104-JAG010 | GANDHI PARK:PL | TG-JAG010A-1 | 19500851 | 990 | 320 | 236 | 0.97 | 845 | 222 | 966 | 227 | 963 | 395 | 1694 | 729 | 2019-06-11 00:30 | 162.7 | 56.7 | 1820 | B | 83 | 80 | 137 | 57 | 0.3 | 20.3 | 78.4 | 1 | 3 | 12 |  |  | 424.2 | 424.27 | 424.27 | 262.27 | 289.54 | 280.47 | 490.14 | 443.58 |  |  | 104.3 | 10.49 |  |  | 67.3 |  | 717.14 | 2.46 | 0.56 | 0.85
20 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG010 | 1S-DL-YP-ETC-DKRN-2104-JAG010 | GANDHI PARK:PL | TG-JAG010A-2 | 19500750 | 990 | 320 | 238 | 0.98 | 869 | 269 | 1143 | 278 | 1190 | 322 | 1366 | 203 | 2019-06-11 | 139.8 | 39.7 | 1381 | B | 94 | 93 | 113 | 20 |  | 1.2 | 74.5 | 24.4 | 3 | 5.3 |  |  | 346.28 | 338.28 | 338.28 | 291.58 | 364.35 | 370.55 | 471.35 | 416.55 | 3.5 | 3 | 72.5 | 9 |  |  |  |  | 717.53 | 2.07 | 0.54 | 0.88
21 | 2019-06-02 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG011 | 1S-DL-YP-ETC-DKRN-2104-JAG011 | GANESH PARK:PL | TG-JAG011A-1 | 19500776 | 990 | 320 | 243.7427 | 0.97273 | 1006.82 | 267.321 | 1068.2586 | 338.3303 | 1370.924 | 401.1686 | 1630.1041 | 487.058 | 2019-06-30 | [15 empty] | 0 |  |  |  | 26 |  |  |  | 558.5 |  |  |  | 108.5 |  |  |  | 2 | 695 |  | 0.6016 | 1.017
22 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG011 | 1S-DL-YP-ETC-DKRN-2104-JAG011 | GANESH PARK:PL | TG-JAG011A-2 | 19505000 | 990 | 200 | 238 | 0.97 | 926 | 303 | 1251 | 343 | 1409 | 280 | 1142 | 232 | 2019-06-30 | 182.2 | 65.3 | 1503 | R | 103 | 107 | 90 | 17 |  |  | 31.4 | 68.6 |  |  |  |  | 19.05 | 17.35 | 17.35 | 24.05 | 627.53 | 597.53 | 632.29 | 633.53 | 69.47 | 99.17 | 10.3 | 58.47 |  | 2 |  |  | 716.45 | 3.15 | 0.62 | 0.94
23 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG012 | 1S-DL-YP-ETC-DKRN-2104-JAG012 | GOLDEN PARK:ID | TG-JAG012A-1 | 19502152 | 990 | 320 | 233 | 0.97 | 564 | 201 | 882 | 174 | 763 | 189 | 825 | 103 | 2019-06-03 | 136.9 | 47.8 | 1025 | R | 108 | 83 | 110 | 27 |  | 0.1 | 11.8 | 88.1 |  | 15 |  |  | 353.2 | 628.3 | 628.3 | 439.3 | 366.3 | 76.2 | 460.5 | 280.2 | [8 empty] | 719.5 | 0.1 | 0.68 | 0.57
24 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG012 | 1S-DL-YP-ETC-DKRN-2104-JAG012 | GOLDEN PARK:ID | TG-JAG012A-2 | 19500817 | 990 | 320 | 237 | 0.99 | 827 | 260 | 1135 | 262 | 1134 | 305 | 1312 | 178 | 2019-06-03 | 63.3 | -100.1 | 1340 | B | 95 | 95 | 111 | 16 |  | 0.3 | 72.9 | 26.7 |  |  |  |  | 137.53 | 133.53 | 133.53 | 81.53 | 581.5 | 585.5 | 619.47 | 633.2 |  |  | 63 | 4.3 |  |  |  |  | 719.43 | 0.17 | 0.63 | 0.84
25 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG013 | 1S-DL-YP-ETC-DKRN-2104-JAG013 | GOPAL PARK:PL | TG-JAG013A-1 | 19506543 | 990 | 320 | 236.4244 | 0.97416 | 1408.0413 | 492.6622 | 2114.4301 | 459.5723 | 1942.9766 | 455.8068 | 1954.7424 | 165.8838 | 2019-06-02 02:00 | [15 empty] | 0 |  |  |  | 58.5 |  |  |  | 469.5 |  |  |  | 105 |  |  |  | 83.5 | 716.5 |  | 0.46469 | 1.4223
26 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG013 | 1S-DL-YP-ETC-DKRN-2104-JAG013 | GOPAL PARK:PL | TG-JAG013A-2 | 19506648 | 990 | 320 | 237.6162 | 0.97824 | 998.2955 | 271.1006 | 1164.972 | 466.6589 | 2100.553 | 260.536 | 1140.8504 | 947.8721 | 2019-06-02 23:30 | [15 empty] | 0 |  |  |  | 220.5 |  |  |  | 436.5 |  |  |  | 60.5 |  |  |  | 0.5 | 718 |  | 0.51034 | 1.0084
27 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG014 | 1S-DL-YP-ETC-DKRN-2104-JAG014 | GOVIND PARK | TG-JAG014A-1 | 19500778 | 990 | 320 | 238 | 0.97 | 322 | 143 | 593 | 96 | 397 | 84 | 345 | 227 | 2019-06-29 23:30 | 55.2 | 17.7 | 630 | R | 128 | 85 | 87 | 43 |  |  | 3.1 | 96.9 | 304 | 622.28 | 579.28 | 475.28 | 388.58 | 97.3 | 97.3 | 244.3 | 27 | [11 empty] | 719.58 | 0.02 | 0.57 | 0.33
28 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG014 | 1S-DL-YP-ETC-DKRN-2104-JAG014 | GOVIND PARK | TG-JAG014A-2 | 19500780 | 990 | 320 | 238 | 0.97 | 655 | 175 | 724 | 214 | 886 | 265 | 1100 | 327 | 2019-06-30 | 128.8 | 47.1 | 1100 | B | 85 | 99 | 116 | 31 |  |  |  | 100 | 32.3 | 6.3 |  | 8 | 528.58 | 469.28 | 469.28 | 460.58 | 158.3 | 244 | 374.28 | 251 |  |  | 0.3 | [5 empty] | 719.58 | 0.02 | 0.57 | 0.66
29 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG015 | 1S-DL-YP-ETC-DKRN-2104-JAG015 | GOVIND PURA(NEW):ID | TG-JAG015A-1 | 19506655 | 990 | 320 | 239 | 0.97 | 1136 | 348 | 1545 | 393 | 1756 | 396 | 1760 | 213 | 2019-06-01 | 173.1 | 35.2 | 1760 | B | 98 | 105 | 97 | 8 | 0.1 | 0.1 | 28.4 | 71.4 | 4.3 | 1 | 5.3 | 1 | 399.37 | 303.34 | 303.34 | 375.37 | 289.22 | 388.55 | 304.22 | 316.22 |  |  |  | 0.3 | 0.18 | 0.18 | 0.48 | 0.18 | 693.47 | 26.13 | 0.37 | 1.15
30 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG016 | 1S-DL-YP-ETC-DKRN-2104-JAG016 | GOVIND PURA(OLD):ID | TG-JAG016A-1 | 19503083 | 990 | 320 | 232 | 0.97 | 758 | 209 | 928 | 190 | 840 | 359 | 1594 | 714 | 2019-06-03 00:30 | 140.6 | 39 | 1594 | B | 95 | 86 | 119 | 33 |  |  | 6.1 | 93.9 |  | 0.3 | 0.3 | 0.3 | 327.3 | 426.3 | 426.3 | 255 | 392.21 | 292.51 | 553.21 | 464.21 |  |  | 50.3 |  |  |  | 2 |  | 719.51 | 0.09 | 0.59 | 0.77
31 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG016 | 1S-DL-YP-ETC-DKRN-2104-JAG016 | GOVIND PURA(OLD):ID | TG-JAG016A-2 | 19505580 | 990 | 320 | 244 | 0.97 | 884 | 320 | 1330 | 313 | 1296 | 251 | 1025 | 290 | 2019-06-10 03:00 | 288 | 53.4 | 1845 | R | 112 | 104 | 84 | 28 | 0.6 | 11.9 | 86.6 | 0.9 | 2.3 | 2.3 | 5 | 2.3 | 93.3 | 179 | 179 | 203.3 | 557 | 492 | 342 | 492.3 | 57 | 36.3 |  | 12.3 | 1 | 1 |  |  | 711 | 9 | 0.56 | 0.89
32 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG018 | 1S-DL-YP-ETC-DKRN-2104-JAG018 | JAGAT PURI A BLK:PL | TG-JAG018A-1 | 19504763 | 990 | 320 | 243 | 0.97 | 870 | 258 | 1051 | 280 | 1130 | 331 | 1344 | 262 | 2019-06-30 01:00 | 189.9 | 71.4 | 1344 | B | 91 | 100 | 109 | 18 |  |  | 6.4 | 93.6 |  |  |  |  | 162.48 | 81 | 81 | 82.3 | 554.55 | 633.43 | 602.21 | 632.43 |  | 3 | 60.52 | 2.3 |  |  | 0.3 |  | 717.43 | 2.17 | 0.6 | 0.88
33 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG018 | 1S-DL-YP-ETC-DKRN-2104-JAG018 | JAGAT PURI A BLK:PL | TG-JAG018A-2 | 19506823 | 630 | 200 | 244 | 0.97 | 464 | 221 | 896 | 123 | 498 | 120 | 481 | 406 | 2019-06-30 01:00 | 143.2 | 44.6 | 896 | R | 103 | 87 | 110 | 23 |  | 0.1 | 1.3 | 98.6 |  |  |  |  | 197.3 | 352.39 | 352.39 | 174.09 | 491.01 | 352.3 | 622.39 | 531 | 14.29 |  |  |  | 2.09 |  |  |  | 705.09 | 14.51 | 0.64 | 0.74
34 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG018 | 1S-DL-YP-ETC-DKRN-2104-JAG018 | JAGAT PURI A BLK:PL | TG-JAG018A-3 | 19505712 | 630 | 200 | 242 | 0.97 | 824 | 307 | 1262 | 283 | 1142 | 234 | 944 | 278 | 2019-06-30 06:00 | 239.8 | 60.8 | 1443 | B | 102 | 86 | 112 | 26 | 0.4 | 6.2 | 33.1 | 60.2 | 0.3 | 0.3 | 0.3 | 0.3 | 4 | 48.32 | 48.32 | 9 | 544.28 | 621.48 | 485.35 | 557.58 | 142.27 | 44.01 | 131.53 | 113.32 | 24.27 | 1.01 | 89.24 | 34.52 | 715.52 | 4.08 | 0.51 | 1.31
35 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG019 | 1S-DL-YP-ETC-DKRN-2104-JAG019 | JAGAT PURI B BLK:ID | TG-JAG019A-1 | 19506860 | 1600 | 500 | 244 | 0.97 | 1211 | 399 | 1699 | 353 | 1489 | 460 | 1974 | 420 | 2019-06-29 23:00 | 306.5 | 94 | 1974 | B | 100 | 93 | 107 | 14 | 0.4 |  | 12.8 | 86.8 |  |  |  |  | 165.57 | 204.27 | 204.27 | 170.57 | 254.19 | 215.49 | 266.19 | 249.19 |  |  | 8 | [5 empty] | 704.38 | 15.22 | 0.59 | 0.76
36 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG020 | 1S-DL-YP-ETC-DKRN-2104-JAG020 | JAGAT PURI F BLK:PL | TG-JAG020A-1 | 19506790 | 990 | 320 | 242 | 0.98 | 930 | 351 | 1433 | 290 | 1175 | 289 | 1182 | 254 | 2019-06-30 14:00 | 201.9 | 58.2 | 1542 | R | 114 | 91 | 95 | 23 | 0.2 | 0.1 | 5 | 94.7 |  |  |  |  | 4.3 | 49.3 | 49.3 | 19 | 456.36 | 644.47 | 635.55 | 629.17 | 225.41 | 9.3 | 32 | 55.3 | 17 |  |  |  | 703.47 | 16.13 | 0.68 | 0.94
37 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG020 | 1S-DL-YP-ETC-DKRN-2104-JAG020 | JAGAT PURI F BLK:PL | TG-JAG020A-2 | 19506785 | 990 | 320 | 239 | 0.98 | 430 | 151 | 633 | 132 | 548 | 146 | 608 | 75 | 2019-06-15 15:30 | 129 | 9.6 | 829 | R | 102 | 99 | 99 | 3 | 0.1 |  | 5.8 | 94.2 | 278.54 | 275.56 | 382.24 | 324.54 | 387.51 | 416.19 | 416.19 | 358.21 | 37 | 11.3 | 74.14 | 20.3 | [8 empty] | 703.45 | 16.15 | 0.56 | 0.43
38 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG021 | 1S-DL-YP-ETC-DKRN-2104-JAG021 | JAGAT PURI RD NO.57:PL | TG-JAG021A-1 | 19505096 | 990 | 320 | 242 | 0.98 | 840 | 394 | 1659 | 271 | 1101 | 175 | 722 | 816 | 2019-06-15 16:30 | 239.4 | 45.8 | 1659 | R | 111 | 92 | 97 | 19 | 0.1 | 0.1 | 4 | 95.8 |  | 6 |  |  | 213.48 | 340.28 | 340.28 | 267.46 | 478.17 | 348.07 | 423.37 | 426.49 | 2.3 | 0.3 |  | 0.3 | 0.3 |  |  |  | 695.05 | 24.55 | 0.52 | 0.85
39 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG022 | 1S-DL-YP-ETC-DKRN-2104-JAG022 | JITAR NAGAR:K | TG-JAG022A-1 | 19506657 | 990 | 320 | 248 | 0.97 | 693 | 226 | 905 | 171 | 692 | 296 | 1193 | 436 | 2019-06-30 | 156.2 | 52.2 | 1202 | B | 96 | 84 | 120 | 36 | 0.1 | 0.1 | 1.1 | 98.7 |  | 7 |  |  | 259.28 | 306.58 | 306.58 | 226.28 | 159.3 | 105 | 268.12 | 192.3 |  |  | 14 | [5 empty] | 703.23 | 16.37 | 0.58 | 0.7
40 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG022 | 1S-DL-YP-ETC-DKRN-2104-JAG022 | JITAR NAGAR:K | TG-JAG022A-2 | 19506650 | 990 | 320 | 245 | 0.97 | 1053 | 477 | 2083 | 394 | 1927 | 183 | 793 | 1219 | 2019-06-18 17:00 | 225 | 66.6 | 2083 | R | 115 | 89 | 96 | 26 | 0.6 | 1.8 | 44.4 | 53.2 |  |  | 0.3 |  | 15.25 | 92.2 | 92.2 | 49.51 | 502.29 | 603.04 | 484.33 | 544.03 | 120 | 7.3 | 109.3 | 107.3 | 65.3 | 0.3 | 5.3 | 2 | 703.24 | 16.36 | 0.57 | 1.06
41 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG023 | 1S-DL-YP-ETC-DKRN-2104-JAG023 | KHUREJI:ID | TG-JAG023A-1 | 19506153 | 630 | 200 | 243 | 0.98 | 544 | 193 | 801 | 179 | 741 | 171 | 712 | 79 | 2019-06-12 | 151.2 | 32.4 | 875 | B | 95 | 112 | 94 | 18 | 0.2 | 0.1 | 20.8 | 78.8 | 0.3 | 0.3 | 0.3 | 0.3 | 22 |  |  |  | 678.08 | 631.52 | 689.1 | 703.08 | 17.3 | 85.46 | 11.58 | 14.3 |  |  |  |  | 718.08 | 1.52 | 0.72 | 0.86
42 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG023 | 1S-DL-YP-ETC-DKRN-2104-JAG023 | KHUREJI:ID | TG-JAG023A-2 | 19503528 | 990 | 320 | 242 | 0.98 | 1014 | 298 | 1265 | 361 | 1555 | 355 | 1528 | 278 | 2019-06-30 | 192.8 | 82.4 | 1617 | Y | 91 | 107 | 103 | 16 |  | 0.3 | 84.4 | 15.3 |  |  |  |  | 1 |  |  |  | 628.09 | 427.27 | 480.59 | 521.46 | 86.52 | 254.17 | 226.2 | 191.33 |  | 34.17 | 8.42 | 2.42 | 716.01 | 3.59 | 0.71 | 1.02
43 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG024 | 1S-DL-YP-ETC-DKRN-2104-JAG024 | MAUSAM VIHAR:ID | TG-JAG024A-1 | 19505935 | 990 | 320 | 245 | 0.98 | 540 | 181 | 754 | 174 | 728 | 184 | 767 | 34 | 2019-06-12 00:30 | 105 | 28.5 | 821 | R | 112 | 92 | 96 | 20 |  |  | 0.1 | 99.9 | 32.3 | 106 | 107.3 | 62.3 | 463.08 | 501.58 | 501.58 | 502.28 | 207.5 | 95.3 | 134 | 138.3 | [8 empty] | 703.28 | 16.32 | 0.57 | 0.55
44 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG024 | 1S-DL-YP-ETC-DKRN-2104-JAG024 | MAUSAM VIHAR:ID | TG-JAG024A-2 | 19505721 | 630 | 200 | 243 | 0.98 | 533 | 202 | 861 | 149 | 633 | 183 | 785 | 202 | 2019-06-11 00:30 | 99.4 | 23.4 | 891 | R | 110 | 81 | 109 | 29 |  | 0.1 | 11.3 | 88.6 | 3 | 36 | 1 | 1.3 | 188 | 414.13 | 414.13 | 283.21 | 489.04 | 252.21 | 456.13 | 414.43 | 22 |  | 17 | 3 | 0.3 |  |  |  | 702.34 | 17.26 | 0.53 | 0.85
45 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG025 | 1S-DL-YP-ETC-DKRN-2104-JAG025 | NEW LAYALPUR:K | TG-JAG025A-1 | 19506786 | 990 | 320 | 238 | 0.97 | 931 | 271 | 1160 | 293 | 1262 | 367 | 1594 | 394 | 2019-06-01 00:30 | 230.4 | 54.1 | 1634 | Y | 95 | 101 | 104 | 9 | 0.4 | 2.6 | 17.7 | 79.2 |  |  |  |  | 288.29 | 265.29 | 265.29 | 252.59 | 403.17 | 385.17 | 484.5 | 412.47 | 12.3 | 46.3 | 34 | 39 | 0.3 | 7.3 | 4.3 |  | 704.46 | 15.14 | 0.53 | 0.94
46 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG025 | 1S-DL-YP-ETC-DKRN-2104-JAG025 | NEW LAYALPUR:K | TG-JAG025A-2 | 19506781 | 990 | 320 | 239 | 0.97 | 904 | 275 | 1151 | 247 | 1038 | 382 | 1639 | 553 | 2019-06-30 | 191 | 55.4 | 1661 | B | 100 | 94 | 106 | 12 | 0.7 | 0.9 | 9.3 | 89.1 |  |  |  |  | 218.37 | 255.15 | 255.15 | 207.15 | 435.44 | 444.06 | 482.22 | 456.36 | 46.3 | 2.3 | 54.3 | 38 | 1 |  | 4 |  | 701.51 | 18.09 | 0.55 | 0.91
47 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG025 | 1S-DL-YP-ETC-DKRN-2104-JAG025 | NEW LAYALPUR:K | TG-JAG025A-3 | 19506855 | 630 | 200 | 240 | 0.97 | 492 | 127 | 578 | 168 | 767 | 197 | 904 | 283 | 2019-06-10 23:00 | 119 | 26.8 | 904 | B | 87 | 105 | 108 | 21 | 0.1 | 0.1 | 1.7 | 98.1 | 19 | 10.3 | 4 | 4.3 | 519.14 | 370.45 | 370.45 | 428.45 | 166.13 | 319.2 | 324.51 | 271.12 |  | 3.52 | 6.21 | [5 empty] | 704.27 | 15.33 | 0.5 | 0.78
48 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG026 | 1S-DL-YP-ETC-DKRN-2104-JAG026 | PREET VIHAR POLICE STN:ID | TG-JAG026A-1 | 19506011 | 630 | 200 | 245 | 0.97 | 399 | 80 | 336 | 108 | 457 | 211 | 925 | 539 | 2019-06-14 | 114.6 | 24.2 | 925 | B | 73 | 109 | 118 | 45 | 0.5 | 0.9 | 25 | 73.6 | 250.54 | 28 | 8 | 26.3 | 459.08 | 490.55 | 490.55 | 549.11 | 5.3 | 196.37 | 234.51 | 139.51 |  |  | 5 |  |  |  | 0.3 |  | 715.32 | 4.28 | 0.5 | 0.63
49 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG026 | 1S-DL-YP-ETC-DKRN-2104-JAG026 | PREET VIHAR POLICE STN:ID | TG-JAG026A-2 | 19500834 | 990 | 320 | 233 | 0.98 | 753 | 307 | 1397 | 241 | 1088 | 205 | 924 | 416 | 2019-06-03 00:30 | 120.7 | 39.7 | 1446 | R | 112 | 93 | 96 | 19 |  | 0.1 | 66.3 | 33.5 | 0.29 | 11.29 | 4.29 | 2.59 | 286.06 | 415.04 | 415.04 | 377.42 | 409.39 | 289.11 | 307.01 | 335.03 | 19.3 | [7 empty] | 715.44 | 4.16 | 0.55 | 0.76
50 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG027 | 1S-DL-YP-ETC-DKRN-2104-JAG027 | RADHEY SHAYAM PARK:PL | TG-JAG027A-1 | 19506867 | 990 | 320 | 240 | 0.98 | 1075 | 329 | 1400 | 515 | 2252 | 231 | 986 | 1118 | 2019-06-11 00:30 | 194.9 | 41.9 | 2252 | Y | 95 | 125 | 80 | 45 | 0.2 | 1.6 | 34.9 | 63.2 |  |  |  |  | 191.23 | 44.32 | 44.32 | 132 | 445.25 | 461.55 | 413.44 | 479.57 | 67.3 | 96.3 |  | 91.21 | 2.52 | 104.13 |  | 3.52 | 707.1 | 12.5 | 0.51 | 1.09
51 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG028 | 1S-DL-YP-ETC-DKRN-2104-JAG028 | RAM NAGAR EXT:K | TG-JAG028A-1 | 19505825 | 990 | 320 | 248 | 0.97 | 883 | 269 | 1076 | 379 | 1529 | 235 | 941 | 533 | 2019-06-12 02:00 | 248.6 | 26.9 | 1529 | Y | 113 | 96 | 90 | 23 | 0.3 | 0.4 | 68.4 | 31 | 1 | 7 | 10 | 2 | 147.4 | 344.56 | 344.56 | 311.58 | 533.2 | 340.52 | 290.1 | 388.49 | 23.04 | 12.02 | 8 | 3.17 | 1 | 1.14 |  |  | 706.04 | 13.56 | 0.51 | 0.89
52 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG028 | 1S-DL-YP-ETC-DKRN-2104-JAG028 | RAM NAGAR EXT:K | TG-JAG028A-2 | 19506788 | 1600 | 500 | 243 | 0.97 | 882 | 257 | 1075 | 244 | 1025 | 381 | 1619 | 571 | 2019-06-12 00:30 | 286 | 51 | 2014 | B | 90 | 88 | 121 | 33 | 0.3 | 0.2 | 79.7 | 19.8 | 20.3 | 36.31 | 5.3 | 14 | 630.58 | 649.57 | 649.57 | 569.58 | 55.14 | 20.14 | 275.08 | 122.44 |  |  | 0.3 | [5 empty] | 706.42 | 13.18 | 0.59 | 0.55
53 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG029 | 1S-DL-YP-ETC-DKRN-2104-JAG029 | SHIV PURI:PM | TG-JAG029A-1 | 19506151 | 990 | 200 | 235 | 0.98 | 976 | 320 | 1424 | 407 | 1856 | 249 | 1106 | 652 | 2019-06-29 23:00 | 237.4 | 54.4 | 2189 | Y | 99 | 112 | 89 | 23 | 0.8 | 2.6 | 39.2 | 57.4 |  |  |  |  | 34 | 4 | 4 | 19 | 626.56 | 585.53 | 572.37 | 645.53 | 32.41 | 85.3 | 1.3 | 28.44 |  | 18.14 |  |  | 693.37 | 26.23 | 0.6 | 0.99
54 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG030 | 1S-DL-YP-ETC-DKRN-2104-JAG030 | SILVER PARK:ID | TG-JAG030A-1 | 19506008 | 990 | 320 | 229 | 0.98 | 944 | 202 | 907 | 373 | 1742 | 369 | 1702 | 815 | 2019-06-02 15:30 | 307.5 | 53.4 | 2174 | B | 102 | 93 | 106 | 13 | 0.4 | 0.6 | 60.6 | 38.3 |  |  |  |  | 120.27 | 237.22 | 237.22 | 148.53 | 572.05 | 454.17 | 511.34 | 529.04 | 8.21 | 8.51 | 47.21 | 22.56 |  | 0.23 | 10.05 |  | 700.53 | 19.07 | 0.54 | 0.95
55 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG031 | 1S-DL-YP-ETC-DKRN-2104-JAG031 | SOUTH ANARKALI:PL | TG-JAG031A-1 | 19506660 | 990 | 320 | 245 | 0.97 | 1035 | 346 | 1464 | 378 | 1597 | 311 | 1301 | 256 | 2019-06-05 02:30 | 246.7 | 64.3 | 1637 | Y | 100 | 107 | 92 | 15 | 0.4 | 0.2 | 14.8 | 84.7 | 0.06 | 1.13 | 1.13 | 0.13 | 79.57 | 42.23 | 42.23 | 76.53 | 523.58 | 517.42 | 477.52 | 519.42 | 87.58 | 112.13 | 72.22 | 97.11 | 3.54 | 22.22 |  | 1.54 | 695.53 | 24.07 | 0.56 | 1.05
56 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG031 | 1S-DL-YP-ETC-DKRN-2104-JAG031 | SOUTH ANARKALI:PL | TG-JAG031A-2 | 19506868 | 990 | 320 | 238 | 0.97 | 1166 | 395 | 1779 | 355 | 1587 | 416 | 1875 | 254 | 2019-06-10 00:30 | 253.8 | 67.8 | 1953 | R | 109 | 95 | 96 | 14 | 0.4 | 0.6 | 30.9 | 68.1 |  |  |  |  | 17.54 | 80.55 | 80.55 | 46.55 | 496.35 | 485.49 | 468.11 | 501.1 | 115.28 | 117.34 | 115.39 | 115.58 | 65.29 | 11.08 | 24.23 | 31.23 | 695.26 | 24.34 | 0.54 | 1.18
57 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG031 | 1S-DL-YP-ETC-DKRN-2104-JAG031 | SOUTH ANARKALI:PL | TG-JAG031A-3 | 19506472 | 630 | 200 | 238 | 0.98 | 712 | 266 | 1192 | 226 | 1001 | 220 | 981 | 202 | 2019-06-10 00:30 | 127.8 | 39.8 | 1192 | R | 108 | 98 | 94 | 14 | 0.2 | 0.4 | 18.6 | 80.8 | 0.06 | 0.06 | 0.06 | 0.06 | 32.24 | 61.31 | 61.31 | 47.24 | 476.14 | 496.41 | 485.11 | 498.54 | 124.23 | 119.14 | 117.12 | 128.22 | 62.47 | 18.22 | 5.24 | 21.08 | 695.54 | 24.06 | 0.55 | 1.13
58 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG032 | 1S-DL-YP-ETC-DKRN-2104-JAG032 | SOUTH ANARKALI (NALAH):PL | TG-JAG032A-1 | 19506107 | 990 | 320 | 246 | 0.97 | 778 | 254 | 1111 | 231 | 999 | 293 | 1276 | 242 | 2019-06-11 00:30 | 182.7 | 57.6 | 1311 | B | 102 | 90 | 108 | 18 |  | 0.2 | 15.2 | 84.7 |  |  |  |  | 179.58 | 296.35 | 296.35 | 218.57 | 365.07 | 250 | 351.59 | 327.38 | 1.3 |  | 25.3 | [5 empty] | 702.04 | 17.56 | 0.58 | 0.79
59 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG033 | 1S-DL-YP-ETC-DKRN-2104-JAG033 | VIVEKANAND:PL | TG-JAG033A-1 | 19505080 | 990 | 320 | 233 | 0.97 | 743 | 247 | 1129 | 232 | 1053 | 265 | 1210 | 136 | 2019-06-02 | 161.9 | 72.1 | 1267 | R | 101 | 100 | 99 | 2 |  |  | 2.9 | 97.1 |  |  |  |  | 30.01 | 10.3 | 10.3 | 16.01 | 676.16 | 705.17 | 693.46 | 699.46 | 9.3 |  | 2.3 | [5 empty] | 715.47 | 4.13 | 0.73 | 0.75
60 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG033 | 1S-DL-YP-ETC-DKRN-2104-JAG033 | VIVEKANAND:PL | TG-JAG033A-2 | 19505543 | 630 | 200 | 239 | 0.97 | 416 | 125 | 524 | 131 | 550 | 160 | 675 | 140 | 2019-06-11 01:30 | 106.6 | 37.4 | 720 | B | 91 | 92 | 117 | 26 | 0.1 | 0.2 | 53.3 | 46.4 | 1.18 | 1.18 | 1.18 | 1.18 | 157.53 | 139.5 | 139.5 | 51.55 | 543.46 | 561.49 | 687.09 | 649.44 |  |  | 1 | [5 empty] | 702.57 | 17.03 | 0.75 | 0.66
61 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG034 | 1S-DL-YP-ETC-DKRN-2104-JAG034 | JAGAT PURI G BLK:PL | TG-JAG034A-1 | 19505835 | 990 | 320 | 237 | 0.97 | 971 | 299 | 1282 | 331 | 1432 | 342 | 1483 | 180 | 2019-06-30 | 223.7 | 64.6 | 1726 | B | 110 | 81 | 110 | 29 | 0.2 | 0.9 | 45.2 | 53.6 |  | 0.3 |  |  | 50.24 | 329.57 | 329.57 | 130.51 | 567.59 | 364.26 | 494.58 | 518.32 | 68.3 | 8.3 | 110.28 | 55 | 17.3 | 1 | 6 |  | 704.23 | 15.37 | 0.55 | 0.98
62 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG034 | 1S-DL-YP-ETC-DKRN-2104-JAG034 | JAGAT PURI G BLK:PL | TG-JAG034A-2 | 19505711 | 990 | 320 | 243 | 0.97 | 818 | 237 | 995 | 351 | 1474 | 230 | 958 | 499 | 2019-06-11 23:30 | 199 | 57.3 | 1681 | Y | 79 | 122 | 99 | 43 | 0.2 | 0.1 | 2.3 | 97.4 | 1 |  |  |  | 430.28 | 84.27 | 84.27 | 194.27 | 273.26 | 503.57 | 447.57 | 506.57 |  | 95.3 | 21.3 | 3.3 |  | 21 | 0.3 |  | 704.54 | 15.06 | 0.59 | 0.83
63 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG036 | 1S-DL-YP-ETC-DKRN-2104-JAG036 | LAXMAN PARK S/STN | TG-JAG036A-1 | 19506649 | 990 | 320 | 233 | 0.98 | 573 | 210 | 922 | 156 | 683 | 207 | 903 | 230 | 2019-06-11 | 114.6 | 21.4 | 1131 | B | 99 | 88 | 114 | 26 | 0.3 |  | 46.3 | 53.3 | 45.3 | 126.33 | 24.3 | 40 | 553.02 | 514.24 | 514.24 | 537.03 | 107.01 | 64.36 | 218.3 | 128.3 | [8 empty] | 705.33 | 14.27 | 0.54 | 0.58
64 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG036 | 1S-DL-YP-ETC-DKRN-2104-JAG036 | LAXMAN PARK S/STN | TG-JAG036A-2 | 19506460 | 630 | 200 | 238 | 0.97 | 422 | 200 | 945 | 121 | 563 | 100 | 465 | 440 | 2019-06-08 23:30 | 99.6 | 27.6 | 945 | R | 104 | 93 | 103 | 11 | 0.3 | 0.1 | 43.1 | 56.5 | 18.59 | 44.29 | 5.29 | 10.29 | 418 | 447.27 | 447.27 | 461 | 269.38 | 215.11 | 256.08 | 235.38 | 0.3 | [7 empty] | 707.07 | 12.53 | 0.56 | 0.67
65 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG039 | 1S-DL-YP-ETC-DKRN-2104-JAG039 | R.S. PARK (PARKWALA) | TG-JAG039A-1 | 19505833 | 990 | 320 | 244.7375 | 0.97683 | 1009.759 | 329.1388 | 1437.35 | 360.5541 | 1575.0223 | 320.0661 | 1411.6618 | 152.1515 | 2019-06-11 00:30 | [15 empty] | 0 |  |  |  | 69.5 |  |  |  | 540.5 |  |  |  | 101.5 |  |  |  | 4 | 715.5 |  | 0.57674 | 1.02
66 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG039 | 1S-DL-YP-ETC-DKRN-2104-JAG039 | R.S. PARK (PARKWALA) | TG-JAG039A-2 | 19506106 | 630 | 200 | 245 | 0.97 | 584 | 141 | 577 | 177 | 728 | 266 | 1120 | 486 | 2019-06-11 23:30 | 139 | 30.6 | 1160 | B | 78 | 104 | 118 | 40 | 1.7 | 4.5 | 21.3 | 72.5 | 19.57 | 1 | 1 | 1 | 445.58 | 253.5 | 253.5 | 306.13 | 240.36 | 421.45 | 414.45 | 372.08 | 0.3 | 30.26 | 66.12 | 27.4 |  |  | 36.28 |  | 707.01 | 12.59 | 0.51 | 0.93
67 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN001 | 1S-DL-YP-ETC-DKRN-2102-GAN001 | AHATA KARAM CHAND:PL | TG-GAN001A-1 | 19505208 | 990 | 320 | 237 | 0.98 | 759 | 247 | 1054 | 284 | 1207 | 228 | 948 | 225 | 2019-06-30 16:00 | 166.7 | 28.5 | 1234 | Y | 99 | 106 | 95 | 11 | 10 | 38.5 | 50 | 1.5 |  |  |  |  | 276.02 | 243.3 | 243.3 | 272.36 | 427.18 | 435.2 | 412.44 | 430.44 |  | 24.3 | [6 empty] | 703.2 | 16.4 | 0.61 | 0.77
68 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN002 | 1S-DL-YP-ETC-DKRN-2102-GAN002 | AJIT NAGAR GALI NO 8:PL | TG-GAN002A-1 | 19506803 | 990 | 320 | 230 | 0.98 | 924 | 311 | 1362 | 285 | 1232 | 328 | 1428 | 172 | 2019-06-02 12:30 | 204.5 | 43.8 | 1462 | B | 99 | 92 | 109 | 17 |  | 0.1 | 37.6 | 62.3 |  |  |  |  | 4 | 12 | 12 | 1.3 | 589.09 | 676.57 | 495.28 | 618.06 | 112.32 | 17.14 | 210.13 | 86.35 | 0.3 |  | 0.3 |  | 706.11 | 13.49 | 0.7 | 0.93
69 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN003 | 1S-DL-YP-ETC-DKRN-2102-GAN003 | AMAR MOHALLA:PL | TG-GAN003A-1 | 19506101 | 990 | 320 | 234 | 0.98 | 1237 | 457 | 2015 | 378 | 1640 | 402 | 1740 | 336 | 2019-06-30 17:30 | 223 | 54.1 | 2015 | R | 116 | 93 | 91 | 25 | 0.1 | 7.3 | 83.9 | 8.7 |  |  |  |  | 8.3 | 54.18 | 54.18 | 29 | 411.25 | 541.23 | 504.22 | 499.33 | 205.14 | 101.39 | 110.11 | 167.48 | 74.03 | 1.52 | 2.51 | 2.51 | 699.12 | 20.48 | 0.52 | 1.25
70 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN003 | 1S-DL-YP-ETC-DKRN-2102-GAN003 | AMAR MOHALLA:PL | TG-GAN003A-2 | 19506348 | 630 | 200 | 241 | 0.97 | 532 | 156 | 664 | 160 | 671 | 217 | 939 | 272 | 2019-06-02 16:00 | 130.4 | 19.4 | 985 | B | 95 | 88 | 117 | 29 | 0.1 | 19.5 | 74.6 | 5.7 | 36 | 6.3 |  | 3.3 | 281.54 | 440.54 | 440.54 | 295.45 | 381.21 | 251.51 | 396.44 | 392.3 |  |  | 49.46 | 7.3 |  |  | 5 |  | 699.15 | 20.45 | 0.51 | 0.84
71 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN004 | 1S-DL-YP-ETC-DKRN-2102-GAN004 | ASHOK GALI NO. 1:PL | TG-GAN004A-1 | 19506804 | 990 | 320 | 237 | 0.99 | 712 | 220 | 999 | 295 | 1411 | 197 | 860 | 496 | 2019-06-30 14:00 | 166.4 | -6.4 | 1411 | Y | 109 | 100 | 91 | 18 | 0.1 | 0.1 | 6.3 | 93.5 | 445.09 | 435.39 | 454.09 | 441.09 | 27 | 36 | 36 | 33.3 | 234.1 | 234.1 | 225.11 | 232.1 | 0.3 | 1 | [6 empty] | 706.49 | 13.11 | 0.32 | 0.72
72 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN004 | 1S-DL-YP-ETC-DKRN-2102-GAN004 | ASHOK GALI NO. 1:PL | TG-GAN004A-2 | 19506810 | 990 | 320 | 237 | 0.98 | 594 | 182 | 791 | 216 | 934 | 196 | 850 | 125 | 2019-06-26 15:00 | 153.9 | 1.6 | 1124 | R | 103 | 105 | 92 | 13 | 0.1 |  | 39.1 | 60.9 | 447.08 | 449.08 | 451.08 | 448.08 | 52.3 | 48 | 48 | 55.59 | 207.1 | 209.4 | 195.41 | 202.41 | [8 empty] | 706.48 | 13.12 | 0.34 | 0.6
73 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN004 | 1S-DL-YP-ETC-DKRN-2102-GAN004 | ASHOK GALI NO. 1:PL | TG-GAN004A-3 | 19506807 | 630 | 200 | 239 | 0.98 | 201 | 62 | 255 | 75 | 314 | 64 | 267 | 54 | 2019-06-20 15:30 | 38.4 | 0.4 | 330 | B | 88 | 106 | 106 | 18 | 14.5 |  | 37 | 48.5 | 436.39 | 415.39 | 420.39 | 418.39 | 162.26 | 183.26 | 183.26 | 180.26 | [12 empty] | 706.49 | 13.11 | 0.34 | 0.32
74 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN005 | 1S-DL-YP-ETC-DKRN-2102-GAN005 | CHEMALI DEVI (INSIDE):PL | TG-GAN005A-1 | 19500172 | 990 | 320 | 240 | 0.97 | 947 | 313 | 1345 | 320 | 1369 | 314 | 1350 | 21 | 2019-06-30 16:00 | 226 | 40.5 | 1479 | Y | 91 | 102 | 106 | 15 |  |  | 26.8 | 73.2 | 60.3 |  |  |  | 53.58 | 43.57 | 43.57 | 52.28 | 521.23 | 527.54 | 543.59 | 550.59 | 83.28 | 145.58 | 152.22 | 116.22 | 0.3 | 2 |  |  | 719.49 | 0.11 | 0.65 | 0.96
75 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN007 | 1S-DL-YP-ETC-DKRN-2102-GAN007 | DUDLELA CHOWK:PL | TG-GAN007A-1 | 19506102 | 990 | 320 | 231 | 0.98 | 796 | 227 | 994 | 271 | 1198 | 298 | 1315 | 282 | 2019-06-02 14:30 | 188.8 | 48.6 | 1436 | B | 95 | 100 | 105 | 10 | 0.1 | 0.1 | 18.1 | 81.8 |  |  |  |  | 92.4 | 63.47 | 63.47 | 38.3 | 606.57 | 633.59 | 675.47 | 662.07 | 1.3 | 3.21 | 6.2 | 0.3 |  |  |  |  | 701.07 | 18.53 | 0.67 | 0.8
76 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN007 | 1S-DL-YP-ETC-DKRN-2102-GAN007 | DUDLELA CHOWK:PL | TG-GAN007A-2 | 19506103 | 990 | 320 | 237 | 0.97 | 733 | 217 | 931 | 264 | 1130 | 252 | 1074 | 178 | 2019-06-28 09:00 | 229.4 | 70.1 | 1364 | Y | 84 | 127 | 89 | 43 | 0.1 | 5.3 | 78.1 | 16.4 |  |  |  |  | 101.34 |  |  | 14.3 | 599.32 | 601.49 | 626.41 | 686.36 |  | 99.17 | [6 empty] | 701.06 | 18.54 | 0.75 | 0.74
77 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN008 | 1S-DL-YP-ETC-DKRN-2102-GAN008 | GALI GURDWARA NO. 2:ID | TG-GAN008A-1 | 19506797 | 990 | 320 | 244 | 0.97 | 725 | 267 | 1131 | 242 | 1026 | 216 | 902 | 199 | 2019-06-30 15:00 | 161.9 | 25 | 1270 | R | 104 | 100 | 95 | 9 | 0.2 | 0.1 | 52.2 | 47.5 | 1 | 59.18 | 4.3 | 5.3 | 354.29 | 235.29 | 235.29 | 357.29 | 347.2 | 409.02 | 298.2 | 340.5 | 1 | [7 empty] | 703.49 | 16.11 | 0.58 | 0.73
78 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN008 | 1S-DL-YP-ETC-DKRN-2102-GAN008 | GALI GURDWARA NO. 2:ID | TG-GAN008A-2 | 19506796 | 1600 | 500 | 244 | 0.97 | 1217 | 406 | 1692 | 388 | 1619 | 423 | 1753 | 116 | 2019-06-02 16:00 | 276.5 | 81 | 1789 | R | 104 | 96 | 100 | 8 | 0.1 |  | 6.3 | 93.6 |  |  |  |  | 59.3 | 150.3 | 150.3 | 105.3 | 643.52 | 552.52 | 577.52 | 597.52 | [8 empty] | 703.22 | 16.38 | 0.69 | 0.76
79 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN008 | 1S-DL-YP-ETC-DKRN-2102-GAN008 | GALI GURDWARA NO. 2:ID | TG-GAN008A-3 | 19505541 | 400 | 120 | 244 | 0.99 | 393 | 142 | 599 | 101 | 427 | 149 | 640 | 196 | 2019-06-30 15:00 | 56.3 | -16.3 | 710 | B | 96 | 73 | 130 | 57 | 4 | 6.8 | 50.2 | 39 | 276 | 370.02 | 27 | 255 | 158.41 | 82.11 | 82.11 | 168.16 | 174.53 | 246.3 | 106.01 | 186.3 | 86.22 |  | 140.18 | 88.57 | 2.47 |  | 76.22 |  | 698.43 | 21.17 | 0.42 | 0.98
80 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN008 | 1S-DL-YP-ETC-DKRN-2102-GAN008 | GALI GURDWARA NO. 2:ID | TG-GAN008A-4 | 19504381 | 400 | 120 | 244 | 0.98 | 322 | 67 | 277 | 152 | 652 | 104 | 440 | 326 | 2019-06-02 16:30 | 57.7 | 0.6 | 683 | Y | 68 | 114 | 118 | 50 | 1.4 | 16.3 | 66.9 | 15.5 | 454.06 | 354.29 | 364.13 | 410.47 | 69.37 | 96.11 | 96.11 | 61.19 | 191.1 | 200.29 | 201.33 | 242.17 |  | 55.14 | 55.44 | 0.3 |  | 8.3 |  |  | 714.53 | 5.07 | 0.38 | 0.81
81 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN009 | 1S-DL-YP-ETC-DKRN-2102-GAN009 | GANDHI NAGAR KIOSK:K | TG-GAN009A-1 | 19506800 | 990 | 320 | 244 | 0.97 | 351 | 128 | 524 | 108 | 436 | 115 | 470 | 77 | 2019-06-29 17:00 | 82.9 | 7.7 | 634 | B | 102 | 97 | 101 | 5 | 0.1 |  | 33.9 | 66 | 426.47 | 423.17 | 438.17 | 429.47 | 276.21 | 280.21 | 280.21 | 274.21 | 1 | 0.3 | 1 | [9 empty] | 704.08 | 15.52 | 0.53 | 0.35
82 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN010 | 1S-DL-YP-ETC-DKRN-2102-GAN010 | GANDHI NAGAR POLICE ST.:PL | TG-GAN010A-1 | 19506799 | 990 | 320 | 234 | 0.98 | 786 | 230 | 1024 | 324 | 1440 | 233 | 1025 | 416 | 2019-06-02 15:00 | 182.7 | 21.8 | 1608 | Y | 96 | 111 | 93 | 18 | 0.3 | 0.1 | 44.9 | 54.7 | 324.53 | 357.53 | 419.23 | 383.23 | 138 | 94.3 | 94.3 | 76 | 242.06 | 180.41 | 235.09 | 245.36 |  | 70.55 | 3.3 |  |  | 1 |  |  | 704.59 | 15.01 | 0.42 | 0.79
83 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN010 | 1S-DL-YP-ETC-DKRN-2102-GAN010 | GANDHI NAGAR POLICE ST.:PL | TG-GAN010A-2 | 19506802 | 990 | 320 | 244 | 0.98 | 832 | 282 | 1229 | 204 | 884 | 346 | 1524 | 555 | 2019-06-29 15:00 | 210.9 | 9.9 | 1684 | B | 105 | 84 | 111 | 27 | 0.4 |  | 11.2 | 88.4 | 361.22 | 381.22 | 377.23 | 374.52 | 88 | 91.57 | 91.57 | 77.3 | 230.16 | 231.49 | 131.02 | 246.46 | 25.3 |  | 128.44 | 6 |  |  | 2.3 |  | 705.08 | 14.52 | 0.41 | 0.84
84 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN011 | 1S-DL-YP-ETC-DKRN-2102-GAN011 | HATHI WALA PARK:PL | TG-GAN011A-1 | 19506798 | 990 | 320 | 238 | 0.97 | 703 | 230 | 974 | 245 | 1032 | 229 | 976 | 56 | 2019-06-15 15:30 | 169 | 36.8 | 1076 | Y | 97 | 112 | 91 | 21 | 0.4 |  | 27.5 | 72.2 | 4.3 |  | 30 | 2 | 433.46 | 263.03 | 263.03 | 416.16 | 265.5 | 441.03 | 248.2 | 285.5 | [8 empty] | 704.06 | 15.54 | 0.56 | 0.71
85 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN012 | 1S-DL-YP-ETC-DKRN-2102-GAN012 | JANTA PARK NO. 1:PL | TG-GAN012A-1 | 19505864 | 990 | 320 | 237 | 0.99 | 1057 | 314 | 1369 | 360 | 1571 | 383 | 1683 | 275 | 2019-06-30 11:30 | 229.8 | -39.4 | 1683 | B | 103 | 99 | 98 | 5 | 0.3 | 0.3 | 61.1 | 38.3 | 399.09 | 415.39 | 418.47 | 410.39 | 51.2 | 38.5 | 38.5 | 42.5 | 225.22 | 226.22 | 234.23 | 239.22 | 24 | 18.3 | 9.59 | 6.3 |  | 0.3 | 0.3 | 0.3 | 699.51 | 20.09 | 0.29 | 1.07
86 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN012 | 1S-DL-YP-ETC-DKRN-2102-GAN012 | JANTA PARK NO. 1:PL | TG-GAN012A-2 | 19506604 | 990 | 320 | 237 | 0.98 | 810 | 259 | 1116 | 298 | 1279 | 253 | 1087 | 180 | 2019-06-28 17:00 | 180.5 | -2.9 | 1351 | R | 101 | 103 | 96 | 7 | 0.1 | 0.1 | 22.9 | 76.9 | 427.35 | 421.35 | 430.35 | 428.35 | 27.52 | 36.22 | 36.22 | 31.22 | 245.39 | 215.12 | 231.39 | 238.09 | 1 | 28.57 | 4 | 4 |  |  |  |  | 702.06 | 17.54 | 0.36 | 0.82
87 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN012 | 1S-DL-YP-ETC-DKRN-2102-GAN012 | JANTA PARK NO. 1:PL | TG-GAN012A-3 | 19505184 | 990 | 320 | 237 | 0.99 | 805 | 362 | 1744 | 219 | 993 | 224 | 971 | 763 | 2019-06-30 14:30 | 220.2 | -1.3 | 1744 | R | 104 | 96 | 101 | 8 | 0.3 | 0.1 | 21.7 | 77.9 | 441.35 | 434.37 | 436.37 | 436.37 | 25.55 | 36.23 | 36.23 | 30.23 | 230.09 | 229.39 | 236.39 | 235.09 | 5 | 2.3 | 2.3 | 1 | 0.3 |  |  |  | 703.09 | 16.51 | 0.31 | 0.81
88 | 2019-06-01 | 2019-06-27 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN013 | 1S-DL-YP-ETC-DKRN-2102-GAN013 | KAILASH NAGAR (KHATTA):PL | TG-GAN013A-1 | 19501982 | 990 | 320 | 236 | 0.97 | 498 | 194 | 802 | 152 | 625 | 153 | 632 | 173 | 2019-06-12 18:30 | 128.1 | 18.4 | 908 | R | 119 | 93 | 88 | 31 |  |  | 1 | 99 | 0.3 | 7 | 11.3 | 2.3 | 178.18 | 380.55 | 380.55 | 321.55 | 290.48 | 81.41 | 25.3 | 145.11 | [8 empty] | 469.36 | 10.24 | 0.72 | 0.5
89 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN014 | 1S-DL-YP-ETC-DKRN-2102-GAN014 | KAILASH NAGAR NO. 1:PL | TG-GAN014A-1 | 19505517 | 990 | 320 | 235 | 0.97 | 811 | 262 | 1117 | 266 | 1136 | 283 | 1200 | 76 | 2019-06-26 14:30 | 217.3 | 53.8 | 1411 | B | 94 | 100 | 105 | 11 | 0.4 | 0.1 | 27.5 | 72.1 |  |  |  |  | 108.29 | 65.59 | 65.59 | 74.29 | 598.35 | 640.05 | 615.35 | 631.35 | 0.3 | 1.3 | 30.3 | 1.3 |  |  |  |  | 707.34 | 12.26 | 0.68 | 0.82
90 | 2019-06-15 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN014 | 1S-DL-YP-ETC-DKRN-2102-GAN014 | KAILASH NAGAR NO. 1:PL | TG-GAN014A-2 | 19505862 | 990 | 320 | 245 | 0.97 | 675 | 243 | 1021 | 208 | 878 | 224 | 943 | 124 | 2019-06-29 23:00 | 197.1 | -13.1 | 1087 | R | 108 | 103 | 89 | 19 | 0.1 | 0.1 | 29.9 | 69.8 |  |  | 18.3 |  | 152.2 | 175.13 | 175.13 | 192.5 | 205.05 | 182.12 | 91.3 | 164.35 | [8 empty] | 357.25 | 26.35 | 0.58 | 0.68
91 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN014 | 1S-DL-YP-ETC-DKRN-2102-GAN014 | KAILASH NAGAR NO. 1:PL | TG-GAN014A-3 | 19506861 | 990 | 320 | 243 | 0.96 | 598 | 175 | 745 | 221 | 945 | 203 | 867 | 175 | 2019-06-01 15:30 | 190.7 | 52.2 | 1008 | Y | 94 | 106 | 100 | 12 | 0.1 |  | 50.2 | 49.7 | 1 |  |  |  | 346.09 | 267.3 | 267.3 | 270.32 | 361.34 | 441.13 | 447.2 | 438.11 | [8 empty] | 708.43 | 11.17 | 0.7 | 0.6
92 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN015 | 1S-DL-YP-ETC-DKRN-2102-GAN015 | KAILASH NAGAR NO. 15:PL | TG-GAN015A-1 | 19505931 | 990 | 320 | 241 | 0.97 | 846 | 208 | 857 | 285 | 1184 | 354 | 1467 | 529 | 2019-06-03 01:00 | 214.4 | 73.3 | 1489 | B | 89 | 102 | 109 | 20 | 0.1 | 0.4 | 24.3 | 75.2 |  |  |  |  | 89.3 | 40 | 40 | 36.3 | 628.06 | 658.4 | 632.32 | 673.36 |  | 18.26 | 55.04 | 7.3 |  | 0.3 | 8.3 |  | 717.36 | 2.24 | 0.68 | 0.85
93 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN015 | 1S-DL-YP-ETC-DKRN-2102-GAN015 | KAILASH NAGAR NO. 15:PL | TG-GAN015A-2 | 19505011 | 990 | 320 | 238 | 0.97 | 746 | 242 | 1020 | 237 | 1040 | 267 | 1152 | 123 | 2019-06-30 15:00 | 181.1 | 42.7 | 1257 | B | 96 | 92 | 112 | 20 | 99.9 | 0.1 | [6 empty] | 101.47 | 133.47 | 133.47 | 78.49 | 616.23 | 584.23 | 644.32 | 639.21 |  |  | 32.08 | [5 empty] | 718.1 | 1.5 | 0.7 | 0.75
94 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN015 | 1S-DL-YP-ETC-DKRN-2102-GAN015 | KAILASH NAGAR NO. 15:PL | TG-GAN015A-3 | 19506875 | 990 | 320 | 247 | 0.96 | 795 | 369 | 1672 | 208 | 860 | 218 | 929 | 779 | 2019-06-30 14:00 | 233.3 | 65.9 | 1672 | R | 117 | 84 | 99 | 33 | 0.3 | 3.5 | 87.6 | 8.7 |  |  |  |  | 17.3 | 200.29 | 200.29 | 58.3 | 608.28 | 507.02 | 630.31 | 648.31 | 80.03 |  |  | 0.3 | 1.3 |  |  |  | 707.31 | 12.29 | 0.68 | 0.8
95 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN016 | 1S-DL-YP-ETC-DKRN-2102-GAN016 | KAILASH NAGAR SCHOOL:PL | TG-GAN016A-1 | 19506801 | 990 | 320 | 237 | 0.98 | 953 | 276 | 1178 | 328 | 1446 | 350 | 1601 | 370 | 2019-06-30 14:00 | 234.6 | 30.1 | 1641 | B | 95 | 113 | 92 | 21 | 0.1 | 0.1 | 13 | 86.8 | 1.3 |  | 2 |  | 366.17 | 219.17 | 219.17 | 341.17 | 255.53 | 277.04 | 225.23 | 237.53 | 84.48 | 190.07 | 82.48 | 129.18 |  | 22 | 1 |  | 708.28 | 11.32 | 0.54 | 0.96
96 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN016 | 1S-DL-YP-ETC-DKRN-2102-GAN016 | KAILASH NAGAR SCHOOL:PL | TG-GAN016A-2 | 19506645 | 630 | 200 | 244 | 0.97 | 297 | 85 | 353 | 87 | 373 | 126 | 533 | 171 | 2019-06-01 16:30 | 70.6 | 12 | 732 | B | 91 | 93 | 116 | 25 | 1 | 29.2 | 42.6 | 27.2 | 410.47 | 286.46 | 251.16 | 322.46 | 266.38 | 420.09 | 420.09 | 361.39 | 31 | 1.3 | 152.47 | 24 |  |  | 0.3 | [5 empty] | 708.25 | 11.35 | 0.51 | 0.47
97 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN020 | 1S-DL-YP-ETC-DKRN-2102-GAN020 | KOTHI BHAGWAN DASS (INSIDE):ID | TG-GAN020A-1 | 19506646 | 990 | 320 | 241 | 0.98 | 739 | 199 | 824 | 284 | 1195 | 256 | 1084 | 330 | 2019-06-02 12:30 | 178.2 | -1.3 | 1687 | B | 77 | 103 | 121 | 44 | 68.5 | 17.4 | 13.8 | 0.4 | 437.02 | 430.32 | 423.32 | 432.02 | 58.46 | 31.21 | 31.21 | 32.21 | 207.28 | 239.53 | 234.28 | 238.53 |  | 1.3 | 15.25 |  |  |  | 0.3 |  | 703.16 | 16.44 | 0.35 | 0.75
98 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN021 | 1S-DL-YP-ETC-DKRN-2102-GAN021 | MAHILA COLONY:K | TG-GAN021A-1 | 19506793 | 990 | 320 | 245 | 0.97 | 645 | 186 | 766 | 220 | 899 | 238 | 992 | 197 | 2019-06-01 12:00 | 168.6 | 5.1 | 1007 | B | 97 | 100 | 103 | 6 | 0.2 | 3.1 | 83.8 | 12.8 | 329 | 369 | 392 | 381.3 | 207.3 | 112 | 112 | 98 | 168.46 | 224.16 | 241.46 | 225.46 | [8 empty] | 705.16 | 14.44 | 0.42 | 0.65
99 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN021 | 1S-DL-YP-ETC-DKRN-2102-GAN021 | MAHILA COLONY:K | TG-GAN021A-2 | 19506874 | 990 | 320 | 245 | 0.95 | 639 | 237 | 975 | 202 | 826 | 200 | 827 | 149 | 2019-06-01 12:00 | 187.2 | 44.5 | 975 | R | 92 | 112 | 96 | 20 | 0.2 |  | 15.4 | 84.3 | 47 |  | 27 | 10 | 423.57 | 386.27 | 386.27 | 444.27 | 234.21 | 318.51 | 234.21 | 250.51 | [8 empty] | 705.18 | 14.42 | 0.57 | 0.65
100 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN022 | 1S-DL-YP-ETC-DKRN-2102-GAN022 | NEHRU GALI:PL | TG-GAN022A-1 | 19504382 | 2000 | 640 | 245 | 0.99 | 1400 | 504 | 2114 | 432 | 1790 | 463 | 1912 | 283 | 2019-06-30 14:30 | 191.4 | -4.4 | 2114 | R | 109 | 93 | 98 | 16 |  | 0.1 | 51 | 48.9 | 451.04 | 455.52 | 449.22 | 452.22 | 34.48 | 43 | 43 | 40.3 | 231.27 | 218.27 | 214.57 | 224.27 | [8 empty] | 717.19 | 2.41 | 0.29 | 0.7
101 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN023 | 1S-DL-YP-ETC-DKRN-2102-GAN023 | PEEPAL WALA SCHOOL:PL | TG-GAN023A-1 | 19506794 | 990 | 320 | 245 | 0.98 | 811 | 275 | 1127 | 259 | 1061 | 276 | 1132 | 68 | 2019-06-02 12:00 | 167.4 | -12.8 | 1236 | R | 106 | 100 | 95 | 11 | 0.1 |  | 11.3 | 88.7 | 43.21 | 241.51 | 192.21 | 142.51 | 380.55 | 180.25 | 180.25 | 285.55 | 270.48 | 260.25 | 269.48 | 274.48 | 10 | 22.23 | 2 | 1.3 |  |  |  |  | 705.04 | 14.56 | 0.48 | 0.82
102 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN023 | 1S-DL-YP-ETC-DKRN-2102-GAN023 | PEEPAL WALA SCHOOL:PL | TG-GAN023A-2 | 19506795 | 630 | 200 | 244 | 0.96 | 575 | 302 | 1283 | 127 | 525 | 146 | 597 | 725 | 2019-06-02 17:30 | 174 | 5.6 | 1283 | R | 117 | 92 | 92 | 25 | 0.1 |  | 13 | 86.9 | 275.51 | 367.21 | 356.21 | 340.21 | 140 | 71.3 | 71.3 | 88.3 | 241.11 | 266.03 | 261.09 | 275.03 | 47.22 |  |  | 1 | 0.3 |  | 0.24 |  | 704.54 | 15.06 | 0.37 | 0.91
103 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN024 | 1S-DL-YP-ETC-DKRN-2102-GAN024 | R. PURA GALI NO. 8:PL | TG-GAN024A-1 | 19506002 | 990 | 320 | 245 | 0.96 | 920 | 300 | 1229 | 311 | 1286 | 309 | 1279 | 54 | 2019-06-02 15:30 | 227.5 | 57 | 1425 | Y | 91 | 110 | 99 | 19 |  | 1 | 83.5 | 15.5 | 2.3 | 1 | 6 | 1 | 336.51 | 252.21 | 252.21 | 285.21 | 353.44 | 300.15 | 372.06 | 367.35 | 11 | 149.29 | 47.08 | 50.09 |  | 1 |  |  | 704.05 | 15.55 | 0.55 | 0.93
104 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN025 | 1S-DL-YP-ETC-DKRN-2102-GAN025 | R.PURA GALI NO 6 (IN SIDE):PL | TG-GAN025A-1 | 19506600 | 990 | 320 | 238 | 0.97 | 1025 | 333 | 1403 | 335 | 1423 | 356 | 1516 | 105 | 2019-06-01 12:30 | 270.7 | 1.3 | 1574 | B | 96 | 101 | 103 | 7 | 0.1 | 0.1 | 66.3 | 33.5 | 96.51 | 42.21 | 87.51 | 71.51 | 279.21 | 316.21 | 316.21 | 296.51 | 173 | 176.24 | 116.28 | 148.58 | 151.44 | 167.2 | 200.16 | 185.46 | 4 | 2.3 | 17.3 | 1.3 | 704.56 | 15.04 | 0.48 | 1.03
105 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN028 | 1S-DL-YP-ETC-DKRN-2102-GAN028 | SEELAMPUR OLD PR. SCHOOL NO. 1:K | TG-GAN028A-1 | 19505116 | 990 | 320 | 242 | 0.98 | 907 | 310 | 1292 | 305 | 1288 | 292 | 1244 | 46 | 2019-06-02 16:30 | 191.7 | 45.1 | 1359 | B | 93 | 113 | 94 | 20 | 16.9 | 4.3 | 77.6 | 1.2 |  |  |  |  | 27.3 | 0.3 | 0.3 | 9.3 | 657.2 | 643.5 | 660.2 | 672.5 | 19.59 | 60.29 | 17.59 | 22.29 |  |  |  |  | 704.49 | 15.11 | 0.64 | 0.92
106 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN028 | 1S-DL-YP-ETC-DKRN-2102-GAN028 | SEELAMPUR OLD PR. SCHOOL NO. 1:K | TG-GAN028A-2 | 19505099 | 990 | 320 | 236 | 0.98 | 823 | 321 | 1413 | 252 | 1112 | 250 | 1105 | 304 | 2019-06-01 16:30 | 162.2 | 32.6 | 1456 | R | 114 | 89 | 97 | 25 |  |  | 29.3 | 70.7 |  | 1 |  |  | 15.39 | 287.57 | 287.57 | 92.27 | 638.28 | 398.4 | 627.36 | 600.4 | 47.3 | 16 |  | 10.3 | 2 |  |  |  | 703.37 | 16.23 | 0.64 | 0.83
107 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN028 | 1S-DL-YP-ETC-DKRN-2102-GAN028 | SEELAMPUR OLD PR. SCHOOL NO. 1:K | TG-GAN028A-3 | 19505100 | 630 | 200 | 248 | 0.98 | 492 | 245 | 1028 | 97 | 396 | 149 | 611 | 556 | 2019-06-18 01:30 | 134.6 | 12.8 | 1028 | R | 98 | 78 | 124 | 46 | 0.4 | 8.7 | 85.6 | 5.3 |  | 9.3 |  |  | 211.4 | 490.39 | 490.39 | 216.11 | 489.29 | 201.51 | 576.53 | 486.19 | 0.51 |  | 50.2 |  | 0.3 | 0.3 | 1.3 |  | 702.3 | 17.3 | 0.59 | 0.78
108 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN028 | 1S-DL-YP-ETC-DKRN-2102-GAN028 | SEELAMPUR OLD PR. SCHOOL NO. 1:K | TG-GAN028A-4 | 19505119 | 990 | 320 | 243 | 0.97 | 683 | 230 | 965 | 230 | 957 | 222 | 934 | 28 | 2019-06-26 11:30 | 173.8 | 20.8 | 1137 | Y | 91 | 104 | 105 | 14 |  | 0.1 | 53.4 | 46.4 | 126.19 | 44 | 8.3 | 50.49 | 316.29 | 333.49 | 333.49 | 350.59 | 262.34 | 327.03 | 343.33 | 303.34 |  | 0.3 | [6 empty] | 705.22 | 14.38 | 0.58 | 0.69
109 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN029 | 1S-DL-YP-ETC-DKRN-2102-GAN029 | SEELAMPUR PHATAK:PL | TG-GAN029A-1 | 19506480 | 990 | 320 | 241 | 0.99 | 965 | 292 | 1292 | 360 | 1583 | 313 | 1399 | 255 | 2019-06-29 15:00 | 159.4 | 23.4 | 1583 | Y | 105 | 95 | 100 | 10 | 0.1 | 0.3 | 50 | 49.6 |  |  |  |  | 4.56 | 71.56 | 71.56 | 13.3 | 466.57 | 405.24 | 416.35 | 470.36 | 52.46 | 46.2 | 60.34 | 40.33 |  | 0.59 |  |  | 524.39 | 51.21 | 0.61 | 0.97
110 | 2019-06-25 11:30 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN029 | 1S-DL-YP-ETC-DKRN-2102-GAN029 | SEELAMPUR PHATAK:PL | TG-GAN029A-2 | 19505653 | 630 | 200 | 245.1083 | 0.99127 | 384.1368 | 85.2976 | 347.3878 | 165.7628 | 681.9271 | 133.0764 | 542.3719 | 291.0421 | 2019-06-28 18:00 | [15 empty] | 0 |  |  |  | 59 |  |  |  | 71 |  |  |  | 0 |  |  |  | 0 | 130 |  | 0.68894 | 0.60974
111 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN032 | 1S-DL-YP-ETC-DKRN-2102-GAN032 | SHIV KUTI R.L.G. NO. 1:ID | TG-GAN032A-1 | 19502033 | 990 | 320 | 235 | 0.96 | 658 | 227 | 989 | 197 | 850 | 235 | 1020 | 156 | 2019-06-01 12:30 | 181.1 | 8.1 | 1108 | B | 102 | 82 | 116 | 34 |  | 0.1 | 37 | 62.9 | 397.24 | 424.49 | 362.54 | 400.23 | 67.25 | 120.16 | 120.16 | 66.56 | 254.22 | 174.06 | 266.52 | 251.52 | [8 empty] | 719.11 | 0.49 | 0.43 | 0.67
112 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN032 | 1S-DL-YP-ETC-DKRN-2102-GAN032 | SHIV KUTI R.L.G. NO. 1:ID | TG-GAN032A-2 | 19506574 | 990 | 320 | 243 | 0.97 | 863 | 262 | 1107 | 311 | 1312 | 289 | 1215 | 178 | 2019-06-30 16:00 | 239.7 | -17.9 | 1769 | Y | 93 | 108 | 99 | 15 | 0.2 | 0.1 | 29.7 | 69.9 | 439.23 | 416.23 | 412.23 | 416.23 | 36.3 | 38 | 38 | 40 | 218.47 | 144.03 | 211.05 | 214.35 | 10.3 | 105.44 | 41.12 | 34.12 |  | 1 |  |  | 705.1 | 14.5 | 0.36 | 0.87
113 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN032 | 1S-DL-YP-ETC-DKRN-2102-GAN032 | SHIV KUTI R.L.G. NO. 1:ID | TG-GAN032A-3 | 19505443 | 990 | 320 | 243 | 0.98 | 692 | 270 | 1133 | 214 | 898 | 208 | 865 | 253 | 2019-06-02 16:00 | 150.4 | -18.9 | 1196 | R | 116 | 96 | 88 | 28 | 0.1 | 0.2 | 11.4 | 88.3 | 372.25 | 406.24 | 407.24 | 392.54 | 63.59 | 60 | 60 | 60 | 259.32 | 237.32 | 233.38 | 251.02 | 8 | [7 empty] | 703.56 | 16.04 | 0.42 | 0.7
114 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN032 | 1S-DL-YP-ETC-DKRN-2102-GAN032 | SHIV KUTI R.L.G. NO. 1:ID | TG-GAN032A-4 | 19505384 | 990 | 320 | 242 | 0.97 | 1009 | 329 | 1389 | 375 | 1585 | 305 | 1291 | 259 | 2019-06-02 12:00 | 242.6 | 5.1 | 1585 | Y | 97 | 107 | 96 | 11 | 0.1 | 0.1 | 5.3 | 94.5 | 23.3 | 8.3 | 11 | 8 | 342.23 | 333.54 | 333.54 | 352.54 | 172.24 | 128.38 | 213.44 | 154.03 | 166.08 | 189.53 | 126.18 | 188.58 |  | 43.3 |  | 0.3 | 704.25 | 15.35 | 0.52 | 1.02
115 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN032 | 1S-DL-YP-ETC-DKRN-2102-GAN032 | SHIV KUTI R.L.G. NO. 1:ID | TG-GAN032A-5 | 19505393 | 990 | 320 | 239 | 0.98 | 666 | 192 | 822 | 271 | 1156 | 203 | 870 | 313 | 2019-06-02 12:00 | 150.4 | -29.8 | 1185 | Y | 93 | 112 | 95 | 19 | 0.1 |  | 23.1 | 76.8 | 354.27 | 335.57 | 332.27 | 342.27 | 97.35 | 77.29 | 77.29 | 79.29 | 253.02 | 288.4 | 272.08 | 283.08 |  | 2.58 | [6 empty] | 705.04 | 14.56 | 0.48 | 0.67
116 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN032 | 1S-DL-YP-ETC-DKRN-2102-GAN032 | SHIV KUTI R.L.G. NO. 1:ID | TG-GAN032A-6 | 19505140 | 990 | 320 | 245 | 0.97 | 795 | 276 | 1160 | 215 | 902 | 304 | 1281 | 335 | 2019-06-26 16:00 | 242.9 | -0.3 | 1328 | R | 103 | 84 | 114 | 30 | 0.1 | 0.1 | 11.5 | 88.2 | 401.27 | 414.27 | 382.58 | 399.27 | 43.3 | 50 | 50 | 46 | 222.5 | 241.5 | 182.52 | 259.2 | 38.3 |  | 88.58 | 1.3 |  |  |  |  | 706.17 | 13.43 | 0.4 | 0.8
117 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN032 | 1S-DL-YP-ETC-DKRN-2102-GAN032 | SHIV KUTI R.L.G. NO. 1:ID | TG-GAN032A-7 | 19505967 | 630 | 200 | 239 | 0.97 | 284 | 64 | 274 | 104 | 442 | 116 | 492 | 198 | 2019-06-02 12:00 | 67.6 | -1.2 | 496 | B | 85 | 97 | 118 | 33 |  |  | 6 | 94 | 426.03 | 386.58 | 371.27 | 394.27 | 273.51 | 290.26 | 290.26 | 281.27 | 6 | 28.3 | 162.28 | 30 | [8 empty] | 705.54 | 14.06 | 0.47 | 0.45
118 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN033 | 1S-DL-YP-ETC-DKRN-2102-GAN033 | SUBHASH MOHALLA NO.1:PM | TG-GAN033A-1 | 19505968 | 990 | 320 | 237 | 0.96 | 707 | 230 | 994 | 232 | 999 | 245 | 1047 | 51 | 2019-06-30 16:30 | 198.7 | 14.4 | 1273 | B | 94 | 92 | 114 | 22 | 0.1 | 0.1 | 9.4 | 90.5 | 229.02 | 292.32 | 95.56 | 220.5 | 205.09 | 140.48 | 140.48 | 201 | 267.43 | 268.34 | 272.34 | 280.04 |  |  | 22.27 | [5 empty] | 701.54 | 18.06 | 0.5 | 0.71
119 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN033 | 1S-DL-YP-ETC-DKRN-2102-GAN033 | SUBHASH MOHALLA NO.1:PM | TG-GAN033A-2 | 19505124 | 990 | 320 | 243 | 0.98 | 855 | 301 | 1242 | 294 | 1208 | 260 | 1056 | 172 | 2019-06-01 18:00 | 215.7 | 10.6 | 1265 | Y | 107 | 103 | 90 | 17 | 0.1 | 0.8 | 83.7 | 15.4 | 0.1 | 3 | 24.38 | 1.1 | 316.24 | 379.09 | 379.09 | 381.01 | 341.54 | 239 | 281.12 | 288.58 | 40.36 | 77.55 | 6.27 | 27.55 |  |  |  |  | 699.04 | 20.56 | 0.54 | 0.86
120 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN033 | 1S-DL-YP-ETC-DKRN-2102-GAN033 | SUBHASH MOHALLA NO.1:PM | TG-GAN033A-3 | 19506659 | 990 | 320 | 242 | 0.96 | 863 | 268 | 1125 | 294 | 1245 | 300 | 1269 | 133 | 2019-06-01 12:00 | 245.1 | 0.6 | 1304 | B | 99 | 98 | 103 | 5 |  | 0.1 | 27.9 | 72 | 167.29 | 231.12 | 141.47 | 178.42 | 220.56 | 164.13 | 164.13 | 211.43 | 295.03 | 237.03 | 248.15 | 267.52 | 18.28 | 69.28 | 66.16 | 43.39 |  |  |  |  | 701.56 | 18.04 | 0.49 | 0.87
121 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN033 | 1S-DL-YP-ETC-DKRN-2102-GAN033 | SUBHASH MOHALLA NO.1:PM | TG-GAN033A-4 | 19505135 | 990 | 320 | 243 | 0.97 | 926 | 298 | 1237 | 323 | 1337 | 305 | 1271 | 89 | 2019-06-23 15:30 | 202.6 | 28.8 | 1447 | R | 98 | 102 | 100 | 4 |  | 0.1 | 8.9 | 91 |  |  |  |  | 267.03 | 129.18 | 129.18 | 215.33 | 409.48 | 575.42 | 453.59 | 483.48 | 28.36 | 0.57 | 9.39 | 6.36 | 0.3 |  |  |  | 705.57 | 14.03 | 0.53 | 0.94
122 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN034 | 1S-DL-YP-ETC-DKRN-2102-GAN034 | AJIT NAGAR GALI NO 10:PL | TG-GAN034A-1 | 19506811 | 990 | 320 | 231 | 0.98 | 757 | 273 | 1137 | 270 | 1127 | 214 | 894 | 239 | 2019-06-29 22:00 | 194.6 | 51.2 | 1204 | R | 107 | 103 | 90 | 17 |  |  | 2.5 | 97.5 |  |  |  |  | 4 | 14.59 | 14.59 | 13.29 | 697.41 | 686.12 | 664.5 | 691.12 | 3 | 3.3 | [6 empty] | 704.41 | 15.19 | 0.74 | 0.76
123 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN034 | 1S-DL-YP-ETC-DKRN-2102-GAN034 | AJIT NAGAR GALI NO 10:PL | TG-GAN034A-2 | 19505987 | 990 | 320 | 232 | 0.98 | 826 | 327 | 1403 | 366 | 1518 | 132 | 539 | 926 | 2019-06-08 03:30 | 244.8 | 33 | 1518 | Y | 91 | 97 | 112 | 21 | 0.1 | 0.1 | 37.8 | 62 |  |  |  |  | 428.13 | 362.49 | 362.49 | 236.44 | 276.05 | 341.29 | 579.3 | 467.34 | 0.3 |  |  | 0.3 |  | 0.3 |  |  | 704.48 | 15.12 | 0.51 | 0.83
124 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN036 | 1S-DL-YP-ETC-DKRN-2102-GAN036 | KOTHI BHAGWAN DAS OUTSIDE:PL | TG-GAN036A-1 | 19506539 | 990 | 320 | 244 | 0.99 | 1099 | 397 | 1665 | 353 | 1501 | 349 | 1470 | 182 | 2019-06-02 16:00 | 207.7 | -2.6 | 1971 | B | 97 | 100 | 103 | 6 | 0.3 | 0.2 | 37.9 | 61.6 | 366.28 | 367.47 | 361.09 | 365.28 | 64.08 | 63.26 | 63.26 | 67.38 | 107.01 | 106.3 | 106.57 | 105.37 | 123.18 | 98.42 | 120.07 | 124.08 | 42.4 | 67.1 | 35.55 | 40.44 | 703.35 | 16.25 | 0.35 | 1.11
125 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN037 | 1S-DL-YP-ETC-DKRN-2102-GAN037 | R.PURA GALI NO 6 (OUTSIDE):PM | TG-GAN037A-1 | 19506347 | 630 | 200 | 246 | 0.96 | 466 | 155 | 627 | 141 | 571 | 170 | 683 | 97 | 2019-06-26 16:30 | 164.6 | 6.6 | 712 | B | 110 | 79 | 111 | 32 | 0.2 |  | 35.6 | 64.2 | 50.51 | 318.21 | 80.21 | 146.51 | 351.3 | 147.25 | 147.25 | 264.27 | 292.36 | 230.11 | 308.39 | 284.39 | 1 |  | 4 | [5 empty] | 695.57 | 24.03 | 0.5 | 0.74
126 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN039 | 1S-DL-YP-ETC-DKRN-2102-GAN039 | CHANDER PURI | TG-GAN039A-1 | 19506437 | 990 | 320 | 231 | 0.97 | 619 | 206 | 913 | 203 | 887 | 209 | 924 | 33 | 2019-06-02 16:00 | 197.4 | 46.4 | 997 | B | 101 | 93 | 106 | 13 |  |  | 77.5 | 22.5 |  |  |  |  | 157.33 | 215.09 | 215.09 | 136.13 | 533.5 | 476.14 | 616.25 | 555.1 | [8 empty] | 691.23 | 28.37 | 0.73 | 0.63
127 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN040 | 1S-DL-YP-ETC-DKRN-2102-GAN040 | GYAN MOHLLA | TG-GAN040A-1 | 19502011 | 990 | 320 | 237 | 0.98 | 924 | 327 | 1448 | 313 | 1373 | 284 | 1256 | 168 | 2019-06-01 16:30 | 193.6 | 25 | 1477 | R | 112 | 102 | 86 | 26 |  | 0.1 | 33 | 66.8 | 3.3 | 110.3 | 260 | 75.3 | 394 | 302.3 | 302.3 | 344.59 | 176.44 | 180.58 | 269.37 | 208.29 | 143.22 | 125.08 | 7.3 | 90.08 | 1.3 |  |  |  | 719.06 | 0.54 | 0.47 | 0.93
128 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN041 | 1S-DL-YP-ETC-DKRN-2102-GAN041 | TAGORE GALI | TG-GAN041A-1 | 19506862 | 990 | 320 | 238 | 0.96 | 686 | 226 | 962 | 210 | 900 | 249 | 1067 | 147 | 2019-06-30 16:00 | 179.8 | 6.7 | 1220 | B | 101 | 97 | 102 | 5 | 0.1 | 0.1 | 24.3 | 75.5 | 408 | 402.3 | 393 | 403 | 55 | 70.3 | 70.3 | 61.3 | 242.03 | 232.03 | 244.03 | 240.33 | [8 empty] | 705.03 | 14.57 | 0.41 | 0.69
129 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN041 | 1S-DL-YP-ETC-DKRN-2102-GAN041 | TAGORE GALI | TG-GAN041A-2 | 19506030 | 630 | 200 | 239 | 0.96 | 416 | 165 | 703 | 120 | 506 | 131 | 548 | 180 | 2019-06-27 16:00 | 141.6 | 6 | 708 | R | 117 | 89 | 94 | 28 | 0.3 | 5.2 | 38.8 | 55.6 | 309.3 | 378.3 | 394.3 | 377 | 136 | 122.53 | 122.53 | 82.3 | 259.44 | 203.51 | 236.51 | 245.44 | [8 empty] | 705.14 | 14.46 | 0.44 | 0.66
130 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN042 | 1S-DL-YP-ETC-DKRN-2102-GAN042 | SEELAM PUR PULIA | TG-GAN042A-1 | 19505456 | 990 | 320 | 234 | 0.99 | 341 | 111 | 479 | 84 | 362 | 146 | 631 | 234 | 2019-06-01 11:00 | 42.9 | 1.9 | 732 | B | 87 | 81 | 132 | 51 | 24 | 0.3 | 36.7 | 39 | 452.35 | 551.18 | 154.08 | 357.35 | 262.49 | 164.06 | 164.06 | 357.49 |  |  | 21.26 | [9 empty] | 715.24 | 4.36 | 0.59 | 0.34
131 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN042 | 1S-DL-YP-ETC-DKRN-2102-GAN042 | SEELAM PUR PULIA | TG-GAN042A-2 | 19505098 | 630 | 200 | 228 | 0.99 | 432 | 142 | 587 | 153 | 643 | 137 | 575 | 63 | 2019-06-30 12:00 | 63 | 7.2 | 747 | Y | 93 | 108 | 99 | 15 |  | 8.8 | 73.7 | 17.5 | 0.3 |  |  |  | 423.58 | 291.33 | 291.33 | 352 | 292.2 | 425.15 | 390.44 | 364.48 | [8 empty] | 716.48 | 3.12 | 0.62 | 0.69
132 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN045 | 1S-DL-YP-ETC-DKRN-2102-GAN045 | SJ/STN RATTEY WALA SUBHASH MOHALLA | TG-GAN045A-1 | 19506863 | 990 | 320 | 236 | 0.97 | 840 | 253 | 1056 | 297 | 1258 | 289 | 1225 | 187 | 2019-06-02 16:30 | 205.8 | 9.3 | 1521 | Y | 93 | 111 | 96 | 18 | 0.4 | 1.1 | 71.9 | 26.7 | 377.25 | 332.55 | 380.38 | 361.55 | 53.33 | 78.22 | 78.22 | 65.03 | 270.3 | 231.41 | 259 | 272.3 | 4.3 | 62.3 | 7 | 6.3 |  | 0.3 |  |  | 705.58 | 14.02 | 0.41 | 0.85
133 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL001 | 1S-DL-YP-ETC-DKRN-2103-GCL001 | 9BLK, GEETA CLY:K | TG-GCL001A-1 | 19505050 | 990 | 320 | 242 | 0.97 | 495 | 181 | 778 | 166 | 715 | 148 | 629 | 130 | 2019-06-06 | 90.5 | 40.5 | 930 | R | 121 | 85 | 94 | 36 |  | 1.9 | 97.9 | 0.2 | 18.3 | 150.23 | 36.58 | 36.58 | 471.44 | 537.34 | 537.34 | 573.29 | 229.13 | 31.3 | 54 | 109 | [8 empty] | 719.27 | 0.33 | 0.6 | 0.5
134 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL001 | 1S-DL-YP-ETC-DKRN-2103-GCL001 | 9BLK, GEETA CLY:K | TG-GCL001A-2 | 19506607 | 990 | 320 | 241 | 0.97 | 552 | 221 | 1021 | 169 | 737 | 162 | 752 | 276 | 2019-06-11 01:00 | 142.7 | 36.2 | 1021 | R | 83 | 108 | 108 | 25 | 0.2 | 0.1 | 70.7 | 29 | 12.58 | 4.3 |  | 1 | 686.47 | 492.45 | 492.45 | 561.45 | 5.43 | 208.13 | 228.13 | 142.43 | [8 empty] | 705.28 | 14.32 | 0.61 | 0.56
135 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL002 | 1S-DL-YP-ETC-DKRN-2103-GCL002 | ALOK BHARTI | TG-GCL002A-1 | 19503703 | 990 | 320 | 232 | 0.98 | 941 | 376 | 1596 | 307 | 1293 | 259 | 1081 | 448 | 2019-06-30 | 159 | 62.6 | 1671 | R | 120 | 93 | 87 | 33 |  | 5.1 | 74.5 | 20.4 | [5 empty] | 16.3 | 16.3 | 6 | 486.47 | 679.58 | 680.28 | 664.58 | 206.11 | 22 | 2 | 47.3 | 25.3 |  |  |  | 718.28 | 1.32 | 0.66 | 0.95
136 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL003 | 1S-DL-YP-ETC-DKRN-2103-GCL003 | AMBEDKAR COLLEGE:PM | TG-GCL003A-1 | 19505048 | 630 | 200 | 244 | 0.98 | 287 | 86 | 342 | 73 | 291 | 128 | 508 | 197 | 2019-06-11 03:00 | 61.6 | 20.7 | 514 | B | 94 | 81 | 125 | 44 |  |  | 0.5 | 99.5 | 5 | 15.3 |  | 2.3 | 623.56 | 704.26 | 704.26 | 554.28 | 91 |  | 500.26 | 162.58 | [8 empty] | 719.56 | 0.04 | 0.77 | 0.46
137 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL004 | 1S-DL-YP-ETC-DKRN-2103-GCL004 | B.T.S MULTANI MOHOLLA:PL | TG-GCL004A-1 | 19505189 | 990 | 320 | 240 | 0.97 | 639 | 226 | 945 | 268 | 1115 | 146 | 611 | 445 | 2019-06-30 16:30 | 193 | 58.9 | 1498 | R | 107 | 130 | 62 | 68 | 0.3 |  | 63 | 36.7 |  |  | 113.55 |  | 143.48 | 29.52 | 29.52 | 213.18 | 561.01 | 670.31 | 46.3 | 492.01 | 0.3 | 4.56 | [6 empty] | 705.19 | 14.41 | 0.69 | 0.65
138 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL004 | 1S-DL-YP-ETC-DKRN-2103-GCL004 | B.T.S MULTANI MOHOLLA:PL | TG-GCL004A-2 | 19506538 | 400 | 120 | 240 | 0.98 | 324 | 163 | 736 | 74 | 317 | 88 | 382 | 391 | 2019-06-05 | 77.4 | 14.8 | 736 | R | 94 | 97 | 109 | 15 | 0.6 | 3.4 | 81 | 15 |  |  |  |  | 129.18 | 141.28 | 141.28 | 56.23 | 568.31 | 547.29 | 634.24 | 647.56 | 6.3 | 15.52 | 28 | 1 | 1 | 0.3 | 0.3 |  | 705.19 | 14.41 | 0.66 | 0.81
139 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL005 | 1S-DL-YP-ETC-DKRN-2103-GCL005 | JHEEL (BHOOSA MANDI):PL | TG-GCL005A-1 | 19506909 | 990 | 320 | 242 | 0.98 | 880 | 251 | 1048 | 348 | 1451 | 281 | 1183 | 355 | 2019-06-27 | 183.4 | 25 | 1451 | Y | 91 | 108 | 101 | 17 | 0.6 | 0.3 | 60.7 | 38.4 |  | 1.3 | 1.3 |  | 208.3 | 71.3 | 71.3 | 98 | 499.21 | 601.51 | 594.51 | 602.21 | 0.3 | 30.3 | 5.3 | 8 |  | 3 |  |  | 708.21 | 11.39 | 0.56 | 0.89
140 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL005 | 1S-DL-YP-ETC-DKRN-2103-GCL005 | JHEEL (BHOOSA MANDI):PL | TG-GCL005A-2 | 19505932 | 400 | 120 | 242 | 0.97 | 443 | 165 | 695 | 85 | 359 | 193 | 826 | 418 | 2019-06-12 00:30 | 99.6 | 14.6 | 896 | B | 104 | 69 | 127 | 58 | 0.2 | 3.9 | 79.3 | 16.6 |  | 15.3 |  |  | 193.38 | 371.26 | 371.26 | 195.59 | 382.45 | 320.55 | 394.01 | 412.52 | 93.58 | 0.3 | 121.51 | 79.3 | 38 |  | 109 | 20 | 708.21 | 11.39 | 0.51 | 1.11
141 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL007 | 1S-DL-YP-ETC-DKRN-2103-GCL007 | DARBAR MARG:K | TG-GCL007A-1 | 19503706 | 630 | 200 | 243 | 0.99 | 344 | 125 | 523 | 86 | 357 | 132 | 559 | 187 | 2019-06-26 01:00 | 59.3 | -6.9 | 565 | B | 114 | 75 | 112 | 39 |  | 0.1 | 70.8 | 29.2 | 30.3 | 326.29 | 22 | 82 | 554.21 | 376.22 | 376.22 | 585.21 | 135 | 17 | 129.55 | 52.3 | [8 empty] | 719.51 | 0.09 | 0.53 | 0.55
142 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL008 | 1S-DL-YP-ETC-DKRN-2103-GCL008 | EKTA APARTMENTS:ID | TG-GCL008A-1 | 19501458 | 400 | 120 | 246 | 0.97 | 67 | 31 | 124 | 24 | 101 | 12 | 48 | 67 | 2019-06-10 01:30 | 14.4 | 0.6 | 146 | R | 147 | 108 | 45 | 102 | 43.6 | 56.4 |  |  | 642.28 | 718.28 | 719.58 | 719.58 | 77.3 | 1.3 | 1.3 | [13 empty] | 719.58 | 0.02 | 0.49 | 0.17
143 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL008 | 1S-DL-YP-ETC-DKRN-2103-GCL008 | EKTA APARTMENTS:ID | TG-GCL008A-2 | 19501457 | 400 | 120 | 245 | 0.97 | 92 | 34 | 144 | 25 | 106 | 34 | 142 | 37 | 2019-06-29 23:30 | 22.4 | 1.7 | 160 | B | 93 | 90 | 116 | 26 |  |  | 48.1 | 51.9 | 677.27 | 713.27 | 566.57 | 678.27 | 42.3 | 6.3 | 6.3 | 41.3 | [12 empty] | 719.57 | 0.03 | 0.49 | 0.23
144 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL009 | 1S-DL-YP-ETC-DKRN-2103-GCL009 | GANDHI NGR PRIMARY SCHOOL:PL | TG-GCL009A-1 | 19504802 | 990 | 320 | 241 | 0.98 | 673 | 192 | 816 | 241 | 995 | 240 | 995 | 179 | 2019-06-29 16:30 | 122.2 | 22.1 | 1133 | Y | 89 | 110 | 101 | 21 | 66.2 | 33.8 |  |  | 2 | 1.3 | 1 |  | 393.1 | 212.26 | 212.26 | 289.59 | 319.39 | 500.53 | 413.5 | 424.5 | [8 empty] | 714.49 | 5.11 | 0.64 | 0.68
145 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL010 | 1S-DL-YP-ETC-DKRN-2103-GCL010 | GEETA APPT.S/STAT.NO.1:ID | TG-GCL010A-1 | 19506508 | 400 | 120 | 246 | 0.93 | 89 | 38 | 160 | 21 | 89 | 29 | 122 | 61 | 2019-06-02 23:30 | 32.9 | 4 | 206 | Y | 108 | 83 | 109 | 26 | 0.2 | 0.1 | 18.2 | 81.5 | 666.58 | 692.58 | 676.58 | 692.58 | 29.3 | 3.3 | 3.3 | 3.3 | [12 empty] | 696.28 | 23.32 | 0.5 | 0.22
146 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL010 | 1S-DL-YP-ETC-DKRN-2103-GCL010 | GEETA APPT.S/STAT.NO.1:ID | TG-GCL010A-2 | 19501288 | 400 | 120 | 254 | 0.98 | 139 | 37 | 150 | 41 | 171 | 61 | 232 | 73 | 2019-06-06 | 25.4 | 3.6 | 239 | B | 72 | 101 | 127 | 55 | 100 |  |  |  | 641.56 | 473.26 | 273.26 | 478.26 | 78 | 246.3 | 246.3 | 241.3 |  |  | 42 | [9 empty] | 719.56 | 0.04 | 0.52 | 0.35
147 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL011 | 1S-DL-YP-ETC-DKRN-2103-GCL011 | GEETA COLONY, 14 BLK:ID | TG-GCL011A-1 | 19505719 | 990 | 320 | 233 | 0.97 | 955 | 290 | 1294 | 224 | 1043 | 440 | 2230 | 1084 | 2019-06-11 01:00 | 251.2 | 65 | 2230 | B | 107 | 87 | 106 | 20 | 0.5 | 0.2 | 91.2 | 8.2 |  |  |  |  | 30.58 | 162.24 | 162.24 | 50 | 596.3 | 553.25 | 650.21 | 641.58 | 88.51 | 1 | 35.45 | 24.51 | 0.3 |  | 0.43 |  | 716.49 | 3.11 | 0.58 | 0.96
148 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL012 | 1S-DL-YP-ETC-DKRN-2103-GCL012 | GEETA COLONY, 16 BLK:ID | TG-GCL012A-1 | 19501601 | 630 | 200 | 240 | 0.97 | 372 | 131 | 565 | 107 | 462 | 134 | 580 | 112 | 2019-06-01 23:30 | 62.6 | 27.6 | 603 | R | 105 | 88 | 107 | 19 |  | 0.3 | 74.1 | 25.6 | 11.3 | 19.57 | 1 | 6.3 | 470.53 | 609.37 | 609.37 | 524.39 | 236.41 | 89.3 | 246.25 | 187.55 | [8 empty] | 719.04 | 0.56 | 0.59 | 0.59
149 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL012 | 1S-DL-YP-ETC-DKRN-2103-GCL012 | GEETA COLONY, 16 BLK:ID | TG-GCL012A-2 | 19500749 | 630 | 200 | 246.4307 | 0.97857 | 456.2784 | 144.5923 | 610.3515 | 171.4819 | 721.0576 | 140.2042 | 588.401 | 123.1573 | 2019-06-11 00:30 | [15 empty] | 5 |  |  |  | 439.5 |  |  |  | 275.5 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.54962 | 0.72425
150 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL012 | 1S-DL-YP-ETC-DKRN-2103-GCL012 | GEETA COLONY, 16 BLK:ID | TG-GCL012A-3 | 19503469 | 400 | 120 | 243 | 0.97 | 268 | 89 | 380 | 75 | 316 | 104 | 441 | 108 | 2019-06-08 16:00 | 62.9 | 27.3 | 488 | B | 92 | 97 | 112 | 20 | 0.1 |  | 3.2 | 96.7 |  |  |  |  | 219 | 151.59 | 151.59 | 87.3 | 499.36 | 566.37 | 682.06 | 631.06 |  |  | 1 | [5 empty] | 718.36 | 1.24 | 0.71 | 0.67
151 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL013 | 1S-DL-YP-ETC-DKRN-2103-GCL013 | GEETA COLONY,10, BLK:K | TG-GCL013A-1 | 19506174 | 990 | 320 | 244 | 0.97 | 566 | 182 | 752 | 204 | 840 | 180 | 739 | 95 | 2019-06-12 00:30 | 169.3 | 50.6 | 1185 | Y | 98 | 120 | 82 | 38 | 0.4 | 0.4 | 82.9 | 16.3 |  |  | 13 |  | 433.28 | 158 | 158 | 413.56 | 272.55 | 547.23 | 86.3 | 292.27 |  | 1 | [6 empty] | 706.23 | 13.37 | 0.68 | 0.57
152 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL013 | 1S-DL-YP-ETC-DKRN-2103-GCL013 | GEETA COLONY,10, BLK:K | TG-GCL013A-2 | 19505738 | 630 | 200 | 239 | 0.97 | 356 | 187 | 802 | 66 | 291 | 102 | 413 | 462 | 2019-06-12 | 104.2 | 23.2 | 846 | R | 129 | 68 | 103 | 61 | 99.9 | 0.1 |  |  | 4.3 | 443.57 | 28.3 | 47 | 490.27 | 275.58 | 275.58 | 578.25 | 217.58 |  | 119 | 94.3 | 7 | [7 empty] | 719.55 | 0.05 | 0.52 | 0.56
153 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL014 | 1S-DL-YP-ETC-DKRN-2103-GCL014 | GEETA COLONY,11, BLK:PL | TG-GCL014A-1 | 19502875 | 990 | 320 | 240 | 0.97 | 996 | 332 | 1381 | 293 | 1249 | 371 | 1587 | 296 | 2019-06-11 01:00 | 183.3 | 55.2 | 1587 | B | 102 | 106 | 92 | 14 | 99.7 | 0.3 | [6 empty] | 188.58 | 141.1 | 141.1 | 186.06 | 420.2 | 502.08 | 421.35 | 469.12 | 104.13 | 71.13 | 10.02 | 58.13 | 1 |  | 3.06 | 1 | 714.31 | 5.29 | 0.51 | 1.01
154 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL015 | 1S-DL-YP-ETC-DKRN-2103-GCL015 | GEETA COLONY,12, BLK:K | TG-GCL015A-1 | 19503665 | 990 | 320 | 236 | 0.97 | 754 | 267 | 1145 | 220 | 941 | 266 | 1131 | 197 | 2019-06-30 | 163.4 | 61.8 | 1196 | R | 115 | 83 | 101 | 32 | 0.1 | 6.7 | 78.8 | 14.5 |  |  |  |  | 12 | 351.22 | 351.22 | 95.59 | 703.22 | 368.3 | 607.23 | 623.53 | 4.3 |  | 4 | [5 empty] | 719.52 | 0.08 | 0.66 | 0.76
155 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL015 | 1S-DL-YP-ETC-DKRN-2103-GCL015 | GEETA COLONY,12, BLK:K | TG-GCL015A-2 | 19506809 | 630 | 120 | 237 | 0.98 | 556 | 102 | 433 | 168 | 726 | 286 | 1238 | 705 | 2019-06-29 23:30 | 131.4 | 38.3 | 1238 | B | 78 | 101 | 121 | 43 | 0.5 | 0.6 | 30.9 | 68.1 | 0.3 |  |  |  | 262.27 | 59.59 | 59.59 | 37 | 444.54 | 607.52 | 547.21 | 654.21 | 1.3 | 41.3 | 127 | 18 |  |  | 31 |  | 709.21 | 10.39 | 0.63 | 0.88
156 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL016 | 1S-DL-YP-ETC-DKRN-2103-GCL016 | GEETA COLONY,13, BLK:ID | TG-GCL016A-1 | 19506146 | 990 | 320 | 241 | 0.98 | 815 | 265 | 1147 | 280 | 1220 | 270 | 1166 | 65 | 2019-06-11 01:30 | 188.2 | 39 | 1445 | R | 95 | 103 | 101 | 8 | 0.3 | 0.1 | 66.9 | 32.7 |  | 0.3 |  |  | 327.41 | 273.53 | 273.53 | 298.43 | 364.12 | 413.3 | 390.15 | 394.1 | 1.51 | 5.51 | 7.51 | 0.51 |  |  |  |  | 693.44 | 26.16 | 0.55 | 0.82
157 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL016 | 1S-DL-YP-ETC-DKRN-2103-GCL016 | GEETA COLONY,13, BLK:ID | TG-GCL016A-2 | 19506110 | 990 | 320 | 241.4173 | 0.9853 | 1134.3448 | 322.5094 | 1425.3297 | 523.7515 | 2336.8203 | 288.0839 | 1253.5743 | 1008.399 | 2019-06-12 00:30 | [15 empty] | 0 |  |  |  | 202 |  |  |  | 421.5 |  |  |  | 76.5 |  |  |  | 16.5 | 716.5 |  | 0.46954 | 1.1458
158 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL016 | 1S-DL-YP-ETC-DKRN-2103-GCL016 | GEETA COLONY,13, BLK:ID | TG-GCL016A-3 | 19501569 | 990 | 200 | 234 | 0.97 | 793 | 289 | 1282 | 218 | 973 | 286 | 1289 | 312 | 2019-06-11 01:30 | 135.7 | 45.5 | 1289 | R | 109 | 82 | 109 | 27 |  | 0.7 | 89.7 | 9.6 | 1 | 20.28 |  |  | 291.5 | 485.31 | 485.31 | 372.34 | 411.59 | 210.13 | 431.07 | 343.26 | 11.23 |  | 7.5 | 0.12 |  |  |  |  | 716.12 | 3.48 | 0.54 | 0.8
159 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL016 | 1S-DL-YP-ETC-DKRN-2103-GCL016 | GEETA COLONY,13, BLK:ID | TG-GCL016A-4 | 19505933 | 630 | 120 | 235 | 0.97 | 497 | 205 | 890 | 140 | 596 | 152 | 648 | 271 | 2019-06-30 03:30 | 147.5 | 15.8 | 934 | R | 116 | 91 | 94 | 25 | 0.6 | 0.6 | 52.4 | 46.4 | 52.01 | 202.31 | 148.31 | 102.01 | 461.13 | 423 | 423 | 488.31 | 196.45 | 88.58 | 97.4 | 123.57 | 4.3 | [7 empty] | 714.29 | 5.31 | 0.39 | 0.79
160 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL017 | 1S-DL-YP-ETC-DKRN-2103-GCL017 | GEETA COLONY,15, BLK:PL | TG-GCL017A-1 | 19501030 | 990 | 320 | 240 | 0.98 | 521 | 197 | 850 | 129 | 547 | 195 | 833 | 295 | 2019-06-30 | 73.6 | 33.9 | 981 | R | 124 | 79 | 97 | 45 |  |  | 70.3 | 29.7 | 2.3 | 185.53 | 85.27 | 38.27 | 446.13 | 527.49 | 527.49 | 553.46 | 270.59 | 6 | 136.19 | 127.29 | [8 empty] | 719.42 | 0.18 | 0.59 | 0.53
161 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL017 | 1S-DL-YP-ETC-DKRN-2103-GCL017 | GEETA COLONY,15, BLK:PL | TG-GCL017A-2 | 19506379 | 630 | 200 | 240 | 0.98 | 666 | 200 | 902 | 292 | 1384 | 174 | 750 | 574 | 2019-06-11 01:00 | 195 | 34.8 | 1384 | Y | 105 | 91 | 104 | 14 | 0.4 | 0.7 | 63.2 | 35.7 |  |  |  |  | 201.57 | 300.31 | 300.31 | 233.01 | 424.04 | 401.2 | 488.2 | 444.5 | 71.2 | 2 | 31 | 26 | 7 | 0.3 | 0.3 | 0.3 | 704.21 | 15.39 | 0.47 | 1.06
162 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL018 | 1S-DL-YP-ETC-DKRN-2103-GCL018 | GEETA COLONY,17, BLK COM CENTRE:PL | TG-GCL018A-1 | 19505190 | 630 | 200 | 234 | 0.98 | 590 | 194 | 856 | 197 | 870 | 198 | 871 | 14 | 2019-06-30 00:30 | 91.2 | 23.2 | 927 | B | 96 | 116 | 88 | 28 | 0.1 | 0.2 | 10.7 | 88.9 | 1.3 |  | 39.3 |  | 302.41 | 126.44 | 126.44 | 286.08 | 388.2 | 526.33 | 299.36 | 393.23 | 10 | 49.14 | 16.3 | 23 |  |  | 0.3 |  | 702.31 | 17.29 | 0.49 | 0.94
163 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL018 | 1S-DL-YP-ETC-DKRN-2103-GCL018 | GEETA COLONY,17, BLK COM CENTRE:PL | TG-GCL018A-2 | 19506741 | 630 | 200 | 234 | 0.97 | 627 | 207 | 928 | 231 | 1037 | 188 | 843 | 168 | 2019-06-15 00:30 | 130 | 15.2 | 1037 | Y | 103 | 108 | 89 | 19 | 0.1 |  | 3.8 | 96.1 | 200.03 | 126.19 | 134.28 | 135.34 | 326.05 | 396.49 | 396.49 | 420.34 | 166.24 | 170.54 | 74.36 | 141.5 | 7.14 | 6.49 | 1.24 | 4.17 | 2.29 | 1.24 |  |  | 702.15 | 17.45 | 0.31 | 0.99
164 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL019 | 1S-DL-YP-ETC-DKRN-2103-GCL019 | GEETA COLONY,17,BLK:PL | TG-GCL019A-1 | 19506130 | 990 | 320 | 230 | 0.98 | 1196 | 393 | 1666 | 439 | 1973 | 364 | 1635 | 323 | 2019-06-30 02:00 | 282.2 | 35.5 | 1973 | Y | 95 | 110 | 95 | 15 | 39.7 | 1.1 | 8.4 | 50.7 | 0.3 |  |  |  | 8.3 | 1.3 | 1.3 | 8.3 | 516.05 | 418.51 | 521.24 | 501.21 | 148.42 | 180.47 | 138.23 | 153.26 | 30.19 | 102.58 | 21.19 | 40.49 | 704.06 | 15.54 | 0.59 | 1.21
165 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL019 | 1S-DL-YP-ETC-DKRN-2103-GCL019 | GEETA COLONY,17,BLK:PL | TG-GCL019A-2 | 19504388 | 630 | 200 | 239 | 0.97 | 621 | 209 | 882 | 237 | 1007 | 175 | 735 | 235 | 2019-06-12 | 102.6 | 6.9 | 1045 | Y | 95 | 94 | 112 | 18 |  |  | 14.6 | 85.4 | 385.41 | 390.41 | 109.29 | 345.41 | 68.1 | 47.1 | 47.1 | 96.1 | 225.53 | 214.38 | 262.43 | 233.34 | 37 | 44.15 | 14.3 | 41.19 |  | 20 |  |  | 716.44 | 3.16 | 0.34 | 0.99
166 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL020 | 1S-DL-YP-ETC-DKRN-2103-GCL020 | GEETA COLONY,18, BLK:PG | TG-GCL020A-1 | 19506109 | 990 | 320 | 242 | 0.97 | 633 | 228 | 985 | 186 | 798 | 219 | 942 | 170 | 2019-06-12 | 168 | 49.9 | 1474 | B | 105 | 92 | 104 | 13 | 0.4 | 0.3 | 22.1 | 77.3 |  | 4.3 | 2 |  | 399.47 | 480.55 | 480.55 | 428.55 | 295.37 | 209.59 | 291.42 | 266.29 |  |  | 0.3 | [5 empty] | 695.24 | 24.36 | 0.61 | 0.64
167 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL021 | 1S-DL-YP-ETC-DKRN-2103-GCL021 | GEETA COLONY,2,BLK:PL | TG-GCL021A-1 | 19505822 | 630 | 200 | 242 | 0.99 | 480 | 151 | 641 | 193 | 821 | 136 | 580 | 217 | 2019-06-26 23:00 | 112 | -17.8 | 826 | Y | 84 | 116 | 100 | 32 | 0.3 | 0.1 | 60.2 | 39.4 | 189.03 | 12.3 | 10 | 27.58 | 446 | 464.58 | 464.58 | 553.2 | 69.34 | 216.09 | 85.49 | 123.19 |  | 11 | [6 empty] | 704.37 | 15.23 | 0.42 | 0.76
168 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL021 | 1S-DL-YP-ETC-DKRN-2103-GCL021 | GEETA COLONY,2,BLK:PL | TG-GCL021A-2 | 19505821 | 990 | 320 | 242 | 0.97 | 1036 | 426 | 2047 | 263 | 1153 | 348 | 1625 | 774 | 2019-06-11 01:00 | 366.4 | 46.4 | 2047 | R | 91 | 100 | 109 | 18 | 0.5 | 0.2 | 62.7 | 36.6 | 35.53 | 2.3 | 0.45 | 0.3 | 410.55 | 375.21 | 375.21 | 365.48 | 257.11 | 324.15 | 381.15 | 336.48 |  | 1.3 | 14.3 | 0.53 | 0.07 | 0.3 | 2.16 | 0.07 | 704.06 | 15.54 | 0.4 | 1.05
169 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL022 | 1S-DL-YP-ETC-DKRN-2103-GCL022 | GEETA COLONY,3, BLK:K | TG-GCL022A-1 | 19505141 | 990 | 320 | 246 | 0.98 | 794 | 295 | 1235 | 262 | 1154 | 236 | 988 | 218 | 2019-06-12 01:00 | 144.3 | 46.7 | 1297 | B | 104 | 101 | 95 | 9 | 90.7 | 5.7 | 2.9 | 0.6 |  |  |  |  | 171.43 | 194.39 | 194.39 | 195.09 | 294.35 | 285.39 | 249.56 | 284.39 | 14 |  | 2 | 0.3 |  |  |  |  | 706.35 | 13.25 | 0.57 | 0.8
170 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL022 | 1S-DL-YP-ETC-DKRN-2103-GCL022 | GEETA COLONY,3, BLK:K | TG-GCL022A-2 | 19505718 | 630 | 200 | 241 | 0.97 | 473 | 134 | 573 | 147 | 634 | 191 | 818 | 221 | 2019-06-12 01:00 | 108.8 | 31.6 | 907 | B | 87 | 95 | 118 | 31 | 0.4 |  | 34 | 65.5 | 10.28 | 5.3 |  |  | 472.53 | 438.21 | 438.21 | 431.21 | 222.35 | 262.35 | 357.06 | 275.05 | 0.3 |  | 50.35 | [5 empty] | 706.26 | 13.34 | 0.55 | 0.75
171 | 2019-06-04 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL023 | 1S-DL-YP-ETC-DKRN-2103-GCL023 | GEETA COLONY,5,BLK:ID | TG-GCL023A-1 | 19506808 | 990 | 320 | 235 | 0.98 | 878 | 416 | 2065 | 197 | 881 | 265 | 1265 | 1046 | 2019-06-11 01:00 | 275.2 | 54.1 | 2065 | R | 123 | 94 | 83 | 40 | 0.3 | 2.4 | 86.3 | 11 |  |  | 6 |  | 191.19 | 368.56 | 368.56 | 332.11 | 356.22 | 250.2 | 174.3 | 287 | 64 |  | 0.05 | 0.05 | 7.35 |  |  |  | 619.16 | 28.44 | 0.48 | 0.89
172 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL024 | 1S-DL-YP-ETC-DKRN-2103-GCL024 | GEETA COLONY,6, BLK:PL | TG-GCL024A-1 | 19506114 | 990 | 320 | 236 | 0.97 | 801 | 287 | 1252 | 246 | 1074 | 268 | 1158 | 154 | 2019-06-11 23:30 | 199.7 | 65 | 1586 | Y | 97 | 100 | 103 | 6 | 0.4 | 0.1 | 52.9 | 46.6 |  |  |  |  | 158.59 | 147.31 | 147.31 | 124.12 | 537.5 | 557.18 | 610.34 | 581.07 | 10 | 2 | 8 | 1.3 |  |  |  |  | 706.49 | 13.11 | 0.64 | 0.81
173 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL024 | 1S-DL-YP-ETC-DKRN-2103-GCL024 | GEETA COLONY,6, BLK:PL | TG-GCL024A-2 | 19505716 | 630 | 200 | 242.3411 | 0.97414 | 586.4537 | 184.7647 | 786.3332 | 184.0559 | 779.6995 | 217.6331 | 919.2527 | 136.3575 | 2019-06-12 | [15 empty] | 0.5 |  |  |  | 247.5 |  |  |  | 425 |  |  |  | 46 |  |  |  | 0 | 719 |  | 0.5348 | 0.93088
174 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL025 | 1S-DL-YP-ETC-DKRN-2103-GCL025 | GEETA COLONY,7, BLK:PL | TG-GCL025A-1 | 19506865 | 990 | 320 | 236 | 0.98 | 1022 | 230 | 1032 | 383 | 1880 | 409 | 1978 | 901 | 2019-06-11 01:00 | 337.9 | 46.1 | 1978 | B | 92 | 91 | 117 | 26 | 0.4 | 0.1 | 23.7 | 75.8 | 4 | 0.3 |  |  | 408.25 | 409.55 | 409.55 | 332.25 | 295.35 | 298.3 | 460.27 | 366 | 1.3 | 0.3 | 76 | 11 |  | 0.05 | 3.35 | 0.05 | 709.3 | 10.3 | 0.44 | 1.03
175 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL026 | 1S-DL-YP-ETC-DKRN-2103-GCL026 | GEETA COLONY,8,BLK;PL | TG-GCL026A-1 | 19506452 | 990 | 320 | 245 | 0.97 | 1008 | 136 | 607 | 434 | 2107 | 437 | 2009 | 1453 | 2019-06-02 23:30 | 371.5 | 38.7 | 2107 | Y | 85 | 100 | 114 | 29 | 0.4 |  | 22.8 | 76.8 | 71.25 | 15.3 | 6.3 | 15 | 514.38 | 484.33 | 484.33 | 493.03 | 121.58 | 207.28 | 286.26 | 199.28 |  |  | 0.3 |  |  | 0.3 | 0.3 | 0.3 | 708.01 | 11.59 | 0.34 | 1.02
176 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL026 | 1S-DL-YP-ETC-DKRN-2103-GCL026 | GEETA COLONY,8,BLK;PL | TG-GCL026A-2 | 19506115 | 400 | 120 | 243 | 0.96 | 357 | 108 | 444 | 142 | 591 | 107 | 447 | 146 | 2019-06-16 01:00 | 98.6 | 28.9 | 771 | B | 93 | 113 | 93 | 20 | 0.4 | 0.8 | 71.6 | 27.2 | 0.3 |  |  |  | 89.3 | 22 | 22 | 45 | 606.26 | 508.58 | 597.26 | 607.56 | 12 | 169.28 | 15.3 | 55.3 |  | 8 | 0.3 |  | 708.26 | 11.34 | 0.66 | 0.89
177 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL027 | 1S-DL-YP-ETC-DKRN-2103-GCL027 | GEETA COLONY,8-A,BLK:ID | TG-GCL027A-1 | 19506019 | 990 | 320 | 238 | 0.97 | 919 | 363 | 1555 | 243 | 1029 | 313 | 1336 | 458 | 2019-06-11 23:30 | 258.9 | 58.2 | 1596 | R | 111 | 85 | 104 | 26 | 0.4 |  | 69.2 | 30.4 |  | 2 |  |  | 88 | 353.27 | 353.27 | 175.3 | 517.25 | 351.58 | 546.25 | 482.25 | 99 | 0.3 | 58.3 | 50 | 3.3 |  | 0.3 |  | 707.55 | 12.05 | 0.56 | 0.93
178 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL027 | 1S-DL-YP-ETC-DKRN-2103-GCL027 | GEETA COLONY,8-A,BLK:ID | TG-GCL027A-2 | 19505112 | 630 | 200 | 245 | 0.96 | 259 | 97 | 398 | 95 | 391 | 68 | 280 | 115 | 2019-06-11 01:00 | 83.4 | 19.6 | 479 | R | 114 | 114 | 72 | 42 | 0.2 | 0.1 | 24.3 | 75.5 | 50 | 45.58 | 442.27 | 99.3 | 592.25 | 621.57 | 621.57 | 594.25 | 54 | 28.3 |  | 2.3 | [8 empty] | 696.25 | 23.35 | 0.63 | 0.41
179 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL028 | 1S-DL-YP-ETC-DKRN-2103-GCL028 | GEETA COLONY,POL.STATION | TG-GCL028A-1 | 19505717 | 630 | 200 | 235 | 0.97 | 550 | 129 | 537 | 250 | 1065 | 171 | 715 | 465 | 2019-06-04 01:30 | 138 | 36.6 | 1164 | B | 98 | 74 | 129 | 55 | 1 | 10.2 | 72.1 | 16.7 |  | 2.3 |  |  | 162.29 | 391.32 | 391.32 | 106 | 528.3 | 313.27 | 575.31 | 598.59 | 17 |  | 117.58 | 3 |  | 0.3 | 8 |  | 707.59 | 12.01 | 0.6 | 0.87
180 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL028 | 1S-DL-YP-ETC-DKRN-2103-GCL028 | GEETA COLONY,POL.STATION | TG-GCL028A-2 | 19504342 | 630 | 200 | 253.1685 | 0.98512 | 671.9452 | 130.8245 | 572.2357 | 196.0723 | 848.2469 | 345.0484 | 1492.7469 | 818.2003 | 2019-06-03 | [15 empty] | 0 |  |  |  | 221 |  |  |  | 493.5 |  |  |  | 2.5 |  |  |  | 3 | 720 |  | 0.44515 | 1.0666
181 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL029 | 1S-DL-YP-ETC-DKRN-2103-GCL029 | KANCHAN APPT.:ID | TG-GCL029A-1 | 19501459 | 400 | 120 | 239 | 0.97 | 113 | 35 | 154 | 41 | 178 | 37 | 159 | 22 | 2019-06-30 | 17.9 | 2.2 | 184 | B | 106 | 95 | 99 | 11 | 100 |  |  |  | 627.27 | 631.27 | 581.27 | 608.57 | 92.3 | 88.3 | 88.3 | 111 | [12 empty] | 719.57 | 0.03 | 0.47 | 0.28
182 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL029 | 1S-DL-YP-ETC-DKRN-2103-GCL029 | KANCHAN APPT.:ID | TG-GCL029A-2 | 19506618 | 400 | 120 | 241 | 0.98 | 72 | 35 | 147 | 13 | 54 | 25 | 105 | 81 | 2019-06-05 23:30 | 10.7 | 0.7 | 163 | R | 146 | 54 | 100 | 92 |  |  | 5.2 | 94.8 | 595.28 | 710.28 | 706.28 | 710.28 | 115 | [15 empty] | 710.28 | 9.32 | 0.49 | 0.18
183 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL030 | 1S-DL-YP-ETC-DKRN-2103-GCL030 | NEW LAHORE (MUNSHI COLONY):PL | TG-GCL030A-1 | 19506789 | 990 | 320 | 235 | 0.97 | 1099 | 383 | 1722 | 351 | 1549 | 365 | 1643 | 149 | 2019-06-10 02:00 | 291.5 | 75.5 | 1854 | R | 101 | 99 | 100 | 2 | 0.9 | 6.3 | 80.2 | 12.5 |  |  |  |  | 6.23 | 8.42 | 8.42 | 5.42 | 520.29 | 504.4 | 513.22 | 511.4 | 125.14 | 157.16 | 136.46 | 146.33 | 22.16 | 3.44 | 16.14 | 10.27 | 706.42 | 13.18 | 0.61 | 1.11
184 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL031 | 1S-DL-YP-ETC-DKRN-2103-GCL031 | NEW LAHORE EXTENSION:PL | TG-GCL031A-1 | 19506882 | 630 | 200 | 237 | 0.97 | 692 | 237 | 1024 | 206 | 885 | 249 | 1074 | 170 | 2019-06-29 | 162.2 | 37 | 1258 | R | 84 | 102 | 114 | 30 | 0.2 | 0.1 | 44.2 | 55.5 | 21 |  |  |  | 515.32 | 334.19 | 334.19 | 364.34 | 150.15 | 360.28 | 504.31 | 327.43 | 11 | 8.32 | 7.09 | 11.22 | 7.02 | 1.3 | 1.4 | 1.1 | 704.49 | 15.11 | 0.39 | 1.1
185 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL031 | 1S-DL-YP-ETC-DKRN-2103-GCL031 | NEW LAHORE EXTENSION:PL | TG-GCL031A-2 | 19506866 | 990 | 320 | 243 | 0.97 | 1078 | 389 | 1625 | 375 | 1546 | 314 | 1303 | 291 | 2019-06-28 | 241 | 65.3 | 1661 | R | 111 | 97 | 92 | 19 | 0.4 | 0.8 | 75.3 | 23.4 |  |  |  |  | 59.54 | 105.32 | 105.32 | 95.54 | 519.55 | 562.43 | 521.04 | 552.36 | 112.23 | 31.34 | 8.45 | 50.36 | 9.37 | 2 | 2.22 | 2.43 | 701.49 | 18.11 | 0.5 | 1.09
186 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL032 | 1S-DL-YP-ETC-DKRN-2103-GCL032 | RANI GARDEN NO.2,PARK WALA:PL | TG-GCL032A-1 | 19506148 | 990 | 320 | 242 | 0.98 | 838 | 267 | 1111 | 250 | 1043 | 321 | 1329 | 259 | 2019-06-30 01:30 | 243.2 | 59.5 | 1337 | B | 105 | 92 | 103 | 13 | 0.3 | 0.1 | 67.9 | 31.7 |  |  |  |  | 11.3 | 34 | 34 | 13.3 | 680.44 | 673.11 | 635.26 | 687.37 | 14.57 |  | 54.45 | 6.04 |  |  |  |  | 707.11 | 12.49 | 0.68 | 0.85
187 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL032 | 1S-DL-YP-ETC-DKRN-2103-GCL032 | RANI GARDEN NO.2,PARK WALA:PL | TG-GCL032A-2 | 19505143 | 630 | 200 | 244 | 0.97 | 668 | 264 | 1175 | 152 | 646 | 252 | 1085 | 490 | 2019-06-06 10:00 | 271.2 | 29.2 | 1175 | R | 100 | 108 | 92 | 16 | 0.3 | 0.5 | 46.4 | 52.9 | 5.3 | 5 | 1 | 0.3 | 483.44 | 400.44 | 400.44 | 482.44 | 216.23 | 302.22 | 120 | 225.36 | 2.44 | 1.14 |  |  | 0.59 |  | 0.3 | 0.3 | 709.2 | 10.4 | 0.35 | 1.06
188 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL033 | 1S-DL-YP-ETC-DKRN-2103-GCL033 | RANI GARDEN SCHOOL;PL | TG-GCL033A-1 | 19505991 | 630 | 200 | 245 | 0.93 | 736 | 251 | 1022 | 159 | 634 | 326 | 1313 | 590 | 2019-06-05 17:00 | 323.6 | 89 | 1313 | B | 92 | 95 | 113 | 21 |  | 0.6 | 92.3 | 7.1 | [5 empty] | 1 | 1 |  | 249.4 | 249.23 | 232.1 | 248.4 | 3.07 | 3 | 18.3 | 4.07 | 0.36 |  | 2.43 | 0.36 | 253.24 | 34.36 | 0.52 | 1.17
189 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL033 | 1S-DL-YP-ETC-DKRN-2103-GCL033 | RANI GARDEN SCHOOL;PL | TG-GCL033A-2 | 19505345 | 630 | 200 | 235 | 0.98 | 393 | 115 | 488 | 146 | 622 | 132 | 562 | 116 | 2019-06-09 05:30 | 127.4 | 29.8 | 692 | Y | 88 | 113 | 99 | 25 | 0.1 | 0.1 | 55.7 | 44 | 0.03 |  |  |  | 434.23 | 73.12 | 73.12 | 235.25 | 268.37 | 629.51 | 439.28 | 467.38 | [8 empty] | 703.03 | 16.57 | 0.69 | 0.62
190 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL033 | 1S-DL-YP-ETC-DKRN-2103-GCL033 | RANI GARDEN SCHOOL;PL | TG-GCL033A-3 | 19506835 | 400 | 120 | 242 | 0.98 | 349 | 145 | 619 | 130 | 562 | 74 | 314 | 280 | 2019-06-05 21:30 | 111.1 | 10.3 | 619 | R | 127 | 92 | 81 | 46 | 0.1 | 0 | 29.2 | 70.7 |  | 52.2 | 272.42 | 4.3 | 343.36 | 602.49 | 602.49 | 663.42 | 358.47 | 47.31 | 62.44 | 34.28 | 0.17 | 0.3 |  | 0.3 | 0.3 |  |  |  | 703.1 | 16.5 | 0.37 | 0.87
191 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL034 | 1S-DL-YP-ETC-DKRN-2103-GCL034 | RANI GARDEN SWITCHING S/STN:PL | TG-GCL034A-1 | 19506864 | 630 | 200 | 236 | 0.98 | 598 | 183 | 788 | 215 | 930 | 200 | 862 | 123 | 2019-06-30 | 162.4 | 36.4 | 1015 | Y | 95 | 104 | 100 | 9 | 0.4 | 0.2 | 31 | 68.5 |  |  |  |  | 70.3 | 41 | 41 | 49 | 607.44 | 578.52 | 582.44 | 603.44 | 30.43 | 84.08 | 59.43 | 56.13 |  | 4.57 |  |  | 708.57 | 11.03 | 0.6 | 0.95
192 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL035 | 1S-DL-YP-ETC-DKRN-2103-GCL035 | SARASWATI BHANDAR:PL | TG-GCL035A-1 | 19505989 | 630 | 200 | 245 | 0.99 | 580 | 179 | 751 | 196 | 820 | 205 | 862 | 97 | 2019-06-02 14:30 | 74.2 | 1 | 884 | B | 89 | 100 | 111 | 22 | 0.1 |  | 37.7 | 62.2 | 403 | 377.3 | 375.3 | 386 | 63.59 | 63.59 | 63.59 | 59.29 | 247 | 125 | 86 | 158 | 6 | 153.3 | 192 | 116.3 |  |  |  |  | 719.59 | 0.01 | 0.4 | 0.92
193 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL036 | 1S-DL-YP-ETC-DKRN-2103-GCL036 | SAROJINI PARK:PKG | TG-GCL036A-1 | 19506408 | 990 | 320 | 242 | 0.98 | 820 | 256 | 1069 | 270 | 1161 | 294 | 1241 | 149 | 2019-06-11 23:30 | 194.2 | 47 | 1376 | Y | 96 | 95 | 109 | 14 | 29 | 33.9 | 31.6 | 5.5 |  |  |  |  | 214.2 | 271.19 | 271.19 | 201.19 | 481.13 | 421.44 | 531.12 | 488.14 |  | 2.3 | 42.3 | 6 |  |  |  |  | 695.33 | 24.27 | 0.59 | 0.83
194 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL037 | 1S-DL-YP-ETC-DKRN-2103-GCL037 | SHASTRI NAGAR, NO-1:K | TG-GCL037A-1 | 19506031 | 990 | 320 | 243 | 0.96 | 620 | 199 | 828 | 261 | 1091 | 160 | 667 | 370 | 2019-06-30 | 215.4 | 61.1 | 1151 | Y | 102 | 117 | 81 | 36 | 0.4 |  | 6.7 | 92.9 |  |  | 7.3 |  | 292 | 136 | 136 | 350.26 | 418.21 | 573.21 | 93.29 | 359.55 |  | 1 | [6 empty] | 710.21 | 9.39 | 0.66 | 0.63
195 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL037 | 1S-DL-YP-ETC-DKRN-2103-GCL037 | SHASTRI PARK NAGAR, NO-2:K | TG-GCL037A-2 | 19506787 | 630 | 200 | 242 | 0.97 | 310 | 169 | 742 | 72 | 310 | 69 | 299 | 438 | 2019-06-11 02:00 | 104.6 | 18.2 | 752 | R | 101 | 102 | 97 | 5 | 0.1 | 0.3 | 57.5 | 42.1 | 229.26 | 156.34 | 189.3 | 167.28 | 419.22 | 522.44 | 522.44 | 509.5 | 60 | 31 | 16 | 33 | 1.3 | [7 empty] | 710.18 | 9.42 | 0.52 | 0.49
196 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL038 | 1S-DL-YP-ETC-DKRN-2103-GCL038 | SHASTRI PARK NAGAR, NO-2:K | TG-GCL038A-1 | 19506782 | 990 | 320 | 242 | 0.97 | 914 | 319 | 1395 | 319 | 1379 | 276 | 1192 | 196 | 2019-06-09 00:30 | 227.8 | 55.4 | 1560 | B | 93 | 92 | 114 | 22 | 0.4 | 0.4 | 58.3 | 41 |  |  |  |  | 226.56 | 241.58 | 241.58 | 162.28 | 481.47 | 466.45 | 569.43 | 539.15 | 2 | 2 | 78 | 9 |  |  | 2.3 |  | 710.43 | 9.17 | 0.54 | 0.92
197 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL039 | 1S-DL-YP-ETC-DKRN-2103-GCL039 | SHYAM BLOCK NO. 1:PL | TG-GCL039A-1 | 19503701 | 990 | 320 | 245 | 0.98 | 441 | 130 | 536 | 156 | 654 | 155 | 634 | 110 | 2019-06-02 12:30 | 103 | -4.4 | 688 | Y | 98 | 93 | 109 | 16 |  | 0.5 | 62.9 | 36.6 | 270.29 | 406.29 | 233.59 | 332.29 | 444.23 | 282.23 | 282.23 | 372.23 | 5 | 31 | 48 | 15 | [8 empty] | 719.52 | 0.08 | 0.54 | 0.45
198 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL040 | 1S-DL-YP-ETC-DKRN-2103-GCL040 | SHYAM BLOCK NO. 2:PL | TG-GCL040A-1 | 19504719 | 990 | 320 | 245 | 0.97 | 398 | 121 | 517 | 111 | 474 | 166 | 708 | 216 | 2019-06-01 15:00 | 89.1 | 22.8 | 735 | B | 93 | 85 | 122 | 37 |  |  | 1.9 | 98.1 | 316.29 | 418.29 | 106.59 | 267.59 | 403.15 | 301.15 | 301.15 | 450.15 |  |  | 139.15 | 1.3 | [8 empty] | 719.44 | 0.16 | 0.59 | 0.4
199 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL041 | 1S-DL-YP-ETC-DKRN-2103-GCL041 | SUBASH ROAD, TIKONA PARK:K | TG-GCL041A-1 | 19505574 | 990 | 320 | 251 | 0.98 | 936 | 322 | 1353 | 313 | 1328 | 301 | 1264 | 79 | 2019-06-29 16:00 | 172.2 | 10.2 | 1688 | B | 92 | 106 | 102 | 14 | 0.1 | 0.1 | 38 | 61.8 | 379.56 | 344.03 | 348.03 | 365.03 | 65.57 | 83.5 | 83.5 | 66.5 | 185.44 | 94.41 | 131.12 | 127.12 | 71.3 | 179.33 | 138.04 | 144.02 |  | 1 | 0.58 |  | 703.07 | 16.53 | 0.42 | 0.95
200 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL041 | 1S-DL-YP-ETC-DKRN-2103-GCL041 | SUBASH ROAD, TIKONA PARK:K | TG-GCL041A-2 | 19501917 | 990 | 320 | 238 | 0.99 | 944 | 288 | 1256 | 307 | 1333 | 349 | 1510 | 226 | 2019-06-02 15:00 | 115.6 | 9.6 | 1658 | Y | 90 | 94 | 116 | 26 |  |  | 5.7 | 94.3 | 406.31 | 440.11 | 291.48 | 387.17 | 51.28 | 51.14 | 51.14 | 63.12 | 237.05 | 72.33 | 94.23 | 144.47 | 16.41 | 126.01 | 164.33 | 116.29 |  | 21.46 | 12.2 |  | 711.45 | 8.15 | 0.39 | 0.95
201 | 2019-06-04 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL041 | 1S-DL-YP-ETC-DKRN-2103-GCL041 | SUBASH ROAD, TIKONA PARK:K | TG-GCL041A-3 | 19506377 | 990 | 320 | 245 | 0.99 | 714 | 204 | 840 | 281 | 1170 | 229 | 957 | 290 | 2019-06-13 12:00 | 106.6 | 1.9 | 1170 | Y | 95 | 96 | 109 | 14 | 0.1 | 0.2 | 21.7 | 78.1 | 359.58 | 364.55 | 355.29 | 359.59 | 39.5 | 27.53 | 27.53 | 38.19 | 212.43 | 219.13 | 216.13 | 214.13 |  | 0.3 | [6 empty] | 612.31 | 35.29 | 0.37 | 0.72
202 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL041 | 1S-DL-YP-ETC-DKRN-2103-GCL041 | SUBASH ROAD, TIKONA PARK:K | TG-GCL041A-4 | 19506152 | 990 | 320 | 245 | 0.99 | 778 | 272 | 1198 | 178 | 747 | 328 | 1498 | 655 | 2019-06-30 14:00 | 162.2 | 3.5 | 1498 | B | 119 | 87 | 95 | 32 | 0.3 | 0.1 | 22.1 | 77.6 | 414.34 | 431.16 | 428.04 | 426.04 | 34.59 | 51.15 | 51.15 | 41.57 | 173.14 | 215.52 | 226.52 | 230.22 | 75.36 |  | 1 | [5 empty] | 698.23 | 21.37 | 0.33 | 0.79
203 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL042 | 1S-DL-YP-ETC-DKRN-2103-GCL042 | SWARG ASHARM:PM | TG-GCL042A-1 | 19505737 | 100 | 40 | 243 | 0.76 | 78 | 20 | 82 | 31 | 130 | 27 | 112 | 42 | 2019-06-03 19:00 | 9.6 | -24 | 137 | Y | 70 | 135 | 95 | 65 | 0.4 | 0.6 | 34.1 | 64.9 | 394.54 | 385.25 | 384.54 | 384.55 | 166.3 | 20.3 | 20.3 | 37.29 | 144 | 134.29 | 286.3 | 283.3 | 0.3 | 165.3 | 2 | [5 empty] | 705.54 | 14.06 | 0.33 | 0.78
204 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL043 | 1S-DL-YP-ETC-DKRN-2103-GCL043 | TAJ SARTAJ, S/STAT, NO.1:ID | TG-GCL043A-1 | 19501583 | 630 | 200 | 246 | 0.98 | 122 | 34 | 141 | 42 | 173 | 46 | 190 | 43 | 2019-06-14 01:00 | 31.7 | 2.3 | 248 | B | 124 | 20 | 155 | 135 |  |  | 9.4 | 90.6 | 653.16 | 718.16 | 529.16 | 719.16 | 66 | 1 | 1 | [13 empty] | 719.16 | 0.44 | 0.56 | 0.19
205 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL043 | 1S-DL-YP-ETC-DKRN-2103-GCL043 | TAJ SARTAJ, S/STAT, NO.1:ID | TG-GCL043A-2 | 19505563 | 630 | 200 | 246 | 0.97 | 216 | 98 | 429 | 27 | 106 | 92 | 387 | 305 | 2019-06-30 06:00 | 79.2 | 10 | 429 | R | 111 | 74 | 115 | 41 | 0.4 |  | 57.9 | 41.7 | 407.45 | 674.15 | 391.15 | 495.15 | 300 | 34 | 34 | 213 | 0.3 |  | 0.3 | [9 empty] | 708.15 | 11.45 | 0.5 | 0.34
206 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL044 | 1S-DL-YP-ETC-DKRN-2103-GCL044 | TAJ SARTAJ, S/STAT, NO.2:ID | TG-GCL044A-1 | 19505736 | 630 | 200 | 246 | 0.97 | 199 | 51 | 211 | 72 | 299 | 77 | 322 | 101 | 2019-06-30 01:30 | 44.4 | 8.6 | 381 | Y | 86 | 102 | 111 | 25 | 0.1 |  | 51.8 | 48.1 | 560.16 | 409.46 | 332.46 | 419.16 | 148.3 | 299 | 299 | 289.3 | [12 empty] | 708.46 | 11.14 | 0.61 | 0.32
207 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL044 | 1S-DL-YP-ETC-DKRN-2103-GCL044 | TAJ SARTAJ, S/STAT, NO.2:ID | TG-GCL044A-2 | 19506453 | 630 | 200 | 246 | 0.96 | 197 | 50 | 214 | 112 | 474 | 35 | 137 | 306 | 2019-06-14 05:30 | 74.8 | 10.6 | 474 | Y | 97 | 114 | 89 | 25 | 0.3 | 0.1 | 28.6 | 71.1 | 524.17 | 382.47 | 563.47 | 501.17 | 184.3 | 325.3 | 325.3 | 207.3 |  | 0.3 | [10 empty] | 708.47 | 11.13 | 0.55 | 0.31
208 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL045 | 1S-DL-YP-ETC-DKRN-2103-GCL045 | GEETA APT SS 2:ID | TG-GCL045A-1 | 19501283 | 400 | 120 | 246 | 0.98 | 158 | 38 | 155 | 73 | 302 | 47 | 195 | 132 | 2019-06-11 23:30 | 30.9 | 4.7 | 316 | Y | 79 | 126 | 94 | 47 |  |  | 2.8 | 97.2 | 525.57 | 221.27 | 408.27 | 391.57 | 194 | 396.3 | 396.3 | 328 |  | 102 | [10 empty] | 719.57 | 0.03 | 0.53 | 0.4
209 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL045 | 1S-DL-YP-ETC-DKRN-2103-GCL045 | GEETA APT SS 2:ID | TG-GCL045A-2 | 19506380 | 400 | 120 | 247 | 0.98 | 88 | 22 | 91 | 33 | 141 | 33 | 139 | 49 | 2019-06-29 23:30 | 21.1 | 1.7 | 158 | Y | 63 | 117 | 120 | 57 | 0.1 |  | 32.2 | 67.7 | 719.56 | 672.26 | 655.26 | 713.56 |  | 47.3 | 47.3 | 6 | [12 empty] | 719.56 | 0.04 | 0.49 | 0.22
210 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL049 | 1S-DL-YP-ETC-DKRN-2103-GCL049 | 5 BLOCK GEETA COLONY INDOOR:ID | TG-GCL049A-1 | 19506409 | 630 | 200 | 242 | 0.98 | 504 | 65 | 280 | 239 | 1146 | 200 | 945 | 785 | 2019-06-11 01:00 | 189.2 | 20.2 | 1146 | Y | 70 | 115 | 115 | 45 | 0.4 |  | 11.6 | 88 | 167.52 | 4.58 | 3 | 8.28 | 536.02 | 417.21 | 417.21 | 516.51 | 4.3 | 284 | 329.27 | 183 |  | 2 | 1.35 | 0.05 |  | 0.05 |  |  | 708.24 | 11.36 | 0.44 | 0.8
211 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL049 | 1S-DL-YP-ETC-DKRN-2103-GCL049 | 5 BLOCK GEETA COLONY INDOOR:ID | TG-GCL049A-2 | 19505679 | 630 | 200 | 249 | 0.97 | 299 | 172 | 796 | 86 | 365 | 41 | 182 | 546 | 2019-06-11 01:00 | 103.2 | 12.8 | 796 | R | 123 | 127 | 50 | 77 | 0.2 | 0.2 | 96.4 | 3.2 | 238.44 | 224.22 | 704.47 | 430.11 | 433.57 | 443.19 | 443.19 | 277.56 | 35.26 | 40.36 |  | 0.1 | 0.1 | [7 empty] | 708.17 | 11.43 | 0.42 | 0.48
212 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL052 | 1S-DL-YP-ETC-DKRN-2103-GCL052 | SARWANGHI SOCIETY | TG-GCL052A-1 | 19504718 | 630 | 200 | 242 | 0.97 | 176 | 65 | 276 | 67 | 281 | 44 | 186 | 93 | 2019-06-02 01:00 | 31.3 | 6.4 | 301 | R | 119 | 100 | 81 | 38 |  |  | 44.6 | 55.4 | 489.11 | 610.41 | 696.41 | 616.41 | 230.3 | 109 | 109 | 103 | [12 empty] | 719.41 | 0.19 | 0.54 | 0.28
213 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL052 | 1S-DL-YP-ETC-DKRN-2103-GCL052 | SARWANGHI SOCIETY | TG-GCL052A-2 | 19504720 | 630 | 200 | 242 | 0.98 | 152 | 57 | 241 | 19 | 79 | 77 | 324 | 216 | 2019-06-29 23:30 | 24.8 | 2.3 | 324 | B | 121 | 37 | 142 | 105 |  | 0.1 | 86.9 | 13 | 541.1 | 719.4 | 480.4 | 671.4 | 178.3 |  |  | 48 | [12 empty] | 719.4 | 0.2 | 0.52 | 0.24
214 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL053 | 1S-DL-YP-ETC-DKRN-2103-GCL053 | MULTANI MOHALLA MASJID | TG-GCL053A-1 | 19503702 | 400 | 120 | 241 | 0.98 | 274 | 87 | 365 | 102 | 417 | 85 | 358 | 56 | 2019-06-30 16:00 | 44.7 | 8.6 | 446 | Y | 101 | 114 | 86 | 28 | 1.5 | 86.1 | 12.4 |  | 30.27 | 12.3 | 76.5 | 20 | 424.21 | 356.18 | 356.18 | 437.48 | 264.57 | 350.27 | 210.57 | 261.57 |  | 0.3 | [6 empty] | 719.45 | 0.15 | 0.56 | 0.69
215 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL059 | 1S-DL-YP-ETC-DKRN-2103-GCL059 | MAYUR DHAWAJ NO. 1 | TG-GCL059A-2 | 19505199 | 630 | 200 | 243 | 0.97 | 324 | 102 | 464 | 165 | 773 | 57 | 247 | 458 | 2019-06-11 01:30 | 102.8 | 10 | 773 | Y | 120 | 95 | 85 | 35 | 0.1 |  | 11.7 | 88.2 | 97.43 | 260.17 | 360.4 | 198.4 | 498.57 | 428.53 | 428.53 | 489.3 | 99.3 | 7 |  | 8 | [8 empty] | 696.1 | 23.5 | 0.47 | 0.51
216 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL059 | 1S-DL-YP-ETC-DKRN-2103-GCL059 | MAYUR DHAWAJ NO. 1 | TG-GCL059A-3 | 19505255 | 400 | 120 | 243 | 0.98 | 161 | 45 | 188 | 56 | 241 | 61 | 268 | 70 | 2019-06-11 01:30 | 39.8 | 1.4 | 308 | Y | 96 | 127 | 78 | 49 | 0.3 | 0.1 | 58.9 | 40.7 | 437.03 | 249.29 | 560.15 | 415.45 | 269.12 | 397.16 | 397.16 | 291 | 1 | 60.3 | 0.3 | 0.3 | [8 empty] | 707.15 | 12.45 | 0.49 | 0.4
217 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL063 | 1S-DL-YP-ETC-DKRN-2103-GCL063 | 9 Block, Silai Center Geeta Colony | TG-GCL063A-1 | 19505216 | 990 | 320 | 239 | 0.97 | 619 | 218 | 941 | 223 | 976 | 178 | 772 | 189 | 2019-06-30 00:30 | 185.9 | 43.5 | 1032 | Y | 100 | 113 | 87 | 26 | 0.3 |  | 36.3 | 63.4 | 9 | 7.04 | 20.34 | 4 | 486.12 | 394.57 | 394.57 | 508.59 | 200.17 | 293.28 | 113 | 182.3 | [8 empty] | 695.29 | 24.31 | 0.57 | 0.63
218 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL068 | 1S-DL-YP-ETC-DKRN-2103-GCL068 | MAHESHWARI PETROL PUMP | TG-GCL068A-1 | 19506602 | 400 | 120 | 244 | 0.86 | 119 | 37 | 152 | 47 | 189 | 34 | 137 | 46 | 2019-06-29 20:00 | 18.8 | -25.3 | 217 | B | 91 | 111 | 98 | 20 | 0.2 | 0.1 | 92.7 | 6.9 | 267.23 | 239.3 | 255 | 247 | 440.17 | 468.1 | 468.1 | 460.4 | [12 empty] | 707.4 | 12.2 | 0.62 | 0.3
219 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | GAN006 | 1S-DL-YP-ETC-DKRN-2102-GAN006 | D.A.V. SCHOOL GANDHI NGR.:PL | TG-GAN006A-1 | 19506595 | 990 | 320 | 244 | 0.95 | 308 | 124 | 524 | 104 | 437 | 80 | 331 | 167 | 2019-06-02 16:00 | 100.5 | 19.8 | 524 | R | 103 | 105 | 91 | 14 | 0.1 |  | 65.8 | 34.1 | 386.23 | 395.41 | 497.28 | 418.23 | 313.49 | 304.31 | 304.31 | 281.49 | [12 empty] | 700.12 | 19.48 | 0.61 | 0.31
220 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | GAN017 | 1S-DL-YP-ETC-DKRN-2102-GAN017 | KAUSHIK PURI KIOSK:K | TG-GAN017A-1 | 19502029 | 990 | 320 | 244 | 0.98 | 813 | 350 | 1476 | 232 | 979 | 231 | 938 | 519 | 2019-06-01 19:30 | 157.5 | 33.1 | 1476 | R | 118 | 90 | 92 | 28 | 100 |  |  |  | 82.59 |  |  |  |  | 187.05 | 187.05 | 93.57 | 533.05 | 532.18 | 602.57 | 624.56 | 97.49 |  |  | 0.3 | 5.3 |  |  |  | 719.23 | 0.37 | 0.62 | 0.82
221 | 2019-06-20 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | GAN018 | 1S-DL-YP-ETC-DKRN-2102-GAN018 | KAUSHIK PURI PARK:PL | TG-GAN018A-1 | 19506930 | 990 | 320 | 240 | 0.98 | 534 | 168 | 723 | 156 | 675 | 210 | 917 | 222 | 2019-06-30 14:00 | 93.8 | 36.2 | 950 | B | 92 | 85 | 123 | 38 |  | 1.9 | 84.5 | 13.6 |  |  |  |  | 146.09 | 186.01 | 186.01 | 94.44 | 92.51 | 52.59 | 218.3 | 144.16 | [8 empty] | 239 | 25 | 0.77 | 0.54
222 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | GAN018 | 1S-DL-YP-ETC-DKRN-2102-GAN018 | KAUSHIK PURI PARK:PL | TG-GAN018A-2 | 19504747 | 630 | 200 | 246 | 0.98 | 491 | 151 | 610 | 140 | 564 | 201 | 807 | 224 | 2019-06-01 19:30 | 84.6 | 13.8 | 865 | B | 101 | 78 | 121 | 43 | 0 |  | 36.7 | 63.3 | 0.3 | 1 | 1 | 1 | 48.45 | 417.59 | 417.59 | 47.21 | 668.07 | 298.23 | 629.17 | 669.01 |  |  | 80.05 | [5 empty] | 717.22 | 2.38 | 0.66 | 0.78
223 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | GAN019 | 1S-DL-YP-ETC-DKRN-2102-GAN019 | KAUSHIK PURI GALI NO. 4:PL | TG-GAN019A-1 | 19505854 | 990 | 320 | 240 | 0.98 | 522 | 162 | 667 | 184 | 755 | 176 | 727 | 78 | 2019-06-02 01:00 | 121.6 | 16.3 | 897 | Y | 95 | 105 | 100 | 10 | 0.3 |  | 59.7 | 40 | 8.18 | 1.18 | 6.18 | 3.48 | 589.49 | 472.19 | 472.19 | 541.19 | 104.3 | 229 | 158.3 | 157.3 | [8 empty] | 702.37 | 17.23 | 0.65 | 0.53
224 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | GAN026 | 1S-DL-YP-ETC-DKRN-2102-GAN026 | SATSANG MARG:PL | TG-GAN026A-1 | 19500930 | 990 | 320 | 239 | 0.97 | 850 | 329 | 1437 | 260 | 1120 | 261 | 1133 | 311 | 2019-06-30 00:30 | 163.4 | 53.7 | 1477 | R | 102 | 106 | 92 | 14 |  |  | 23.8 | 76.2 |  |  |  |  | 151.04 | 100.04 | 100.04 | 152.04 | 545.08 | 616.08 | 463.22 | 560.38 | 21 | 1 | 3.3 | 4.3 |  |  |  |  | 717.12 | 2.48 | 0.58 | 0.86
225 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | GAN026 | 1S-DL-YP-ETC-DKRN-2102-GAN026 | SATSANG MARG:PL | TG-GAN026A-2 | 19500966 | 630 | 200 | 239 | 0.97 | 669 | 231 | 1023 | 206 | 905 | 233 | 1026 | 120 | 2019-06-01 23:30 | 142.1 | 34.5 | 1118 | R | 107 | 100 | 93 | 14 |  |  | 40.4 | 59.6 |  |  | 18 |  | 124.27 | 129.28 | 129.28 | 147.57 | 479.06 | 509.37 | 382.39 | 476.38 | 74.22 | 74.46 | 86.08 | 78.38 | 39.18 | 3.22 | 11.3 | 14 | 717.13 | 2.47 | 0.52 | 1.06
226 | 2019-06-04 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | GAN027 | 1S-DL-YP-ETC-DKRN-2102-GAN027 | SEELAMPUR DOUBLE STORY:ID | TG-GAN027A-1 | 19505501 | 990 | 320 | 230 | 0.98 | 1179 | 384 | 1728 | 428 | 1927 | 367 | 1627 | 264 | 2019-06-30 15:30 | 237.1 | 32.3 | 1927 | Y | 103 | 112 | 85 | 27 | 0.2 | 5.6 | 92.1 | 2.1 |  |  | 0.3 |  | 58.32 | 49 | 49 | 117.26 | 373.46 | 360.48 | 211.34 | 319.52 | 164.52 | 119.52 | 110.58 | 158.4 | 15.08 | 82.38 | 1.08 | 16.2 | 612.18 | 35.42 | 0.5 | 1.19
227 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | GAN027 | 1S-DL-YP-ETC-DKRN-2102-GAN027 | SEELAMPUR DOUBLE STORY:ID | TG-GAN027A-2 | 19505502 | 990 | 320 | 236 | 0.98 | 541 | 174 | 754 | 213 | 925 | 154 | 662 | 232 | 2019-06-04 15:00 | 87 | -102.4 | 950 | Y | 93 | 107 | 101 | 14 |  |  | 45.5 | 54.5 | 135.27 | 105.3 | 89 | 109.57 | 59.3 | 81.27 | 81.27 | 82 | 40.35 | 48.35 | 31.05 | 43.35 | [8 empty] | 691.48 | 28.12 | 0.4 | 0.55
228 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | GAN030 | 1S-DL-YP-ETC-DKRN-2102-GAN030 | SHANTI MOHALL GALI NO. 7:K | TG-GAN030A-1 | 19500931 | 990 | 320 | 243 | 0.97 | 583 | 197 | 809 | 173 | 726 | 213 | 894 | 146 | 2019-06-28 23:00 | 127.3 | 37.5 | 933 | B | 98 | 91 | 111 | 20 |  | 63.5 | 36.4 | 0.1 |  | 0.3 |  |  | 356.17 | 489.34 | 489.34 | 336.13 | 358.16 | 224.29 | 517.26 | 378.2 | [8 empty] | 714.33 | 5.27 | 0.69 | 0.59
229 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | GAN031 | 1S-DL-YP-ETC-DKRN-2102-GAN031 | SHANTI MOHALLA WATER SUPP OFF JAL BD:PL | TG-GAN031A-1 | 19500960 | 990 | 320 | 240 | 0.98 | 707 | 239 | 1020 | 234 | 1004 | 234 | 1006 | 14 | 2019-06-30 23:30 | 139.1 | 47.8 | 1057 | Y | 101 | 101 | 98 | 3 | 0.1 | 9.3 | 89.5 | 1.1 |  |  |  |  | 26.58 | 56.4 | 56.4 | 36.57 | 691 | 661.18 | 656.17 | 681.01 | [8 empty] | 717.58 | 2.02 | 0.71 | 0.71
230 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | GAN035 | 1S-DL-YP-ETC-DKRN-2102-GAN035 | CHAMELI DEVI OUTSIDE:PL | TG-GAN035A-1 | 19506068 | 990 | 320 | 236 | 0.97 | 809 | 274 | 1174 | 219 | 941 | 316 | 1371 | 373 | 2019-06-30 15:30 | 201.3 | 33.3 | 1433 | B | 98 | 87 | 115 | 28 | 0.2 | 0.6 | 71.2 | 28 | 1 | 7 |  |  | 241.4 | 370.52 | 370.52 | 249.4 | 456.03 | 322.21 | 488.27 | 449.03 | 1.3 |  | 56.3 | 1.3 |  |  |  |  | 700.13 | 19.47 | 0.59 | 0.82
231 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | GAN038 | 1S-DL-YP-ETC-DKRN-2102-GAN038 | SHANTI MOHALL WATER SUPP OFF INSIDE:PL | TG-GAN038A-1 | 19506067 | 990 | 320 | 237 | 0.98 | 553 | 204 | 863 | 195 | 836 | 153 | 654 | 196 | 2019-06-01 19:30 | 119 | 34.2 | 977 | R | 111 | 101 | 88 | 23 | 0.2 | 0.1 | 82.2 | 17.5 |  |  | 0.3 |  | 387.15 | 502.34 | 502.34 | 534 | 328.11 | 212.52 | 87.21 | 181.26 | [8 empty] | 715.26 | 4.34 | 0.66 | 0.56
232 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | GAN043 | 1S-DL-YP-ETC-DKRN-2102-GAN043 | GALI NO.-5 SHANTI MOHLLA | TG-GAN043A-1 | 19505478 | 630 | 200 | 236 | 0.97 | 476 | 159 | 671 | 168 | 714 | 149 | 623 | 79 | 2019-06-30 23:00 | 129.6 | 32 | 739 | Y | 104 | 105 | 91 | 14 | 0.1 | 1.3 | 95.1 | 3.6 |  |  |  |  | 74.16 | 96.08 | 96.08 | 135.38 | 628.11 | 604.19 | 425.55 | 566.49 |  | 2 | [6 empty] | 702.27 | 17.33 | 0.64 | 0.76
233 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI002 | 1S-DL-YP-ETC-DKRN-2101-KRI002 | AZAD NAGAR WATER TANK:PL | TG-KRI002A-1 | 19503599 | 990 | 320 | 244 | 0.97 | 895 | 311 | 1257 | 275 | 1108 | 309 | 1237 | 140 | 2019-06-29 23:30 | 176.6 | 63.3 | 1463 | R | 107 | 85 | 108 | 23 |  | 0.1 | 17.1 | 82.8 |  |  |  |  | 68 | 302.22 | 302.22 | 100.56 | 569.56 | 400.34 | 595.56 | 574.3 | 75 | 15.3 | 73.3 | 43 | 5.3 |  |  |  | 718.26 | 1.34 | 0.6 | 0.9
234 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI006 | 1S-DL-YP-ETC-DKRN-2101-KRI006 | BHAGAT SINGH PARK NO 1:PL | TG-KRI006A-1 | 19501914 | 990 | 320 | 243 | 0.97 | 1127 | 383 | 1618 | 366 | 1532 | 378 | 1601 | 79 | 2019-06-14 | 223.7 | 67 | 1637 | R | 104 | 92 | 104 | 12 |  |  | 74 | 26 | 0.3 | 0.3 | 0.3 | 0.3 | 52.3 | 155.06 | 155.06 | 88.52 | 525.14 | 462.47 | 509.35 | 504.02 | 109.57 | 89.47 | 121.05 | 108.46 | 24.4 | 4.41 | 13.41 | 10.41 | 712.51 | 7.09 | 0.52 | 1.14
235 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI006 | 1S-DL-YP-ETC-DKRN-2101-KRI006 | BHAGAT SINGH PARK NO 1:PL | TG-KRI006A-2 | 19505735 | 630 | 200 | 245 | 0.97 | 727 | 263 | 1107 | 224 | 929 | 240 | 1010 | 154 | 2019-06-02 23:30 | 139.6 | 24.6 | 1107 | R | 96 | 83 | 121 | 38 | 0.3 | 10.1 | 83 | 6.6 | 41.11 | 17.11 | 0.11 | 0.11 | 366.39 | 508.43 | 508.43 | 398.2 | 285.37 | 169.02 | 460.43 | 295.56 | 4.56 | 3.57 | 20.55 | 3.56 | 2 | 1.3 | 3 | 2 | 700.23 | 19.37 | 0.35 | 1.15
236 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI012 | 1S-DL-YP-ETC-DKRN-2101-KRI012 | EAST AZAD NAGAR TIKONA PARK:ID | TG-KRI012A-1 | 19506591 | 990 | 320 | 237 | 0.97 | 738 | 251 | 1098 | 214 | 921 | 273 | 1187 | 235 | 2019-06-17 22:00 | 286.1 | 57.6 | 1853 | B | 91 | 89 | 120 | 31 | 0.4 | 0.4 | 59.1 | 40.1 |  |  |  |  | 312.51 | 306.44 | 306.44 | 178.35 | 392.49 | 398.26 | 611.49 | 527.05 |  | 0.3 | 39.3 |  |  |  | 1 |  | 705.4 | 14.2 | 0.63 | 0.75
237 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI023 | 1S-DL-YP-ETC-DKRN-2101-KRI023 | JHEEL NO. 4 NO 1:ID | TG-KRI023A-1 | 19505187 | 630 | 200 | 242 | 0.98 | 143 | 11 | 45 | 12 | 50 | 119 | 497 | 450 | 2019-06-05 04:30 | 87.4 | 2.4 | 497 | B | 74 | 132 | 94 | 58 | 0.2 |  | 63.8 | 36 | 694.02 | 468.55 | 691.32 | 682.32 |  | 225.07 | 225.07 | 11.3 |  |  | 0.3 | [9 empty] | 694.02 | 25.58 | 0.48 | 0.23
238 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI023 | 1S-DL-YP-ETC-DKRN-2101-KRI023 | JHEEL NO. 4 NO 1:ID | TG-KRI023A-2 | 19501978 | 990 | 320 | 233 | 0.97 | 781 | 246 | 1103 | 258 | 1164 | 278 | 1238 | 117 | 2019-06-29 16:30 | 162.7 | 15.5 | 1284 | Y | 95 | 102 | 104 | 9 |  | 3.3 | 61.9 | 34.8 | 0.3 | 0.3 | 0.3 | 0.3 | 213.39 | 194.05 | 194.05 | 176.38 | 503.16 | 515.5 | 577.47 | 540.17 |  | 7 | 2 | [5 empty] | 717.25 | 2.35 | 0.63 | 0.79
239 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI026 | 1S-DL-YP-ETC-DKRN-2101-KRI026 | KANTI NAGAR EXT. GALI NO. 5:PL | TG-KRI026A-1 | 19504956 | 990 | 320 | 246 | 0.97 | 925 | 303 | 1242 | 296 | 1215 | 326 | 1329 | 104 | 2019-06-02 00:30 | 203.9 | 75.8 | 1407 | B | 104 | 96 | 100 | 8 |  |  | 34.7 | 65.3 |  |  |  |  | 5.3 | 6 | 6 | 6.3 | 566.16 | 651.46 | 578.46 | 617.46 | 145.3 | 59.3 | 127 | 93 |  |  | 1 |  | 717.16 | 2.44 | 0.71 | 0.93
240 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI027 | 1S-DL-YP-ETC-DKRN-2101-KRI027 | KANTI NAGAR EXT. GALI NO. 9:PL | TG-KRI027A-1 | 19505349 | 990 | 320 | 250 | 0.98 | 520 | 155 | 622 | 198 | 798 | 167 | 666 | 158 | 2019-06-28 21:30 | 155.2 | 33.9 | 798 | Y | 103 | 102 | 95 | 8 |  | 0.1 | 85.7 | 14.2 | 1 |  | 2 |  | 538.31 | 550.51 | 550.51 | 573.04 | 154.26 | 143.06 | 78.53 | 120.53 | [8 empty] | 693.57 | 26.03 | 0.66 | 0.52
241 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI027 | 1S-DL-YP-ETC-DKRN-2101-KRI027 | KANTI NAGAR EXT. GALI NO. 9:PL | TG-KRI027A-2 | 19505347 | 990 | 320 | 250 | 0.97 | 892 | 274 | 1114 | 243 | 975 | 374 | 1532 | 503 | 2019-06-30 23:30 | 259.5 | 67.5 | 1535 | B | 95 | 91 | 114 | 23 | 0.2 | 3 | 84.5 | 12.3 |  |  |  |  | 89.39 | 118.3 | 118.3 | 66 | 613.25 | 585.34 | 568.11 | 629.44 | 1 |  | 87.03 | 8.2 |  |  | 10.2 |  | 704.04 | 15.56 | 0.6 | 0.9
242 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI028 | 1S-DL-YP-ETC-DKRN-2101-KRI028 | KANTI NAGAR EXT.(NALAH):PL | TG-KRI028A-1 | 19506442 | 630 | 200 | 241 | 0.98 | 423 | 222 | 953 | 113 | 484 | 88 | 369 | 536 | 2019-06-26 14:30 | 141.6 | 27.2 | 961 | R | 154 | 91 | 56 | 98 |  | 0.4 | 24.8 | 74.8 |  |  | 78.33 |  | 1 | 318.16 | 318.16 | 170.51 | 584.35 | 385.19 | 1.3 | 532.44 | 116.3 |  |  |  | 1.3 |  |  |  | 703.35 | 16.25 | 0.67 | 0.67
243 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI028 | 1S-DL-YP-ETC-DKRN-2101-KRI028 | KANTI NAGAR EXT.(NALAH):PL | TG-KRI028A-2 | 19505458 | 630 | 200 | 243 | 0.98 | 285 | 107 | 448 | 82 | 345 | 96 | 402 | 89 | 2019-06-26 16:30 | 74.4 | 6.8 | 499 | B | 112 | 87 | 101 | 25 | 0.1 | 0.2 | 65.7 | 33.9 | 5.3 | 89.41 | 25.3 | 10.3 | 562.35 | 616.19 | 616.19 | 665.3 | 138.25 | 0.3 | 77.28 | 30.3 | [8 empty] | 706.3 | 13.3 | 0.67 | 0.45
244 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI029 | 1S-DL-YP-ETC-DKRN-2101-KRI029 | KANTI NAGAR KIOSK:ID | TG-KRI029A-1 | 19503467 | 990 | 320 | 242 | 0.98 | 703 | 267 | 1100 | 219 | 895 | 217 | 881 | 212 | 2019-06-26 16:00 | 175.9 | 46.4 | 1273 | R | 119 | 87 | 94 | 32 |  | 4.5 | 94.8 | 0.7 |  |  |  |  | 9.14 | 168.13 | 168.13 | 40.14 | 689.08 | 550.22 | 655.21 | 678.21 | 20.13 | [7 empty] | 718.35 | 1.25 | 0.73 | 0.71
245 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI029 | 1S-DL-YP-ETC-DKRN-2101-KRI029 | KANTI NAGAR KIOSK:ID | TG-KRI029A-2 | 19506353 | 630 | 200 | 237 | 0.98 | 421 | 211 | 918 | 119 | 514 | 91 | 394 | 476 | 2019-06-30 23:00 | 106 | 19.4 | 918 | R | 135 | 88 | 77 | 58 | 0.3 |  | 0.5 | 99.2 |  | 10.49 | 31.27 |  | 85.43 | 493.49 | 493.49 | 354.57 | 596.51 | 200.56 | 89.19 | 350.37 | 22.3 |  |  |  | 0.3 |  |  |  | 705.34 | 14.26 | 0.6 | 0.67
246 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI030 | 1S-DL-YP-ETC-DKRN-2101-KRI030 | KANTI NAGAR MAIN ROAD:PL | TG-KRI030A-1 | 19505897 | 630 | 200 | 236 | 0.98 | 436 | 147 | 643 | 128 | 554 | 161 | 705 | 132 | 2019-06-30 23:30 | 112.6 | 35.8 | 741 | B | 95 | 88 | 116 | 28 | 0.3 | 0.3 | 87 | 12.4 |  | 1.3 |  |  | 267.04 | 340.53 | 340.53 | 198.09 | 437.07 | 361.48 | 666.44 | 506.02 | [8 empty] | 704.11 | 15.49 | 0.67 | 0.69
247 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI030 | 1S-DL-YP-ETC-DKRN-2101-KRI030 | KANTI NAGAR MAIN ROAD:PL | TG-KRI030A-2 | 19503425 | 630 | 200 | 238 | 0.98 | 332 | 107 | 462 | 106 | 457 | 119 | 516 | 57 | 2019-06-27 16:30 | 84.2 | 14.7 | 517 | B | 98 | 108 | 93 | 15 |  | 0.1 | 12.3 | 87.7 | 42.13 | 12 | 215.12 | 35.13 | 586.45 | 596.25 | 596.25 | 578.39 | 89.43 | 110.16 | 141.13 | 104.49 | [8 empty] | 718.41 | 1.19 | 0.58 | 0.53
248 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI031 | 1S-DL-YP-ETC-DKRN-2101-KRI031 | KANTI NAGAR(SATISH AGGARWAL):PL | TG-KRI031A-1 | 19504957 | 630 | 200 | 243 | 0.99 | 391 | 134 | 547 | 127 | 515 | 129 | 527 | 29 | 2019-06-26 17:30 | 110.9 | -28.1 | 566 | R | 101 | 102 | 98 | 4 |  | 0.1 | 81 | 18.9 | 156.2 | 89 | 114.3 | 109 | 336.23 | 413.43 | 413.43 | 406.13 | 226.1 | 216.1 | 181.2 | 203.4 | [8 empty] | 718.53 | 1.07 | 0.52 | 0.62
249 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI032 | 1S-DL-YP-ETC-DKRN-2101-KRI032 | KRISHNA NAGAR POLICE STATION NO. 1:ID | TG-KRI032A-1 | 19504522 | 400 | 120 | 243 | 0.98 | 62 | 9 | 37 | 32 | 137 | 21 | 90 | 87 | 2019-06-08 16:30 | 16.8 | -0.8 | 138 | Y | 33 | 153 | 114 | 120 |  |  | 55.6 | 44.4 | 718.02 | 668.32 | 718.02 | 718.02 |  | 49.3 | 49.3 | [13 empty] | 718.02 | 1.58 | 0.66 | 0.15
250 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI032 | 1S-DL-YP-ETC-DKRN-2101-KRI032 | KRISHNA NAGAR POLICE STATION NO. 1:ID | TG-KRI032A-2 | 19501913 | 400 | 120 | 257 | 0.97 | 41 | 26 | 105 | 12 | 47 | 3 | 11 | 82 | 2019-06-02 23:00 | 10.8 | 0.8 | 105 | R | 191 | 93 | 16 | 175 |  | 0.1 | 73.7 | 26.2 | 718 | 718 | 718 | 718 | [16 empty] | 718 | 2 | 0.52 | 0.1
251 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI039 | 1S-DL-YP-ETC-DKRN-2101-KRI039 | RAJGARH EXTN.(MINI STADIUM):ID | TG-KRI039A-1 | 19506625 | 990 | 320 | 241 | 0.97 | 793 | 236 | 1099 | 207 | 914 | 350 | 1707 | 719 | 2019-06-11 01:00 | 248 | 32 | 1744 | B | 97 | 99 | 104 | 7 | 0.4 | 0.2 | 81.2 | 18.1 | 14.21 | 20.3 | 19.21 | 19.51 | 433.17 | 419.3 | 419.3 | 418.09 | 253.42 | 261.5 | 288.59 | 263.2 | 0.3 |  | 3.51 | 0.3 |  |  | 1 |  | 701.5 | 18.1 | 0.48 | 0.8
252 | 2019-06-14 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI039 | 1S-DL-YP-ETC-DKRN-2101-KRI039 | RAJGARH EXTN.(MINI STADIUM):ID | TG-KRI039A-2 | 19505976 | 990 | 320 | 236 | 0.97 | 1007 | 441 | 2016 | 259 | 1145 | 307 | 1347 | 789 | 2019-06-29 23:00 | 247.7 | 50.6 | 2016 | R | 100 | 97 | 103 | 6 | 0.5 | 0.4 | 55.5 | 43.6 |  | 1 | 1.1 |  | 157.07 | 138.22 | 138.22 | 141.22 | 196.15 | 227.3 | 210.15 | 214 | 23.3 | 12.3 | 34.3 | 23 | 2.3 |  | 1.3 | 1 | 379.22 | 28.38 | 0.48 | 1.02
253 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI040 | 1S-DL-YP-ETC-DKRN-2101-KRI040 | RAJGARH MOTHER DAIRY GALI NO 6:PL | TG-KRI040A-1 | 19500881 | 990 | 320 | 238 | 0.97 | 963 | 334 | 1476 | 337 | 1503 | 292 | 1297 | 194 | 2019-06-11 | 193.6 | 64 | 1602 | Y | 97 | 109 | 95 | 14 |  | 0.6 | 68.2 | 31.1 |  |  |  |  | 180.48 | 65.16 | 65.16 | 134.47 | 468.35 | 554.46 | 473.37 | 515.45 | 64.03 | 88.54 | 42.13 | 63.1 | 0.16 | 4.46 |  |  | 713.42 | 6.18 | 0.56 | 0.97
254 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI040 | 1S-DL-YP-ETC-DKRN-2101-KRI040 | RAJGARH MOTHER DAIRY GALI NO 6:PL | TG-KRI040A-2 | 19504387 | 990 | 320 | 240 | 0.97 | 836 | 334 | 1416 | 246 | 1031 | 257 | 1087 | 360 | 2019-06-12 02:30 | 178.8 | 51.5 | 1416 | R | 112 | 95 | 94 | 18 |  |  | 65.5 | 34.5 |  |  | 0.3 |  | 170.34 | 332.08 | 332.08 | 266.08 | 502.56 | 382.12 | 394.29 | 445.44 | 40.29 |  | 0.18 | 2.28 | 0.21 |  |  |  | 714.2 | 5.4 | 0.55 | 0.84
255 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI044 | 1S-DL-YP-ETC-DKRN-2101-KRI044 | SHANKAR NAGAR EXT.:PL | TG-KRI044A-1 | 19506066 | 990 | 320 | 240 | 0.98 | 671 | 231 | 964 | 259 | 1093 | 181 | 758 | 292 | 2019-06-02 15:30 | 149.8 | 27.8 | 1317 | Y | 107 | 127 | 66 | 61 | 0.2 | 9.8 | 84.8 | 5.1 |  |  | 24.21 |  | 116.51 | 18.51 | 18.51 | 156.51 | 601.28 | 678.15 | 107.09 | 561.28 |  | 21.13 | [6 empty] | 718.19 | 1.41 | 0.71 | 0.68
256 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI044 | 1S-DL-YP-ETC-DKRN-2101-KRI044 | SHANKAR NAGAR EXT.:PL | TG-KRI044A-2 | 19506141 | 630 | 120 | 240 | 0.98 | 470 | 126 | 524 | 160 | 672 | 184 | 768 | 213 | 2019-06-02 15:30 | 88.9 | 7.2 | 813 | B | 81 | 98 | 121 | 40 | 0.1 | 0.4 | 0.4 | 99.2 | 54.3 | 6.3 | 0.3 | 4.3 | 399.53 | 332.51 | 332.51 | 336.51 | 240.52 | 355.54 | 418.34 | 353.54 |  |  | 41.5 | [5 empty] | 695.15 | 24.45 | 0.58 | 0.75
257 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI045 | 1S-DL-YP-ETC-DKRN-2101-KRI045 | SHANKAR NAGAR MAIN ROAD SCHOOL NO 1:PL | TG-KRI045A-1 | 19501909 | 990 | 320 | 239 | 0.97 | 740 | 285 | 1233 | 225 | 959 | 230 | 988 | 261 | 2019-06-29 23:30 | 163.4 | 49.3 | 1233 | R | 107 | 92 | 101 | 15 |  | 0.3 | 76.9 | 22.7 |  |  |  |  | 108.19 | 232.19 | 232.19 | 128.49 | 603.52 | 483.12 | 583.18 | 586.42 | 3.2 | [7 empty] | 715.31 | 4.29 | 0.65 | 0.75
258 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI045 | 1S-DL-YP-ETC-DKRN-2101-KRI045 | SHANKAR NAGAR MAIN ROAD SCHOOL NO 1:PL | TG-KRI045A-2 | 19506354 | 990 | 320 | 245 | 0.97 | 1018 | 335 | 1366 | 432 | 1765 | 251 | 1018 | 647 | 2019-06-01 01:00 | 223.7 | 71.4 | 1765 | Y | 99 | 124 | 77 | 47 | 0.3 |  | 2 | 97.8 |  |  |  |  | 18 |  |  | 11.3 | 655.51 | 485.09 | 525.15 | 659.05 | 30.28 | 175.22 |  | 34.44 | 1.45 | 45.33 |  | 0.45 | 706.04 | 13.56 | 0.59 | 1.03
259 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI052 | 1S-DL-YP-ETC-DKRN-2101-KRI052 | WEST AZAD NAGAR (RASGULLA):PL | TG-KRI052A-1 | 19506565 | 990 | 320 | 251 | 0.97 | 882 | 252 | 1015 | 318 | 1268 | 312 | 1256 | 247 | 2019-06-11 23:30 | 215.7 | 60.5 | 1356 | B | 89 | 106 | 104 | 17 | 0.3 | 0.1 | 46.5 | 53.2 |  |  |  |  | 342.08 | 180.11 | 180.11 | 246.33 | 360.03 | 462.14 | 416.33 | 428.38 | 0.3 | 60.16 | 62 | 27.3 |  |  |  |  | 702.41 | 17.19 | 0.55 | 0.89
260 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI053 | 1S-DL-YP-ETC-DKRN-2101-KRI053 | WEST AZAD NAGAR SHD ROAD B&D BL NO. 1:ID | TG-KRI053A-1 | 19506717 | 990 | 320 | 236 | 0.98 | 832 | 251 | 1021 | 371 | 1994 | 210 | 915 | 1031 | 2019-06-10 23:00 | 269.1 | 45.1 | 1994 | Y | 96 | 94 | 109 | 15 | 94 | 5.2 | 0.8 | [5 empty] | 170.17 | 221.15 | 221.15 | 121.45 | 523.07 | 480.34 | 629.49 | 578.34 | 8.55 |  | 3 | 2 |  | 0.3 |  |  | 702.19 | 17.41 | 0.59 | 0.84
261 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI053 | 1S-DL-YP-ETC-DKRN-2101-KRI053 | WEST AZAD NAGAR SHD ROAD B&D BL NO. 1:ID | TG-KRI053A-2 | 19501884 | 990 | 200 | 240 | 0.97 | 954 | 322 | 1346 | 281 | 1151 | 351 | 1463 | 273 | 2019-06-10 03:00 | 196.9 | 71.8 | 1475 | B | 103 | 89 | 108 | 19 |  | 0.8 | 67.5 | 31.7 |  |  |  |  | 87 | 218.15 | 218.15 | 105.01 | 586.35 | 481.01 | 538.09 | 564.26 | 39.25 | 13.44 | 94.54 | 43.33 |  |  | 3.55 |  | 713 | 7 | 0.56 | 0.96
262 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI053 | 1S-DL-YP-ETC-DKRN-2101-KRI053 | WEST AZAD NAGAR SHD ROAD B&D BL NO. 1:ID | TG-KRI053A-3 | 19505228 | 630 | 200 | 241 | 0.96 | 768 | 253 | 1090 | 258 | 1129 | 257 | 1123 | 36 | 2019-06-11 01:00 | 179.4 | 64 | 1281 | R | 107 | 97 | 96 | 11 | 0.3 | 0.1 | 49.4 | 50.3 |  |  |  |  | 3 | 6 | 6 | 5 | 452.01 | 522.52 | 520.22 | 506.52 | 161.51 | 136.45 | 138.3 | 142 | 89.25 | 40.4 | 37.55 | 52.25 | 706.17 | 13.43 | 0.58 | 1.22
263 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI055 | 1S-DL-YP-ETC-DKRN-2101-KRI055 | WEST AZAD NAGAR(KEHAR SINGH)RLG NO 1:ID | TG-KRI055A-1 | 19501973 | 990 | 320 | 241 | 0.97 | 888 | 290 | 1237 | 300 | 1302 | 298 | 1286 | 59 | 2019-06-30 23:30 | 161.9 | 62.6 | 1302 | Y | 105 | 103 | 93 | 12 |  | 1.7 | 97.8 | 0.6 |  |  | 1 |  | 197.35 | 224.1 | 224.1 | 263.2 | 497.36 | 469.01 | 347.43 | 432.21 | 22 | 24 | 14.3 | 21.3 |  |  |  |  | 717.11 | 2.49 | 0.53 | 0.9
264 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI055 | 1S-DL-YP-ETC-DKRN-2101-KRI055 | WEST AZAD NAGAR(KEHAR SINGH)RLG NO 1:ID | TG-KRI055A-2 | 19501602 | 990 | 320 | 242 | 0.98 | 785 | 296 | 1262 | 210 | 882 | 279 | 1194 | 351 | 2019-06-11 23:30 | 139.8 | 47.8 | 1280 | B | 109 | 82 | 109 | 27 |  | 1.4 | 94.4 | 4.1 | 1.3 | 1.3 | 1.3 | 1.3 | 89.47 | 396.43 | 396.43 | 163.3 | 614.02 | 319.36 | 619.35 | 552.49 | 12.3 |  | 9.3 | [5 empty] | 717.49 | 2.11 | 0.61 | 0.79
265 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI057 | 1S-DL-YP-ETC-DKRN-2101-KRI057 | WEST KANTI NAGAR:ID | TG-KRI057A-1 | 19504088 | 990 | 320 | 244 | 0.97 | 866 | 244 | 990 | 280 | 1140 | 342 | 1390 | 350 | 2019-06-29 22:30 | 206.1 | 72.9 | 1450 | B | 86 | 94 | 120 | 34 |  |  | 0.3 | 99.7 |  |  |  |  | 14 | 1 | 1 |  | 705.58 | 717.58 | 530.58 | 710.28 |  | 1 | 181.3 | 9.3 |  |  | 7.3 |  | 719.58 | 0.02 | 0.7 | 0.87
266 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI066 | 1S-DL-YP-ETC-DKRN-2101-KRI066 | East Azad Nagar Primary School | TG-KRI066A-1 | 19506021 | 990 | 320 | 245 | 0.96 | 874 | 268 | 1102 | 283 | 1170 | 323 | 1324 | 197 | 2019-06-02 23:00 | 234.9 | 64 | 2011 | R | 93 | 98 | 110 | 17 | 0.4 | 0.1 | 37.6 | 62 |  |  |  |  | 269.4 | 216.19 | 216.19 | 195.49 | 426.18 | 479.45 | 490.36 | 476.45 | 9 | 9 | 97.08 | 32.3 | 0.06 |  |  |  | 705.04 | 14.56 | 0.58 | 0.88
267 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI067 | 1S-DL-YP-ETC-DKRN-2101-KRI067 | DAV School Rajgarh Extension | TG-KRI067A-1 | 19505185 | 990 | 320 | 247 | 0.96 | 712 | 241 | 1030 | 143 | 640 | 328 | 1533 | 776 | 2019-06-11 01:00 | 208.6 | 36.5 | 1533 | B | 123 | 88 | 89 | 35 | 0.1 | 6.1 | 89.8 | 4 | 0.3 |  | 0.3 | 0.3 | 59.57 | 395.51 | 395.51 | 208.08 | 631.45 | 297.16 | 277.16 | 484.29 | 0.55 |  | 0.3 | [5 empty] | 693.07 | 26.53 | 0.61 | 0.72
268 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI070 | 1S-DL-YP-ETC-DKRN-2101-KRI070 | DDA Park West Kanti Nagar | TG-KRI070A-1 | 19506563 | 630 | 200 | 243 | 0.98 | 317 | 104 | 431 | 97 | 402 | 116 | 475 | 63 | 2019-06-30 16:30 | 84.8 | 16.2 | 516 | B | 105 | 91 | 103 | 14 | 0.1 |  | 73.7 | 26.2 |  | 7.3 |  | 1 | 390.24 | 576.08 | 576.08 | 507.14 | 316.46 | 123.32 | 297.47 | 198.56 | [8 empty] | 707.1 | 12.5 | 0.74 | 0.5
269 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI001 | 1S-DL-YP-ETC-DKRN-2101-KRI001 | A-BLOCK KRN:PL | TG-KRI001A-1 | 19505570 | 990 | 320 | 238 | 0.98 | 896 | 249 | 1104 | 372 | 1718 | 275 | 1254 | 555 | 2019-06-11 01:00 | 208 | 29.4 | 1807 | Y | 91 | 107 | 102 | 16 | 1.9 | 37.8 | 56.5 | 3.7 |  |  |  |  | 108.49 | 60.58 | 60.58 | 72.5 | 592.2 | 544.18 | 561.48 | 584.56 |  | 90.53 | 60.32 | 43.23 |  | 5 |  |  | 701.09 | 18.51 | 0.62 | 0.91
270 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI001 | 1S-DL-YP-ETC-DKRN-2101-KRI001 | A-BLOCK KRN:PL | TG-KRI001A-2 | 19505929 | 630 | 200 | 240 | 0.97 | 275 | 66 | 270 | 103 | 429 | 106 | 443 | 166 | 2019-06-11 17:00 | 84 | 1.4 | 480 | Y | 68 | 124 | 108 | 56 | 0.4 | 0.6 | 95.3 | 3.7 | 468.25 | 397.49 | 426.15 | 444.2 | 231.47 | 216.22 | 216.22 | 250.22 | 1 | 87.01 | 15.13 | 6.3 | [8 empty] | 701.12 | 18.48 | 0.44 | 0.44
271 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI003 | 1S-DL-YP-ETC-DKRN-2101-KRI003 | B-BLOCK KRISHNA NAGAR 8/24:PM | TG-KRI003A-1 | 19505516 | 630 | 200 | 238 | 0.98 | 587 | 205 | 877 | 201 | 866 | 180 | 769 | 103 | 2019-06-12 00:30 | 125 | 35.6 | 1211 | Y | 97 | 102 | 101 | 5 | 0.4 | 0.2 | 58 | 41.4 |  |  |  |  | 115.33 | 52.03 | 52.03 | 48.03 | 535.5 | 587.15 | 646.32 | 611.51 | 54.45 | 66.2 | 21.03 | 46.14 |  | 0.3 |  |  | 706.08 | 13.52 | 0.6 | 0.93
272 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI004 | 1S-DL-YP-ETC-DKRN-2101-KRI004 | K-BLK KRN GHONOLI CHOWK:PL | TG-KRI004A-1 | 19500863 | 990 | 320 | 243 | 0.97 | 953 | 300 | 1254 | 351 | 1475 | 302 | 1265 | 216 | 2019-06-12 | 206.8 | 87.6 | 1552 | Y | 89 | 115 | 96 | 26 |  | 0.8 | 85.9 | 13.3 |  |  |  |  | 8 |  |  |  | 679.31 | 400.49 | 652.01 | 610.38 | 28.59 | 277.03 | 63.59 | 105.52 |  | 38.38 |  |  | 716.3 | 3.3 | 0.71 | 0.96
273 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI004 | 1S-DL-YP-ETC-DKRN-2101-KRI004 | K-BLK KRN GHONOLI CHOWK:PL | TG-KRI004A-2 | 19504624 | 990 | 320 | 244 | 0.97 | 756 | 290 | 1198 | 271 | 1122 | 195 | 796 | 370 | 2019-06-27 00:30 | 178.1 | 56.7 | 1228 | R | 105 | 106 | 89 | 17 |  | 0.9 | 90.8 | 8.3 |  |  |  |  | 157.3 | 123 | 123 | 169 | 547.13 | 591.43 | 434.43 | 547.28 | 11.45 | 1.45 | [6 empty] | 716.28 | 3.32 | 0.63 | 0.76
274 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI005 | 1S-DL-YP-ETC-DKRN-2101-KRI005 | B - BLOCK MEERA MANDAL | TG-KRI005A-1 | 19504858 | 1600 | 500 | 244 | 0.97 | 1085 | 328 | 1421 | 437 | 1869 | 320 | 1391 | 463 | 2019-06-30 00:30 | 259.9 | 84 | 1951 | Y | 94 | 123 | 83 | 40 |  | 10.6 | 89.3 | 0.1 |  |  | 2.3 |  | 382.24 | 72.3 | 72.3 | 318.24 | 335.52 | 638.04 | 201.37 | 399.52 |  | 7.42 | [6 empty] | 718.16 | 1.44 | 0.63 | 0.68
275 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI008 | 1S-DL-YP-ETC-DKRN-2101-KRI008 | C-BLOCK KRISHNA NAGAR NO 1:ID | TG-KRI008A-1 | 19505740 | 990 | 320 | 245 | 0.98 | 876 | 303 | 1253 | 285 | 1171 | 288 | 1194 | 74 | 2019-06-01 20:30 | 159 | 47.4 | 1261 | Y | 97 | 101 | 102 | 5 | 0.1 |  | 46.8 | 53.1 | 0.3 | 0.3 | 0.3 | 0.3 | 121 | 67.3 | 67.3 | 83.3 | 559 | 614.3 | 606.3 | 603.3 | 27.28 | 25.28 | 19.58 | 20.28 |  |  |  |  | 707.58 | 12.02 | 0.64 | 0.89
276 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI008 | 1S-DL-YP-ETC-DKRN-2101-KRI008 | C-BLOCK KRISHNA NAGAR NO 1:ID | TG-KRI008A-2 | 19506020 | 990 | 320 | 245 | 0.98 | 1185 | 220 | 927 | 438 | 2069 | 527 | 2370 | 1319 | 2019-06-01 19:30 | 374.7 | 38.4 | 2370 | B | 84 | 108 | 107 | 24 | 0.4 | 0.1 | 40.8 | 58.7 | 2.3 |  | 0.3 |  | 229 | 99 | 99 | 149.3 | 465.09 | 394.35 | 388.36 | 417.35 | 9.58 | 195.33 | 162.36 | 138.36 | 0.25 | 17.54 | 22.51 | 1.21 | 707.02 | 12.58 | 0.49 | 1.2
277 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI010 | 1S-DL-YP-ETC-DKRN-2101-KRI010 | CHHACHHI BUILDING:PL | TG-KRI010A-1 | 19506777 | 990 | 320 | 246 | 0.97 | 926 | 300 | 1352 | 376 | 1625 | 250 | 1043 | 504 | 2019-06-01 19:00 | 294.7 | 35.8 | 1704 | B | 87 | 108 | 105 | 21 | 0.3 |  | 49.1 | 50.6 | 122.13 | 24.21 | 70.43 | 65.13 | 333.4 | 303.31 | 303.31 | 333.38 | 247.1 | 374.11 | 314.42 | 304.12 | 0.3 | 1.3 | 7.3 | 1 | 0.3 | 0.3 | 0.3 |  | 704.03 | 15.57 | 0.44 | 0.94
278 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI011 | 1S-DL-YP-ETC-DKRN-2101-KRI011 | D-BLOCK KRISHNA NAGAR:PL | TG-KRI011A-1 | 19506772 | 990 | 320 | 238 | 0.98 | 1201 | 449 | 1967 | 309 | 1313 | 444 | 2053 | 701 | 2019-06-01 19:00 | 393.9 | 35.5 | 2053 | B | 104 | 101 | 94 | 10 | 72 | 2.3 | 12 | 13.6 |  |  |  |  | 42 | 137.3 | 137.3 | 71 | 592.06 | 514.22 | 650.18 | 610.52 | 69.05 | 51.19 | 3.53 | 22.49 | 2 | 2 | 1 | 0.3 | 705.11 | 14.49 | 0.48 | 1.21
279 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI013 | 1S-DL-YP-ETC-DKRN-2101-KRI013 | F-BLOCK KRISHNA NAGAR:K | TG-KRI013A-1 | 19506776 | 990 | 320 | 243.0487 | 0.97068 | 1058.1356 | 364.2844 | 1638.8537 | 424.5189 | 1845.574 | 269.3322 | 1131.6956 | 636.2252 | 2019-06-01 19:00 | [15 empty] | 0 |  |  |  | 9.5 |  |  |  | 546 |  |  |  | 150.5 |  |  |  | 8 | 714 |  | 0.64202 | 1.0688
280 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI013 | 1S-DL-YP-ETC-DKRN-2101-KRI013 | F-BLOCK KRISHNA NAGAR:K | TG-KRI013A-2 | 19505739 | 630 | 200 | 245 | 0.98 | 404 | 129 | 550 | 129 | 561 | 146 | 617 | 62 | 2019-06-30 23:30 | 80.8 | -8 | 623 | B | 99 | 102 | 99 | 3 | 81.6 | 12.3 | 4.6 | 1.5 | 4 |  | 1 |  | 413.13 | 398.43 | 398.43 | 410.13 | 286.19 | 304.49 | 298.34 | 293.19 | [8 empty] | 703.32 | 16.28 | 0.61 | 0.64
281 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI014 | 1S-DL-YP-ETC-DKRN-2101-KRI014 | E-BLOCK KRN (PARK) E 15,16:PL | TG-KRI014A-1 | 19506370 | 990 | 320 | 239 | 0.97 | 899 | 210 | 886 | 265 | 1145 | 423 | 1807 | 823 | 2019-06-11 23:00 | 225.3 | 37.4 | 1807 | B | 91 | 106 | 102 | 15 |  | 0.1 | 1.6 | 98.3 | 8.3 | 2 | 10.3 | 3.3 | 410.57 | 324 | 324 | 370.59 | 288.42 | 369.09 | 327.4 | 331.4 |  | 12 | 11.3 | 2 |  | 1 | 0.3 |  | 708.09 | 11.51 | 0.47 | 0.91
282 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI015 | 1S-DL-YP-ETC-DKRN-2101-KRI015 | E-BLOCK KRN LAJ PAT RAI CHOWK:PL | TG-KRI015A-1 | 19505576 | 990 | 320 | 239 | 0.97 | 760 | 170 | 778 | 410 | 2012 | 180 | 800 | 1223 | 2019-06-11 01:00 | 255 | 45.1 | 2012 | Y | 93 | 102 | 105 | 12 | 0.4 |  | 68.5 | 31.1 | 14 | 2.3 | 0.3 | 0.3 | 300.3 | 214.35 | 214.35 | 233.35 | 333.47 | 430.42 | 409.22 | 414.42 | 0.3 | 0.3 |  |  |  | 0.3 |  |  | 648.47 | 47.13 | 0.56 | 0.77
283 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI015 | 1S-DL-YP-ETC-DKRN-2101-KRI015 | E-BLOCK KRN LAJ PAT RAI CHOWK:PL | TG-KRI015A-2 | 19505772 | 630 | 200 | 238 | 0.98 | 537 | 228 | 1103 | 172 | 794 | 136 | 607 | 433 | 2019-06-11 01:00 | 175.6 | 32.4 | 1148 | Y | 101 | 107 | 92 | 15 | 0.4 | 0.1 | 54 | 45.5 |  |  |  |  | 23.01 | 21.02 | 21.02 | 21.01 | 677.12 | 640.53 | 651.02 | 682.42 | 4 | 42.18 | 1 | 1 | 0.3 | 0.3 |  |  | 704.43 | 15.17 | 0.67 | 0.85
284 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI016 | 1S-DL-YP-ETC-DKRN-2101-KRI016 | F-BLOCK KRN:K | TG-KRI016A-1 | 29502000 | 990 | 320 | 244 | 0.97 | 494 | 145 | 623 | 166 | 710 | 184 | 789 | 143 | 2019-06-03 02:00 | 128.8 | 20.6 | 892 | B | 101 | 89 | 110 | 21 |  |  | 6.5 | 93.5 | 48.59 | 111.53 | 26.24 | 36.47 | 576.34 | 566.11 | 566.11 | 609.17 | 87.01 | 34.3 | 153.03 | 66.3 | [8 empty] | 712.34 | 7.26 | 0.6 | 0.5
285 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI017 | 1S-DL-YP-ETC-DKRN-2101-KRI017 | F-BLOCK KRN PLM:PL | TG-KRI017A-1 | 19506778 | 990 | 320 | 239 | 0.98 | 986 | 427 | 2101 | 297 | 1384 | 262 | 1224 | 809 | 2019-06-11 03:30 | 247 | 32.3 | 2101 | R | 104 | 112 | 84 | 28 | 0.4 |  | 10.1 | 89.5 | 22.02 | 0.02 | 60.48 | 4.46 | 332.58 | 299.08 | 299.08 | 374.4 | 329 | 382.26 | 195.08 | 315 | 13.52 | 15.38 | 0.3 | 4.18 | 0.52 | 1.3 |  |  | 698.44 | 21.16 | 0.41 | 1
286 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI017 | 1S-DL-YP-ETC-DKRN-2101-KRI017 | F-BLOCK KRN PLM:PL | TG-KRI017A-2 | 19506503 | 630 | 200 | 239 | 0.98 | 556 | 147 | 652 | 228 | 1011 | 181 | 799 | 312 | 2019-06-11 01:00 | 157.6 | 8.8 | 1564 | Y | 100 | 112 | 88 | 24 | 0.3 | 0.1 | 49.6 | 50 | 120.53 | 155.21 | 285.38 | 172.35 | 392.32 | 290.25 | 290.25 | 297.56 | 182.04 | 201.05 | 181.06 | 221.36 | 3.3 | 44.22 | 0.3 | 6.52 |  | 7.46 |  |  | 698.59 | 21.01 | 0.38 | 0.88
287 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI018 | 1S-DL-YP-ETC-DKRN-2101-KRI018 | H-BLOCK KRISHNA NAGAR (MOTHER DAIRY):K | TG-KRI018A-1 | 19506775 | 990 | 320 | 231.0076 | 0.9804 | 735.1891 | 209.8819 | 924.7938 | 254.4 | 1130.6667 | 270.9072 | 1220.2476 | 262.3941 | 2019-06-03 12:00 | [15 empty] | 0 |  |  |  | 300 |  |  |  | 416.5 |  |  |  | 0 |  |  |  | 0 | 716.5 |  | 0.55897 | 0.74262
288 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI018 | 1S-DL-YP-ETC-DKRN-2101-KRI018 | H-BLOCK KRISHNA NAGAR (MOTHER DAIRY):K | TG-KRI018A-2 | 19506531 | 630 | 200 | 235 | 0.97 | 629 | 167 | 751 | 222 | 995 | 240 | 1074 | 291 | 2019-06-11 00:30 | 176.6 | 17.4 | 1263 | R | 81 | 109 | 110 | 29 | 0.5 | 0.7 | 5.4 | 93.4 | 3.05 | 0.2 | 0.22 | 0.2 | 340.38 | 96.26 | 96.26 | 156.42 | 340.27 | 556.46 | 485.08 | 510.56 | 9.39 | 41.27 | 79.18 | 28.21 | 2.3 | 1.2 | 6.23 |  | 696.19 | 23.41 | 0.52 | 1
289 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI019 | 1S-DL-YP-ETC-DKRN-2101-KRI019 | J-BLOCK KRN:PL | TG-KRI019A-1 | 19506883 | 1600 | 500 | 244 | 0.97 | 1299 | 382 | 1663 | 360 | 1564 | 556 | 2455 | 846 | 2019-06-03 | 449 | 83 | 2455 | B | 100 | 99 | 100 | 1 | 0.3 |  | 8.2 | 91.5 |  |  |  |  | 285.38 | 302.25 | 302.25 | 311.3 | 421.15 | 390.28 | 354.11 | 394.54 |  | 14 | 23.05 | 0.29 |  |  | 0.29 |  | 706.53 | 13.07 | 0.55 | 0.81
290 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI019 | 1S-DL-YP-ETC-DKRN-2101-KRI019 | J-BLOCK KRN:PL | TG-KRI019A-2 | 19505280 | 990 | 320 | 244 | 0.97 | 1013 | 335 | 1417 | 334 | 1419 | 343 | 1445 | 27 | 2019-06-11 03:30 | 325.4 | 58.9 | 1866 | Y | 94 | 103 | 102 | 9 | 0.3 |  | 1.3 | 98.4 |  |  | 0.3 |  | 19.3 | 2 | 2 | 5.3 | 612.42 | 595.07 | 585.23 | 605.26 | 70.37 | 103.23 | 106.42 | 92.1 | 1.16 | 3.35 | 2 | 0.59 | 704.05 | 15.55 | 0.63 | 1.02
291 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI020 | 1S-DL-YP-ETC-DKRN-2101-KRI020 | JHEEL NO. 1:PL | TG-KRI020A-1 | 19503581 | 630 | 200 | 240 | 0.98 | 528 | 172 | 729 | 183 | 775 | 173 | 723 | 49 | 2019-06-02 16:00 | 125.1 | -0.9 | 860 | Y | 101 | 105 | 93 | 12 |  |  | 58.9 | 41.1 |  |  |  |  | 67 | 77.3 | 77.3 | 95.3 | 651.41 | 566.46 | 557.41 | 616.41 | 1 | 75.25 | 9.3 | 7.3 |  |  |  |  | 719.41 | 0.19 | 0.67 | 0.84
292 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI021 | 1S-DL-YP-ETC-DKRN-2101-KRI021 | JHEEL NO. 2:PL | TG-KRI021A-1 | 19506780 | 990 | 320 | 240 | 0.99 | 885 | 298 | 1255 | 279 | 1176 | 307 | 1303 | 110 | 2019-06-30 16:00 | 220.2 | -20.2 | 2080 | B | 96 | 98 | 106 | 10 | 0.3 | 0.1 | 35.3 | 64.3 | 0.02 | 0.02 | 0.02 | 0.02 | 10.3 | 5 | 5 | 6.3 | 675.29 | 637.5 | 623.32 | 672.02 | 15 | 58.39 | 74.57 | 22.57 | 0.3 |  | 0.3 |  | 701.31 | 18.29 | 0.71 | 0.89
293 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI021 | 1S-DL-YP-ETC-DKRN-2101-KRI021 | JHEEL NO. 2:PL | TG-KRI021A-2 | 19506368 | 630 | 200 | 246 | 0.97 | 240 | 85 | 350 | 79 | 324 | 76 | 310 | 36 | 2019-06-12 17:30 | 69 | 0.6 | 441 | Y | 81 | 127 | 92 | 46 | 0.3 |  | 66.1 | 33.7 | 453.11 | 200.08 | 405.31 | 365.01 | 247.44 | 500.47 | 500.47 | 336.24 | 0.3 | 0.3 | 1.3 | [9 empty] | 701.25 | 18.35 | 0.51 | 0.38
294 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI025 | 1S-DL-YP-ETC-DKRN-2101-KRI025 | JHEEL NO. 3-5:PL | TG-KRI025A-1 | 19505930 | 990 | 300 | 245 | 0.98 | 923 | 255 | 1061 | 189 | 823 | 479 | 2286 | 1360 | 2019-06-30 14:30 | 265.2 | 34.8 | 2286 | B | 109 | 81 | 110 | 29 | 0.4 | 1.8 | 94.2 | 3.6 | 0.3 | 14.14 | 0.3 | 0.17 | 138.54 | 333.47 | 333.47 | 203.22 | 561.37 | 362 | 552.23 | 505.52 | 10 | 1 | 7.53 | 1.3 |  |  | 0.3 |  | 711.01 | 8.59 | 0.53 | 0.93
295 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI025 | 1S-DL-YP-ETC-DKRN-2101-KRI025 | JHEEL NO. 3-5:PL | TG-KRI025A-2 | 19505404 | 630 | 200 | 237 | 0.97 | 594 | 210 | 951 | 102 | 430 | 283 | 1241 | 712 | 2019-06-30 19:00 | 220.8 | 41.4 | 1241 | B | 106 | 94 | 100 | 12 | 0.3 |  | 15.2 | 84.5 |  |  |  |  | 108.52 | 185.16 | 185.16 | 118.52 | 561.22 | 504.31 | 596.44 | 570.25 | 19.33 |  |  | 0.3 |  |  | 0.3 |  | 689.47 | 30.13 | 0.54 | 0.94
296 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI034 | 1S-DL-YP-ETC-DKRN-2101-KRI034 | OLD ANARKALI:ID | TG-KRI034A-1 | 19505248 | 990 | 320 | 244 | 0.96 | 711 | 241 | 976 | 225 | 906 | 245 | 995 | 81 | 2019-06-30 01:00 | 172.5 | 36.8 | 1150 | R | 118 | 88 | 95 | 30 | 0.3 |  | 2.9 | 96.8 | 1.18 | 27.43 | 17.43 | 8.48 | 326.58 | 509.42 | 509.42 | 453.22 | 372.32 | 165.53 | 219.01 | 241.08 | 2.3 | [7 empty] | 703.18 | 16.42 | 0.52 | 0.72
297 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI034 | 1S-DL-YP-ETC-DKRN-2101-KRI034 | OLD ANARKALI:ID | TG-KRI034A-2 | 19506681 | 990 | 320 | 242.4105 | 0.97121 | 1155.2748 | 434.2842 | 1825.3371 | 333.0169 | 1392.2691 | 387.9737 | 1609.5823 | 375.0487 | 2019-06-11 23:30 | [15 empty] | 0 |  |  |  | 42.5 |  |  |  | 520.5 |  |  |  | 105.5 |  |  |  | 49.5 | 718 |  | 0.54331 | 1.1669
298 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI034 | 1S-DL-YP-ETC-DKRN-2101-KRI034 | OLD ANARKALI:ID | TG-KRI034A-3 | 19506766 | 630 | 200 | 243 | 0.97 | 538 | 214 | 918 | 170 | 721 | 153 | 649 | 241 | 2019-06-30 23:30 | 149.4 | 16.2 | 956 | R | 120 | 96 | 84 | 36 | 0.4 | 5 | 47.5 | 47.1 | 48.17 | 0.3 | 48.17 | 29.3 | 11.3 | 221.24 | 221.24 | 108.43 | 541.14 | 480.37 | 413.5 | 553.48 | 100.3 | 4 | 0.3 | 14.3 | 5 |  |  |  | 706.31 | 13.29 | 0.59 | 0.85
299 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI035 | 1S-DL-YP-ETC-DKRN-2101-KRI035 | PANDIT PARK:PM | TG-KRI035A-1 | 19500865 | 990 | 320 | 234.6773 | 0.9577 | 1067.1793 | 324.445 | 1399.4348 | 368.913 | 1605.5751 | 373.8213 | 1604.4523 | 205.5812 | 2019-06-01 16:00 | [15 empty] | 0 |  |  |  | 12.5 |  |  |  | 560.5 |  |  |  | 143.5 |  |  |  | 3 | 719.5 |  | 0.6205 | 1.078
300 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI036 | 1S-DL-YP-ETC-DKRN-2101-KRI036 | RADHA PURI EXTN.(NALAH) NO. 1:PL | TG-KRI036A-1 | 19506680 | 990 | 320 | 238 | 0.98 | 915 | 224 | 969 | 361 | 1583 | 329 | 1449 | 559 | 2019-06-30 23:00 | 234.6 | 57.6 | 1863 | Y | 83 | 112 | 105 | 29 | 0.4 |  | 11.4 | 88.2 |  |  |  |  | 325.3 | 91.43 | 91.43 | 160.11 | 380.06 | 482.23 | 489.23 | 483.55 |  | 115.3 | 88 | 61.3 |  | 16 | 2 |  | 705.36 | 14.24 | 0.57 | 0.92
301 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI036 | 1S-DL-YP-ETC-DKRN-2101-KRI036 | RADHA PURI EXTN.(NALAH) NO. 1:PL | TG-KRI036A-2 | 19505285 | 630 | 200 | 244 | 0.96 | 376 | 176 | 739 | 125 | 521 | 75 | 310 | 371 | 2019-06-12 | 88.8 | 19 | 809 | R | 123 | 110 | 67 | 56 | 0.2 | 0.1 | 4.2 | 95.5 | 28 | 55 | 294.23 | 59.3 | 406.24 | 405.5 | 405.5 | 472.35 | 266.11 | 245.45 | 1 | 174.3 | 6 | [7 empty] | 706.35 | 13.25 | 0.54 | 0.6
302 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI037 | 1S-DL-YP-ETC-DKRN-2101-KRI037 | RADHEY PURI EXTN.-2 (NALLA):PL | TG-KRI037A-1 | 19506678 | 990 | 320 | 243 | 0.97 | 748 | 267 | 1147 | 239 | 1016 | 241 | 1025 | 127 | 2019-06-30 23:30 | 211.5 | 61.1 | 1397 | B | 113 | 86 | 101 | 27 | 0.4 | 0.1 | 4.8 | 94.6 |  | 1.3 |  |  | 31 | 316.53 | 316.53 | 134 | 661.17 | 376.24 | 564.17 | 560.47 | 2.3 |  | 1 | [5 empty] | 694.47 | 25.13 | 0.65 | 0.76
303 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI038 | 1S-DL-YP-ETC-DKRN-2101-KRI038 | RADHA PURI NEW KRISHNA NAGAR:PL | TG-KRI038A-1 | 19506679 | 990 | 200 | 244 | 0.98 | 849 | 164 | 705 | 285 | 1228 | 399 | 1723 | 882 | 2019-06-30 23:30 | 131.8 | 30.8 | 1723 | B | 61 | 110 | 129 | 68 | 0.1 | 0.1 | 0.8 | 99 | 110.58 |  |  |  | 497.56 | 218.56 | 218.56 | 301.24 | 98.17 | 449.28 | 459.3 | 397.17 |  | 38.47 | 112.47 | 8.3 |  |  | 31 |  | 707.11 | 12.49 | 0.54 | 0.86
304 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI041 | 1S-DL-YP-ETC-DKRN-2101-KRI041 | RAM NAGAR L.N.MANDIR:PL | TG-KRI041A-1 | 19506779 | 1600 | 500 | 251 | 0.96 | 1465 | 776 | 3572 | 313 | 1264 | 375 | 1596 | 2161 | 2019-06-11 01:00 | 551 | 90.5 | 3572 | R | 107 | 96 | 97 | 11 | 0.4 | 0.1 | 61.4 | 38.2 |  | 3.3 | 0.3 |  | 224.3 | 339.28 | 339.28 | 290.58 | 453.42 | 364.14 | 409.44 | 413.44 | 28.3 | 0.3 |  | 3 | 1 |  |  |  | 707.42 | 12.18 | 0.51 | 0.92
305 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI042 | 1S-DL-YP-ETC-DKRN-2101-KRI042 | RAM NAGAR PARK(PLM) | TG-KRI042A-1 | 19506848 | 990 | 320 | 245 | 0.97 | 552 | 147 | 604 | 287 | 1334 | 119 | 516 | 777 | 2019-06-11 01:00 | 167 | 27.5 | 1334 | Y | 106 | 96 | 98 | 10 | 0.4 | 0.1 | 65.3 | 34.2 | 82.14 | 213.27 | 116.14 | 125.44 | 510.22 | 401.51 | 401.51 | 496.04 | 112.03 | 88.51 | 42.44 | 82.51 |  | 0.3 | [6 empty] | 704.39 | 15.21 | 0.49 | 0.56
306 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI042 | 1S-DL-YP-ETC-DKRN-2101-KRI042 | RAM NAGAR PARK(PLM) | TG-KRI042A-2 | 19505114 | 990 | 320 | 238.7578 | 0.97271 | 826.7989 | 208.5421 | 891.8152 | 297.6415 | 1280.1783 | 320.6154 | 1381.308 | 447.5804 | 2019-06-11 19:30 | [15 empty] | 0 |  |  |  | 349.5 |  |  |  | 368.5 |  |  |  | 1.5 |  |  |  | 0 | 719.5 |  | 0.52922 | 0.83515
307 | 2019-06-03 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI043 | 1S-DL-YP-ETC-DKRN-2101-KRI043 | SCHOOL BLOCK KRN:PL | TG-KRI043A-1 | 19503670 | 990 | 320 | 235 | 0.97 | 783 | 247 | 1068 | 274 | 1163 | 262 | 1103 | 83 | 2019-06-05 21:00 | 181.1 | 66.2 | 1330 | R | 106 | 102 | 91 | 15 | 8.4 | 8.3 | 77.6 | 5.7 |  |  |  |  | 37.13 | 59.43 | 59.43 | 77.13 | 425.59 | 402.45 | 310.45 | 388.15 | 2.16 | 3 | [6 empty] | 536.15 | 39.45 | 0.66 | 0.79
308 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI043 | 1S-DL-YP-ETC-DKRN-2101-KRI043 | SCHOOL BLOCK KRN:PL | TG-KRI043A-2 | 19505158 | 630 | 200 | 249 | 0.97 | 799 | 273 | 1160 | 258 | 1102 | 268 | 1147 | 53 | 2019-06-11 13:30 | 206.4 | 24 | 1230 | B | 82 | 96 | 122 | 40 | 0.4 | 0.6 | 63.9 | 35 | 45.17 | 3 |  |  | 591.23 | 478.12 | 478.12 | 397.26 | 64.1 | 219.38 | 467.43 | 303.24 |  |  | 1 |  | 0.38 | 0.38 | 0.38 | 0.38 | 701.28 | 18.32 | 0.3 | 1.27
309 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI047 | 1S-DL-YP-ETC-DKRN-2101-KRI047 | SHASTRI PARK:PL | TG-KRI047A-1 | 19502447 | 990 | 320 | 235 | 0.97 | 989 | 315 | 1363 | 336 | 1466 | 338 | 1472 | 106 | 2019-06-11 23:30 | 244.4 | 65.5 | 1583 | Y | 98 | 104 | 98 | 6 |  |  | 30 | 70 |  |  |  |  | 5.35 | 4.29 | 4.29 | 1.18 | 562.44 | 522.13 | 593.24 | 567.01 | 144.18 | 179.28 | 114.25 | 144.18 |  | 6.27 | 2.3 |  | 712.37 | 7.23 | 0.69 | 1
310 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI048 | 1S-DL-YP-ETC-DKRN-2101-KRI048 | ST.LIGHT OPP SWARN CINEMA ROAD NO 57:PM | TG-KRI048A-1 | 19505726 | 630 | 200 | 240 | 0.98 | 569 | 150 | 649 | 129 | 557 | 289 | 1288 | 690 | 2019-06-26 23:30 | 155.4 | 31.8 | 1288 | B | 98 | 85 | 117 | 32 | 0.1 | 0.6 | 9.6 | 89.8 |  | 0.3 |  |  | 207.54 | 352.24 | 352.24 | 195.24 | 488.15 | 350.45 | 476.45 | 496.15 | 7.3 |  | 95.3 | 12 |  |  | 10.3 |  | 703.39 | 16.21 | 0.55 | 0.9
311 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI049 | 1S-DL-YP-ETC-DKRN-2101-KRI049 | SURYA HOSPITAL:PL | TG-KRI049A-1 | 19506773 | 990 | 320 | 239 | 0.99 | 708 | 248 | 1043 | 232 | 971 | 229 | 962 | 78 | 2019-06-01 22:30 | 145.3 | 8.3 | 1148 | R | 103 | 95 | 103 | 8 | 0.1 |  | 0.5 | 99.4 |  |  |  |  | 94.3 | 178.3 | 178.3 | 114.3 | 608.27 | 524.27 | 619.4 | 588.27 | [8 empty] | 702.57 | 17.03 | 0.69 | 0.72
312 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI050 | 1S-DL-YP-ETC-DKRN-2101-KRI050 | VAISH DHARAM SHALA:PM | TG-KRI050A-1 | 19505865 | 400 | 120 | 244 | 0.98 | 305 | 96 | 395 | 110 | 450 | 98 | 403 | 51 | 2019-06-05 04:30 | 99.7 | 15.2 | 576 | R | 88 | 114 | 98 | 26 | 0.3 |  | 5.9 | 93.7 | 33 |  | 2 | 0.3 | 413.52 | 161.22 | 161.22 | 269.22 | 269.06 | 552.36 | 414.51 | 446.36 | 0.3 | 2.3 | 0.3 | [5 empty] | 716.28 | 3.32 | 0.56 | 0.76
313 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI051 | 1S-DL-YP-ETC-DKRN-2101-KRI051 | WEST ARJUN NAGAR:ID | TG-KRI051A-1 | 19506783 | 990 | 320 | 240 | 0.97 | 704 | 232 | 962 | 246 | 1022 | 226 | 936 | 76 | 2019-06-12 | 136.6 | 50.6 | 1091 | Y | 96 | 109 | 96 | 13 |  |  | 0.3 | 99.7 | 4.3 | 3 | 5.3 | 0.3 | 435 | 335.51 | 335.51 | 409.51 | 269.26 | 370.05 | 273.05 | 298.35 | [8 empty] | 708.56 | 11.04 | 0.56 | 0.71
314 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI051 | 1S-DL-YP-ETC-DKRN-2101-KRI051 | WEST ARJUN NAGAR:ID | TG-KRI051A-2 | 19506784 | 630 | 200 | 245 | 0.97 | 621 | 198 | 813 | 193 | 794 | 230 | 952 | 149 | 2019-06-09 23:30 | 124.4 | 45.4 | 977 | B | 94 | 100 | 106 | 12 |  | 0.1 | 4.4 | 95.5 |  |  |  |  | 44.55 | 28.3 | 28.3 | 20 | 594.17 | 573.45 | 508.15 | 581.28 | 70.27 | 107.24 | 169.24 | 108.11 |  |  | 18.3 |  | 709.39 | 10.21 | 0.65 | 0.99
315 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI068 | 1S-DL-YP-ETC-DKRN-2101-KRI068 | ANANDPUR TRUST HOSPITAL | TG-KRI068A-1 | 19505729 | 400 | 120 | 244 | 0.97 | 237 | 79 | 335 | 82 | 348 | 76 | 324 | 21 | 2019-06-27 11:00 | 22 | -45.6 | 348 | Y | 96 | 105 | 99 | 9 | 0.1 |  | 16.1 | 83.8 | 381 | 353.3 | 374.3 | 375 | 161 | 146.3 | 146.3 | 142.3 | 167.54 | 209.54 | 194.24 | 192.24 | [8 empty] | 709.54 | 10.06 | 0.46 | 0.59