## Loading Condition > 80%
MIS Report of Distribution Transformer - Jun19
Jun19 1220 KRISHNA NAGAR (Loading Condition > 80% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG002 | 1S-DL-YP-ETC-DKRN-2104-JAG002 | BEDI MKT:ID | TG-JAG002A-2 | 19506104 | 1600 | 500 | 243 | 0.97 | 2307 | 457 | 1978 | 874 | 4198 | 976 | 4330 | 2289 | 2019-06-08 23:00 | 710.5 | 44.5 | 4330 | B | 105 | 92 | 103 | 13 | 0.8 | 0.3 | 56.4 | 42.5 | 0.57 | 0.57 | 0.05 | 0.05 | 111.24 | 220.13 | 220.13 | 146.46 | 470.54 | 423 | 464.44 | 457.47 | 101.35 | 49.47 | 88.01 | 86.1 | 11.01 | 1.54 | 15.35 | 5.03 | 695.51 | 24.09 | 0.38 | 1.44
2 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG004 | 1S-DL-YP-ETC-DKRN-2104-JAG004 | BALDEV PARK(PARK WALA):PL | TG-JAG004A-1 | 19504993 | 990 | 320 | 236 | 0.97 | 760 | 182 | 801 | 239 | 1078 | 340 | 1537 | 643 | 2019-06-30 23:30 | 128.8 | 42.7 | 1641 | B | 78 | 90 | 132 | 54 | 0.1 | 43.5 | 56.3 |  | 28.02 | 16 |  | 4.3 | 514.43 | 451.45 | 451.45 | 382.45 | 176 | 251 | 463.2 | 331.3 |  |  | 98.3 |  |  |  | 9 |  | 718.45 | 1.15 | 0.55 | 0.77
3 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG006 | 1S-DL-YP-ETC-DKRN-2104-JAG006 | CHANDER NAGAR:ID | TG-JAG006A-2 | 19500787 | 990 | 320 | 236 | 0.97 | 983 | 296 | 1284 | 362 | 1590 | 325 | 1416 | 266 | 2019-06-11 18:30 | 228.2 | 69.9 | 1643 | Y | 96 | 107 | 96 | 11 |  |  | 13.2 | 86.8 |  |  |  |  | 99.3 | 55 | 55 | 83.3 | 547.1 | 530.1 | 495.35 | 532.1 | 71.1 | 114.4 | 91.45 | 102.1 |  | 18 | 1 |  | 717.5 | 2.1 | 0.58 | 0.99
4 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG008 | 1S-DL-YP-ETC-DKRN-2104-JAG008 | GAGAN VIHAR:ID | TG-JAG008A-2 | 19506108 | 990 | 320 | 244 | 0.98 | 889 | 237 | 985 | 391 | 1659 | 262 | 1099 | 624 | 2019-06-12 00:30 | 192 | 48.6 | 1738 | Y | 91 | 110 | 99 | 19 |  | 0.6 | 2.2 | 97.2 |  |  |  |  | 250.13 | 104.4 | 104.4 | 164.3 | 458.51 | 515.24 | 541.04 | 528.34 |  | 78 | 6.3 | 16 |  | 11 | 0.3 |  | 709.04 | 10.56 | 0.57 | 0.9
5 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG010 | 1S-DL-YP-ETC-DKRN-2104-JAG010 | GANDHI PARK:PL | TG-JAG010A-2 | 19500750 | 990 | 320 | 238 | 0.98 | 869 | 269 | 1143 | 278 | 1190 | 322 | 1366 | 203 | 2019-06-11 | 139.8 | 39.7 | 1381 | B | 94 | 93 | 113 | 20 |  | 1.2 | 74.5 | 24.4 | 3 | 5.3 |  |  | 346.28 | 338.28 | 338.28 | 291.58 | 364.35 | 370.55 | 471.35 | 416.55 | 3.5 | 3 | 72.5 | 9 |  |  |  |  | 717.53 | 2.07 | 0.54 | 0.88
6 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG011 | 1S-DL-YP-ETC-DKRN-2104-JAG011 | GANESH PARK:PL | TG-JAG011A-2 | 19505000 | 990 | 200 | 238 | 0.97 | 926 | 303 | 1251 | 343 | 1409 | 280 | 1142 | 232 | 2019-06-30 | 182.2 | 65.3 | 1503 | R | 103 | 107 | 90 | 17 |  |  | 31.4 | 68.6 |  |  |  |  | 19.05 | 17.35 | 17.35 | 24.05 | 627.53 | 597.53 | 632.29 | 633.53 | 69.47 | 99.17 | 10.3 | 58.47 |  | 2 |  |  | 716.45 | 3.15 | 0.62 | 0.94
7 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG012 | 1S-DL-YP-ETC-DKRN-2104-JAG012 | GOLDEN PARK:ID | TG-JAG012A-2 | 19500817 | 990 | 320 | 237 | 0.99 | 827 | 260 | 1135 | 262 | 1134 | 305 | 1312 | 178 | 2019-06-03 | 63.3 | -100.1 | 1340 | B | 95 | 95 | 111 | 16 |  | 0.3 | 72.9 | 26.7 |  |  |  |  | 137.53 | 133.53 | 133.53 | 81.53 | 581.5 | 585.5 | 619.47 | 633.2 |  |  | 63 | 4.3 |  |  |  |  | 719.43 | 0.17 | 0.63 | 0.84
8 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG016 | 1S-DL-YP-ETC-DKRN-2104-JAG016 | GOVIND PURA(OLD):ID | TG-JAG016A-1 | 19503083 | 990 | 320 | 232 | 0.97 | 758 | 209 | 928 | 190 | 840 | 359 | 1594 | 714 | 2019-06-03 00:30 | 140.6 | 39 | 1594 | B | 95 | 86 | 119 | 33 |  |  | 6.1 | 93.9 |  | 0.3 | 0.3 | 0.3 | 327.3 | 426.3 | 426.3 | 255 | 392.21 | 292.51 | 553.21 | 464.21 |  |  | 50.3 |  |  |  | 2 |  | 719.51 | 0.09 | 0.59 | 0.77
9 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG016 | 1S-DL-YP-ETC-DKRN-2104-JAG016 | GOVIND PURA(OLD):ID | TG-JAG016A-2 | 19505580 | 990 | 320 | 244 | 0.97 | 884 | 320 | 1330 | 313 | 1296 | 251 | 1025 | 290 | 2019-06-10 03:00 | 288 | 53.4 | 1845 | R | 112 | 104 | 84 | 28 | 0.6 | 11.9 | 86.6 | 0.9 | 2.3 | 2.3 | 5 | 2.3 | 93.3 | 179 | 179 | 203.3 | 557 | 492 | 342 | 492.3 | 57 | 36.3 |  | 12.3 | 1 | 1 |  |  | 711 | 9 | 0.56 | 0.89
10 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG018 | 1S-DL-YP-ETC-DKRN-2104-JAG018 | JAGAT PURI A BLK:PL | TG-JAG018A-1 | 19504763 | 990 | 320 | 243 | 0.97 | 870 | 258 | 1051 | 280 | 1130 | 331 | 1344 | 262 | 2019-06-30 01:00 | 189.9 | 71.4 | 1344 | B | 91 | 100 | 109 | 18 |  |  | 6.4 | 93.6 |  |  |  |  | 162.48 | 81 | 81 | 82.3 | 554.55 | 633.43 | 602.21 | 632.43 |  | 3 | 60.52 | 2.3 |  |  | 0.3 |  | 717.43 | 2.17 | 0.6 | 0.88
11 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG020 | 1S-DL-YP-ETC-DKRN-2104-JAG020 | JAGAT PURI F BLK:PL | TG-JAG020A-1 | 19506790 | 990 | 320 | 242 | 0.98 | 930 | 351 | 1433 | 290 | 1175 | 289 | 1182 | 254 | 2019-06-30 14:00 | 201.9 | 58.2 | 1542 | R | 114 | 91 | 95 | 23 | 0.2 | 0.1 | 5 | 94.7 |  |  |  |  | 4.3 | 49.3 | 49.3 | 19 | 456.36 | 644.47 | 635.55 | 629.17 | 225.41 | 9.3 | 32 | 55.3 | 17 |  |  |  | 703.47 | 16.13 | 0.68 | 0.94
12 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG023 | 1S-DL-YP-ETC-DKRN-2104-JAG023 | KHUREJI:ID | TG-JAG023A-1 | 19506153 | 630 | 200 | 243 | 0.98 | 544 | 193 | 801 | 179 | 741 | 171 | 712 | 79 | 2019-06-12 | 151.2 | 32.4 | 875 | B | 95 | 112 | 94 | 18 | 0.2 | 0.1 | 20.8 | 78.8 | 0.3 | 0.3 | 0.3 | 0.3 | 22 |  |  |  | 678.08 | 631.52 | 689.1 | 703.08 | 17.3 | 85.46 | 11.58 | 14.3 |  |  |  |  | 718.08 | 1.52 | 0.72 | 0.86
13 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG025 | 1S-DL-YP-ETC-DKRN-2104-JAG025 | NEW LAYALPUR:K | TG-JAG025A-2 | 19506781 | 990 | 320 | 239 | 0.97 | 904 | 275 | 1151 | 247 | 1038 | 382 | 1639 | 553 | 2019-06-30 | 191 | 55.4 | 1661 | B | 100 | 94 | 106 | 12 | 0.7 | 0.9 | 9.3 | 89.1 |  |  |  |  | 218.37 | 255.15 | 255.15 | 207.15 | 435.44 | 444.06 | 482.22 | 456.36 | 46.3 | 2.3 | 54.3 | 38 | 1 |  | 4 |  | 701.51 | 18.09 | 0.55 | 0.91
14 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG025 | 1S-DL-YP-ETC-DKRN-2104-JAG025 | NEW LAYALPUR:K | TG-JAG025A-1 | 19506786 | 990 | 320 | 238 | 0.97 | 931 | 271 | 1160 | 293 | 1262 | 367 | 1594 | 394 | 2019-06-01 00:30 | 230.4 | 54.1 | 1634 | Y | 95 | 101 | 104 | 9 | 0.4 | 2.6 | 17.7 | 79.2 |  |  |  |  | 288.29 | 265.29 | 265.29 | 252.59 | 403.17 | 385.17 | 484.5 | 412.47 | 12.3 | 46.3 | 34 | 39 | 0.3 | 7.3 | 4.3 |  | 704.46 | 15.14 | 0.53 | 0.94
15 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG029 | 1S-DL-YP-ETC-DKRN-2104-JAG029 | SHIV PURI:PM | TG-JAG029A-1 | 19506151 | 990 | 200 | 235 | 0.98 | 976 | 320 | 1424 | 407 | 1856 | 249 | 1106 | 652 | 2019-06-29 23:00 | 237.4 | 54.4 | 2189 | Y | 99 | 112 | 89 | 23 | 0.8 | 2.6 | 39.2 | 57.4 |  |  |  |  | 34 | 4 | 4 | 19 | 626.56 | 585.53 | 572.37 | 645.53 | 32.41 | 85.3 | 1.3 | 28.44 |  | 18.14 |  |  | 693.37 | 26.23 | 0.6 | 0.99
16 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG030 | 1S-DL-YP-ETC-DKRN-2104-JAG030 | SILVER PARK:ID | TG-JAG030A-1 | 19506008 | 990 | 320 | 229 | 0.98 | 944 | 202 | 907 | 373 | 1742 | 369 | 1702 | 815 | 2019-06-02 15:30 | 307.5 | 53.4 | 2174 | B | 102 | 93 | 106 | 13 | 0.4 | 0.6 | 60.6 | 38.3 |  |  |  |  | 120.27 | 237.22 | 237.22 | 148.53 | 572.05 | 454.17 | 511.34 | 529.04 | 8.21 | 8.51 | 47.21 | 22.56 |  | 0.23 | 10.05 |  | 700.53 | 19.07 | 0.54 | 0.95
17 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG031 | 1S-DL-YP-ETC-DKRN-2104-JAG031 | SOUTH ANARKALI:PL | TG-JAG031A-1 | 19506660 | 990 | 320 | 245 | 0.97 | 1035 | 346 | 1464 | 378 | 1597 | 311 | 1301 | 256 | 2019-06-05 02:30 | 246.7 | 64.3 | 1637 | Y | 100 | 107 | 92 | 15 | 0.4 | 0.2 | 14.8 | 84.7 | 0.06 | 1.13 | 1.13 | 0.13 | 79.57 | 42.23 | 42.23 | 76.53 | 523.58 | 517.42 | 477.52 | 519.42 | 87.58 | 112.13 | 72.22 | 97.11 | 3.54 | 22.22 |  | 1.54 | 695.53 | 24.07 | 0.56 | 1.05
18 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG034 | 1S-DL-YP-ETC-DKRN-2104-JAG034 | JAGAT PURI G BLK:PL | TG-JAG034A-2 | 19505711 | 990 | 320 | 243 | 0.97 | 818 | 237 | 995 | 351 | 1474 | 230 | 958 | 499 | 2019-06-11 23:30 | 199 | 57.3 | 1681 | Y | 79 | 122 | 99 | 43 | 0.2 | 0.1 | 2.3 | 97.4 | 1 |  |  |  | 430.28 | 84.27 | 84.27 | 194.27 | 273.26 | 503.57 | 447.57 | 506.57 |  | 95.3 | 21.3 | 3.3 |  | 21 | 0.3 |  | 704.54 | 15.06 | 0.59 | 0.83
19 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG034 | 1S-DL-YP-ETC-DKRN-2104-JAG034 | JAGAT PURI G BLK:PL | TG-JAG034A-1 | 19505835 | 990 | 320 | 237 | 0.97 | 971 | 299 | 1282 | 331 | 1432 | 342 | 1483 | 180 | 2019-06-30 | 223.7 | 64.6 | 1726 | B | 110 | 81 | 110 | 29 | 0.2 | 0.9 | 45.2 | 53.6 |  | 0.3 |  |  | 50.24 | 329.57 | 329.57 | 130.51 | 567.59 | 364.26 | 494.58 | 518.32 | 68.3 | 8.3 | 110.28 | 55 | 17.3 | 1 | 6 |  | 704.23 | 15.37 | 0.55 | 0.98
20 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN002 | 1S-DL-YP-ETC-DKRN-2102-GAN002 | AJIT NAGAR GALI NO 8:PL | TG-GAN002A-1 | 19506803 | 990 | 320 | 230 | 0.98 | 924 | 311 | 1362 | 285 | 1232 | 328 | 1428 | 172 | 2019-06-02 12:30 | 204.5 | 43.8 | 1462 | B | 99 | 92 | 109 | 17 |  | 0.1 | 37.6 | 62.3 |  |  |  |  | 4 | 12 | 12 | 1.3 | 589.09 | 676.57 | 495.28 | 618.06 | 112.32 | 17.14 | 210.13 | 86.35 | 0.3 |  | 0.3 |  | 706.11 | 13.49 | 0.7 | 0.93
21 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN003 | 1S-DL-YP-ETC-DKRN-2102-GAN003 | AMAR MOHALLA:PL | TG-GAN003A-2 | 19506348 | 630 | 200 | 241 | 0.97 | 532 | 156 | 664 | 160 | 671 | 217 | 939 | 272 | 2019-06-02 16:00 | 130.4 | 19.4 | 985 | B | 95 | 88 | 117 | 29 | 0.1 | 19.5 | 74.6 | 5.7 | 36 | 6.3 |  | 3.3 | 281.54 | 440.54 | 440.54 | 295.45 | 381.21 | 251.51 | 396.44 | 392.3 |  |  | 49.46 | 7.3 |  |  | 5 |  | 699.15 | 20.45 | 0.51 | 0.84
22 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN005 | 1S-DL-YP-ETC-DKRN-2102-GAN005 | CHEMALI DEVI (INSIDE):PL | TG-GAN005A-1 | 19500172 | 990 | 320 | 240 | 0.97 | 947 | 313 | 1345 | 320 | 1369 | 314 | 1350 | 21 | 2019-06-30 16:00 | 226 | 40.5 | 1479 | Y | 91 | 102 | 106 | 15 |  |  | 26.8 | 73.2 | 60.3 |  |  |  | 53.58 | 43.57 | 43.57 | 52.28 | 521.23 | 527.54 | 543.59 | 550.59 | 83.28 | 145.58 | 152.22 | 116.22 | 0.3 | 2 |  |  | 719.49 | 0.11 | 0.65 | 0.96
23 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN007 | 1S-DL-YP-ETC-DKRN-2102-GAN007 | DUDLELA CHOWK:PL | TG-GAN007A-2 | 19506103 | 990 | 320 | 237 | 0.97 | 733 | 217 | 931 | 264 | 1130 | 252 | 1074 | 178 | 2019-06-28 09:00 | 229.4 | 70.1 | 1364 | Y | 84 | 127 | 89 | 43 | 0.1 | 5.3 | 78.1 | 16.4 |  |  |  |  | 101.34 |  |  | 14.3 | 599.32 | 601.49 | 626.41 | 686.36 |  | 99.17 | [6 empty] | 701.06 | 18.54 | 0.75 | 0.74
24 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN008 | 1S-DL-YP-ETC-DKRN-2102-GAN008 | GALI GURDWARA NO. 2:ID | TG-GAN008A-4 | 19504381 | 400 | 120 | 244 | 0.98 | 322 | 67 | 277 | 152 | 652 | 104 | 440 | 326 | 2019-06-02 16:30 | 57.7 | 0.6 | 683 | Y | 68 | 114 | 118 | 50 | 1.4 | 16.3 | 66.9 | 15.5 | 454.06 | 354.29 | 364.13 | 410.47 | 69.37 | 96.11 | 96.11 | 61.19 | 191.1 | 200.29 | 201.33 | 242.17 |  | 55.14 | 55.44 | 0.3 |  | 8.3 |  |  | 714.53 | 5.07 | 0.38 | 0.81
25 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN010 | 1S-DL-YP-ETC-DKRN-2102-GAN010 | GANDHI NAGAR POLICE ST.:PL | TG-GAN010A-1 | 19506799 | 990 | 320 | 234 | 0.98 | 786 | 230 | 1024 | 324 | 1440 | 233 | 1025 | 416 | 2019-06-02 15:00 | 182.7 | 21.8 | 1608 | Y | 96 | 111 | 93 | 18 | 0.3 | 0.1 | 44.9 | 54.7 | 324.53 | 357.53 | 419.23 | 383.23 | 138 | 94.3 | 94.3 | 76 | 242.06 | 180.41 | 235.09 | 245.36 |  | 70.55 | 3.3 |  |  | 1 |  |  | 704.59 | 15.01 | 0.42 | 0.79
26 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN010 | 1S-DL-YP-ETC-DKRN-2102-GAN010 | GANDHI NAGAR POLICE ST.:PL | TG-GAN010A-2 | 19506802 | 990 | 320 | 244 | 0.98 | 832 | 282 | 1229 | 204 | 884 | 346 | 1524 | 555 | 2019-06-29 15:00 | 210.9 | 9.9 | 1684 | B | 105 | 84 | 111 | 27 | 0.4 |  | 11.2 | 88.4 | 361.22 | 381.22 | 377.23 | 374.52 | 88 | 91.57 | 91.57 | 77.3 | 230.16 | 231.49 | 131.02 | 246.46 | 25.3 |  | 128.44 | 6 |  |  | 2.3 |  | 705.08 | 14.52 | 0.41 | 0.84
27 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN014 | 1S-DL-YP-ETC-DKRN-2102-GAN014 | KAILASH NAGAR NO. 1:PL | TG-GAN014A-1 | 19505517 | 990 | 320 | 235 | 0.97 | 811 | 262 | 1117 | 266 | 1136 | 283 | 1200 | 76 | 2019-06-26 14:30 | 217.3 | 53.8 | 1411 | B | 94 | 100 | 105 | 11 | 0.4 | 0.1 | 27.5 | 72.1 |  |  |  |  | 108.29 | 65.59 | 65.59 | 74.29 | 598.35 | 640.05 | 615.35 | 631.35 | 0.3 | 1.3 | 30.3 | 1.3 |  |  |  |  | 707.34 | 12.26 | 0.68 | 0.82
28 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN015 | 1S-DL-YP-ETC-DKRN-2102-GAN015 | KAILASH NAGAR NO. 15:PL | TG-GAN015A-2 | 19505011 | 990 | 320 | 238 | 0.97 | 746 | 242 | 1020 | 237 | 1040 | 267 | 1152 | 123 | 2019-06-30 15:00 | 181.1 | 42.7 | 1257 | B | 96 | 92 | 112 | 20 | 99.9 | 0.1 | [6 empty] | 101.47 | 133.47 | 133.47 | 78.49 | 616.23 | 584.23 | 644.32 | 639.21 |  |  | 32.08 | [5 empty] | 718.1 | 1.5 | 0.7 | 0.75
29 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN015 | 1S-DL-YP-ETC-DKRN-2102-GAN015 | KAILASH NAGAR NO. 15:PL | TG-GAN015A-1 | 19505931 | 990 | 320 | 241 | 0.97 | 846 | 208 | 857 | 285 | 1184 | 354 | 1467 | 529 | 2019-06-03 01:00 | 214.4 | 73.3 | 1489 | B | 89 | 102 | 109 | 20 | 0.1 | 0.4 | 24.3 | 75.2 |  |  |  |  | 89.3 | 40 | 40 | 36.3 | 628.06 | 658.4 | 632.32 | 673.36 |  | 18.26 | 55.04 | 7.3 |  | 0.3 | 8.3 |  | 717.36 | 2.24 | 0.68 | 0.85
30 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN015 | 1S-DL-YP-ETC-DKRN-2102-GAN015 | KAILASH NAGAR NO. 15:PL | TG-GAN015A-3 | 19506875 | 990 | 320 | 247 | 0.96 | 795 | 369 | 1672 | 208 | 860 | 218 | 929 | 779 | 2019-06-30 14:00 | 233.3 | 65.9 | 1672 | R | 117 | 84 | 99 | 33 | 0.3 | 3.5 | 87.6 | 8.7 |  |  |  |  | 17.3 | 200.29 | 200.29 | 58.3 | 608.28 | 507.02 | 630.31 | 648.31 | 80.03 |  |  | 0.3 | 1.3 |  |  |  | 707.31 | 12.29 | 0.68 | 0.8
31 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN016 | 1S-DL-YP-ETC-DKRN-2102-GAN016 | KAILASH NAGAR SCHOOL:PL | TG-GAN016A-1 | 19506801 | 990 | 320 | 237 | 0.98 | 953 | 276 | 1178 | 328 | 1446 | 350 | 1601 | 370 | 2019-06-30 14:00 | 234.6 | 30.1 | 1641 | B | 95 | 113 | 92 | 21 | 0.1 | 0.1 | 13 | 86.8 | 1.3 |  | 2 |  | 366.17 | 219.17 | 219.17 | 341.17 | 255.53 | 277.04 | 225.23 | 237.53 | 84.48 | 190.07 | 82.48 | 129.18 |  | 22 | 1 |  | 708.28 | 11.32 | 0.54 | 0.96
32 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN023 | 1S-DL-YP-ETC-DKRN-2102-GAN023 | PEEPAL WALA SCHOOL:PL | TG-GAN023A-2 | 19506795 | 630 | 200 | 244 | 0.96 | 575 | 302 | 1283 | 127 | 525 | 146 | 597 | 725 | 2019-06-02 17:30 | 174 | 5.6 | 1283 | R | 117 | 92 | 92 | 25 | 0.1 |  | 13 | 86.9 | 275.51 | 367.21 | 356.21 | 340.21 | 140 | 71.3 | 71.3 | 88.3 | 241.11 | 266.03 | 261.09 | 275.03 | 47.22 |  |  | 1 | 0.3 |  | 0.24 |  | 704.54 | 15.06 | 0.37 | 0.91
33 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN024 | 1S-DL-YP-ETC-DKRN-2102-GAN024 | R. PURA GALI NO. 8:PL | TG-GAN024A-1 | 19506002 | 990 | 320 | 245 | 0.96 | 920 | 300 | 1229 | 311 | 1286 | 309 | 1279 | 54 | 2019-06-02 15:30 | 227.5 | 57 | 1425 | Y | 91 | 110 | 99 | 19 |  | 1 | 83.5 | 15.5 | 2.3 | 1 | 6 | 1 | 336.51 | 252.21 | 252.21 | 285.21 | 353.44 | 300.15 | 372.06 | 367.35 | 11 | 149.29 | 47.08 | 50.09 |  | 1 |  |  | 704.05 | 15.55 | 0.55 | 0.93
34 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN025 | 1S-DL-YP-ETC-DKRN-2102-GAN025 | R.PURA GALI NO 6 (IN SIDE):PL | TG-GAN025A-1 | 19506600 | 990 | 320 | 238 | 0.97 | 1025 | 333 | 1403 | 335 | 1423 | 356 | 1516 | 105 | 2019-06-01 12:30 | 270.7 | 1.3 | 1574 | B | 96 | 101 | 103 | 7 | 0.1 | 0.1 | 66.3 | 33.5 | 96.51 | 42.21 | 87.51 | 71.51 | 279.21 | 316.21 | 316.21 | 296.51 | 173 | 176.24 | 116.28 | 148.58 | 151.44 | 167.2 | 200.16 | 185.46 | 4 | 2.3 | 17.3 | 1.3 | 704.56 | 15.04 | 0.48 | 1.03
35 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN028 | 1S-DL-YP-ETC-DKRN-2102-GAN028 | SEELAMPUR OLD PR. SCHOOL NO. 1:K | TG-GAN028A-2 | 19505099 | 990 | 320 | 236 | 0.98 | 823 | 321 | 1413 | 252 | 1112 | 250 | 1105 | 304 | 2019-06-01 16:30 | 162.2 | 32.6 | 1456 | R | 114 | 89 | 97 | 25 |  |  | 29.3 | 70.7 |  | 1 |  |  | 15.39 | 287.57 | 287.57 | 92.27 | 638.28 | 398.4 | 627.36 | 600.4 | 47.3 | 16 |  | 10.3 | 2 |  |  |  | 703.37 | 16.23 | 0.64 | 0.83
36 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN028 | 1S-DL-YP-ETC-DKRN-2102-GAN028 | SEELAMPUR OLD PR. SCHOOL NO. 1:K | TG-GAN028A-3 | 19505100 | 630 | 200 | 248 | 0.98 | 492 | 245 | 1028 | 97 | 396 | 149 | 611 | 556 | 2019-06-18 01:30 | 134.6 | 12.8 | 1028 | R | 98 | 78 | 124 | 46 | 0.4 | 8.7 | 85.6 | 5.3 |  | 9.3 |  |  | 211.4 | 490.39 | 490.39 | 216.11 | 489.29 | 201.51 | 576.53 | 486.19 | 0.51 |  | 50.2 |  | 0.3 | 0.3 | 1.3 |  | 702.3 | 17.3 | 0.59 | 0.78
37 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN028 | 1S-DL-YP-ETC-DKRN-2102-GAN028 | SEELAMPUR OLD PR. SCHOOL NO. 1:K | TG-GAN028A-1 | 19505116 | 990 | 320 | 242 | 0.98 | 907 | 310 | 1292 | 305 | 1288 | 292 | 1244 | 46 | 2019-06-02 16:30 | 191.7 | 45.1 | 1359 | B | 93 | 113 | 94 | 20 | 16.9 | 4.3 | 77.6 | 1.2 |  |  |  |  | 27.3 | 0.3 | 0.3 | 9.3 | 657.2 | 643.5 | 660.2 | 672.5 | 19.59 | 60.29 | 17.59 | 22.29 |  |  |  |  | 704.49 | 15.11 | 0.64 | 0.92
38 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN029 | 1S-DL-YP-ETC-DKRN-2102-GAN029 | SEELAMPUR PHATAK:PL | TG-GAN029A-1 | 19506480 | 990 | 320 | 241 | 0.99 | 965 | 292 | 1292 | 360 | 1583 | 313 | 1399 | 255 | 2019-06-29 15:00 | 159.4 | 23.4 | 1583 | Y | 105 | 95 | 100 | 10 | 0.1 | 0.3 | 50 | 49.6 |  |  |  |  | 4.56 | 71.56 | 71.56 | 13.3 | 466.57 | 405.24 | 416.35 | 470.36 | 52.46 | 46.2 | 60.34 | 40.33 |  | 0.59 |  |  | 524.39 | 51.21 | 0.61 | 0.97
39 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN032 | 1S-DL-YP-ETC-DKRN-2102-GAN032 | SHIV KUTI R.L.G. NO. 1:ID | TG-GAN032A-6 | 19505140 | 990 | 320 | 245 | 0.97 | 795 | 276 | 1160 | 215 | 902 | 304 | 1281 | 335 | 2019-06-26 16:00 | 242.9 | -0.3 | 1328 | R | 103 | 84 | 114 | 30 | 0.1 | 0.1 | 11.5 | 88.2 | 401.27 | 414.27 | 382.58 | 399.27 | 43.3 | 50 | 50 | 46 | 222.5 | 241.5 | 182.52 | 259.2 | 38.3 |  | 88.58 | 1.3 |  |  |  |  | 706.17 | 13.43 | 0.4 | 0.8
40 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN032 | 1S-DL-YP-ETC-DKRN-2102-GAN032 | SHIV KUTI R.L.G. NO. 1:ID | TG-GAN032A-2 | 19506574 | 990 | 320 | 243 | 0.97 | 863 | 262 | 1107 | 311 | 1312 | 289 | 1215 | 178 | 2019-06-30 16:00 | 239.7 | -17.9 | 1769 | Y | 93 | 108 | 99 | 15 | 0.2 | 0.1 | 29.7 | 69.9 | 439.23 | 416.23 | 412.23 | 416.23 | 36.3 | 38 | 38 | 40 | 218.47 | 144.03 | 211.05 | 214.35 | 10.3 | 105.44 | 41.12 | 34.12 |  | 1 |  |  | 705.1 | 14.5 | 0.36 | 0.87
41 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN033 | 1S-DL-YP-ETC-DKRN-2102-GAN033 | SUBHASH MOHALLA NO.1:PM | TG-GAN033A-2 | 19505124 | 990 | 320 | 243 | 0.98 | 855 | 301 | 1242 | 294 | 1208 | 260 | 1056 | 172 | 2019-06-01 18:00 | 215.7 | 10.6 | 1265 | Y | 107 | 103 | 90 | 17 | 0.1 | 0.8 | 83.7 | 15.4 | 0.1 | 3 | 24.38 | 1.1 | 316.24 | 379.09 | 379.09 | 381.01 | 341.54 | 239 | 281.12 | 288.58 | 40.36 | 77.55 | 6.27 | 27.55 |  |  |  |  | 699.04 | 20.56 | 0.54 | 0.86
42 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN033 | 1S-DL-YP-ETC-DKRN-2102-GAN033 | SUBHASH MOHALLA NO.1:PM | TG-GAN033A-3 | 19506659 | 990 | 320 | 242 | 0.96 | 863 | 268 | 1125 | 294 | 1245 | 300 | 1269 | 133 | 2019-06-01 12:00 | 245.1 | 0.6 | 1304 | B | 99 | 98 | 103 | 5 |  | 0.1 | 27.9 | 72 | 167.29 | 231.12 | 141.47 | 178.42 | 220.56 | 164.13 | 164.13 | 211.43 | 295.03 | 237.03 | 248.15 | 267.52 | 18.28 | 69.28 | 66.16 | 43.39 |  |  |  |  | 701.56 | 18.04 | 0.49 | 0.87
43 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN040 | 1S-DL-YP-ETC-DKRN-2102-GAN040 | GYAN MOHLLA | TG-GAN040A-1 | 19502011 | 990 | 320 | 237 | 0.98 | 924 | 327 | 1448 | 313 | 1373 | 284 | 1256 | 168 | 2019-06-01 16:30 | 193.6 | 25 | 1477 | R | 112 | 102 | 86 | 26 |  | 0.1 | 33 | 66.8 | 3.3 | 110.3 | 260 | 75.3 | 394 | 302.3 | 302.3 | 344.59 | 176.44 | 180.58 | 269.37 | 208.29 | 143.22 | 125.08 | 7.3 | 90.08 | 1.3 |  |  |  | 719.06 | 0.54 | 0.47 | 0.93
44 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN045 | 1S-DL-YP-ETC-DKRN-2102-GAN045 | SJ/STN RATTEY WALA SUBHASH MOHALLA | TG-GAN045A-1 | 19506863 | 990 | 320 | 236 | 0.97 | 840 | 253 | 1056 | 297 | 1258 | 289 | 1225 | 187 | 2019-06-02 16:30 | 205.8 | 9.3 | 1521 | Y | 93 | 111 | 96 | 18 | 0.4 | 1.1 | 71.9 | 26.7 | 377.25 | 332.55 | 380.38 | 361.55 | 53.33 | 78.22 | 78.22 | 65.03 | 270.3 | 231.41 | 259 | 272.3 | 4.3 | 62.3 | 7 | 6.3 |  | 0.3 |  |  | 705.58 | 14.02 | 0.41 | 0.85
45 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL002 | 1S-DL-YP-ETC-DKRN-2103-GCL002 | ALOK BHARTI | TG-GCL002A-1 | 19503703 | 990 | 320 | 232 | 0.98 | 941 | 376 | 1596 | 307 | 1293 | 259 | 1081 | 448 | 2019-06-30 | 159 | 62.6 | 1671 | R | 120 | 93 | 87 | 33 |  | 5.1 | 74.5 | 20.4 | [5 empty] | 16.3 | 16.3 | 6 | 486.47 | 679.58 | 680.28 | 664.58 | 206.11 | 22 | 2 | 47.3 | 25.3 |  |  |  | 718.28 | 1.32 | 0.66 | 0.95
46 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL005 | 1S-DL-YP-ETC-DKRN-2103-GCL005 | JHEEL (BHOOSA MANDI):PL | TG-GCL005A-1 | 19506909 | 990 | 320 | 242 | 0.98 | 880 | 251 | 1048 | 348 | 1451 | 281 | 1183 | 355 | 2019-06-27 | 183.4 | 25 | 1451 | Y | 91 | 108 | 101 | 17 | 0.6 | 0.3 | 60.7 | 38.4 |  | 1.3 | 1.3 |  | 208.3 | 71.3 | 71.3 | 98 | 499.21 | 601.51 | 594.51 | 602.21 | 0.3 | 30.3 | 5.3 | 8 |  | 3 |  |  | 708.21 | 11.39 | 0.56 | 0.89
47 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL011 | 1S-DL-YP-ETC-DKRN-2103-GCL011 | GEETA COLONY, 14 BLK:ID | TG-GCL011A-1 | 19505719 | 990 | 320 | 233 | 0.97 | 955 | 290 | 1294 | 224 | 1043 | 440 | 2230 | 1084 | 2019-06-11 01:00 | 251.2 | 65 | 2230 | B | 107 | 87 | 106 | 20 | 0.5 | 0.2 | 91.2 | 8.2 |  |  |  |  | 30.58 | 162.24 | 162.24 | 50 | 596.3 | 553.25 | 650.21 | 641.58 | 88.51 | 1 | 35.45 | 24.51 | 0.3 |  | 0.43 |  | 716.49 | 3.11 | 0.58 | 0.96
48 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL014 | 1S-DL-YP-ETC-DKRN-2103-GCL014 | GEETA COLONY,11, BLK:PL | TG-GCL014A-1 | 19502875 | 990 | 320 | 240 | 0.97 | 996 | 332 | 1381 | 293 | 1249 | 371 | 1587 | 296 | 2019-06-11 01:00 | 183.3 | 55.2 | 1587 | B | 102 | 106 | 92 | 14 | 99.7 | 0.3 | [6 empty] | 188.58 | 141.1 | 141.1 | 186.06 | 420.2 | 502.08 | 421.35 | 469.12 | 104.13 | 71.13 | 10.02 | 58.13 | 1 |  | 3.06 | 1 | 714.31 | 5.29 | 0.51 | 1.01
49 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL017 | 1S-DL-YP-ETC-DKRN-2103-GCL017 | GEETA COLONY,15, BLK:PL | TG-GCL017A-2 | 19506379 | 630 | 200 | 240 | 0.98 | 666 | 200 | 902 | 292 | 1384 | 174 | 750 | 574 | 2019-06-11 01:00 | 195 | 34.8 | 1384 | Y | 105 | 91 | 104 | 14 | 0.4 | 0.7 | 63.2 | 35.7 |  |  |  |  | 201.57 | 300.31 | 300.31 | 233.01 | 424.04 | 401.2 | 488.2 | 444.5 | 71.2 | 2 | 31 | 26 | 7 | 0.3 | 0.3 | 0.3 | 704.21 | 15.39 | 0.47 | 1.06
50 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL018 | 1S-DL-YP-ETC-DKRN-2103-GCL018 | GEETA COLONY,17, BLK COM CENTRE:PL | TG-GCL018A-1 | 19505190 | 630 | 200 | 234 | 0.98 | 590 | 194 | 856 | 197 | 870 | 198 | 871 | 14 | 2019-06-30 00:30 | 91.2 | 23.2 | 927 | B | 96 | 116 | 88 | 28 | 0.1 | 0.2 | 10.7 | 88.9 | 1.3 |  | 39.3 |  | 302.41 | 126.44 | 126.44 | 286.08 | 388.2 | 526.33 | 299.36 | 393.23 | 10 | 49.14 | 16.3 | 23 |  |  | 0.3 |  | 702.31 | 17.29 | 0.49 | 0.94
51 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL019 | 1S-DL-YP-ETC-DKRN-2103-GCL019 | GEETA COLONY,17,BLK:PL | TG-GCL019A-2 | 19504388 | 630 | 200 | 239 | 0.97 | 621 | 209 | 882 | 237 | 1007 | 175 | 735 | 235 | 2019-06-12 | 102.6 | 6.9 | 1045 | Y | 95 | 94 | 112 | 18 |  |  | 14.6 | 85.4 | 385.41 | 390.41 | 109.29 | 345.41 | 68.1 | 47.1 | 47.1 | 96.1 | 225.53 | 214.38 | 262.43 | 233.34 | 37 | 44.15 | 14.3 | 41.19 |  | 20 |  |  | 716.44 | 3.16 | 0.34 | 0.99
52 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL022 | 1S-DL-YP-ETC-DKRN-2103-GCL022 | GEETA COLONY,3, BLK:K | TG-GCL022A-2 | 19505718 | 630 | 200 | 241 | 0.97 | 473 | 134 | 573 | 147 | 634 | 191 | 818 | 221 | 2019-06-12 01:00 | 108.8 | 31.6 | 907 | B | 87 | 95 | 118 | 31 | 0.4 |  | 34 | 65.5 | 10.28 | 5.3 |  |  | 472.53 | 438.21 | 438.21 | 431.21 | 222.35 | 262.35 | 357.06 | 275.05 | 0.3 |  | 50.35 | [5 empty] | 706.26 | 13.34 | 0.55 | 0.75
53 | 2019-06-04 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL023 | 1S-DL-YP-ETC-DKRN-2103-GCL023 | GEETA COLONY,5,BLK:ID | TG-GCL023A-1 | 19506808 | 990 | 320 | 235 | 0.98 | 878 | 416 | 2065 | 197 | 881 | 265 | 1265 | 1046 | 2019-06-11 01:00 | 275.2 | 54.1 | 2065 | R | 123 | 94 | 83 | 40 | 0.3 | 2.4 | 86.3 | 11 |  |  | 6 |  | 191.19 | 368.56 | 368.56 | 332.11 | 356.22 | 250.2 | 174.3 | 287 | 64 |  | 0.05 | 0.05 | 7.35 |  |  |  | 619.16 | 28.44 | 0.48 | 0.89
54 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL025 | 1S-DL-YP-ETC-DKRN-2103-GCL025 | GEETA COLONY,7, BLK:PL | TG-GCL025A-1 | 19506865 | 990 | 320 | 236 | 0.98 | 1022 | 230 | 1032 | 383 | 1880 | 409 | 1978 | 901 | 2019-06-11 01:00 | 337.9 | 46.1 | 1978 | B | 92 | 91 | 117 | 26 | 0.4 | 0.1 | 23.7 | 75.8 | 4 | 0.3 |  |  | 408.25 | 409.55 | 409.55 | 332.25 | 295.35 | 298.3 | 460.27 | 366 | 1.3 | 0.3 | 76 | 11 |  | 0.05 | 3.35 | 0.05 | 709.3 | 10.3 | 0.44 | 1.03
55 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL026 | 1S-DL-YP-ETC-DKRN-2103-GCL026 | GEETA COLONY,8,BLK;PL | TG-GCL026A-2 | 19506115 | 400 | 120 | 243 | 0.96 | 357 | 108 | 444 | 142 | 591 | 107 | 447 | 146 | 2019-06-16 01:00 | 98.6 | 28.9 | 771 | B | 93 | 113 | 93 | 20 | 0.4 | 0.8 | 71.6 | 27.2 | 0.3 |  |  |  | 89.3 | 22 | 22 | 45 | 606.26 | 508.58 | 597.26 | 607.56 | 12 | 169.28 | 15.3 | 55.3 |  | 8 | 0.3 |  | 708.26 | 11.34 | 0.66 | 0.89
56 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL027 | 1S-DL-YP-ETC-DKRN-2103-GCL027 | GEETA COLONY,8-A,BLK:ID | TG-GCL027A-1 | 19506019 | 990 | 320 | 238 | 0.97 | 919 | 363 | 1555 | 243 | 1029 | 313 | 1336 | 458 | 2019-06-11 23:30 | 258.9 | 58.2 | 1596 | R | 111 | 85 | 104 | 26 | 0.4 |  | 69.2 | 30.4 |  | 2 |  |  | 88 | 353.27 | 353.27 | 175.3 | 517.25 | 351.58 | 546.25 | 482.25 | 99 | 0.3 | 58.3 | 50 | 3.3 |  | 0.3 |  | 707.55 | 12.05 | 0.56 | 0.93
57 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL028 | 1S-DL-YP-ETC-DKRN-2103-GCL028 | GEETA COLONY,POL.STATION | TG-GCL028A-1 | 19505717 | 630 | 200 | 235 | 0.97 | 550 | 129 | 537 | 250 | 1065 | 171 | 715 | 465 | 2019-06-04 01:30 | 138 | 36.6 | 1164 | B | 98 | 74 | 129 | 55 | 1 | 10.2 | 72.1 | 16.7 |  | 2.3 |  |  | 162.29 | 391.32 | 391.32 | 106 | 528.3 | 313.27 | 575.31 | 598.59 | 17 |  | 117.58 | 3 |  | 0.3 | 8 |  | 707.59 | 12.01 | 0.6 | 0.87
58 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL030 | 1S-DL-YP-ETC-DKRN-2103-GCL030 | NEW LAHORE (MUNSHI COLONY):PL | TG-GCL030A-1 | 19506789 | 990 | 320 | 235 | 0.97 | 1099 | 383 | 1722 | 351 | 1549 | 365 | 1643 | 149 | 2019-06-10 02:00 | 291.5 | 75.5 | 1854 | R | 101 | 99 | 100 | 2 | 0.9 | 6.3 | 80.2 | 12.5 |  |  |  |  | 6.23 | 8.42 | 8.42 | 5.42 | 520.29 | 504.4 | 513.22 | 511.4 | 125.14 | 157.16 | 136.46 | 146.33 | 22.16 | 3.44 | 16.14 | 10.27 | 706.42 | 13.18 | 0.61 | 1.11
59 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL031 | 1S-DL-YP-ETC-DKRN-2103-GCL031 | NEW LAHORE EXTENSION:PL | TG-GCL031A-2 | 19506866 | 990 | 320 | 243 | 0.97 | 1078 | 389 | 1625 | 375 | 1546 | 314 | 1303 | 291 | 2019-06-28 | 241 | 65.3 | 1661 | R | 111 | 97 | 92 | 19 | 0.4 | 0.8 | 75.3 | 23.4 |  |  |  |  | 59.54 | 105.32 | 105.32 | 95.54 | 519.55 | 562.43 | 521.04 | 552.36 | 112.23 | 31.34 | 8.45 | 50.36 | 9.37 | 2 | 2.22 | 2.43 | 701.49 | 18.11 | 0.5 | 1.09
60 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL032 | 1S-DL-YP-ETC-DKRN-2103-GCL032 | RANI GARDEN NO.2,PARK WALA:PL | TG-GCL032A-1 | 19506148 | 990 | 320 | 242 | 0.98 | 838 | 267 | 1111 | 250 | 1043 | 321 | 1329 | 259 | 2019-06-30 01:30 | 243.2 | 59.5 | 1337 | B | 105 | 92 | 103 | 13 | 0.3 | 0.1 | 67.9 | 31.7 |  |  |  |  | 11.3 | 34 | 34 | 13.3 | 680.44 | 673.11 | 635.26 | 687.37 | 14.57 |  | 54.45 | 6.04 |  |  |  |  | 707.11 | 12.49 | 0.68 | 0.85
61 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL033 | 1S-DL-YP-ETC-DKRN-2103-GCL033 | RANI GARDEN SCHOOL;PL | TG-GCL033A-1 | 19505991 | 630 | 200 | 245 | 0.93 | 736 | 251 | 1022 | 159 | 634 | 326 | 1313 | 590 | 2019-06-05 17:00 | 323.6 | 89 | 1313 | B | 92 | 95 | 113 | 21 |  | 0.6 | 92.3 | 7.1 | [5 empty] | 1 | 1 |  | 249.4 | 249.23 | 232.1 | 248.4 | 3.07 | 3 | 18.3 | 4.07 | 0.36 |  | 2.43 | 0.36 | 253.24 | 34.36 | 0.52 | 1.17
62 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL034 | 1S-DL-YP-ETC-DKRN-2103-GCL034 | RANI GARDEN SWITCHING S/STN:PL | TG-GCL034A-1 | 19506864 | 630 | 200 | 236 | 0.98 | 598 | 183 | 788 | 215 | 930 | 200 | 862 | 123 | 2019-06-30 | 162.4 | 36.4 | 1015 | Y | 95 | 104 | 100 | 9 | 0.4 | 0.2 | 31 | 68.5 |  |  |  |  | 70.3 | 41 | 41 | 49 | 607.44 | 578.52 | 582.44 | 603.44 | 30.43 | 84.08 | 59.43 | 56.13 |  | 4.57 |  |  | 708.57 | 11.03 | 0.6 | 0.95
63 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL035 | 1S-DL-YP-ETC-DKRN-2103-GCL035 | SARASWATI BHANDAR:PL | TG-GCL035A-1 | 19505989 | 630 | 200 | 245 | 0.99 | 580 | 179 | 751 | 196 | 820 | 205 | 862 | 97 | 2019-06-02 14:30 | 74.2 | 1 | 884 | B | 89 | 100 | 111 | 22 | 0.1 |  | 37.7 | 62.2 | 403 | 377.3 | 375.3 | 386 | 63.59 | 63.59 | 63.59 | 59.29 | 247 | 125 | 86 | 158 | 6 | 153.3 | 192 | 116.3 |  |  |  |  | 719.59 | 0.01 | 0.4 | 0.92
64 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL036 | 1S-DL-YP-ETC-DKRN-2103-GCL036 | SAROJINI PARK:PKG | TG-GCL036A-1 | 19506408 | 990 | 320 | 242 | 0.98 | 820 | 256 | 1069 | 270 | 1161 | 294 | 1241 | 149 | 2019-06-11 23:30 | 194.2 | 47 | 1376 | Y | 96 | 95 | 109 | 14 | 29 | 33.9 | 31.6 | 5.5 |  |  |  |  | 214.2 | 271.19 | 271.19 | 201.19 | 481.13 | 421.44 | 531.12 | 488.14 |  | 2.3 | 42.3 | 6 |  |  |  |  | 695.33 | 24.27 | 0.59 | 0.83
65 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL038 | 1S-DL-YP-ETC-DKRN-2103-GCL038 | SHASTRI PARK NAGAR, NO-2:K | TG-GCL038A-1 | 19506782 | 990 | 320 | 242 | 0.97 | 914 | 319 | 1395 | 319 | 1379 | 276 | 1192 | 196 | 2019-06-09 00:30 | 227.8 | 55.4 | 1560 | B | 93 | 92 | 114 | 22 | 0.4 | 0.4 | 58.3 | 41 |  |  |  |  | 226.56 | 241.58 | 241.58 | 162.28 | 481.47 | 466.45 | 569.43 | 539.15 | 2 | 2 | 78 | 9 |  |  | 2.3 |  | 710.43 | 9.17 | 0.54 | 0.92
66 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL041 | 1S-DL-YP-ETC-DKRN-2103-GCL041 | SUBASH ROAD, TIKONA PARK:K | TG-GCL041A-2 | 19501917 | 990 | 320 | 238 | 0.99 | 944 | 288 | 1256 | 307 | 1333 | 349 | 1510 | 226 | 2019-06-02 15:00 | 115.6 | 9.6 | 1658 | Y | 90 | 94 | 116 | 26 |  |  | 5.7 | 94.3 | 406.31 | 440.11 | 291.48 | 387.17 | 51.28 | 51.14 | 51.14 | 63.12 | 237.05 | 72.33 | 94.23 | 144.47 | 16.41 | 126.01 | 164.33 | 116.29 |  | 21.46 | 12.2 |  | 711.45 | 8.15 | 0.39 | 0.95
67 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL041 | 1S-DL-YP-ETC-DKRN-2103-GCL041 | SUBASH ROAD, TIKONA PARK:K | TG-GCL041A-1 | 19505574 | 990 | 320 | 251 | 0.98 | 936 | 322 | 1353 | 313 | 1328 | 301 | 1264 | 79 | 2019-06-29 16:00 | 172.2 | 10.2 | 1688 | B | 92 | 106 | 102 | 14 | 0.1 | 0.1 | 38 | 61.8 | 379.56 | 344.03 | 348.03 | 365.03 | 65.57 | 83.5 | 83.5 | 66.5 | 185.44 | 94.41 | 131.12 | 127.12 | 71.3 | 179.33 | 138.04 | 144.02 |  | 1 | 0.58 |  | 703.07 | 16.53 | 0.42 | 0.95
68 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL041 | 1S-DL-YP-ETC-DKRN-2103-GCL041 | SUBASH ROAD, TIKONA PARK:K | TG-GCL041A-4 | 19506152 | 990 | 320 | 245 | 0.99 | 778 | 272 | 1198 | 178 | 747 | 328 | 1498 | 655 | 2019-06-30 14:00 | 162.2 | 3.5 | 1498 | B | 119 | 87 | 95 | 32 | 0.3 | 0.1 | 22.1 | 77.6 | 414.34 | 431.16 | 428.04 | 426.04 | 34.59 | 51.15 | 51.15 | 41.57 | 173.14 | 215.52 | 226.52 | 230.22 | 75.36 |  | 1 | [5 empty] | 698.23 | 21.37 | 0.33 | 0.79
69 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL042 | 1S-DL-YP-ETC-DKRN-2103-GCL042 | SWARG ASHARM:PM | TG-GCL042A-1 | 19505737 | 100 | 40 | 243 | 0.76 | 78 | 20 | 82 | 31 | 130 | 27 | 112 | 42 | 2019-06-03 19:00 | 9.6 | -24 | 137 | Y | 70 | 135 | 95 | 65 | 0.4 | 0.6 | 34.1 | 64.9 | 394.54 | 385.25 | 384.54 | 384.55 | 166.3 | 20.3 | 20.3 | 37.29 | 144 | 134.29 | 286.3 | 283.3 | 0.3 | 165.3 | 2 | [5 empty] | 705.54 | 14.06 | 0.33 | 0.78
70 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | GAN017 | 1S-DL-YP-ETC-DKRN-2102-GAN017 | KAUSHIK PURI KIOSK:K | TG-GAN017A-1 | 19502029 | 990 | 320 | 244 | 0.98 | 813 | 350 | 1476 | 232 | 979 | 231 | 938 | 519 | 2019-06-01 19:30 | 157.5 | 33.1 | 1476 | R | 118 | 90 | 92 | 28 | 100 |  |  |  | 82.59 |  |  |  |  | 187.05 | 187.05 | 93.57 | 533.05 | 532.18 | 602.57 | 624.56 | 97.49 |  |  | 0.3 | 5.3 |  |  |  | 719.23 | 0.37 | 0.62 | 0.82
71 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | GAN018 | 1S-DL-YP-ETC-DKRN-2102-GAN018 | KAUSHIK PURI PARK:PL | TG-GAN018A-2 | 19504747 | 630 | 200 | 246 | 0.98 | 491 | 151 | 610 | 140 | 564 | 201 | 807 | 224 | 2019-06-01 19:30 | 84.6 | 13.8 | 865 | B | 101 | 78 | 121 | 43 | 0 |  | 36.7 | 63.3 | 0.3 | 1 | 1 | 1 | 48.45 | 417.59 | 417.59 | 47.21 | 668.07 | 298.23 | 629.17 | 669.01 |  |  | 80.05 | [5 empty] | 717.22 | 2.38 | 0.66 | 0.78
72 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | GAN035 | 1S-DL-YP-ETC-DKRN-2102-GAN035 | CHAMELI DEVI OUTSIDE:PL | TG-GAN035A-1 | 19506068 | 990 | 320 | 236 | 0.97 | 809 | 274 | 1174 | 219 | 941 | 316 | 1371 | 373 | 2019-06-30 15:30 | 201.3 | 33.3 | 1433 | B | 98 | 87 | 115 | 28 | 0.2 | 0.6 | 71.2 | 28 | 1 | 7 |  |  | 241.4 | 370.52 | 370.52 | 249.4 | 456.03 | 322.21 | 488.27 | 449.03 | 1.3 |  | 56.3 | 1.3 |  |  |  |  | 700.13 | 19.47 | 0.59 | 0.82
73 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI002 | 1S-DL-YP-ETC-DKRN-2101-KRI002 | AZAD NAGAR WATER TANK:PL | TG-KRI002A-1 | 19503599 | 990 | 320 | 244 | 0.97 | 895 | 311 | 1257 | 275 | 1108 | 309 | 1237 | 140 | 2019-06-29 23:30 | 176.6 | 63.3 | 1463 | R | 107 | 85 | 108 | 23 |  | 0.1 | 17.1 | 82.8 |  |  |  |  | 68 | 302.22 | 302.22 | 100.56 | 569.56 | 400.34 | 595.56 | 574.3 | 75 | 15.3 | 73.3 | 43 | 5.3 |  |  |  | 718.26 | 1.34 | 0.6 | 0.9
74 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI006 | 1S-DL-YP-ETC-DKRN-2101-KRI006 | BHAGAT SINGH PARK NO 1:PL | TG-KRI006A-1 | 19501914 | 990 | 320 | 243 | 0.97 | 1127 | 383 | 1618 | 366 | 1532 | 378 | 1601 | 79 | 2019-06-14 | 223.7 | 67 | 1637 | R | 104 | 92 | 104 | 12 |  |  | 74 | 26 | 0.3 | 0.3 | 0.3 | 0.3 | 52.3 | 155.06 | 155.06 | 88.52 | 525.14 | 462.47 | 509.35 | 504.02 | 109.57 | 89.47 | 121.05 | 108.46 | 24.4 | 4.41 | 13.41 | 10.41 | 712.51 | 7.09 | 0.52 | 1.14
75 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI012 | 1S-DL-YP-ETC-DKRN-2101-KRI012 | EAST AZAD NAGAR TIKONA PARK:ID | TG-KRI012A-1 | 19506591 | 990 | 320 | 237 | 0.97 | 738 | 251 | 1098 | 214 | 921 | 273 | 1187 | 235 | 2019-06-17 22:00 | 286.1 | 57.6 | 1853 | B | 91 | 89 | 120 | 31 | 0.4 | 0.4 | 59.1 | 40.1 |  |  |  |  | 312.51 | 306.44 | 306.44 | 178.35 | 392.49 | 398.26 | 611.49 | 527.05 |  | 0.3 | 39.3 |  |  |  | 1 |  | 705.4 | 14.2 | 0.63 | 0.75
76 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI026 | 1S-DL-YP-ETC-DKRN-2101-KRI026 | KANTI NAGAR EXT. GALI NO. 5:PL | TG-KRI026A-1 | 19504956 | 990 | 320 | 246 | 0.97 | 925 | 303 | 1242 | 296 | 1215 | 326 | 1329 | 104 | 2019-06-02 00:30 | 203.9 | 75.8 | 1407 | B | 104 | 96 | 100 | 8 |  |  | 34.7 | 65.3 |  |  |  |  | 5.3 | 6 | 6 | 6.3 | 566.16 | 651.46 | 578.46 | 617.46 | 145.3 | 59.3 | 127 | 93 |  |  | 1 |  | 717.16 | 2.44 | 0.71 | 0.93
77 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI027 | 1S-DL-YP-ETC-DKRN-2101-KRI027 | KANTI NAGAR EXT. GALI NO. 9:PL | TG-KRI027A-2 | 19505347 | 990 | 320 | 250 | 0.97 | 892 | 274 | 1114 | 243 | 975 | 374 | 1532 | 503 | 2019-06-30 23:30 | 259.5 | 67.5 | 1535 | B | 95 | 91 | 114 | 23 | 0.2 | 3 | 84.5 | 12.3 |  |  |  |  | 89.39 | 118.3 | 118.3 | 66 | 613.25 | 585.34 | 568.11 | 629.44 | 1 |  | 87.03 | 8.2 |  |  | 10.2 |  | 704.04 | 15.56 | 0.6 | 0.9
78 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI028 | 1S-DL-YP-ETC-DKRN-2101-KRI028 | KANTI NAGAR EXT.(NALAH):PL | TG-KRI028A-1 | 19506442 | 630 | 200 | 241 | 0.98 | 423 | 222 | 953 | 113 | 484 | 88 | 369 | 536 | 2019-06-26 14:30 | 141.6 | 27.2 | 961 | R | 154 | 91 | 56 | 98 |  | 0.4 | 24.8 | 74.8 |  |  | 78.33 |  | 1 | 318.16 | 318.16 | 170.51 | 584.35 | 385.19 | 1.3 | 532.44 | 116.3 |  |  |  | 1.3 |  |  |  | 703.35 | 16.25 | 0.67 | 0.67
79 | 2019-06-14 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI039 | 1S-DL-YP-ETC-DKRN-2101-KRI039 | RAJGARH EXTN.(MINI STADIUM):ID | TG-KRI039A-2 | 19505976 | 990 | 320 | 236 | 0.97 | 1007 | 441 | 2016 | 259 | 1145 | 307 | 1347 | 789 | 2019-06-29 23:00 | 247.7 | 50.6 | 2016 | R | 100 | 97 | 103 | 6 | 0.5 | 0.4 | 55.5 | 43.6 |  | 1 | 1.1 |  | 157.07 | 138.22 | 138.22 | 141.22 | 196.15 | 227.3 | 210.15 | 214 | 23.3 | 12.3 | 34.3 | 23 | 2.3 |  | 1.3 | 1 | 379.22 | 28.38 | 0.48 | 1.02
80 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI040 | 1S-DL-YP-ETC-DKRN-2101-KRI040 | RAJGARH MOTHER DAIRY GALI NO 6:PL | TG-KRI040A-1 | 19500881 | 990 | 320 | 238 | 0.97 | 963 | 334 | 1476 | 337 | 1503 | 292 | 1297 | 194 | 2019-06-11 | 193.6 | 64 | 1602 | Y | 97 | 109 | 95 | 14 |  | 0.6 | 68.2 | 31.1 |  |  |  |  | 180.48 | 65.16 | 65.16 | 134.47 | 468.35 | 554.46 | 473.37 | 515.45 | 64.03 | 88.54 | 42.13 | 63.1 | 0.16 | 4.46 |  |  | 713.42 | 6.18 | 0.56 | 0.97
81 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI040 | 1S-DL-YP-ETC-DKRN-2101-KRI040 | RAJGARH MOTHER DAIRY GALI NO 6:PL | TG-KRI040A-2 | 19504387 | 990 | 320 | 240 | 0.97 | 836 | 334 | 1416 | 246 | 1031 | 257 | 1087 | 360 | 2019-06-12 02:30 | 178.8 | 51.5 | 1416 | R | 112 | 95 | 94 | 18 |  |  | 65.5 | 34.5 |  |  | 0.3 |  | 170.34 | 332.08 | 332.08 | 266.08 | 502.56 | 382.12 | 394.29 | 445.44 | 40.29 |  | 0.18 | 2.28 | 0.21 |  |  |  | 714.2 | 5.4 | 0.55 | 0.84
82 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI044 | 1S-DL-YP-ETC-DKRN-2101-KRI044 | SHANKAR NAGAR EXT.:PL | TG-KRI044A-2 | 19506141 | 630 | 120 | 240 | 0.98 | 470 | 126 | 524 | 160 | 672 | 184 | 768 | 213 | 2019-06-02 15:30 | 88.9 | 7.2 | 813 | B | 81 | 98 | 121 | 40 | 0.1 | 0.4 | 0.4 | 99.2 | 54.3 | 6.3 | 0.3 | 4.3 | 399.53 | 332.51 | 332.51 | 336.51 | 240.52 | 355.54 | 418.34 | 353.54 |  |  | 41.5 | [5 empty] | 695.15 | 24.45 | 0.58 | 0.75
83 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI052 | 1S-DL-YP-ETC-DKRN-2101-KRI052 | WEST AZAD NAGAR (RASGULLA):PL | TG-KRI052A-1 | 19506565 | 990 | 320 | 251 | 0.97 | 882 | 252 | 1015 | 318 | 1268 | 312 | 1256 | 247 | 2019-06-11 23:30 | 215.7 | 60.5 | 1356 | B | 89 | 106 | 104 | 17 | 0.3 | 0.1 | 46.5 | 53.2 |  |  |  |  | 342.08 | 180.11 | 180.11 | 246.33 | 360.03 | 462.14 | 416.33 | 428.38 | 0.3 | 60.16 | 62 | 27.3 |  |  |  |  | 702.41 | 17.19 | 0.55 | 0.89
84 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI053 | 1S-DL-YP-ETC-DKRN-2101-KRI053 | WEST AZAD NAGAR SHD ROAD B&D BL NO. 1:ID | TG-KRI053A-2 | 19501884 | 990 | 200 | 240 | 0.97 | 954 | 322 | 1346 | 281 | 1151 | 351 | 1463 | 273 | 2019-06-10 03:00 | 196.9 | 71.8 | 1475 | B | 103 | 89 | 108 | 19 |  | 0.8 | 67.5 | 31.7 |  |  |  |  | 87 | 218.15 | 218.15 | 105.01 | 586.35 | 481.01 | 538.09 | 564.26 | 39.25 | 13.44 | 94.54 | 43.33 |  |  | 3.55 |  | 713 | 7 | 0.56 | 0.96
85 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI057 | 1S-DL-YP-ETC-DKRN-2101-KRI057 | WEST KANTI NAGAR:ID | TG-KRI057A-1 | 19504088 | 990 | 320 | 244 | 0.97 | 866 | 244 | 990 | 280 | 1140 | 342 | 1390 | 350 | 2019-06-29 22:30 | 206.1 | 72.9 | 1450 | B | 86 | 94 | 120 | 34 |  |  | 0.3 | 99.7 |  |  |  |  | 14 | 1 | 1 |  | 705.58 | 717.58 | 530.58 | 710.28 |  | 1 | 181.3 | 9.3 |  |  | 7.3 |  | 719.58 | 0.02 | 0.7 | 0.87
86 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI066 | 1S-DL-YP-ETC-DKRN-2101-KRI066 | East Azad Nagar Primary School | TG-KRI066A-1 | 19506021 | 990 | 320 | 245 | 0.96 | 874 | 268 | 1102 | 283 | 1170 | 323 | 1324 | 197 | 2019-06-02 23:00 | 234.9 | 64 | 2011 | R | 93 | 98 | 110 | 17 | 0.4 | 0.1 | 37.6 | 62 |  |  |  |  | 269.4 | 216.19 | 216.19 | 195.49 | 426.18 | 479.45 | 490.36 | 476.45 | 9 | 9 | 97.08 | 32.3 | 0.06 |  |  |  | 705.04 | 14.56 | 0.58 | 0.88
87 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI001 | 1S-DL-YP-ETC-DKRN-2101-KRI001 | A-BLOCK KRN:PL | TG-KRI001A-1 | 19505570 | 990 | 320 | 238 | 0.98 | 896 | 249 | 1104 | 372 | 1718 | 275 | 1254 | 555 | 2019-06-11 01:00 | 208 | 29.4 | 1807 | Y | 91 | 107 | 102 | 16 | 1.9 | 37.8 | 56.5 | 3.7 |  |  |  |  | 108.49 | 60.58 | 60.58 | 72.5 | 592.2 | 544.18 | 561.48 | 584.56 |  | 90.53 | 60.32 | 43.23 |  | 5 |  |  | 701.09 | 18.51 | 0.62 | 0.91
88 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI003 | 1S-DL-YP-ETC-DKRN-2101-KRI003 | B-BLOCK KRISHNA NAGAR 8/24:PM | TG-KRI003A-1 | 19505516 | 630 | 200 | 238 | 0.98 | 587 | 205 | 877 | 201 | 866 | 180 | 769 | 103 | 2019-06-12 00:30 | 125 | 35.6 | 1211 | Y | 97 | 102 | 101 | 5 | 0.4 | 0.2 | 58 | 41.4 |  |  |  |  | 115.33 | 52.03 | 52.03 | 48.03 | 535.5 | 587.15 | 646.32 | 611.51 | 54.45 | 66.2 | 21.03 | 46.14 |  | 0.3 |  |  | 706.08 | 13.52 | 0.6 | 0.93
89 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI008 | 1S-DL-YP-ETC-DKRN-2101-KRI008 | C-BLOCK KRISHNA NAGAR NO 1:ID | TG-KRI008A-2 | 19506020 | 990 | 320 | 245 | 0.98 | 1185 | 220 | 927 | 438 | 2069 | 527 | 2370 | 1319 | 2019-06-01 19:30 | 374.7 | 38.4 | 2370 | B | 84 | 108 | 107 | 24 | 0.4 | 0.1 | 40.8 | 58.7 | 2.3 |  | 0.3 |  | 229 | 99 | 99 | 149.3 | 465.09 | 394.35 | 388.36 | 417.35 | 9.58 | 195.33 | 162.36 | 138.36 | 0.25 | 17.54 | 22.51 | 1.21 | 707.02 | 12.58 | 0.49 | 1.2
90 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI011 | 1S-DL-YP-ETC-DKRN-2101-KRI011 | D-BLOCK KRISHNA NAGAR:PL | TG-KRI011A-1 | 19506772 | 990 | 320 | 238 | 0.98 | 1201 | 449 | 1967 | 309 | 1313 | 444 | 2053 | 701 | 2019-06-01 19:00 | 393.9 | 35.5 | 2053 | B | 104 | 101 | 94 | 10 | 72 | 2.3 | 12 | 13.6 |  |  |  |  | 42 | 137.3 | 137.3 | 71 | 592.06 | 514.22 | 650.18 | 610.52 | 69.05 | 51.19 | 3.53 | 22.49 | 2 | 2 | 1 | 0.3 | 705.11 | 14.49 | 0.48 | 1.21
91 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI015 | 1S-DL-YP-ETC-DKRN-2101-KRI015 | E-BLOCK KRN LAJ PAT RAI CHOWK:PL | TG-KRI015A-2 | 19505772 | 630 | 200 | 238 | 0.98 | 537 | 228 | 1103 | 172 | 794 | 136 | 607 | 433 | 2019-06-11 01:00 | 175.6 | 32.4 | 1148 | Y | 101 | 107 | 92 | 15 | 0.4 | 0.1 | 54 | 45.5 |  |  |  |  | 23.01 | 21.02 | 21.02 | 21.01 | 677.12 | 640.53 | 651.02 | 682.42 | 4 | 42.18 | 1 | 1 | 0.3 | 0.3 |  |  | 704.43 | 15.17 | 0.67 | 0.85
92 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI017 | 1S-DL-YP-ETC-DKRN-2101-KRI017 | F-BLOCK KRN PLM:PL | TG-KRI017A-2 | 19506503 | 630 | 200 | 239 | 0.98 | 556 | 147 | 652 | 228 | 1011 | 181 | 799 | 312 | 2019-06-11 01:00 | 157.6 | 8.8 | 1564 | Y | 100 | 112 | 88 | 24 | 0.3 | 0.1 | 49.6 | 50 | 120.53 | 155.21 | 285.38 | 172.35 | 392.32 | 290.25 | 290.25 | 297.56 | 182.04 | 201.05 | 181.06 | 221.36 | 3.3 | 44.22 | 0.3 | 6.52 |  | 7.46 |  |  | 698.59 | 21.01 | 0.38 | 0.88
93 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI018 | 1S-DL-YP-ETC-DKRN-2101-KRI018 | H-BLOCK KRISHNA NAGAR (MOTHER DAIRY):K | TG-KRI018A-2 | 19506531 | 630 | 200 | 235 | 0.97 | 629 | 167 | 751 | 222 | 995 | 240 | 1074 | 291 | 2019-06-11 00:30 | 176.6 | 17.4 | 1263 | R | 81 | 109 | 110 | 29 | 0.5 | 0.7 | 5.4 | 93.4 | 3.05 | 0.2 | 0.22 | 0.2 | 340.38 | 96.26 | 96.26 | 156.42 | 340.27 | 556.46 | 485.08 | 510.56 | 9.39 | 41.27 | 79.18 | 28.21 | 2.3 | 1.2 | 6.23 |  | 696.19 | 23.41 | 0.52 | 1
94 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI019 | 1S-DL-YP-ETC-DKRN-2101-KRI019 | J-BLOCK KRN:PL | TG-KRI019A-2 | 19505280 | 990 | 320 | 244 | 0.97 | 1013 | 335 | 1417 | 334 | 1419 | 343 | 1445 | 27 | 2019-06-11 03:30 | 325.4 | 58.9 | 1866 | Y | 94 | 103 | 102 | 9 | 0.3 |  | 1.3 | 98.4 |  |  | 0.3 |  | 19.3 | 2 | 2 | 5.3 | 612.42 | 595.07 | 585.23 | 605.26 | 70.37 | 103.23 | 106.42 | 92.1 | 1.16 | 3.35 | 2 | 0.59 | 704.05 | 15.55 | 0.63 | 1.02
95 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI020 | 1S-DL-YP-ETC-DKRN-2101-KRI020 | JHEEL NO. 1:PL | TG-KRI020A-1 | 19503581 | 630 | 200 | 240 | 0.98 | 528 | 172 | 729 | 183 | 775 | 173 | 723 | 49 | 2019-06-02 16:00 | 125.1 | -0.9 | 860 | Y | 101 | 105 | 93 | 12 |  |  | 58.9 | 41.1 |  |  |  |  | 67 | 77.3 | 77.3 | 95.3 | 651.41 | 566.46 | 557.41 | 616.41 | 1 | 75.25 | 9.3 | 7.3 |  |  |  |  | 719.41 | 0.19 | 0.67 | 0.84
96 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI021 | 1S-DL-YP-ETC-DKRN-2101-KRI021 | JHEEL NO. 2:PL | TG-KRI021A-1 | 19506780 | 990 | 320 | 240 | 0.99 | 885 | 298 | 1255 | 279 | 1176 | 307 | 1303 | 110 | 2019-06-30 16:00 | 220.2 | -20.2 | 2080 | B | 96 | 98 | 106 | 10 | 0.3 | 0.1 | 35.3 | 64.3 | 0.02 | 0.02 | 0.02 | 0.02 | 10.3 | 5 | 5 | 6.3 | 675.29 | 637.5 | 623.32 | 672.02 | 15 | 58.39 | 74.57 | 22.57 | 0.3 |  | 0.3 |  | 701.31 | 18.29 | 0.71 | 0.89
97 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI034 | 1S-DL-YP-ETC-DKRN-2101-KRI034 | OLD ANARKALI:ID | TG-KRI034A-3 | 19506766 | 630 | 200 | 243 | 0.97 | 538 | 214 | 918 | 170 | 721 | 153 | 649 | 241 | 2019-06-30 23:30 | 149.4 | 16.2 | 956 | R | 120 | 96 | 84 | 36 | 0.4 | 5 | 47.5 | 47.1 | 48.17 | 0.3 | 48.17 | 29.3 | 11.3 | 221.24 | 221.24 | 108.43 | 541.14 | 480.37 | 413.5 | 553.48 | 100.3 | 4 | 0.3 | 14.3 | 5 |  |  |  | 706.31 | 13.29 | 0.59 | 0.85
98 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI036 | 1S-DL-YP-ETC-DKRN-2101-KRI036 | RADHA PURI EXTN.(NALAH) NO. 1:PL | TG-KRI036A-1 | 19506680 | 990 | 320 | 238 | 0.98 | 915 | 224 | 969 | 361 | 1583 | 329 | 1449 | 559 | 2019-06-30 23:00 | 234.6 | 57.6 | 1863 | Y | 83 | 112 | 105 | 29 | 0.4 |  | 11.4 | 88.2 |  |  |  |  | 325.3 | 91.43 | 91.43 | 160.11 | 380.06 | 482.23 | 489.23 | 483.55 |  | 115.3 | 88 | 61.3 |  | 16 | 2 |  | 705.36 | 14.24 | 0.57 | 0.92
99 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI041 | 1S-DL-YP-ETC-DKRN-2101-KRI041 | RAM NAGAR L.N.MANDIR:PL | TG-KRI041A-1 | 19506779 | 1600 | 500 | 251 | 0.96 | 1465 | 776 | 3572 | 313 | 1264 | 375 | 1596 | 2161 | 2019-06-11 01:00 | 551 | 90.5 | 3572 | R | 107 | 96 | 97 | 11 | 0.4 | 0.1 | 61.4 | 38.2 |  | 3.3 | 0.3 |  | 224.3 | 339.28 | 339.28 | 290.58 | 453.42 | 364.14 | 409.44 | 413.44 | 28.3 | 0.3 |  | 3 | 1 |  |  |  | 707.42 | 12.18 | 0.51 | 0.92
100 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI047 | 1S-DL-YP-ETC-DKRN-2101-KRI047 | SHASTRI PARK:PL | TG-KRI047A-1 | 19502447 | 990 | 320 | 235 | 0.97 | 989 | 315 | 1363 | 336 | 1466 | 338 | 1472 | 106 | 2019-06-11 23:30 | 244.4 | 65.5 | 1583 | Y | 98 | 104 | 98 | 6 |  |  | 30 | 70 |  |  |  |  | 5.35 | 4.29 | 4.29 | 1.18 | 562.44 | 522.13 | 593.24 | 567.01 | 144.18 | 179.28 | 114.25 | 144.18 |  | 6.27 | 2.3 |  | 712.37 | 7.23 | 0.69 | 1
101 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI048 | 1S-DL-YP-ETC-DKRN-2101-KRI048 | ST.LIGHT OPP SWARN CINEMA ROAD NO 57:PM | TG-KRI048A-1 | 19505726 | 630 | 200 | 240 | 0.98 | 569 | 150 | 649 | 129 | 557 | 289 | 1288 | 690 | 2019-06-26 23:30 | 155.4 | 31.8 | 1288 | B | 98 | 85 | 117 | 32 | 0.1 | 0.6 | 9.6 | 89.8 |  | 0.3 |  |  | 207.54 | 352.24 | 352.24 | 195.24 | 488.15 | 350.45 | 476.45 | 496.15 | 7.3 |  | 95.3 | 12 |  |  | 10.3 |  | 703.39 | 16.21 | 0.55 | 0.9
102 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI051 | 1S-DL-YP-ETC-DKRN-2101-KRI051 | WEST ARJUN NAGAR:ID | TG-KRI051A-2 | 19506784 | 630 | 200 | 245 | 0.97 | 621 | 198 | 813 | 193 | 794 | 230 | 952 | 149 | 2019-06-09 23:30 | 124.4 | 45.4 | 977 | B | 94 | 100 | 106 | 12 |  | 0.1 | 4.4 | 95.5 |  |  |  |  | 44.55 | 28.3 | 28.3 | 20 | 594.17 | 573.45 | 508.15 | 581.28 | 70.27 | 107.24 | 169.24 | 108.11 |  |  | 18.3 |  | 709.39 | 10.21 | 0.65 | 0.99

## Loading Condition > 100%
MIS Report of Distribution Transformer - Jun19
Jun19 1220 KRISHNA NAGAR (Loading Condition > 100% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG001 | 1S-DL-YP-ETC-DKRN-2104-JAG001 | ARAM PARK:PL | TG-JAG001A-1 | 19500853 | 990 | 320 | 239 | 0.97 | 1406 | 463 | 1979 | 504 | 2156 | 439 | 1857 | 260 | 2019-06-11 23:00 | 281.9 | 108.2 | 2297 | Y | 100 | 108 | 93 | 15 |  |  | 28.3 | 71.7 |  |  |  |  | 1.3 |  |  | 1.3 | 433.42 | 356.26 | 463.43 | 426.19 | 125.15 | 172.31 | 103.59 | 127.08 | 151.22 | 182.52 | 131.37 | 156.52 | 711.49 | 8.11 | 0.57 | 1.42
2 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG002 | 1S-DL-YP-ETC-DKRN-2104-JAG002 | BEDI MKT:ID | TG-JAG002A-1 | 19506105 | 990 | 320 | 238 | 0.97 | 1022 | 303 | 1265 | 415 | 1772 | 304 | 1279 | 501 | 2019-06-03 02:00 | 279 | 11.2 | 1888 | R | 102 | 103 | 95 | 8 | 0.5 | 4.7 | 28.2 | 66.6 | 0.23 | 0.23 | 0.23 | 0.23 | 40.54 | 90.49 | 90.49 | 76.54 | 595.08 | 517.42 | 541.14 | 550.13 | 55.37 | 45.57 | 21.28 | 63.31 | 0.16 | 37.27 | 6.3 | 1.17 | 692.18 | 27.42 | 0.55 | 1.03
3 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG002 | 1S-DL-YP-ETC-DKRN-2104-JAG002 | BEDI MKT:ID | TG-JAG002A-3 | 19506656 | 990 | 320 | 244 | 0.97 | 1057 | 398 | 1668 | 337 | 1408 | 321 | 1339 | 300 | 2019-06-11 00:30 | 267.5 | 66.6 | 1966 | R | 114 | 97 | 90 | 24 | 0.4 | 0.1 | 16.5 | 83 |  |  |  |  | 69.44 | 169.09 | 169.09 | 143.09 | 453.07 | 446.06 | 435.15 | 453.39 | 113.3 | 68.22 | 32.23 | 87.06 | 51.51 | 4.35 |  | 4.18 | 688.12 | 31.48 | 0.52 | 1.07
4 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG009 | 1S-DL-YP-ETC-DKRN-2104-JAG009 | GAGAN VIHAR EXT:ID | TG-JAG009A-2 | 19506155 | 990 | 200 | 248 | 0.97 | 1397 | 464 | 1946 | 416 | 1740 | 517 | 2199 | 398 | 2019-06-11 01:30 | 278.2 | 55.2 | 2199 | B | 104 | 96 | 100 | 8 |  | 0.1 | 6.6 | 93.3 |  |  |  |  | 51.13 | 99.01 | 99.01 | 77.43 | 334.14 | 316.26 | 318.44 | 325.44 | 70.15 | 62.34 | 65.57 | 62.07 | 97.08 | 74.49 | 88.26 | 87.16 | 704.09 | 15.51 | 0.48 | 1.41
5 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG010 | 1S-DL-YP-ETC-DKRN-2104-JAG010 | GANDHI PARK:PL | TG-JAG010A-1 | 19500851 | 990 | 320 | 236 | 0.97 | 845 | 222 | 966 | 227 | 963 | 395 | 1694 | 729 | 2019-06-11 00:30 | 162.7 | 56.7 | 1820 | B | 83 | 80 | 137 | 57 | 0.3 | 20.3 | 78.4 | 1 | 3 | 12 |  |  | 424.2 | 424.27 | 424.27 | 262.27 | 289.54 | 280.47 | 490.14 | 443.58 |  |  | 104.3 | 10.49 |  |  | 67.3 |  | 717.14 | 2.46 | 0.56 | 0.85
6 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG018 | 1S-DL-YP-ETC-DKRN-2104-JAG018 | JAGAT PURI A BLK:PL | TG-JAG018A-3 | 19505712 | 630 | 200 | 242 | 0.97 | 824 | 307 | 1262 | 283 | 1142 | 234 | 944 | 278 | 2019-06-30 06:00 | 239.8 | 60.8 | 1443 | B | 102 | 86 | 112 | 26 | 0.4 | 6.2 | 33.1 | 60.2 | 0.3 | 0.3 | 0.3 | 0.3 | 4 | 48.32 | 48.32 | 9 | 544.28 | 621.48 | 485.35 | 557.58 | 142.27 | 44.01 | 131.53 | 113.32 | 24.27 | 1.01 | 89.24 | 34.52 | 715.52 | 4.08 | 0.51 | 1.31
7 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG022 | 1S-DL-YP-ETC-DKRN-2104-JAG022 | JITAR NAGAR:K | TG-JAG022A-2 | 19506650 | 990 | 320 | 245 | 0.97 | 1053 | 477 | 2083 | 394 | 1927 | 183 | 793 | 1219 | 2019-06-18 17:00 | 225 | 66.6 | 2083 | R | 115 | 89 | 96 | 26 | 0.6 | 1.8 | 44.4 | 53.2 |  |  | 0.3 |  | 15.25 | 92.2 | 92.2 | 49.51 | 502.29 | 603.04 | 484.33 | 544.03 | 120 | 7.3 | 109.3 | 107.3 | 65.3 | 0.3 | 5.3 | 2 | 703.24 | 16.36 | 0.57 | 1.06
8 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG023 | 1S-DL-YP-ETC-DKRN-2104-JAG023 | KHUREJI:ID | TG-JAG023A-2 | 19503528 | 990 | 320 | 242 | 0.98 | 1014 | 298 | 1265 | 361 | 1555 | 355 | 1528 | 278 | 2019-06-30 | 192.8 | 82.4 | 1617 | Y | 91 | 107 | 103 | 16 |  | 0.3 | 84.4 | 15.3 |  |  |  |  | 1 |  |  |  | 628.09 | 427.27 | 480.59 | 521.46 | 86.52 | 254.17 | 226.2 | 191.33 |  | 34.17 | 8.42 | 2.42 | 716.01 | 3.59 | 0.71 | 1.02
9 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG027 | 1S-DL-YP-ETC-DKRN-2104-JAG027 | RADHEY SHAYAM PARK:PL | TG-JAG027A-1 | 19506867 | 990 | 320 | 240 | 0.98 | 1075 | 329 | 1400 | 515 | 2252 | 231 | 986 | 1118 | 2019-06-11 00:30 | 194.9 | 41.9 | 2252 | Y | 95 | 125 | 80 | 45 | 0.2 | 1.6 | 34.9 | 63.2 |  |  |  |  | 191.23 | 44.32 | 44.32 | 132 | 445.25 | 461.55 | 413.44 | 479.57 | 67.3 | 96.3 |  | 91.21 | 2.52 | 104.13 |  | 3.52 | 707.1 | 12.5 | 0.51 | 1.09
10 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG031 | 1S-DL-YP-ETC-DKRN-2104-JAG031 | SOUTH ANARKALI:PL | TG-JAG031A-3 | 19506472 | 630 | 200 | 238 | 0.98 | 712 | 266 | 1192 | 226 | 1001 | 220 | 981 | 202 | 2019-06-10 00:30 | 127.8 | 39.8 | 1192 | R | 108 | 98 | 94 | 14 | 0.2 | 0.4 | 18.6 | 80.8 | 0.06 | 0.06 | 0.06 | 0.06 | 32.24 | 61.31 | 61.31 | 47.24 | 476.14 | 496.41 | 485.11 | 498.54 | 124.23 | 119.14 | 117.12 | 128.22 | 62.47 | 18.22 | 5.24 | 21.08 | 695.54 | 24.06 | 0.55 | 1.13
11 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG031 | 1S-DL-YP-ETC-DKRN-2104-JAG031 | SOUTH ANARKALI:PL | TG-JAG031A-2 | 19506868 | 990 | 320 | 238 | 0.97 | 1166 | 395 | 1779 | 355 | 1587 | 416 | 1875 | 254 | 2019-06-10 00:30 | 253.8 | 67.8 | 1953 | R | 109 | 95 | 96 | 14 | 0.4 | 0.6 | 30.9 | 68.1 |  |  |  |  | 17.54 | 80.55 | 80.55 | 46.55 | 496.35 | 485.49 | 468.11 | 501.1 | 115.28 | 117.34 | 115.39 | 115.58 | 65.29 | 11.08 | 24.23 | 31.23 | 695.26 | 24.34 | 0.54 | 1.18
12 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GAGAN VIHAR | 1220 | JAG039 | 1S-DL-YP-ETC-DKRN-2104-JAG039 | R.S. PARK (PARKWALA) | TG-JAG039A-2 | 19506106 | 630 | 200 | 245 | 0.97 | 584 | 141 | 577 | 177 | 728 | 266 | 1120 | 486 | 2019-06-11 23:30 | 139 | 30.6 | 1160 | B | 78 | 104 | 118 | 40 | 1.7 | 4.5 | 21.3 | 72.5 | 19.57 | 1 | 1 | 1 | 445.58 | 253.5 | 253.5 | 306.13 | 240.36 | 421.45 | 414.45 | 372.08 | 0.3 | 30.26 | 66.12 | 27.4 |  |  | 36.28 |  | 707.01 | 12.59 | 0.51 | 0.93
13 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN003 | 1S-DL-YP-ETC-DKRN-2102-GAN003 | AMAR MOHALLA:PL | TG-GAN003A-1 | 19506101 | 990 | 320 | 234 | 0.98 | 1237 | 457 | 2015 | 378 | 1640 | 402 | 1740 | 336 | 2019-06-30 17:30 | 223 | 54.1 | 2015 | R | 116 | 93 | 91 | 25 | 0.1 | 7.3 | 83.9 | 8.7 |  |  |  |  | 8.3 | 54.18 | 54.18 | 29 | 411.25 | 541.23 | 504.22 | 499.33 | 205.14 | 101.39 | 110.11 | 167.48 | 74.03 | 1.52 | 2.51 | 2.51 | 699.12 | 20.48 | 0.52 | 1.25
14 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN008 | 1S-DL-YP-ETC-DKRN-2102-GAN008 | GALI GURDWARA NO. 2:ID | TG-GAN008A-3 | 19505541 | 400 | 120 | 244 | 0.99 | 393 | 142 | 599 | 101 | 427 | 149 | 640 | 196 | 2019-06-30 15:00 | 56.3 | -16.3 | 710 | B | 96 | 73 | 130 | 57 | 4 | 6.8 | 50.2 | 39 | 276 | 370.02 | 27 | 255 | 158.41 | 82.11 | 82.11 | 168.16 | 174.53 | 246.3 | 106.01 | 186.3 | 86.22 |  | 140.18 | 88.57 | 2.47 |  | 76.22 |  | 698.43 | 21.17 | 0.42 | 0.98
15 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN032 | 1S-DL-YP-ETC-DKRN-2102-GAN032 | SHIV KUTI R.L.G. NO. 1:ID | TG-GAN032A-4 | 19505384 | 990 | 320 | 242 | 0.97 | 1009 | 329 | 1389 | 375 | 1585 | 305 | 1291 | 259 | 2019-06-02 12:00 | 242.6 | 5.1 | 1585 | Y | 97 | 107 | 96 | 11 | 0.1 | 0.1 | 5.3 | 94.5 | 23.3 | 8.3 | 11 | 8 | 342.23 | 333.54 | 333.54 | 352.54 | 172.24 | 128.38 | 213.44 | 154.03 | 166.08 | 189.53 | 126.18 | 188.58 |  | 43.3 |  | 0.3 | 704.25 | 15.35 | 0.52 | 1.02
16 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GANDHI NAGAR | 1220 | GAN036 | 1S-DL-YP-ETC-DKRN-2102-GAN036 | KOTHI BHAGWAN DAS OUTSIDE:PL | TG-GAN036A-1 | 19506539 | 990 | 320 | 244 | 0.99 | 1099 | 397 | 1665 | 353 | 1501 | 349 | 1470 | 182 | 2019-06-02 16:00 | 207.7 | -2.6 | 1971 | B | 97 | 100 | 103 | 6 | 0.3 | 0.2 | 37.9 | 61.6 | 366.28 | 367.47 | 361.09 | 365.28 | 64.08 | 63.26 | 63.26 | 67.38 | 107.01 | 106.3 | 106.57 | 105.37 | 123.18 | 98.42 | 120.07 | 124.08 | 42.4 | 67.1 | 35.55 | 40.44 | 703.35 | 16.25 | 0.35 | 1.11
17 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL005 | 1S-DL-YP-ETC-DKRN-2103-GCL005 | JHEEL (BHOOSA MANDI):PL | TG-GCL005A-2 | 19505932 | 400 | 120 | 242 | 0.97 | 443 | 165 | 695 | 85 | 359 | 193 | 826 | 418 | 2019-06-12 00:30 | 99.6 | 14.6 | 896 | B | 104 | 69 | 127 | 58 | 0.2 | 3.9 | 79.3 | 16.6 |  | 15.3 |  |  | 193.38 | 371.26 | 371.26 | 195.59 | 382.45 | 320.55 | 394.01 | 412.52 | 93.58 | 0.3 | 121.51 | 79.3 | 38 |  | 109 | 20 | 708.21 | 11.39 | 0.51 | 1.11
18 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL015 | 1S-DL-YP-ETC-DKRN-2103-GCL015 | GEETA COLONY,12, BLK:K | TG-GCL015A-2 | 19506809 | 630 | 120 | 237 | 0.98 | 556 | 102 | 433 | 168 | 726 | 286 | 1238 | 705 | 2019-06-29 23:30 | 131.4 | 38.3 | 1238 | B | 78 | 101 | 121 | 43 | 0.5 | 0.6 | 30.9 | 68.1 | 0.3 |  |  |  | 262.27 | 59.59 | 59.59 | 37 | 444.54 | 607.52 | 547.21 | 654.21 | 1.3 | 41.3 | 127 | 18 |  |  | 31 |  | 709.21 | 10.39 | 0.63 | 0.88
19 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL019 | 1S-DL-YP-ETC-DKRN-2103-GCL019 | GEETA COLONY,17,BLK:PL | TG-GCL019A-1 | 19506130 | 990 | 320 | 230 | 0.98 | 1196 | 393 | 1666 | 439 | 1973 | 364 | 1635 | 323 | 2019-06-30 02:00 | 282.2 | 35.5 | 1973 | Y | 95 | 110 | 95 | 15 | 39.7 | 1.1 | 8.4 | 50.7 | 0.3 |  |  |  | 8.3 | 1.3 | 1.3 | 8.3 | 516.05 | 418.51 | 521.24 | 501.21 | 148.42 | 180.47 | 138.23 | 153.26 | 30.19 | 102.58 | 21.19 | 40.49 | 704.06 | 15.54 | 0.59 | 1.21
20 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | GAN026 | 1S-DL-YP-ETC-DKRN-2102-GAN026 | SATSANG MARG:PL | TG-GAN026A-2 | 19500966 | 630 | 200 | 239 | 0.97 | 669 | 231 | 1023 | 206 | 905 | 233 | 1026 | 120 | 2019-06-01 23:30 | 142.1 | 34.5 | 1118 | R | 107 | 100 | 93 | 14 |  |  | 40.4 | 59.6 |  |  | 18 |  | 124.27 | 129.28 | 129.28 | 147.57 | 479.06 | 509.37 | 382.39 | 476.38 | 74.22 | 74.46 | 86.08 | 78.38 | 39.18 | 3.22 | 11.3 | 14 | 717.13 | 2.47 | 0.52 | 1.06
21 | 2019-06-04 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | GAN027 | 1S-DL-YP-ETC-DKRN-2102-GAN027 | SEELAMPUR DOUBLE STORY:ID | TG-GAN027A-1 | 19505501 | 990 | 320 | 230 | 0.98 | 1179 | 384 | 1728 | 428 | 1927 | 367 | 1627 | 264 | 2019-06-30 15:30 | 237.1 | 32.3 | 1927 | Y | 103 | 112 | 85 | 27 | 0.2 | 5.6 | 92.1 | 2.1 |  |  | 0.3 |  | 58.32 | 49 | 49 | 117.26 | 373.46 | 360.48 | 211.34 | 319.52 | 164.52 | 119.52 | 110.58 | 158.4 | 15.08 | 82.38 | 1.08 | 16.2 | 612.18 | 35.42 | 0.5 | 1.19
22 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI045 | 1S-DL-YP-ETC-DKRN-2101-KRI045 | SHANKAR NAGAR MAIN ROAD SCHOOL NO 1:PL | TG-KRI045A-2 | 19506354 | 990 | 320 | 245 | 0.97 | 1018 | 335 | 1366 | 432 | 1765 | 251 | 1018 | 647 | 2019-06-01 01:00 | 223.7 | 71.4 | 1765 | Y | 99 | 124 | 77 | 47 | 0.3 |  | 2 | 97.8 |  |  |  |  | 18 |  |  | 11.3 | 655.51 | 485.09 | 525.15 | 659.05 | 30.28 | 175.22 |  | 34.44 | 1.45 | 45.33 |  | 0.45 | 706.04 | 13.56 | 0.59 | 1.03
23 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI053 | 1S-DL-YP-ETC-DKRN-2101-KRI053 | WEST AZAD NAGAR SHD ROAD B&D BL NO. 1:ID | TG-KRI053A-3 | 19505228 | 630 | 200 | 241 | 0.96 | 768 | 253 | 1090 | 258 | 1129 | 257 | 1123 | 36 | 2019-06-11 01:00 | 179.4 | 64 | 1281 | R | 107 | 97 | 96 | 11 | 0.3 | 0.1 | 49.4 | 50.3 |  |  |  |  | 3 | 6 | 6 | 5 | 452.01 | 522.52 | 520.22 | 506.52 | 161.51 | 136.45 | 138.3 | 142 | 89.25 | 40.4 | 37.55 | 52.25 | 706.17 | 13.43 | 0.58 | 1.22
24 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI004 | 1S-DL-YP-ETC-DKRN-2101-KRI004 | K-BLK KRN GHONOLI CHOWK:PL | TG-KRI004A-1 | 19500863 | 990 | 320 | 243 | 0.97 | 953 | 300 | 1254 | 351 | 1475 | 302 | 1265 | 216 | 2019-06-12 | 206.8 | 87.6 | 1552 | Y | 89 | 115 | 96 | 26 |  | 0.8 | 85.9 | 13.3 |  |  |  |  | 8 |  |  |  | 679.31 | 400.49 | 652.01 | 610.38 | 28.59 | 277.03 | 63.59 | 105.52 |  | 38.38 |  |  | 716.3 | 3.3 | 0.71 | 0.96
25 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KRISHNA NAGAR | 1220 | KRI038 | 1S-DL-YP-ETC-DKRN-2101-KRI038 | RADHA PURI NEW KRISHNA NAGAR:PL | TG-KRI038A-1 | 19506679 | 990 | 200 | 244 | 0.98 | 849 | 164 | 705 | 285 | 1228 | 399 | 1723 | 882 | 2019-06-30 23:30 | 131.8 | 30.8 | 1723 | B | 61 | 110 | 129 | 68 | 0.1 | 0.1 | 0.8 | 99 | 110.58 |  |  |  | 497.56 | 218.56 | 218.56 | 301.24 | 98.17 | 449.28 | 459.3 | 397.17 |  | 38.47 | 112.47 | 8.3 |  |  | 31 |  | 707.11 | 12.49 | 0.54 | 0.86