## Underload DTs
MIS Report of Distribution Transformer - Jun19
Jun19 1220 KRISHNA NAGAR (Underload DTs)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL008 | 1S-DL-YP-ETC-DKRN-2103-GCL008 | EKTA APARTMENTS:ID | TG-GCL008A-2 | 19501457 | 400 | 120 | 245 | 0.97 | 92 | 34 | 144 | 25 | 106 | 34 | 142 | 37 | 2019-06-29 23:30 | 22.4 | 1.7 | 160 | B | 93 | 90 | 116 | 26 |  |  | 48.1 | 51.9 | 677.27 | 713.27 | 566.57 | 678.27 | 42.3 | 6.3 | 6.3 | 41.3 | [12 empty] | 719.57 | 0.03 | 0.49 | 0.23
2 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL008 | 1S-DL-YP-ETC-DKRN-2103-GCL008 | EKTA APARTMENTS:ID | TG-GCL008A-1 | 19501458 | 400 | 120 | 246 | 0.97 | 67 | 31 | 124 | 24 | 101 | 12 | 48 | 67 | 2019-06-10 01:30 | 14.4 | 0.6 | 146 | R | 147 | 108 | 45 | 102 | 43.6 | 56.4 |  |  | 642.28 | 718.28 | 719.58 | 719.58 | 77.3 | 1.3 | 1.3 | [13 empty] | 719.58 | 0.02 | 0.49 | 0.17
3 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL010 | 1S-DL-YP-ETC-DKRN-2103-GCL010 | GEETA APPT.S/STAT.NO.1:ID | TG-GCL010A-1 | 19506508 | 400 | 120 | 246 | 0.93 | 89 | 38 | 160 | 21 | 89 | 29 | 122 | 61 | 2019-06-02 23:30 | 32.9 | 4 | 206 | Y | 108 | 83 | 109 | 26 | 0.2 | 0.1 | 18.2 | 81.5 | 666.58 | 692.58 | 676.58 | 692.58 | 29.3 | 3.3 | 3.3 | 3.3 | [12 empty] | 696.28 | 23.32 | 0.5 | 0.22
4 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL029 | 1S-DL-YP-ETC-DKRN-2103-GCL029 | KANCHAN APPT.:ID | TG-GCL029A-2 | 19506618 | 400 | 120 | 241 | 0.98 | 72 | 35 | 147 | 13 | 54 | 25 | 105 | 81 | 2019-06-05 23:30 | 10.7 | 0.7 | 163 | R | 146 | 54 | 100 | 92 |  |  | 5.2 | 94.8 | 595.28 | 710.28 | 706.28 | 710.28 | 115 | [15 empty] | 710.28 | 9.32 | 0.49 | 0.18
5 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL043 | 1S-DL-YP-ETC-DKRN-2103-GCL043 | TAJ SARTAJ, S/STAT, NO.1:ID | TG-GCL043A-1 | 19501583 | 630 | 200 | 246 | 0.98 | 122 | 34 | 141 | 42 | 173 | 46 | 190 | 43 | 2019-06-14 01:00 | 31.7 | 2.3 | 248 | B | 124 | 20 | 155 | 135 |  |  | 9.4 | 90.6 | 653.16 | 718.16 | 529.16 | 719.16 | 66 | 1 | 1 | [13 empty] | 719.16 | 0.44 | 0.56 | 0.19
6 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL045 | 1S-DL-YP-ETC-DKRN-2103-GCL045 | GEETA APT SS 2:ID | TG-GCL045A-2 | 19506380 | 400 | 120 | 247 | 0.98 | 88 | 22 | 91 | 33 | 141 | 33 | 139 | 49 | 2019-06-29 23:30 | 21.1 | 1.7 | 158 | Y | 63 | 117 | 120 | 57 | 0.1 |  | 32.2 | 67.7 | 719.56 | 672.26 | 655.26 | 713.56 |  | 47.3 | 47.3 | 6 | [12 empty] | 719.56 | 0.04 | 0.49 | 0.22
7 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL052 | 1S-DL-YP-ETC-DKRN-2103-GCL052 | SARWANGHI SOCIETY | TG-GCL052A-2 | 19504720 | 630 | 200 | 242 | 0.98 | 152 | 57 | 241 | 19 | 79 | 77 | 324 | 216 | 2019-06-29 23:30 | 24.8 | 2.3 | 324 | B | 121 | 37 | 142 | 105 |  | 0.1 | 86.9 | 13 | 541.1 | 719.4 | 480.4 | 671.4 | 178.3 |  |  | 48 | [12 empty] | 719.4 | 0.2 | 0.52 | 0.24
8 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI023 | 1S-DL-YP-ETC-DKRN-2101-KRI023 | JHEEL NO. 4 NO 1:ID | TG-KRI023A-1 | 19505187 | 630 | 200 | 242 | 0.98 | 143 | 11 | 45 | 12 | 50 | 119 | 497 | 450 | 2019-06-05 04:30 | 87.4 | 2.4 | 497 | B | 74 | 132 | 94 | 58 | 0.2 |  | 63.8 | 36 | 694.02 | 468.55 | 691.32 | 682.32 |  | 225.07 | 225.07 | 11.3 |  |  | 0.3 | [9 empty] | 694.02 | 25.58 | 0.48 | 0.23
9 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI032 | 1S-DL-YP-ETC-DKRN-2101-KRI032 | KRISHNA NAGAR POLICE STATION NO. 1:ID | TG-KRI032A-2 | 19501913 | 400 | 120 | 257 | 0.97 | 41 | 26 | 105 | 12 | 47 | 3 | 11 | 82 | 2019-06-02 23:00 | 10.8 | 0.8 | 105 | R | 191 | 93 | 16 | 175 |  | 0.1 | 73.7 | 26.2 | 718 | 718 | 718 | 718 | [16 empty] | 718 | 2 | 0.52 | 0.1
10 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | KANTI NAGAR | 1220 | KRI032 | 1S-DL-YP-ETC-DKRN-2101-KRI032 | KRISHNA NAGAR POLICE STATION NO. 1:ID | TG-KRI032A-1 | 19504522 | 400 | 120 | 243 | 0.98 | 62 | 9 | 37 | 32 | 137 | 21 | 90 | 87 | 2019-06-08 16:30 | 16.8 | -0.8 | 138 | Y | 33 | 153 | 114 | 120 |  |  | 55.6 | 44.4 | 718.02 | 668.32 | 718.02 | 718.02 |  | 49.3 | 49.3 | [13 empty] | 718.02 | 1.58 | 0.66 | 0.15