## Complete Report
MIS Report of Distribution Transformer - Jun19
Jun19 1220 KRISHNA NAGAR (Complete Report)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | KRISHNA NAGAR | GEETA COLONY | 1220 | GCL042 | 1S-DL-YP-ETC-DKRN-2103-GCL042 | SWARG ASHARM:PM | TG-GCL042A-1 | 19505737 | 100 | 40 | 243 | 0.76 | 78 | 20 | 82 | 31 | 130 | 27 | 112 | 42 | 2019-06-03 19:00 | 9.6 | -24 | 137 | Y | 70 | 135 | 95 | 65 | 0.4 | 0.6 | 34.1 | 64.9 | 394.54 | 385.25 | 384.54 | 384.55 | 166.3 | 20.3 | 20.3 | 37.29 | 144 | 134.29 | 286.3 | 283.3 | 0.3 | 165.3 | 2 | [5 empty] | 705.54 | 14.06 | 0.33 | 0.78