## Complete Report
MIS Report of Distribution Transformer - Jun19
Jun19 1230 LAXMI NAGAR (Complete Report)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | LGR073 | 1S-DL-YP-ETC-DLNR-2501-LGR073 | RISHABH IPEX MALL:ID | TG-LGR073A-1 | 19506541 | 400 | 120 | 240 | 0.97 | 88 | 15 | 67 | 31 | 133 | 42 | 181 | 100 | 2019-06-10 13:30 | 27.1 | 1.4 | 183 | B | 59 | 85 | 157 | 98 |  | 0.1 | 5.5 | 94.3 | 696.26 | 659.26 | 521.26 | 683.56 |  | 37 | 37 | 12.3 | [12 empty] | 696.26 | 23.34 | 0.33 | 0.22
2 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | LGR074 | 1S-DL-YP-ETC-DLNR-2501-LGR074 | CSC PANKAJ PLAZA:ID | TG-LGR074A-1 | 19502764 | 630 | 200 | 247 | 0.98 | 187 | 62 | 257 | 59 | 249 | 66 | 274 | 22 | 2019-06-11 13:00 | 40 | 3.2 | 283 | B | 85 | 111 | 104 | 26 |  |  | 8 | 92 | 552.28 | 498.28 | 488.28 | 503.28 | 143.3 | 197.3 | 197.3 | 192.3 | [12 empty] | 695.58 | 0.02 | 0.42 | 0.3
3 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | LGR075 | 1S-DL-YP-ETC-DLNR-2501-LGR075 | DP ANAND VIHAR:PM | TG-LGR075A-1 | 19505783 | 100 | 40 | 249 | 0.74 | 78 | 16 | 67 | 15 | 61 | 47 | 193 | 130 | 2019-06-21 23:00 | 63.3 | 0 | 193 | B | 107 | 100 | 93 | 14 |  | 0.2 | 41 | 58.8 | 410.25 | 410.25 | 409.55 | 410.25 |  | 52.3 | 52.3 | 19 | 298.27 | 244.27 | 107.3 | 279.27 |  | 1.3 | 0.3 |  |  |  | 0.3 |  | 708.52 | 11.08 | 0.26 | 0.78
4 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN001 | 1S-DL-YP-ETC-DLNR-2503-MAN001 | GAURAV APARTMENT, PPG:ID | TG-MAN001A-1 | 19504776 | 630 | 200 | 240 | 0.98 | 209 | 64 | 274 | 90 | 386 | 56 | 241 | 132 | 2019-06-30 00:30 | 42.8 | 6.9 | 420 | Y | 98 | 120 | 81 | 39 |  |  | 5.5 | 94.5 | 496.07 | 377.4 | 624.02 | 484.07 | 223.23 | 326.2 | 326.2 | 235.23 |  | 15.3 | [10 empty] | 719.3 | 0.3 | 0.53 | 0.33
5 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN001 | 1S-DL-YP-ETC-DLNR-2503-MAN001 | GAURAV APARTMENT, PPG:ID | TG-MAN001A-2 | 19504138 | 630 | 200 | 239 | 0.98 | 193 | 61 | 264 | 68 | 299 | 63 | 271 | 32 | 2019-06-09 23:30 | 40 | 3.7 | 343 | Y | 95 | 112 | 93 | 19 |  | 1 | 78.4 | 20.6 | 534.02 | 435.35 | 564.02 | 518.02 | 185.28 | 283.55 | 283.55 | 201.28 | [12 empty] | 719.3 | 0.3 | 0.54 | 0.31
6 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN022 | 1S-DL-YP-ETC-DLNR-2503-MAN022 | JOSHI COLONY:ID | TG-MAN022A-1 | 19501921 | 630 | 200 | 241 | 0.96 | 306 | 145 | 623 | 82 | 353 | 80 | 340 | 277 | 2019-06-11 23:30 | 83.7 | 31.7 | 627 | R | 129 | 93 | 78 | 51 |  |  | 2.2 | 97.8 |  | 4 | 69.27 | 1 | 269.01 | 694.02 | 694.02 | 594.18 | 449.31 | 20.3 | 1.3 | 123.14 | [8 empty] | 718.32 | 1.28 | 0.7 | 0.49
7 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN022 | 1S-DL-YP-ETC-DLNR-2503-MAN022 | JOSHI COLONY:ID | TG-MAN022A-2 | 19505405 | 990 | 320 | 241 | 0.97 | 900 | 316 | 1382 | 300 | 1324 | 285 | 1248 | 116 | 2019-06-29 23:00 | 249.9 | 68.8 | 1492 | Y | 110 | 99 | 92 | 18 | 0.1 | 0.1 | 16.9 | 82.9 |  |  |  |  | 16.42 | 138.08 | 138.08 | 64.42 | 618.42 | 521.46 | 556.12 | 607.42 | 59.3 | 35 | 4.3 | 22.3 |  |  |  |  | 694.54 | 25.06 | 0.61 | 0.91
8 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN028 | 1S-DL-YP-ETC-DLNR-2503-MAN028 | SFS GAZIPUR:ID | TG-MAN028A-1 | 19505327 | 990 | 320 | 253 | 0.98 | 138 | 45 | 181 | 34 | 137 | 60 | 244 | 93 | 2019-06-11 00:30 | 24.3 | 5.1 | 254 | B | 106 | 67 | 128 | 61 | 0.1 |  | 11 | 88.9 | 714.3 | 714.3 | 714.3 | 714.3 | [16 empty] | 714.3 | 5.3 | 0.52 | 0.14
9 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN028 | 1S-DL-YP-ETC-DLNR-2503-MAN028 | SFS GAZIPUR:ID | TG-MAN028A-2 | 19506204 | 630 | 200 | 253 | 0.96 | 139 | 48 | 196 | 29 | 120 | 62 | 250 | 113 | 2019-06-12 | 45.8 | 5.8 | 279 | B | 103 | 58 | 139 | 81 | 0.1 | 0.2 | 9 | 90.7 | 680.3 | 714.3 | 493.3 | 706 | 34 |  |  | 8.3 | [12 empty] | 714.3 | 5.3 | 0.55 | 0.22
10 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN041 | 1S-DL-YP-ETC-DLNR-2503-MAN041 | ST.LTG DP GAZIPUR:PM | TG-MAN041A-1 | 19506126 | 630 | 200 | 245 | 0.98 | 368 | 98 | 412 | 107 | 454 | 164 | 703 | 272 | 2019-06-08 14:30 | 136.6 | 20 | 703 | B | 84 | 102 | 114 | 30 |  | 2.5 | 75.6 | 21.8 |  |  |  |  | 653.3 | 340.3 | 340.3 | 383 | 61 | 374 | 550.3 | 331.3 | [8 empty] | 714.3 | 5.3 | 0.68 | 0.58
11 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN046 | 1S-DL-YP-ETC-DLNR-2503-MAN046 | TAJMAN SINGH:ID | TG-MAN046A-1 | 19500432 | 630 | 200 | 245 | 0.98 | 125 | 39 | 167 | 51 | 216 | 35 | 149 | 60 | 2019-06-02 22:30 | 28.5 | 5.1 | 217 | Y | 103 | 109 | 88 | 21 |  |  | 16.3 | 83.7 | 720 | 709.3 | 720 | 720 |  | 10.3 | 10.3 | [13 empty] | 720 | 0 | 0.52 | 0.2
12 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN046 | 1S-DL-YP-ETC-DLNR-2503-MAN046 | TAJMAN SINGH:ID | TG-MAN046A-2 | 19500435 | 630 | 200 | 248 | 0.97 | 116 | 45 | 184 | 23 | 94 | 48 | 196 | 96 | 2019-06-01 | 23.5 | 2.8 | 213 | B | 114 | 64 | 123 | 59 | 32.3 | 11.4 | 40.5 | 15.8 | 708.3 | 720 | 698 | 720 | 11.3 | [15 empty] | 720 | 0 | 0.53 | 0.18
13 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN049 | 1S-DL-YP-ETC-DLNR-2503-MAN049 | MADHU VIHAR S/STN-1:ID | TG-MAN049A-1 | 19506121 | 990 | 320 | 243 | 0.97 | 801 | 248 | 1042 | 267 | 1120 | 286 | 1209 | 145 | 2019-06-29 16:00 | 224 | 58.9 | 1325 | Y | 84 | 106 | 110 | 26 | 0.1 | 0.1 | 2 | 97.8 | 7.3 |  |  |  | 355.47 | 191 | 191 | 208 | 348.06 | 470.25 | 561.23 | 502.53 | 0.3 | 50.28 | 40 | 1 |  |  |  |  | 711.53 | 8.07 | 0.63 | 0.81
14 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN049 | 1S-DL-YP-ETC-DLNR-2503-MAN049 | MADHU VIHAR S/STN-1:ID | TG-MAN049A-2 | 19501135 | 990 | 320 | 242 | 0.97 | 917 | 324 | 1306 | 299 | 1205 | 294 | 1185 | 113 | 2019-06-12 17:00 | 223 | 72.9 | 1344 | R | 98 | 107 | 95 | 12 |  |  | 1.5 | 98.5 |  |  |  |  | 29.3 | 2 | 2 | 15 | 601.23 | 617.01 | 629.17 | 628.24 | 87.01 | 98.53 | 59.07 | 74.3 |  |  |  |  | 717.54 | 2.06 | 0.67 | 0.93
15 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN051 | 1S-DL-YP-ETC-DLNR-2503-MAN051 | MADHU VIHAR S/STN-II:ID | TG-MAN051A-1 | 19506511 | 990 | 320 | 237.6386 | 0.98267 | 1151.095 | 396.6482 | 1737.4753 | 370.0243 | 1627.1959 | 384.4224 | 1686.1373 | 95.5804 | 2019-06-22 12:00 | [15 empty] | 0 |  |  |  | 264 |  |  |  | 454 |  |  |  | 0 |  |  |  | 0.5 | 718.5 |  | 0.38672 | 1.1627
16 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN051 | 1S-DL-YP-ETC-DLNR-2503-MAN051 | MADHU VIHAR S/STN-II:ID | TG-MAN051A-2 | 19506124 | 630 | 200 | 238 | 0.99 | 431 | 186 | 827 | 139 | 605 | 106 | 456 | 324 | 2019-06-07 12:00 | 118 | -7.8 | 887 | R | 108 | 101 | 91 | 17 | 0.2 | 0.5 | 7.8 | 91.4 | 111.3 | 29.3 | 135 | 66.3 | 305.2 | 450.22 | 450.22 | 411.26 | 266.56 | 214.54 | 183.5 | 216.5 | 11 | [7 empty] | 694.46 | 25.14 | 0.51 | 0.68
17 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN052 | 1S-DL-YP-ETC-DLNR-2503-MAN052 | HASANPUR VILLAGE:PL | TG-MAN052A-1 | 19504543 | 990 | 320 | 244 | 0.99 | 847 | 280 | 1155 | 266 | 1089 | 300 | 1234 | 126 | 2019-06-11 15:00 | 127.3 | 22.1 | 1265 | B | 103 | 94 | 103 | 9 |  |  | 0.6 | 99.4 |  |  |  |  | 221.59 | 361.57 | 361.57 | 265.29 | 473.28 | 356.3 | 441.58 | 439.28 | 24.3 | 1.3 | 48 | 15 |  |  |  |  | 719.57 | 0.03 | 0.57 | 0.86
18 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN053 | 1S-DL-YP-ETC-DLNR-2503-MAN053 | GAZIPUR VILLAGE NEAR TEMPEL:PL | TG-MAN053A-1 | 19506444 | 990 | 320 | 250 | 0.97 | 876 | 295 | 1224 | 298 | 1230 | 282 | 1168 | 59 | 2019-06-27 22:30 | 224.6 | 97.9 | 1319 | Y | 100 | 106 | 94 | 12 | 0.4 |  | 5.2 | 94.4 | [8 empty] | 390.17 | 340.17 | 411.17 | 394.17 | 31 | 81 | 9.3 | 27 |  |  |  |  | 712.11 | 7.49 | 0.76 | 0.88
19 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN054 | 1S-DL-YP-ETC-DLNR-2503-MAN054 | GAZIPUR VILLAGE NEAR SCHOOL:PL | TG-MAN054A-1 | 19502869 | 990 | 320 | 249 | 0.97 | 991 | 371 | 1488 | 285 | 1232 | 336 | 1415 | 228 | 2019-06-13 15:00 | 295.9 | 70.7 | 1524 | R | 107 | 94 | 99 | 13 | 17.3 | 25.1 | 42.1 | 15.5 | [8 empty] | 289.27 | 598.36 | 446.1 | 430.51 | 393.27 | 117.18 | 268.14 | 284.33 | 33 |  | 1.3 | 0.3 | 715.54 | 4.06 | 0.77 | 1
20 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN054 | 1S-DL-YP-ETC-DLNR-2503-MAN054 | GAZIPUR VILLAGE NEAR SCHOOL:PL | TG-MAN054A-2 | 19505949 | 630 | 200 | 244 | 0.98 | 427 | 150 | 614 | 154 | 636 | 122 | 502 | 125 | 2019-06-29 20:30 | 103.6 | 22 | 695 | R | 112 | 114 | 74 | 40 |  | 0.2 | 23.2 | 76.6 |  |  |  |  | 1.3 | 2.3 | 2.3 | 12 | 711.26 | 710.26 | 232.36 | 700.56 | [8 empty] | 712.56 | 7.04 | 0.76 | 0.68
21 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN055 | 1S-DL-YP-ETC-DLNR-2503-MAN055 | GAZIPUR KIOSK:K | TG-MAN055A-1 | 19506792 | 400 | 120 | 248 | 0.98 | 311 | 93 | 377 | 127 | 515 | 91 | 372 | 140 | 2019-06-29 15:00 | 82.8 | 11.5 | 548 | R | 93 | 105 | 102 | 12 | 0.1 | 0.4 | 22.2 | 77.2 |  |  | 1.3 |  | 273.56 | 162.26 | 162.26 | 148.56 | 438.14 | 541.44 | 566.48 | 564.14 | 1 | 9 | 0.3 | [5 empty] | 713.1 | 6.5 | 0.62 | 0.78
22 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN056 | 1S-DL-YP-ETC-DLNR-2503-MAN056 | S/STN.NO-1, GAZIPUR:ID | TG-MAN056A-1 | 19506197 | 400 | 120 | 258 | 0.97 | 291 | 98 | 382 | 85 | 330 | 108 | 419 | 78 | 2019-06-21 03:00 | 84 | 13.1 | 423 | B | 90 | 95 | 115 | 25 |  | 0.1 | 5.8 | 94.1 | 1 | 1.3 |  |  | 471 | 345 | 345 | 304.3 | 220.02 | 346.02 | 572.44 | 388.02 | 0.3 |  | 0.48 | [5 empty] | 692.32 | 27.28 | 0.57 | 0.73
23 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN057 | 1S-DL-YP-ETC-DLNR-2503-MAN057 | S/STN.NO-2, GAZIPUR:ID | TG-MAN057A-1 | 19506839 | 400 | 120 | 257 | 0.86 | 37 | 12 | 43 | 0 | 0 | 26 | 98 | 85 | 2019-06-20 19:00 | 32.8 | 0.1 | 98 | B | 149 | 0 | 151 | 151 | 0.1 | 0.6 | 59.2 | 40.1 | 706.05 | 706.05 | 706.05 | 706.05 | [16 empty] | 706.05 | 13.55 | 0.3 | 0.09
24 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN058 | 1S-DL-YP-ETC-DLNR-2503-MAN058 | S/STN.NO-3, GAZIPUR:ID | TG-MAN058A-1 | 19501786 | 400 | 120 | 248 | 0.88 | 276 | 97 | 405 | 85 | 350 | 94 | 390 | 50 | 2019-06-12 21:00 | 163.1 | 0.3 | 424 | R | 109 | 96 | 94 | 15 |  |  | 89.3 | 10.7 | 298.54 | 441.21 | 443.21 | 436.51 | 166.27 | 37 | 37 | 29 | 134.05 | 121.05 | 128.05 | 133.35 | [8 empty] | 599.26 | 0.34 | 0.3 | 0.69
25 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN065 | 1S-DL-YP-ETC-DLNR-2503-MAN065 | S/STN.NO-8, PPG CGHS:ID | TG-MAN065A-1 | 19506154 | 400 | 120 | 246 | 0.98 | 49 | 18 | 73 | 24 | 93 | 7 | 30 | 56 | 2019-06-12 12:30 | 12 | 1.3 | 101 | R | 122 | 100 | 78 | 44 |  | 0.1 | 19.5 | 80.4 | 705.03 | 705.03 | 705.03 | 705.03 | [16 empty] | 705.03 | 14.57 | 0.66 | 0.12
26 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN066 | 1S-DL-YP-ETC-DLNR-2503-MAN066 | S/STN.NO-9, PPG CGHS:ID | TG-MAN066A-1 | 19500433 | 990 | 320 | 245 | 0.96 | 441 | 171 | 710 | 132 | 558 | 139 | 579 | 143 | 2019-06-30 23:00 | 104.5 | 14.7 | 739 | R | 116 | 89 | 94 | 27 |  | 21.4 | 67.5 | 11.1 | 70.3 | 317.06 | 284.25 | 217.25 | 569.03 | 401.27 | 401.27 | 487.08 | 79.3 | 0.3 | 3.3 | 14.3 | [8 empty] | 719.03 | 0.57 | 0.56 | 0.45
27 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN066 | 1S-DL-YP-ETC-DLNR-2503-MAN066 | S/STN.NO-9, PPG CGHS:ID | TG-MAN066A-2 | 19506561 | 630 | 200 | 244 | 0.96 | 791 | 245 | 1039 | 259 | 1103 | 288 | 1219 | 158 | 2019-06-30 23:30 | 220.6 | 51.8 | 1219 | B | 93 | 103 | 103 | 10 | 0.1 | 0.2 | 5.8 | 93.8 |  |  |  |  | 20 | 2 | 2 | 6.3 | 520 | 480.29 | 467 | 502 | 147.26 | 170.57 | 147.56 | 149.56 | 26.3 | 60.3 | 91.3 | 55.3 | 713.56 | 6.04 | 0.57 | 1.26
28 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN067 | 1S-DL-YP-ETC-DLNR-2503-MAN067 | S/STN.NO-11, PPG CGHS:ID | TG-MAN067A-1 | 19504570 | 400 | 120 | 239 | 0.95 | 196 | 72 | 306 | 61 | 260 | 63 | 268 | 43 | 2019-06-21 17:00 | 67.9 | 8.3 | 334 | R | 138 | 72 | 90 | 66 |  | 0.1 | 75.7 | 24.2 | 282.58 | 574.28 | 454.28 | 368.28 | 324 | 144 | 144 | 333.3 | 113 | 1.3 | 9.3 | 18 | [8 empty] | 719.58 | 0.02 | 0.39 | 0.49
29 | 2019-06-17 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN068 | 1S-DL-YP-ETC-DLNR-2503-MAN068 | S/STN.NO-13, PPG CGHS:ID | TG-MAN068A-1 | 19502466 | 400 | 120 | 236 | 0.97 | 312 | 92 | 408 | 128 | 568 | 91 | 403 | 162 | 2019-06-30 23:00 | 67.3 | 27.9 | 578 | Y | 88 | 120 | 93 | 32 |  |  |  | 100 |  |  |  |  | 46 | 7.3 | 7.3 | 15.3 | 290 | 262.3 | 306 | 320.3 |  | 66 | [6 empty] | 336 | 0 | 0.71 | 0.78
30 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN069 | 1S-DL-YP-ETC-DLNR-2503-MAN069 | S/STN.NO-14, PPG CGHS:ID | TG-MAN069A-1 | 19506149 | 400 | 120 | 246 | 0.98 | 160 | 30 | 125 | 68 | 287 | 62 | 262 | 152 | 2019-06-07 12:00 | 50.8 | -0.8 | 287 | Y | 75 | 94 | 131 | 56 | 0.1 | 0.1 | 1.6 | 98.2 | 603.58 | 520.58 | 375.58 | 470.28 | 116 | 198.3 | 198.3 | 249.3 |  | 0.3 | 26 | [9 empty] | 719.58 | 0.02 | 0.41 | 0.4
31 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN070 | 1S-DL-YP-ETC-DLNR-2503-MAN070 | S/STN.NO-15, PPG CGHS:ID | TG-MAN070A-1 | 19501207 | 400 | 120 | 240 | 0.91 | 94 | 24 | 99 | 42 | 175 | 28 | 118 | 68 | 2019-06-03 13:00 | 36.7 | -0.3 | 176 | Y | 88 | 125 | 87 | 38 |  |  | 12.5 | 87.5 | 694.58 | 606.28 | 708.28 | 676.58 | 25 | 113.3 | 113.3 | 43 | [12 empty] | 719.58 | 0.02 | 0.36 | 0.24
32 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN071 | 1S-DL-YP-ETC-DLNR-2503-MAN071 | S/STN.NO-16, PPG CGHS:ID | TG-MAN071A-1 | 19500772 | 400 | 120 | 240.5239 | 0.93045 | 83.5683 | 37.9889 | 155.673 | 16.5692 | 69.5367 | 29.0102 | 122.6959 | 75.2757 | 2019-06-02 13:00 | [15 empty] | 718 |  |  |  | 2 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.25012 | 0.20892
33 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN072 | 1S-DL-YP-ETC-DLNR-2503-MAN072 | S/STN.NO-19, PPG CGHS:ID | TG-MAN072A-1 | 19500775 | 400 | 120 | 238 | 0.88 | 19 | 9 | 40 | 5 | 22 | 4 | 18 | 20 | 2019-06-10 19:30 | 8.6 | -1.7 | 40 | R | 133 | 75 | 91 | 58 |  |  | 0.2 | 99.8 | 647.31 | 647.31 | 647.31 | 647.31 | [16 empty] | 647.31 | 0.29 | 0.51 | 0.05
34 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN073 | 1S-DL-YP-ETC-DLNR-2503-MAN073 | MAY FAIR CGHS, PPG.:ID | TG-MAN073A-1 | 19505986 | 400 | 120 | 246 | 0.98 | 97 | 19 | 83 | 36 | 156 | 41 | 177 | 86 | 2019-06-05 23:30 | 27 | 2.6 | 186 | Y | 55 | 122 | 123 | 68 | 0.2 |  | 0.3 | 99.4 | 714.58 | 552.28 | 566.28 | 664.58 |  | 162.3 | 162.3 | 50 | [12 empty] | 714.58 | 5.02 | 0.51 | 0.24
35 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN073 | 1S-DL-YP-ETC-DLNR-2503-MAN073 | MAY FAIR CGHS, PPG.:ID | TG-MAN073A-2 | 19501329 | 400 | 120 | 245 | 0.98 | 102 | 35 | 146 | 36 | 152 | 32 | 132 | 18 | 2019-06-03 23:00 | 19.6 | 0.8 | 165 | R | 91 | 104 | 104 | 13 |  | 0.1 | 19.1 | 80.8 | 658.58 | 631.58 | 582 | 629.58 | 61 | 88 | 88 | 90 | [12 empty] | 719.58 | 0.02 | 0.52 | 0.26
36 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN074 | 1S-DL-YP-ETC-DLNR-2503-MAN074 | NAVKRANTI CGHS, PPG:ID | TG-MAN074A-1 | 19501208 | 400 | 120 | 245 | 0.97 | 137 | 47 | 196 | 53 | 226 | 37 | 154 | 63 | 2019-06-11 23:00 | 29 | 4.4 | 249 | Y | 90 | 113 | 97 | 23 | 0.3 | 40 | 55.3 | 4.3 | 547 | 386 | 534 | 520.3 | 172.58 | 327.58 | 327.58 | 199.28 |  | 6 | 1 | [9 empty] | 719.58 | 0.02 | 0.5 | 0.34
37 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN075 | 1S-DL-YP-ETC-DLNR-2503-MAN075 | VI-KALP CGHS, PPG:ID | TG-MAN075A-1 | 19501295 | 400 | 120 | 240 | 0.98 | 107 | 44 | 189 | 34 | 145 | 29 | 121 | 60 | 2019-06-11 00:30 | 17.1 | 2.2 | 193 | R | 127 | 105 | 69 | 58 |  |  | 67.6 | 32.4 | 555.58 | 587.58 | 712.28 | 643.28 | 164 | 132 | 132 | 76.3 | [12 empty] | 719.58 | 0.02 | 0.46 | 0.27
38 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN075 | 1S-DL-YP-ETC-DLNR-2503-MAN075 | VI-KALP CGHS, PPG:ID | TG-MAN075A-2 | 19506577 | 400 | 120 | 241 | 0.98 | 133 | 33 | 145 | 61 | 264 | 39 | 168 | 109 | 2019-06-29 23:00 | 24.1 | 3.4 | 264 | Y | 77 | 134 | 89 | 57 |  | 0.1 | 1.9 | 98.1 | 637.58 | 357 | 577.3 | 513 | 58.3 | 327.58 | 327.58 | 183.28 |  | 11.3 | [10 empty] | 696.28 | 23.32 | 0.48 | 0.33
39 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN076 | 1S-DL-YP-ETC-DLNR-2503-MAN076 | TRILOKYA CGHS, PPG:ID | TG-MAN076A-1 | 19501330 | 630 | 200 | 239 | 0.97 | 264 | 76 | 318 | 94 | 404 | 94 | 405 | 86 | 2019-06-03 | 46.9 | 10.6 | 437 | B | 87 | 109 | 104 | 22 | 40.4 | 56.5 | 2.6 | 0.5 | 398 | 225 | 325.3 | 312 | 321.58 | 478.58 | 478.58 | 406.28 |  | 16 | 25 | 1.3 | [8 empty] | 719.58 | 0.02 | 0.54 | 0.42
40 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN077 | 1S-DL-YP-ETC-DLNR-2503-MAN077 | PARSHWA NATH CGHS, PPG:ID | TG-MAN077A-1 | 19505524 | 400 | 120 | 239 | 0.98 | 267 | 93 | 433 | 77 | 355 | 97 | 445 | 85 | 2019-06-07 23:00 | 41.4 | 9.2 | 445 | B | 93 | 102 | 106 | 13 | 0.1 | 0.1 | 2.4 | 97.3 | 257.09 | 125 | 166.11 | 155.11 | 388.43 | 530.37 | 530.37 | 472.55 | 70.5 | 61.05 | 140.32 | 88.36 | [8 empty] | 716.42 | 3.18 | 0.41 | 0.67
41 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN077 | 1S-DL-YP-ETC-DLNR-2503-MAN077 | PARSHWA NATH CGHS, PPG:ID | TG-MAN077A-2 | 19505416 | 400 | 120 | 245 | 0.98 | 133 | 23 | 95 | 56 | 234 | 54 | 222 | 134 | 2019-06-13 22:00 | 28.9 | 4.3 | 234 | Y | 97 | 111 | 92 | 19 | 29.2 | 28.6 | 39.3 | 2.9 | 404.09 | 312.41 | 418.51 | 386.11 | 151.3 | 241.58 | 241.58 | 169.28 |  | 1 | 3 | [9 empty] | 715.49 | 4.11 | 0.53 | 0.33
42 | 2019-06-08 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN078 | 1S-DL-YP-ETC-DLNR-2503-MAN078 | NEELKANTH CGHS, PPG:ID | TG-MAN078A-1 | 19506184 | 630 | 200 | 247 | 0.98 | 111 | 25 | 104 | 52 | 221 | 34 | 143 | 103 | 2019-06-27 | 19 | 1.6 | 241 | Y | 65 | 136 | 99 | 71 | 0.1 |  | 14 | 85.9 | 551.58 | 508 | 551.58 | 551.58 |  | 43.58 | 43.58 | [13 empty] | 551.58 | 0.02 | 0.5 | 0.18
43 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN078 | 1S-DL-YP-ETC-DLNR-2503-MAN078 | NEELKANTH CGHS, PPG:ID | TG-MAN078A-2 | 19502541 | 630 | 200 | 246 | 0.98 | 134 | 57 | 231 | 24 | 101 | 52 | 221 | 125 | 2019-06-09 23:30 | 26.2 | 3.7 | 276 | R | 139 | 68 | 93 | 71 | 100 |  |  |  | 552 | 719.59 | 699.29 | 713.59 | 167.59 |  |  | 6 | [12 empty] | 719.59 | 0.01 | 0.52 | 0.21
44 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN079 | 1S-DL-YP-ETC-DLNR-2503-MAN079 | ANAMIKA CGHS,PPG:ID | TG-MAN079A-1 | 19501142 | 400 | 120 | 246 | 0.98 | 41 | 9 | 37 | 22 | 90 | 11 | 43 | 50 | 2019-06-12 | 8 | 0.6 | 90 | Y | 86 | 131 | 83 | 48 |  |  | 4.9 | 95.1 | 719.58 | 719.58 | 719.58 | 719.58 | [16 empty] | 719.58 | 0.02 | 0.47 | 0.1
45 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN079 | 1S-DL-YP-ETC-DLNR-2503-MAN079 | ANAMIKA CGHS,PPG:ID | TG-MAN079A-2 | 19505402 | 400 | 120 | 241 | 0.98 | 81 | 25 | 110 | 10 | 44 | 45 | 195 | 131 | 2019-06-29 23:00 | 16 | 1.3 | 195 | B | 91 | 52 | 157 | 105 | 0.1 | 3.6 | 79.8 | 16.5 | 707.28 | 707.28 | 534 | 706.58 |  |  |  | 0.3 | [12 empty] | 707.28 | 12.32 | 0.5 | 0.2
46 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN080 | 1S-DL-YP-ETC-DLNR-2503-MAN080 | FRIENDS CGHS, PPG:ID | TG-MAN080A-1 | 19506122 | 630 | 200 | 240 | 0.98 | 148 | 37 | 154 | 61 | 253 | 51 | 212 | 87 | 2019-06-16 00:30 | 30.2 | 4.2 | 265 | B | 88 | 105 | 108 | 20 | 0.1 |  | 1.6 | 98.3 | 717.28 | 678 | 617 | 693.28 | 2.3 | 41.58 | 41.58 | 26.3 | [12 empty] | 719.58 | 0.02 | 0.52 | 0.23
47 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN080 | 1S-DL-YP-ETC-DLNR-2503-MAN080 | FRIENDS CGHS, PPG:ID | TG-MAN080A-2 | 19506484 | 630 | 200 | 240 | 0.97 | 142 | 71 | 309 | 32 | 139 | 39 | 172 | 156 | 2019-06-10 23:00 | 30.8 | 6.2 | 309 | R | 136 | 75 | 89 | 61 |  |  | 8.2 | 91.8 | 479.58 | 719.58 | 698.28 | 699.28 | 240 |  |  | 20.3 | [12 empty] | 719.58 | 0.02 | 0.58 | 0.23
48 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN081 | 1S-DL-YP-ETC-DLNR-2503-MAN081 | VIDYUT CGHS,PPG :ID | TG-MAN081A-1 | 19501153 | 400 | 120 | 230 | 0.98 | 75 | 17 | 74 | 44 | 193 | 14 | 63 | 125 | 2019-06-09 23:30 | 13.5 | 0.8 | 210 | Y | 72 | 175 | 53 | 122 | 57.7 | 13.8 | 17.9 | 10.6 | 719.58 | 476.3 | 719.58 | 719.58 |  | 243.28 | 243.28 | [13 empty] | 719.58 | 0.02 | 0.54 | 0.19
49 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN081 | 1S-DL-YP-ETC-DLNR-2503-MAN081 | VIDYUT CGHS,PPG :ID | TG-MAN081A-2 | 19501188 | 400 | 120 | 239 | 0.98 | 60 | 17 | 74 | 30 | 132 | 13 | 57 | 69 | 2019-06-05 | 11.6 | 0.3 | 134 | Y | 70 | 149 | 81 | 79 | 49.4 | 44.7 | 4.4 | 1.4 | 719.58 | 711.28 | 719.58 | 719.58 |  | 8.3 | 8.3 | [13 empty] | 719.58 | 0.02 | 0.45 | 0.15
50 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN082 | 1S-DL-YP-ETC-DLNR-2503-MAN082 | VIDISHA CGHS, PPG:ID | TG-MAN082A-1 | 19501155 | 400 | 120 | 239 | 0.98 | 170 | 60 | 264 | 55 | 238 | 55 | 240 | 25 | 2019-06-29 23:30 | 29.5 | 5.2 | 274 | R | 99 | 102 | 100 | 3 |  |  | 15.8 | 84.2 | 344 | 304.3 | 317 | 309.3 | 356.28 | 400.28 | 400.28 | 404.28 | 19.3 | 15 | 7.3 | 6 | [8 empty] | 719.58 | 0.02 | 0.53 | 0.42
51 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN083 | 1S-DL-YP-ETC-DLNR-2503-MAN083 | RAMA KRISHNA CGHS, PPG, S/STN-1:ID | TG-MAN083A-1 | 19501878 | 630 | 200 | 245 | 0.97 | 189 | 47 | 194 | 68 | 281 | 74 | 301 | 99 | 2019-06-09 | 32.2 | 6.4 | 341 | B | 82 | 96 | 122 | 40 |  |  | 21.9 | 78.1 | 654.58 | 568.3 | 448.3 | 556 | 65 | 151.28 | 151.28 | 163.58 | [12 empty] | 719.58 | 0.02 | 0.51 | 0.3
52 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN083 | 1S-DL-YP-ETC-DLNR-2503-MAN083 | RAMA KRISHNA CGHS, PPG, S/STN-1:ID | TG-MAN083A-2 | 19505980 | 630 | 200 | 246 | 0.96 | 213 | 54 | 213 | 87 | 361 | 73 | 302 | 129 | 2019-06-12 00:30 | 46.6 | 10.4 | 413 | Y | 73 | 128 | 99 | 55 | 95.8 |  | 0.6 | 3.5 | 639.58 | 291.3 | 461 | 467.3 | 80 | 418.28 | 418.28 | 252.28 |  | 10 | [10 empty] | 719.58 | 0.02 | 0.54 | 0.34
53 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN084 | 1S-DL-YP-ETC-DLNR-2503-MAN084 | RAMA KRISHNA CGHS, PPG, S/STN-2:ID | TG-MAN084A-1 | 19505396 | 630 | 200 | 240 | 0.97 | 180 | 31 | 136 | 75 | 324 | 74 | 321 | 187 | 2019-06-30 | 34.6 | 7.4 | 350 | B | 51 | 121 | 128 | 77 |  | 0.1 | 0.2 | 99.7 | 707.45 | 472.59 | 454.29 | 591.59 |  | 234.46 | 234.46 | 115.46 | [12 empty] | 707.45 | 12.15 | 0.5 | 0.29
54 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN084 | 1S-DL-YP-ETC-DLNR-2503-MAN084 | RAMA KRISHNA CGHS, PPG, S/STN-2:ID | TG-MAN084A-2 | 19501877 | 630 | 200 | 246 | 0.97 | 139 | 35 | 147 | 40 | 167 | 64 | 269 | 114 | 2019-06-10 23:30 | 32.7 | 5.1 | 278 | B | 82 | 84 | 134 | 52 | 0.2 | 10.6 | 88 | 1.1 | 719.17 | 718.17 | 597.47 | 708.47 |  | 1 | 1 | 10.3 | [12 empty] | 719.17 | 0.43 | 0.51 | 0.22
55 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN085 | 1S-DL-YP-ETC-DLNR-2503-MAN085 | SAHYADRI CGHS, PPG:ID | TG-MAN085A-1 | 19501452 | 400 | 120 | 245 | 0.97 | 64 | 12 | 53 | 27 | 116 | 24 | 101 | 57 | 2019-06-30 23:00 | 9.9 | 0.8 | 124 | Y | 76 | 122 | 102 | 46 |  |  | 2.8 | 97.2 | 719.57 | 717.57 | 719.57 | 719.57 |  | 2 | 2 | [13 empty] | 719.57 | 0.03 | 0.39 | 0.16
56 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN085 | 1S-DL-YP-ETC-DLNR-2503-MAN085 | SAHYADRI CGHS, PPG:ID | TG-MAN085A-2 | 19501455 | 400 | 120 | 245 | 0.96 | 69 | 28 | 120 | 22 | 90 | 18 | 78 | 38 | 2019-06-09 22:30 | 18.8 | 1.4 | 130 | R | 98 | 107 | 95 | 12 |  |  | 10.3 | 89.7 | 718.27 | 718.57 | 719.57 | 719.57 | 1.3 | 1 | 1 | [13 empty] | 719.57 | 0.03 | 0.51 | 0.17
57 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN086 | 1S-DL-YP-ETC-DLNR-2503-MAN086 | PHARMA CGHS, PPG S/STN-1:ID | TG-MAN086A-1 | 19501294 | 400 | 120 | 239 | 0.98 | 80 | 37 | 158 | 21 | 90 | 22 | 92 | 67 | 2019-06-29 | 17.9 | 0.6 | 159 | R | 141 | 78 | 81 | 63 |  |  | 2.9 | 97.1 | 583.26 | 719.56 | 719.56 | 719.56 | 136.3 | [15 empty] | 719.56 | 0.04 | 0.55 | 0.2
58 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN086 | 1S-DL-YP-ETC-DLNR-2503-MAN086 | PHARMA CGHS, PPG S/STN-1:ID | TG-MAN086A-2 | 19501154 | 400 | 120 | 245 | 0.98 | 119 | 62 | 256 | 32 | 130 | 25 | 101 | 143 | 2019-06-11 23:30 | 20.1 | 3.3 | 274 | R | 159 | 62 | 79 | 97 |  |  | 16.4 | 83.6 | 196 | 691.29 | 664.27 | 586.29 | 510.57 | 28.28 | 28.28 | 133.28 | 13 | [11 empty] | 719.57 | 0.03 | 0.53 | 0.3
59 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN087 | 1S-DL-YP-ETC-DLNR-2503-MAN087 | PHARMA CGHS, PPG S/STN-2:ID | TG-MAN087A-1 | 19501266 | 630 | 200 | 244 | 0.98 | 210 | 63 | 255 | 81 | 330 | 67 | 274 | 68 | 2019-06-11 23:30 | 37.3 | 6 | 330 | Y | 87 | 111 | 102 | 24 |  |  | 4.5 | 95.5 | 588.59 | 446.29 | 495.29 | 524.29 | 130.57 | 273.27 | 273.27 | 195.27 | [12 empty] | 719.56 | 0.04 | 0.5 | 0.33
60 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN087 | 1S-DL-YP-ETC-DLNR-2503-MAN087 | PHARMA CGHS, PPG S/STN-2:ID | TG-MAN087A-2 | 19505520 | 630 | 200 | 238 | 0.98 | 180 | 58 | 255 | 72 | 314 | 50 | 220 | 82 | 2019-06-11 | 44.6 | 6 | 320 | Y | 102 | 108 | 90 | 18 | 0.1 |  | 2 | 97.9 | 577.29 | 527.56 | 658.26 | 593.26 | 136.27 | 186 | 186 | 120.3 | [12 empty] | 713.56 | 6.04 | 0.53 | 0.29
61 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN088 | 1S-DL-YP-ETC-DLNR-2503-MAN088 | PHARMA CGHS, PPG S/STN-3:ID | TG-MAN088A-1 | 19501206 | 400 | 120 | 240 | 0.99 | 113 | 51 | 208 | 32 | 132 | 30 | 121 | 82 | 2019-06-13 22:30 | 10.5 | -1.1 | 213 | R | 113 | 96 | 91 | 22 |  |  | 3.1 | 96.9 | 551.29 | 688.26 | 666.56 | 646.29 | 168.27 | 31.3 | 31.3 | 73.27 | [12 empty] | 719.56 | 0.04 | 0.48 | 0.28
62 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN088 | 1S-DL-YP-ETC-DLNR-2503-MAN088 | PHARMA CGHS, PPG S/STN-3:ID | TG-MAN088A-2 | 19501209 | 400 | 120 | 239 | 0.98 | 94 | 35 | 147 | 41 | 173 | 19 | 80 | 84 | 2019-06-01 | 16.8 | 2.5 | 191 | Y | 110 | 128 | 62 | 66 |  |  | 11.5 | 88.5 | 614.29 | 549.59 | 719.56 | 679.26 | 105.27 | 169.57 | 169.57 | 40.3 | [12 empty] | 719.56 | 0.04 | 0.52 | 0.24
63 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN089 | 1S-DL-YP-ETC-DLNR-2503-MAN089 | RAJDHANI NI-KUNJ CGHS PPG:ID | TG-MAN089A-1 | 19501112 | 400 | 120 | 246 | 0.95 | 107 | 52 | 217 | 28 | 117 | 27 | 111 | 103 | 2019-06-02 | 28.4 | 3.3 | 229 | R | 129 | 81 | 90 | 48 |  |  | 7.2 | 92.8 | 442 | 679.28 | 699.58 | 625.58 | 277.28 | 40.3 | 40.3 | 94 | 0.3 | [11 empty] | 719.58 | 0.02 | 0.56 | 0.27
64 | 2019-06-19 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN089 | 1S-DL-YP-ETC-DLNR-2503-MAN089 | RAJDHANI NI-KUNJ CGHS PPG:ID | TG-MAN089A-2 | 19506924 | 400 | 120 | 246 | 0.99 | 38 | 16 | 66 | 10 | 42 | 13 | 55 | 21 | 2019-06-30 23:30 | 10.9 | 0.1 | 71 | Y | 86 | 69 | 145 | 76 |  |  | 0.4 | 99.6 | 264 | 264 | 264 | 264 | [16 empty] | 264 | 24 | 0.59 | 0.1
65 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN090 | 1S-DL-YP-ETC-DLNR-2503-MAN090 | RAJDHANI NI-KUNJ CGHS PPG S/STN-2:ID | TG-MAN090A-1 | 19501115 | 400 | 120 | 245 | 0.97 | 166 | 49 | 204 | 87 | 366 | 30 | 123 | 214 | 2019-06-11 23:30 | 29.8 | 6.6 | 393 | Y | 94 | 142 | 64 | 78 | 45.2 | 54.8 |  |  | 463.3 | 188 | 662.28 | 419.3 | 251.23 | 417.3 | 417.3 | 297.52 | 3.59 | 113.22 |  | 1.3 | [8 empty] | 718.52 | 1.08 | 0.48 | 0.41
66 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN090 | 1S-DL-YP-ETC-DLNR-2503-MAN090 | RAJDHANI NI-KUNJ CGHS PPG S/STN-2:ID | TG-MAN090A-2 | 19501114 | 400 | 120 | 239 | 0.98 | 153 | 56 | 233 | 45 | 190 | 52 | 219 | 38 | 2019-06-16 01:00 | 25.9 | 5 | 277 | B | 110 | 87 | 103 | 23 |  |  | 0.4 | 99.6 | 355.3 | 488.3 | 416 | 436 | 362.28 | 231.28 | 231.28 | 283.58 | 2 |  | 6.3 | [9 empty] | 719.58 | 0.02 | 0.5 | 0.38
67 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN091 | 1S-DL-YP-ETC-DLNR-2503-MAN091 | NARWANA CGHS,PPG S/STN-1:ID | TG-MAN091A-1 | 19501225 | 630 | 200 | 244 | 0.97 | 142 | 37 | 154 | 47 | 196 | 57 | 236 | 71 | 2019-06-01 00:30 | 32.7 | 3.2 | 261 | B | 86 | 98 | 116 | 30 |  |  | 2.1 | 97.9 | 719.26 | 703.26 | 583.29 | 692.26 | 0.3 | 16.3 | 16.3 | 27.3 | [12 empty] | 719.56 | 0.04 | 0.55 | 0.22
68 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN091 | 1S-DL-YP-ETC-DLNR-2503-MAN091 | NARWANA CGHS,PPG S/STN-1:ID | TG-MAN091A-2 | 19501223 | 630 | 200 | 244 | 0.97 | 204 | 84 | 350 | 89 | 367 | 31 | 128 | 231 | 2019-06-02 | 46 | 4.6 | 415 | Y | 118 | 134 | 48 | 86 |  |  | 0.1 | 99.9 | 409.29 | 273.29 | 719.56 | 506.59 | 306.27 | 438.27 | 438.27 | 212.57 | 4 | 8 | [10 empty] | 719.56 | 0.04 | 0.53 | 0.32
69 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN092 | 1S-DL-YP-ETC-DLNR-2503-MAN092 | NARWANA CGHS,PPG S/STN-2:ID | TG-MAN092A-1 | 19501222 | 630 | 200 | 240 | 0.97 | 133 | 50 | 205 | 52 | 219 | 32 | 137 | 75 | 2019-06-11 23:30 | 30.8 | 6 | 242 | Y | 117 | 102 | 81 | 36 | 97.8 | 2.2 |  |  | 648.56 | 681.26 | 719.56 | 711.56 | 71 | 38.3 | 38.3 | 8 | [12 empty] | 719.56 | 0.04 | 0.58 | 0.21
70 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN092 | 1S-DL-YP-ETC-DLNR-2503-MAN092 | NARWANA CGHS,PPG S/STN-2:ID | TG-MAN092A-2 | 19505422 | 630 | 200 | 238 | 0.98 | 166 | 62 | 260 | 21 | 89 | 82 | 347 | 227 | 2019-06-12 | 28.8 | 4.2 | 347 | B | 116 | 42 | 141 | 99 | 0.1 | 0.1 | 14.3 | 85.5 | 549.29 | 719.56 | 436.59 | 638.59 | 170.27 |  |  | 80.57 | [12 empty] | 719.56 | 0.04 | 0.51 | 0.26
71 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN093 | 1S-DL-YP-ETC-DLNR-2503-MAN093 | ASHIRWAD CGHS,PPG S/STN-1:ID | TG-MAN093A-1 | 19506520 | 400 | 120 | 239 | 0.98 | 243 | 62 | 260 | 84 | 355 | 98 | 413 | 134 | 2019-06-02 23:30 | 42 | 5.9 | 413 | B | 69 | 114 | 116 | 47 | 0.1 |  | 12.7 | 87.2 | 424.29 | 73 | 123.3 | 173 | 262.27 | 460.29 | 460.29 | 396.59 | 27.3 | 180.57 | 220.27 | 144.27 | [8 empty] | 714.26 | 5.34 | 0.47 | 0.61
72 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN094 | 1S-DL-YP-ETC-DLNR-2503-MAN094 | ASHIRWAD CGHS,PPG S/STN-2:ID | TG-MAN094A-1 | 19501270 | 630 | 200 | 244 | 0.96 | 153 | 51 | 214 | 29 | 124 | 73 | 308 | 160 | 2019-06-11 00:30 | 48.3 | 5.5 | 329 | B | 92 | 60 | 149 | 89 |  |  | 4.8 | 95.2 | 686.44 | 719.44 | 327.53 | 642.17 | 33 |  |  | 77.27 | [12 empty] | 719.44 | 0.16 | 0.6 | 0.24
73 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN094 | 1S-DL-YP-ETC-DLNR-2503-MAN094 | ASHIRWAD CGHS,PPG S/STN-2:ID | TG-MAN094A-2 | 19502811 | 630 | 200 | 242 | 0.98 | 173 | 45 | 189 | 67 | 275 | 60 | 249 | 77 | 2019-06-12 | 33.6 | 4.1 | 303 | Y | 79 | 125 | 96 | 46 | 4.2 | 12.2 | 23.4 | 60.3 | 691.15 | 503.18 | 619.45 | 621.15 | 28.3 | 216.27 | 216.27 | 98.3 | [12 empty] | 719.45 | 0.15 | 0.49 | 0.27
74 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN095 | 1S-DL-YP-ETC-DLNR-2503-MAN095 | NATRAJ CGHS, PPG:ID | TG-MAN095A-1 | 19505401 | 400 | 120 | 246 | 0.97 | 75 | 24 | 101 | 29 | 123 | 21 | 88 | 30 | 2019-06-05 00:30 | 17.2 | 1.6 | 127 | R | 126 | 87 | 87 | 39 | 0.1 |  | 1.4 | 98.5 | 708.56 | 710.26 | 713.56 | 713.56 | 5 | 3.3 | 3.3 | [13 empty] | 713.56 | 6.04 | 0.48 | 0.19
75 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN095 | 1S-DL-YP-ETC-DLNR-2503-MAN095 | NATRAJ CGHS, PPG:ID | TG-MAN095A-2 | 19501172 | 400 | 120 | 239 | 0.97 | 98 | 29 | 122 | 29 | 123 | 40 | 169 | 46 | 2019-06-01 00:30 | 26.8 | 4.1 | 208 | B | 88 | 81 | 131 | 50 |  |  | 39.2 | 60.8 | 699.26 | 694.26 | 471.29 | 659.26 | 20.3 | 25.3 | 25.3 | 60.3 | [12 empty] | 719.56 | 0.04 | 0.57 | 0.24
76 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN096 | 1S-DL-YP-ETC-DLNR-2503-MAN096 | SAH-VIKAS CGHS, PPG:ID | TG-MAN096A-1 | 19501221 | 630 | 200 | 239 | 0.97 | 118 | 41 | 174 | 39 | 167 | 38 | 165 | 8 | 2019-06-30 00:30 | 24.4 | 2.3 | 177 | B | 104 | 102 | 94 | 10 |  |  | 1.3 | 98.7 | 719.56 | 719.56 | 719.26 | 719.56 | [16 empty] | 719.56 | 0.04 | 0.51 | 0.19
77 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN096 | 1S-DL-YP-ETC-DLNR-2503-MAN096 | SAH-VIKAS CGHS, PPG:ID | TG-MAN096A-2 | 19503809 | 630 | 200 | 239 | 0.98 | 101 | 51 | 203 | 17 | 70 | 34 | 140 | 115 | 2019-06-09 01:00 | 19.3 | 2.3 | 246 | R | 153 | 51 | 96 | 102 | 51.7 | 48.3 |  |  | 631.26 | 719.56 | 719.56 | 719.56 | 88.3 | [15 empty] | 719.56 | 0.04 | 0.5 | 0.16
78 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN097 | 1S-DL-YP-ETC-DLNR-2503-MAN097 | KAMAYANI KUNJ CGHS,PPG:ID | TG-MAN097A-1 | 19505412 | 400 | 120 | 241 | 0.98 | 93 | 21 | 90 | 34 | 144 | 38 | 159 | 63 | 2019-06-02 | 18.1 | 2.3 | 180 | B | 82 | 105 | 113 | 31 |  | 0.2 | 62.7 | 37.1 | 715.58 | 650.28 | 604 | 690.28 | 4 | 69.3 | 69.3 | 29.3 | [12 empty] | 719.58 | 0.02 | 0.53 | 0.23
79 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN097 | 1S-DL-YP-ETC-DLNR-2503-MAN097 | KAMAYANI KUNJ CGHS,PPG:ID | TG-MAN097A-2 | 19505155 | 400 | 120 | 240 | 0.98 | 121 | 43 | 182 | 33 | 140 | 45 | 198 | 52 | 2019-06-11 | 23.4 | -6.8 | 198 | B | 100 | 84 | 116 | 32 | 69.4 | 14.9 | 11.3 | 4.4 | 587.58 | 673.28 | 528.3 | 593.3 | 127 | 41.3 | 41.3 | 121.28 | [12 empty] | 714.58 | 5.02 | 0.47 | 0.3
80 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN098 | 1S-DL-YP-ETC-DLNR-2503-MAN098 | PLATO SCHOOL:PM | TG-MAN098A-1 | 19502763 | 100 | 40 | 246 | 0.96 | 32 | 8 | 31 | 4 | 17 | 20 | 80 | 57 | 2019-06-28 12:30 | 6 | -0.1 | 80 | B | 117 | 70 | 113 | 47 |  |  | 4.1 | 95.9 | 712.58 | 719.58 | 704.28 | 709.58 | 7 |  |  | 10 |  |  | 2.3 | [9 empty] | 719.58 | 0.02 | 0.1 | 0.32
81 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN099 | 1S-DL-YP-ETC-DLNR-2503-MAN099 | MEENA CGHS, PPG:ID | TG-MAN099A-1 | 19502563 | 630 | 200 | 240 | 0.98 | 201 | 55 | 234 | 87 | 368 | 60 | 253 | 126 | 2019-06-03 | 31.3 | 6.4 | 368 | Y | 95 | 107 | 98 | 12 |  |  | 3.7 | 96.3 | 561.3 | 477 | 550 | 530.3 | 158.28 | 242.28 | 242.28 | 189.28 |  | 0.3 | [10 empty] | 719.58 | 0.02 | 0.51 | 0.32
82 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN100 | 1S-DL-YP-ETC-DLNR-2503-MAN100 | POOJA CGHS, PPG:ID | TG-MAN100A-1 | 19501293 | 630 | 200 | 240 | 0.95 | 77 | 23 | 97 | 26 | 111 | 28 | 119 | 19 | 2019-06-30 20:00 | 25.8 | 5.1 | 157 | B | 81 | 103 | 116 | 35 |  |  | 5.3 | 94.7 | 719.53 | 719.53 | 719.53 | 719.53 | [16 empty] | 719.53 | 0.07 | 0.57 | 0.12
83 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN100 | 1S-DL-YP-ETC-DLNR-2503-MAN100 | POOJA CGHS, PPG:ID | TG-MAN100A-2 | 19501113 | 630 | 200 | 245 | 0.98 | 121 | 29 | 120 | 35 | 144 | 56 | 230 | 100 | 2019-06-02 23:30 | 23.9 | 0.5 | 257 | B | 74 | 81 | 145 | 71 | 1.2 | 3.3 | 7.2 | 88.3 | 719.56 | 719.56 | 582.29 | 719.56 | [16 empty] | 719.56 | 0.04 | 0.5 | 0.19
84 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN101 | 1S-DL-YP-ETC-DLNR-2503-MAN101 | MITHILA CGHS, PPG:ID | TG-MAN101A-1 | 19506885 | 630 | 200 | 246 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [7 empty] | 5 | 95 | 711.56 | 711.56 | 711.56 | 711.56 | [16 empty] | 711.56 | 8.04 |  | 0
85 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN101 | 1S-DL-YP-ETC-DLNR-2503-MAN101 | MITHILA CGHS, PPG:ID | TG-MAN101A-2 | 19501111 | 630 | 200 | 245 | 0.97 | 174 | 60 | 253 | 60 | 256 | 54 | 229 | 25 | 2019-06-30 23:30 | 33.1 | 7.8 | 317 | Y | 94 | 123 | 83 | 40 |  |  | 5.4 | 94.6 | 605.57 | 433.3 | 677.57 | 577.3 | 113.3 | 285.57 | 285.57 | 141.57 | [12 empty] | 719.27 | 0.33 | 0.56 | 0.28
86 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN102 | 1S-DL-YP-ETC-DLNR-2503-MAN102 | MAITRI CGHS, PPG:ID | TG-MAN102A-1 | 19501347 | 400 | 120 | 239 | 0.98 | 204 | 62 | 277 | 71 | 317 | 70 | 303 | 35 | 2019-06-30 23:30 | 33.9 | 5.8 | 334 | Y | 93 | 105 | 101 | 12 | 43.4 | 56.6 |  |  | 311.3 | 249.3 | 254.3 | 269 | 375.27 | 379.27 | 379.27 | 397.27 | 33 | 91 | 58.57 | 53.3 | [8 empty] | 719.57 | 0.03 | 0.49 | 0.51
87 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN102 | 1S-DL-YP-ETC-DLNR-2503-MAN102 | MAITRI CGHS, PPG:ID | TG-MAN102A-2 | 19505397 | 400 | 120 | 239 | 0.98 | 127 | 42 | 183 | 46 | 202 | 38 | 165 | 32 | 2019-06-29 23:30 | 31.4 | 1.3 | 226 | Y | 89 | 113 | 98 | 24 | 0.2 | 0.1 | 6.7 | 92.9 | 626.26 | 478.59 | 570.56 | 554.59 | 93.3 | 240.57 | 240.57 | 164.57 | [12 empty] | 719.56 | 0.04 | 0.48 | 0.32
88 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN103 | 1S-DL-YP-ETC-DLNR-2503-MAN103 | SHRI GANESH CGHS, PPG:ID | TG-MAN103A-1 | 19501062 | 630 | 200 | 238.1209 | 0.97963 | 216.6172 | 87.4 | 381.9095 | 88.1533 | 390.6986 | 41.0639 | 180.5243 | 205.9205 | 2019-06-30 23:30 | [15 empty] | 502.5 |  |  |  | 217 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 719.5 |  | 0.50674 | 0.34384
89 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN103 | 1S-DL-YP-ETC-DLNR-2503-MAN103 | SHRI GANESH CGHS, PPG:ID | TG-MAN103A-2 | 19501063 | 630 | 200 | 239 | 0.98 | 121 | 61 | 258 | 43 | 182 | 17 | 73 | 161 | 2019-06-12 00:30 | 23.5 | 3.2 | 269 | R | 143 | 94 | 63 | 80 |  |  | 0.1 | 99.9 | 592.35 | 716.33 | 718.33 | 718.33 | 125.58 | 2 | 2 | [13 empty] | 718.33 | 1.27 | 0.52 | 0.19
90 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN104 | 1S-DL-YP-ETC-DLNR-2503-MAN104 | AGARSAIN CGHS, PPG S/STN-1:ID | TG-MAN104A-1 | 19505728 | 630 | 200 | 246 | 0.98 | 216 | 79 | 326 | 67 | 277 | 70 | 286 | 45 | 2019-06-15 | 46.8 | 8.2 | 336 | R | 112 | 94 | 94 | 18 | 0.1 |  | 2.2 | 97.7 | 385 | 500.3 | 527 | 477.3 | 321.58 | 206.28 | 206.28 | 229.28 | [12 empty] | 706.58 | 13.02 | 0.52 | 0.34
91 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN104 | 1S-DL-YP-ETC-DLNR-2503-MAN104 | AGARSAIN CGHS, PPG S/STN-1:ID | TG-MAN104A-2 | 19506812 | 630 | 200 | 246 | 0.97 | 208 | 75 | 321 | 66 | 282 | 66 | 284 | 38 | 2019-06-29 23:00 | 44.8 | 10.8 | 353 | R | 112 | 91 | 97 | 21 | 0.1 | 0.1 | 5.7 | 94.1 | 370.15 | 527.15 | 486.45 | 466.45 | 343.28 | 186.58 | 186.58 | 247.28 | 0.3 | [11 empty] | 714.13 | 5.47 | 0.55 | 0.33
92 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN105 | 1S-DL-YP-ETC-DLNR-2503-MAN105 | AGARSAIN CGHS, PPG S/STN-2:ID | TG-MAN105A-1 | 19504826 | 630 | 200 | 245 | 0.97 | 191 | 66 | 280 | 74 | 317 | 50 | 214 | 90 | 2019-06-29 23:30 | 48.3 | 6.4 | 331 | Y | 99 | 122 | 79 | 43 |  |  | 0.8 | 99.2 | 530.3 | 407 | 685.58 | 541 | 189.28 | 312.58 | 312.58 | 178.58 | [12 empty] | 719.58 | 0.02 | 0.53 | 0.3
93 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN105 | 1S-DL-YP-ETC-DLNR-2503-MAN105 | AGARSAIN CGHS, PPG S/STN-2:ID | TG-MAN105A-2 | 19500792 | 630 | 200 | 244.5978 | 0.97334 | 156.8167 | 50.7003 | 210.3396 | 50.3653 | 209.7504 | 55.7512 | 230.4148 | 20.3762 | 2019-06-12 | [15 empty] | 679 |  |  |  | 41 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.52852 | 0.24892
94 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN106 | 1S-DL-YP-ETC-DLNR-2503-MAN106 | BALCO CGHS, PPG:ID | TG-MAN106A-1 | 19501069 | 400 | 120 | 245.7369 | 0.9692 | 66.4806 | 28.7173 | 119.2528 | 17.7006 | 74.0705 | 20.0628 | 82.2918 | 41.6842 | 2019-06-11 00:30 | [15 empty] | 720 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.46108 | 0.1662
95 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN106 | 1S-DL-YP-ETC-DLNR-2503-MAN106 | BALCO CGHS, PPG:ID | TG-MAN106A-2 | 19506198 | 400 | 120 | 239 | 0.98 | 153 | 55 | 237 | 49 | 210 | 48 | 208 | 28 | 2019-06-11 23:30 | 36.2 | 6.4 | 291 | R | 113 | 87 | 100 | 26 | 0.1 |  | 0.3 | 99.6 | 206 | 478.58 | 339.28 | 345 | 504.39 | 240.41 | 240.41 | 374.39 | 9 | [11 empty] | 719.39 | 0.21 | 0.56 | 0.38
96 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN107 | 1S-DL-YP-ETC-DLNR-2503-MAN107 | TAKSHSHILA CGHS, PPG S/STN-1:ID | TG-MAN107A-1 | 19501134 | 400 | 120 | 237 | 0.98 | 128 | 71 | 308 | 21 | 94 | 36 | 154 | 191 | 2019-06-05 23:00 | 20.4 | 2.2 | 338 | R | 165 | 78 | 58 | 107 | 3 | 14.7 | 80.1 | 2.2 | 220 | 690.38 | 683.3 | 523 | 388.08 | 28.52 | 28.52 | 196.3 | 111.22 | [11 empty] | 719.3 | 0.3 | 0.52 | 0.32
97 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN107 | 1S-DL-YP-ETC-DLNR-2503-MAN107 | TAKSHSHILA CGHS, PPG S/STN-1:ID | TG-MAN107A-2 | 19501133 | 400 | 120 | 239 | 0.97 | 122 | 39 | 175 | 28 | 123 | 55 | 237 | 99 | 2019-06-11 01:00 | 25.4 | 5 | 254 | B | 78 | 89 | 133 | 55 | 17.2 | 80.9 | 1.9 |  | 644.31 | 588.49 | 264.3 | 490 | 75 | 130.42 | 130.42 | 229.31 |  |  | 12.3 | [9 empty] | 719.31 | 0.29 | 0.58 | 0.3
98 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN108 | 1S-DL-YP-ETC-DLNR-2503-MAN108 | TAKSHSHILA CGHS, PPG S/STN-2:ID | TG-MAN108A-1 | 19501131 | 400 | 120 | 236 | 0.98 | 184 | 73 | 331 | 50 | 230 | 62 | 274 | 88 | 2019-06-30 23:30 | 27.6 | 5.2 | 377 | R | 125 | 72 | 103 | 53 | 100 |  |  |  | 213 | 517.3 | 295 | 344.3 | 371.3 | 202 | 202 | 347.02 | 135 |  | 55.28 | 27.58 | [8 empty] | 719.3 | 0.3 | 0.49 | 0.46
99 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN108 | 1S-DL-YP-ETC-DLNR-2503-MAN108 | TAKSHSHILA CGHS, PPG S/STN-2:ID | TG-MAN108A-2 | 19501132 | 400 | 120 | 237 | 0.98 | 89 | 47 | 194 | 28 | 116 | 14 | 58 | 118 | 2019-06-03 | 13 | 2.5 | 220 | R | 140 | 100 | 60 | 80 |  |  | 2.4 | 97.6 | 533.11 | 709.01 | 719.31 | 711.31 | 186.2 | 10.3 | 10.3 | 8 | [12 empty] | 719.31 | 0.29 | 0.49 | 0.22
100 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN109 | 1S-DL-YP-ETC-DLNR-2503-MAN109 | JAI LAXMI CGHS, PPG AVAS:ID | TG-MAN109A-1 | 19501968 | 630 | 200 | 237 | 0.98 | 174 | 60 | 259 | 58 | 248 | 57 | 244 | 13 | 2019-06-06 00:30 | 30.4 | 6.9 | 300 | R | 118 | 90 | 93 | 28 |  |  | 0.3 | 99.7 | 482.07 | 624.07 | 587.07 | 573.37 | 237.24 | 95.24 | 95.24 | 145.54 | [12 empty] | 719.31 | 0.29 | 0.55 | 0.28
101 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN109 | 1S-DL-YP-ETC-DLNR-2503-MAN109 | JAI LAXMI CGHS, PPG AVAS:ID | TG-MAN109A-2 | 19506199 | 630 | 200 | 237 | 0.98 | 148 | 53 | 227 | 56 | 241 | 39 | 166 | 70 | 2019-06-12 00:30 | 27.4 | 3 | 260 | Y | 106 | 108 | 87 | 21 | 0.1 |  | 0.1 | 99.8 | 622.35 | 588.35 | 695 | 657.05 | 73.25 | 107.25 | 107.25 | 38.55 | [12 empty] | 696 | 24 | 0.51 | 0.23
102 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN120 | 1S-DL-YP-ETC-DLNR-2503-MAN120 | KALLOL CGHS, PPG:ID | TG-MAN120A-1 | 19501241 | 630 | 200 | 245 | 0.97 | 90 | 20 | 83 | 46 | 188 | 24 | 101 | 98 | 2019-06-03 00:30 | 17.9 | 2.8 | 201 | Y | 80 | 138 | 81 | 58 |  |  | 16.7 | 83.3 | 719.58 | 706.58 | 719.58 | 719.58 |  | 13 | 13 | [13 empty] | 719.58 | 0.02 | 0.52 | 0.14
103 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN120 | 1S-DL-YP-ETC-DLNR-2503-MAN120 | KALLOL CGHS, PPG:ID | TG-MAN120A-2 | 19501171 | 630 | 200 | 246 | 0.98 | 111 | 25 | 106 | 30 | 126 | 57 | 240 | 126 | 2019-06-30 23:30 | 15.2 | 2.3 | 240 | B | 72 | 89 | 140 | 68 |  |  | 10.6 | 89.4 | 719.58 | 719.58 | 686.28 | 719.58 | [16 empty] | 719.58 | 0.02 | 0.46 | 0.18
104 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN121 | 1S-DL-YP-ETC-DLNR-2503-MAN121 | ARUNA CGHS, PPG:ID | TG-MAN121A-1 | 19501242 | 400 | 120 | 246 | 0.97 | 79 | 24 | 102 | 32 | 140 | 23 | 101 | 38 | 2019-06-30 23:00 | 17.1 | 2.2 | 151 | Y | 74 | 143 | 82 | 69 |  |  | 1.9 | 98.1 | 719.05 | 604.05 | 719.05 | 719.05 |  | 115 | 115 | [13 empty] | 719.05 | 0.55 | 0.5 | 0.2
105 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN121 | 1S-DL-YP-ETC-DLNR-2503-MAN121 | ARUNA CGHS, PPG:ID | TG-MAN121A-2 | 19506196 | 400 | 120 | 246 | 0.97 | 85 | 32 | 128 | 34 | 139 | 19 | 80 | 55 | 2019-06-26 23:30 | 22 | 2.2 | 184 | Y | 104 | 130 | 67 | 63 | 0.1 |  | 0.7 | 99.2 | 663.06 | 598.06 | 696 | 693 | 32.54 | 97.54 | 97.54 | 3 | [12 empty] | 696 | 24 | 0.49 | 0.21
106 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN122 | 1S-DL-YP-ETC-DLNR-2503-MAN122 | KAILASH APARTMENT, PPG:ID | TG-MAN122A-1 | 19505417 | 630 | 200 | 247 | 0.98 | 114 | 31 | 132 | 15 | 64 | 68 | 287 | 198 | 2019-06-09 23:30 | 28.8 | -9.6 | 295 | B | 87 | 38 | 175 | 137 | 0.1 |  | 0.2 | 99.7 | 719.01 | 719.01 | 555.31 | 719.01 | [16 empty] | 719.01 | 0.59 | 0.43 | 0.18
107 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN122 | 1S-DL-YP-ETC-DLNR-2503-MAN122 | KAILASH APARTMENT, PPG:ID | TG-MAN122A-2 | 19505398 | 630 | 200 | 247 | 0.98 | 149 | 49 | 200 | 68 | 276 | 32 | 130 | 126 | 2019-06-01 22:00 | 31.2 | 3.2 | 331 | Y | 110 | 128 | 62 | 66 | 0.1 |  | 0.3 | 99.7 | 661.06 | 541.04 | 719.05 | 681.06 | 57.59 | 178.01 | 178.01 | 37.59 | [12 empty] | 719.05 | 0.55 | 0.51 | 0.24
108 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN123 | 1S-DL-YP-ETC-DLNR-2503-MAN123 | SITA RAM CGHS,PPG,S/S-1:ID | TG-MAN123A-1 | 19501870 | 400 | 120 | 236 | 0.98 | 93 | 20 | 82 | 45 | 188 | 28 | 118 | 93 | 2019-06-11 23:00 | 15.7 | 1.4 | 212 | Y | 76 | 133 | 91 | 57 |  |  | 2.6 | 97.4 | 719.16 | 504 | 692.16 | 686.28 |  | 215.16 | 215.16 | 32.48 | [12 empty] | 719.16 | 0.44 | 0.54 | 0.23
109 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN123 | 1S-DL-YP-ETC-DLNR-2503-MAN123 | SITA RAM CGHS,PPG,S/S-1:ID | TG-MAN123A-2 | 19501988 | 400 | 120 | 243 | 0.97 | 138 | 67 | 273 | 27 | 108 | 44 | 177 | 143 | 2019-06-02 00:30 | 32.8 | 4.1 | 292 | R | 142 | 66 | 92 | 76 | 0.1 | 0.1 | 4 | 95.8 | 172.3 | 688.52 | 449.35 | 399.3 | 423.52 | 30.25 | 30.25 | 319.47 | 122.55 |  | 0.3 | [9 empty] | 719.17 | 0.43 | 0.58 | 0.34
110 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN124 | 1S-DL-YP-ETC-DLNR-2503-MAN124 | SITA RAM CGHS,PPG,S/S-2:ID | TG-MAN124A-1 | 19505419 | 630 | 200 | 235 | 0.97 | 210 | 71 | 317 | 70 | 310 | 69 | 306 | 9 | 2019-06-26 22:30 | 116.6 | 10.8 | 317 | R | 96 | 97 | 107 | 11 |  | 0.1 | 14.2 | 85.8 | 570.14 | 566.14 | 398.44 | 535.14 | 145.27 | 149.27 | 149.27 | 180.27 | [12 empty] | 715.41 | 4.19 | 0.55 | 0.33
111 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN124 | 1S-DL-YP-ETC-DLNR-2503-MAN124 | SITA RAM CGHS,PPG,S/S-2:ID | TG-MAN124A-2 | 19506620 | 630 | 200 | 234 | 0.99 | 124 | 24 | 114 | 31 | 138 | 70 | 318 | 193 | 2019-06-10 23:30 | 20.2 | 0.8 | 318 | B | 63 | 84 | 152 | 89 | 50.9 | 22.9 | 17.7 | 8.4 | 692.1 | 692.1 | 547.14 | 692.1 | [16 empty] | 692.1 | 27.5 | 0.48 | 0.2
112 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN127 | 1S-DL-YP-ETC-DLNR-2503-MAN127 | ASHIRWAD ENCLAVE, PPG:ID | TG-MAN127A-1 | 19505571 | 630 | 200 | 239 | 0.98 | 79 | 21 | 90 | 26 | 112 | 31 | 133 | 37 | 2019-06-12 00:30 | 16.4 | 0.4 | 143 | Y | 89 | 95 | 116 | 27 | 0.2 | 0.1 | 2.4 | 97.3 | 714.28 | 714.28 | 714.28 | 714.28 | [16 empty] | 714.28 | 5.32 | 0.53 | 0.13
113 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN127 | 1S-DL-YP-ETC-DLNR-2503-MAN127 | ASHIRWAD ENCLAVE, PPG:ID | TG-MAN127A-2 | 19505400 | 630 | 200 | 239 | 0.98 | 165 | 62 | 264 | 57 | 242 | 46 | 193 | 63 | 2019-06-16 00:30 | 34.2 | 4.4 | 282 | R | 113 | 105 | 82 | 31 |  |  | 1.3 | 98.7 | 489 | 595.3 | 692.58 | 619 | 225.28 | 118.58 | 118.58 | 95.28 | [12 empty] | 714.28 | 5.32 | 0.58 | 0.26
114 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN128 | 1S-DL-YP-ETC-DLNR-2503-MAN128 | VARDAN CGHS, PPG:ID | TG-MAN128A-1 | 19501189 | 630 | 200 | 240 | 0.98 | 155 | 37 | 156 | 67 | 281 | 50 | 210 | 108 | 2019-06-10 00:30 | 34 | 5.1 | 281 | Y | 82 | 123 | 96 | 41 |  |  | 19 | 81 | 708.56 | 473.29 | 626.26 | 620.56 | 11 | 246.27 | 246.27 | 99 | [12 empty] | 719.56 | 0.04 | 0.59 | 0.25
115 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN128 | 1S-DL-YP-ETC-DLNR-2503-MAN128 | VARDAN CGHS, PPG:ID | TG-MAN128A-2 | 19501190 | 630 | 200 | 253 | 0.97 | 154 | 47 | 182 | 48 | 188 | 59 | 235 | 50 | 2019-06-11 00:30 | 33.1 | 6.4 | 237 | B | 101 | 77 | 122 | 45 |  |  | 5.8 | 94.2 | 682.26 | 716.56 | 613.59 | 696.56 | 37.3 | 3 | 3 | 23 | [12 empty] | 719.56 | 0.04 | 0.51 | 0.24
116 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN129 | 1S-DL-YP-ETC-DLNR-2503-MAN129 | DELHI RAJDHANI CGHS, PPG:ID | TG-MAN129A-1 | 19501334 | 630 | 200 | 246 | 0.98 | 137 | 47 | 191 | 48 | 194 | 42 | 168 | 25 | 2019-06-11 01:30 | 23.5 | 4.1 | 212 | Y | 101 | 108 | 91 | 17 |  |  | 11.9 | 88.1 | 696.42 | 693.42 | 710.12 | 713.12 | 23 | 26 | 26 | 6.3 | [12 empty] | 719.42 | 0.18 | 0.5 | 0.22
117 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN129 | 1S-DL-YP-ETC-DLNR-2503-MAN129 | DELHI RAJDHANI CGHS, PPG:ID | TG-MAN129A-2 | 19501333 | 630 | 200 | 247 | 0.96 | 113 | 48 | 194 | 28 | 114 | 37 | 151 | 69 | 2019-06-11 23:30 | 26.7 | 5.5 | 194 | R | 113 | 75 | 113 | 38 |  |  | 1.9 | 98.1 | 713.26 | 719.56 | 717.56 | 719.56 | 6.3 | [15 empty] | 719.56 | 0.04 | 0.53 | 0.18
118 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN130 | 1S-DL-YP-ETC-DLNR-2503-MAN130 | ASSOCIATE CGHS, PPG:ID | TG-MAN130A-1 | 19501323 | 400 | 120 | 246 | 0.97 | 141 | 46 | 190 | 50 | 205 | 44 | 181 | 21 | 2019-06-01 23:00 | 27.6 | 5.2 | 227 | Y | 107 | 108 | 85 | 23 |  |  | 1.9 | 98.1 | 474.3 | 449.59 | 596.22 | 514.29 | 245 | 269.01 | 269.01 | 205.01 |  | 0.3 | [10 empty] | 719.3 | 0.3 | 0.48 | 0.35
119 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN130 | 1S-DL-YP-ETC-DLNR-2503-MAN130 | ASSOCIATE CGHS, PPG:ID | TG-MAN130A-2 | 19506323 | 400 | 120 | 253 | 0.98 | 100 | 30 | 132 | 42 | 182 | 28 | 120 | 57 | 2019-06-26 22:30 | 28.9 | 4.6 | 182 | Y | 92 | 125 | 83 | 42 | 0.1 | 0.1 | 0.5 | 99.3 | 656.59 | 517.29 | 711.03 | 644.59 | 62.3 | 202 | 202 | 74.3 | [12 empty] | 719.29 | 0.31 | 0.54 | 0.25
120 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN131 | 1S-DL-YP-ETC-DLNR-2503-MAN131 | MAYUR DHWAJ CGHS,PPG,S/S-1:ID | TG-MAN131A-1 | 19501186 | 630 | 200 | 245 | 0.98 | 144 | 27 | 113 | 67 | 284 | 50 | 213 | 148 | 2019-06-10 23:30 | 20.2 | 2.8 | 290 | Y | 56 | 152 | 92 | 96 |  |  | 0.6 | 99.4 | 719.58 | 538.58 | 710.28 | 715.58 |  | 181 | 181 | 4 | [12 empty] | 719.58 | 0.02 | 0.47 | 0.23
121 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN131 | 1S-DL-YP-ETC-DLNR-2503-MAN131 | MAYUR DHWAJ CGHS,PPG,S/S-1:ID | TG-MAN131A-2 | 19501174 | 630 | 200 | 240 | 0.98 | 153 | 25 | 109 | 54 | 233 | 74 | 327 | 189 | 2019-06-10 23:30 | 29.4 | 3.2 | 331 | B | 49 | 101 | 150 | 101 |  |  | 5.3 | 94.7 | 719.58 | 664.28 | 453.3 | 674.28 |  | 55.3 | 55.3 | 45.3 | [12 empty] | 719.58 | 0.02 | 0.51 | 0.24
122 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN132 | 1S-DL-YP-ETC-DLNR-2503-MAN132 | MAYUR DHWAJ CGHS,PPG,S/S-2:ID | TG-MAN132A-1 | 19505300 | 630 | 200 | 241 | 0.98 | 132 | 46 | 199 | 57 | 248 | 29 | 128 | 104 | 2019-06-05 23:30 | 23.8 | 3 | 248 | Y | 116 | 112 | 72 | 44 | 0.1 |  | 10.7 | 89.2 | 643.28 | 650.58 | 719.58 | 711.58 | 76.3 | 69 | 69 | 8 | [12 empty] | 719.58 | 0.02 | 0.53 | 0.21
123 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN132 | 1S-DL-YP-ETC-DLNR-2503-MAN132 | MAYUR DHWAJ CGHS,PPG,S/S-2:ID | TG-MAN132A-2 | 19501235 | 630 | 200 | 240 | 0.98 | 126 | 26 | 108 | 47 | 200 | 54 | 230 | 110 | 2019-06-02 00:30 | 22.1 | 2.3 | 238 | Y | 50 | 121 | 129 | 79 |  |  | 1.5 | 98.5 | 719.58 | 677.28 | 636.28 | 718.58 |  | 42.3 | 42.3 | 1 | [12 empty] | 719.58 | 0.02 | 0.5 | 0.2
124 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN133 | 1S-DL-YP-ETC-DLNR-2503-MAN133 | MAYUR DHWAJ CGHS,PPG,S/S-3:ID | TG-MAN133A-1 | 19501231 | 400 | 120 | 246 | 0.98 | 89 | 35 | 148 | 18 | 75 | 37 | 153 | 76 | 2019-06-01 23:30 | 14.6 | 0.8 | 169 | R | 122 | 65 | 114 | 57 |  |  | 12.1 | 87.9 | 603.58 | 719.58 | 678.58 | 713.58 | 116 |  |  | 6 | [12 empty] | 719.58 | 0.02 | 0.46 | 0.22
125 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN133 | 1S-DL-YP-ETC-DLNR-2503-MAN133 | MAYUR DHWAJ CGHS,PPG,S/S-3:ID | TG-MAN133A-2 | 19501232 | 400 | 120 | 245 | 0.93 | 130 | 40 | 157 | 35 | 140 | 55 | 221 | 74 | 2019-06-06 19:00 | 66.8 | 13.8 | 237 | B | 81 | 94 | 125 | 44 |  |  | 12.4 | 87.6 | 603.29 | 397 | 141.3 | 316 | 116.3 | 322.59 | 322.59 | 403.59 |  |  | 4 | [9 empty] | 719.59 | 0.01 | 0.63 | 0.33
126 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN134 | 1S-DL-YP-ETC-DLNR-2503-MAN134 | PRINCE CGHS, PPG S/S-1:ID | TG-MAN134A-1 | 19501858 | 630 | 200 | 241 | 0.98 | 176 | 68 | 278 | 67 | 273 | 42 | 173 | 103 | 2019-06-12 00:30 | 32.2 | 3.7 | 298 | R | 106 | 110 | 84 | 26 |  |  | 0.8 | 99.2 | 557.26 | 532.59 | 693.56 | 597.56 | 162.3 | 186.57 | 186.57 | 122 | [12 empty] | 719.56 | 0.04 | 0.5 | 0.28
127 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN134 | 1S-DL-YP-ETC-DLNR-2503-MAN134 | PRINCE CGHS, PPG S/S-1:ID | TG-MAN134A-2 | 19506521 | 630 | 200 | 240 | 0.97 | 170 | 75 | 313 | 59 | 245 | 36 | 147 | 145 | 2019-06-12 | 33.8 | 7.2 | 314 | R | 120 | 103 | 78 | 42 |  | 0.1 | 57 | 42.9 | 498.29 | 614.56 | 692.26 | 620.29 | 215.27 | 99 | 99 | 93.27 | [12 empty] | 713.56 | 6.04 | 0.52 | 0.27
128 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN135 | 1S-DL-YP-ETC-DLNR-2503-MAN135 | PRINCE CGHS,PPG S/S-2:ID | TG-MAN135A-1 | 19501966 | 630 | 200 | 241 | 0.99 | 157 | 53 | 221 | 46 | 192 | 58 | 242 | 43 | 2019-06-11 23:30 | 34.5 | -1.8 | 278 | B | 98 | 89 | 113 | 24 |  |  |  | 100 | 669.26 | 685.56 | 596.56 | 660.26 | 50.3 | 34 | 34 | 59.3 | [12 empty] | 719.56 | 0.04 | 0.56 | 0.25
129 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN135 | 1S-DL-YP-ETC-DLNR-2503-MAN135 | PRINCE CGHS,PPG S/S-2:ID | TG-MAN135A-2 | 19502564 | 630 | 200 | 241 | 0.97 | 134 | 44 | 187 | 45 | 190 | 45 | 191 | 4 | 2019-06-11 22:30 | 23 | 2.3 | 229 | B | 93 | 91 | 115 | 24 |  |  | 19 | 81 | 715.56 | 715.26 | 684.56 | 717.26 | 4 | 4.3 | 4.3 | 2.3 | [12 empty] | 719.56 | 0.04 | 0.48 | 0.21
130 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN136 | 1S-DL-YP-ETC-DLNR-2503-MAN136 | SUKH-SAGAR CGHS,PPG:ID | TG-MAN136A-1 | 19501332 | 630 | 200 | 246 | 0.98 | 93 | 38 | 164 | 22 | 95 | 34 | 146 | 63 | 2019-06-10 23:30 | 25.8 | 0.9 | 180 | R | 127 | 75 | 98 | 52 |  |  | 0.3 | 99.7 | 719 | 719.3 | 719.3 | 719.3 | 0.3 | [15 empty] | 719.3 | 0.3 | 0.49 | 0.15
131 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN136 | 1S-DL-YP-ETC-DLNR-2503-MAN136 | SUKH-SAGAR CGHS,PPG:ID | TG-MAN136A-2 | 19506722 | 630 | 200 | 240 | 0.97 | 190 | 62 | 275 | 61 | 273 | 66 | 296 | 22 | 2019-06-10 23:00 | 67.6 | -2.6 | 359 | B | 117 | 100 | 83 | 34 |  |  | 0.1 | 99.9 | 221 | 471.34 | 451 | 439 | 498.29 | 247.55 | 247.55 | 280.29 |  |  | 0.3 | [9 empty] | 719.29 | 0.31 | 0.62 | 0.3
132 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN137 | 1S-DL-YP-ETC-DLNR-2503-MAN137 | SHIKA APARTMENT,PPG:ID | TG-MAN137A-1 | 19501321 | 400 | 120 | 246 | 0.96 | 73 | 32 | 131 | 12 | 46 | 29 | 119 | 79 | 2019-06-15 23:30 | 22.6 | 0.6 | 145 | R | 137 | 54 | 109 | 83 |  |  | 0.1 | 99.9 | 641.13 | 719.3 | 717 | 719.3 | 78.17 | [15 empty] | 719.3 | 0.3 | 0.53 | 0.18
133 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN137 | 1S-DL-YP-ETC-DLNR-2503-MAN137 | SHIKA APARTMENT,PPG:ID | TG-MAN137A-2 | 19501325 | 400 | 120 | 240 | 0.97 | 62 | 22 | 92 | 23 | 94 | 18 | 73 | 21 | 2019-06-14 | 14.1 | 1.1 | 118 | R | 97 | 102 | 100 | 5 | 3.3 | 17.7 | 12.4 | 66.5 | 719 | 719 | 719.3 | 719.3 | 0.3 | 0.3 | 0.3 | [13 empty] | 719.3 | 0.3 | 0.47 | 0.16
134 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN138 | 1S-DL-YP-ETC-DLNR-2503-MAN138 | HANUMAN MANGLA CGHS,PPG:ID | TG-MAN138A-1 | 19501320 | 400 | 120 | 247 | 0.97 | 95 | 37 | 159 | 28 | 122 | 30 | 131 | 33 | 2019-06-10 23:00 | 22.4 | 3 | 159 | R | 117 | 104 | 79 | 38 |  |  | 0.1 | 99.9 | 611 | 688.32 | 706.3 | 696 | 108.3 | 30.58 | 30.58 | 23.3 | [12 empty] | 719.3 | 0.3 | 0.5 | 0.24
135 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN138 | 1S-DL-YP-ETC-DLNR-2503-MAN138 | HANUMAN MANGLA CGHS,PPG:ID | TG-MAN138A-2 | 19501316 | 400 | 120 | 240 | 0.98 | 80 | 21 | 92 | 24 | 103 | 35 | 150 | 54 | 2019-06-11 23:00 | 14.1 | 2.5 | 150 | B | 105 | 98 | 97 | 8 |  |  | 0.3 | 99.7 | 719.29 | 709.59 | 705.59 | 718.59 |  | 9.3 | 9.3 | 0.3 | [12 empty] | 719.29 | 0.31 | 0.51 | 0.2
136 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN139 | 1S-DL-YP-ETC-DLNR-2503-MAN139 | UNESCO CGHS, S/S-1,PPG:ID | TG-MAN139A-1 | 19501064 | 630 | 200 | 246 | 0.97 | 173 | 50 | 215 | 49 | 210 | 74 | 312 | 100 | 2019-06-10 23:00 | 40.9 | 6.4 | 339 | B | 78 | 91 | 131 | 53 | 37.2 | 62.8 |  |  | 713.56 | 685.56 | 367.28 | 638.56 | 6 | 34 | 34 | 81 | [12 empty] | 719.56 | 0.04 | 0.56 | 0.27
137 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN139 | 1S-DL-YP-ETC-DLNR-2503-MAN139 | UNESCO CGHS, S/S-1,PPG:ID | TG-MAN139A-2 | 19501065 | 630 | 200 | 239 | 0.98 | 162 | 54 | 232 | 57 | 246 | 52 | 223 | 20 | 2019-06-02 | 25.3 | 2.3 | 338 | Y | 88 | 120 | 92 | 32 |  |  | 0.1 | 99.9 | 692.28 | 560 | 694.28 | 656.58 | 27.3 | 159.58 | 159.58 | 63 | [12 empty] | 719.58 | 0.02 | 0.51 | 0.26
138 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN140 | 1S-DL-YP-ETC-DLNR-2503-MAN140 | UNESCO CGHS,S/S-2,PPG:ID | TG-MAN140A-1 | 19505975 | 630 | 200 | 246 | 0.98 | 106 | 53 | 230 | 0 | 0 | 53 | 217 | 224 | 2019-06-30 23:30 | 18.8 | 3 | 253 | B | 138 | 0 | 162 | 162 | 100 |  |  |  | 675.58 | 719.58 | 552.58 | 719.58 | 44 | [15 empty] | 719.58 | 0.02 | 0.59 | 0.17
139 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN140 | 1S-DL-YP-ETC-DLNR-2503-MAN140 | UNESCO CGHS,S/S-2,PPG:ID | TG-MAN140A-2 | 19501987 | 630 | 200 | 246 | 0.97 | 150 | 79 | 334 | 34 | 143 | 37 | 153 | 186 | 2019-06-10 22:00 | 29 | 3.2 | 334 | R | 136 | 84 | 80 | 56 | 87.8 | 12.2 |  |  | 460.3 | 717.58 | 697.58 | 677.58 | 259.28 | 2 | 2 | 42 | [12 empty] | 719.58 | 0.02 | 0.56 | 0.24
140 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN141 | 1S-DL-YP-ETC-DLNR-2503-MAN141 | AMAR PALI CGHS,S/S-1,PPG:ID | TG-MAN141A-1 | 19505271 | 630 | 200 | 246 | 0.97 | 244 | 92 | 380 | 87 | 358 | 65 | 267 | 104 | 2019-06-15 | 52 | 11.2 | 405 | R | 116 | 104 | 80 | 36 | 0.1 |  | 1.7 | 98.1 | 197.3 | 269.3 | 523.3 | 307.3 | 492.58 | 439.28 | 439.28 | 412.28 | 29.3 | 11 | [10 empty] | 719.58 | 0.02 | 0.57 | 0.39
141 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN141 | 1S-DL-YP-ETC-DLNR-2503-MAN141 | AMAR PALI CGHS,S/S-1,PPG:ID | TG-MAN141A-2 | 19506201 | 630 | 200 | 231 | 0.97 | 155 | 56 | 227 | 38 | 152 | 62 | 252 | 90 | 2019-06-03 01:00 | 31.6 | 6.4 | 283 | B | 107 | 74 | 119 | 45 | 37.2 |  | 55.2 | 7.5 | 407.3 | 461.28 | 342 | 425.3 | 55.58 | 2 | 2 | 37.58 | [12 empty] | 714.58 | 5.02 | 0.52 | 0.25
142 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN142 | 1S-DL-YP-ETC-DLNR-2503-MAN142 | AMAR PALI CGHS,S/S-2,PPG:ID | TG-MAN142A-1 | 19506203 | 630 | 200 | 240 | 0.96 | 105 | 30 | 133 | 24 | 105 | 51 | 222 | 106 | 2019-06-30 23:30 | 26 | 3.8 | 222 | B | 102 | 68 | 130 | 62 |  |  | 3.6 | 96.4 | 714.58 | 714.58 | 704.28 | 714.58 | [16 empty] | 714.58 | 5.02 | 0.5 | 0.17
143 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN142 | 1S-DL-YP-ETC-DLNR-2503-MAN142 | AMAR PALI CGHS,S/S-2,PPG:ID | TG-MAN142A-2 | 19505988 | 630 | 200 | 240 | 0.98 | 216 | 68 | 290 | 91 | 391 | 56 | 237 | 135 | 2019-06-03 | 47.8 | 7.4 | 447 | Y | 93 | 122 | 85 | 37 | 0.1 |  | 19.3 | 80.6 | 474 | 326 | 543 | 458.3 | 245.58 | 389.28 | 389.28 | 261.28 |  | 4.3 | [10 empty] | 719.58 | 0.02 | 0.54 | 0.34
144 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN143 | 1S-DL-YP-ETC-DLNR-2503-MAN143 | NAVNEETI CGHS, PPG:ID | TG-MAN143A-1 | 19505341 | 630 | 200 | 248 | 0.97 | 151 | 72 | 297 | 39 | 159 | 40 | 165 | 135 | 2019-06-11 22:30 | 30.6 | 4.8 | 298 | R | 111 | 101 | 87 | 24 | 0.1 |  | 4.8 | 95.1 | 628.56 | 670.56 | 694.56 | 689.56 | 72.3 | 30.3 | 30.3 | 11.3 | [12 empty] | 701.26 | 18.34 | 0.47 | 0.24
145 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN143 | 1S-DL-YP-ETC-DLNR-2503-MAN143 | NAVNEETI CGHS, PPG:ID | TG-MAN143A-2 | 19501187 | 630 | 200 | 246 | 0.96 | 172 | 64 | 261 | 47 | 189 | 62 | 252 | 68 | 2019-06-11 23:30 | 39.6 | 8.3 | 278 | R | 109 | 99 | 92 | 17 |  |  | 20.1 | 79.9 | 550.29 | 606.29 | 650.27 | 614.57 | 169.28 | 113.28 | 113.28 | 105 | [12 empty] | 719.57 | 0.03 | 0.53 | 0.27
146 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN144 | 1S-DL-YP-ETC-DLNR-2503-MAN144 | KAKATYA, CGHS, PPG:ID | TG-MAN144A-1 | 19501228 | 630 | 200 | 246 | 0.95 | 141 | 43 | 183 | 58 | 248 | 40 | 168 | 74 | 2019-06-30 23:30 | 31.3 | 4.1 | 265 | Y | 94 | 129 | 77 | 52 |  |  | 1.4 | 98.6 | 715.28 | 615.3 | 719.58 | 715.28 | 4.3 | 104.28 | 104.28 | 4.3 | [12 empty] | 719.58 | 0.02 | 0.47 | 0.22
147 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN144 | 1S-DL-YP-ETC-DLNR-2503-MAN144 | KAKATYA, CGHS, PPG:ID | TG-MAN144A-2 | 19501066 | 630 | 200 | 246 | 0.97 | 113 | 46 | 192 | 31 | 127 | 35 | 146 | 58 | 2019-06-11 23:30 | 21.2 | 4.1 | 208 | B | 108 | 83 | 108 | 25 |  |  | 0.6 | 99.4 | 713.28 | 719.58 | 715.58 | 719.58 | 6.3 | [15 empty] | 719.58 | 0.02 | 0.51 | 0.18
148 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN145 | 1S-DL-YP-ETC-DLNR-2503-MAN145 | HIMALAYA CGHS, PPG:ID | TG-MAN145A-1 | 19501068 | 400 | 120 | 241.021 | 0.96938 | 20.4533 | 6.922 | 29.4192 | 8.28 | 35.3635 | 5.2513 | 22.3401 | 11.2928 | 2019-06-11 23:00 | [15 empty] | 720 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.50947 | 0.051133
149 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN145 | 1S-DL-YP-ETC-DLNR-2503-MAN145 | HIMALAYA CGHS, PPG:ID | TG-MAN145A-2 | 19501067 | 400 | 120 | 246.6146 | 0.97137 | 170.3058 | 56.9504 | 240.8661 | 50.2775 | 206.6141 | 63.0779 | 266.0057 | 51.636 | 2019-06-10 | [15 empty] | 427.5 |  |  |  | 281.5 |  |  |  | 11 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.47363 | 0.42576
150 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN146 | 1S-DL-YP-ETC-DLNR-2503-MAN146 | AAKRITI CGHS,PPG:ID | TG-MAN146A-1 | 19505979 | 630 | 200 | 240 | 0.97 | 114 | 30 | 127 | 38 | 161 | 46 | 197 | 60 | 2019-06-02 23:30 | 28.4 | 5.4 | 208 | B | 78 | 108 | 114 | 36 |  |  | 1.7 | 98.3 | 719.52 | 716.52 | 699.52 | 719.52 |  | 3 | 3 | [13 empty] | 719.52 | 0.08 | 0.53 | 0.18
151 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN146 | 1S-DL-YP-ETC-DLNR-2503-MAN146 | AAKRITI CGHS,PPG:ID | TG-MAN146A-2 | 19505919 | 630 | 200 | 240 | 0.98 | 116 | 27 | 119 | 50 | 218 | 38 | 167 | 86 | 2019-06-30 23:30 | 19.6 | -23.4 | 242 | Y | 38 | 221 | 41 | 183 | 3.5 | 0.1 | 3.2 | 93.2 | 719.5 | 675.2 | 719.5 | 719.5 |  | 44.3 | 44.3 | [13 empty] | 719.5 | 0.1 | 0.3 | 0.18
152 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN147 | 1S-DL-YP-ETC-DLNR-2503-MAN147 | NEW SURYA KIRAN CGHS,PPG:ID | TG-MAN147A-1 | 19505366 | 630 | 200 | 241 | 0.98 | 147 | 40 | 173 | 45 | 195 | 63 | 275 | 93 | 2019-06-04 23:00 | 25.6 | 5 | 285 | B | 91 | 86 | 123 | 37 |  | 0.1 | 11.3 | 88.6 | 692.33 | 698.33 | 537.05 | 655.33 | 21 | 15 | 15 | 58 | [12 empty] | 713.33 | 6.27 | 0.55 | 0.23
153 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN148 | 1S-DL-YP-ETC-DLNR-2503-MAN148 | DOOR SANCHAR CGHS,PPG:ID | TG-MAN148A-1 | 19506200 | 630 | 200 | 241 | 0.98 | 149 | 67 | 278 | 48 | 200 | 34 | 143 | 118 | 2019-06-11 23:30 | 25.2 | 5.2 | 314 | R | 133 | 97 | 70 | 63 | 0.1 |  | 6.7 | 93.3 | 524.49 | 703.46 | 718.16 | 677.16 | 193.57 | 15 | 15 | 41.3 | [12 empty] | 718.46 | 1.14 | 0.52 | 0.24
154 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN148 | 1S-DL-YP-ETC-DLNR-2503-MAN148 | DOOR SANCHAR CGHS,PPG:ID | TG-MAN148A-2 | 19505425 | 630 | 200 | 240 | 0.97 | 125 | 32 | 135 | 45 | 187 | 48 | 199 | 59 | 2019-06-11 23:30 | 30.6 | 4.6 | 239 | Y | 74 | 113 | 114 | 40 | 0.1 | 0.1 | 4.8 | 95.1 | 718.46 | 679.17 | 706.16 | 718.46 |  | 39.29 | 39.29 | [13 empty] | 718.46 | 1.14 | 0.52 | 0.2
155 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN149 | 1S-DL-YP-ETC-DLNR-2503-MAN149 | SIDH CGHS, PPG:ID | TG-MAN149A-1 | 19505413 | 630 | 200 | 240 | 0.98 | 212 | 73 | 305 | 61 | 256 | 78 | 326 | 63 | 2019-06-01 01:00 | 31.6 | 2.6 | 386 | B | 100 | 87 | 113 | 26 | 0.1 | 0.1 | 1.9 | 97.9 | 684.48 | 673.18 | 641.48 | 670.48 | 34 | 45.3 | 45.3 | 48 |  |  | 0.3 | [9 empty] | 718.48 | 1.12 | 0.34 | 0.34
156 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN149 | 1S-DL-YP-ETC-DLNR-2503-MAN149 | SIDH CGHS, PPG:ID | TG-MAN149A-2 | 19506202 | 630 | 200 | 246 | 0.98 | 107 | 37 | 156 | 43 | 181 | 27 | 114 | 59 | 2019-06-29 23:00 | 25.6 | -0.8 | 189 | Y | 97 | 114 | 89 | 25 | 0.1 |  | 32.1 | 67.8 | 694.48 | 691.48 | 695.18 | 695.18 | 0.3 | 3.3 | 3.3 | [13 empty] | 695.18 | 24.42 | 0.48 | 0.17
157 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN150 | 1S-DL-YP-ETC-DLNR-2503-MAN150 | ARYANAGAR CGHS,S/S-1.PPG:ID | TG-MAN150A-1 | 19503045 | 630 | 200 | 238 | 0.98 | 150 | 58 | 248 | 43 | 187 | 49 | 209 | 54 | 2019-06-11 23:30 | 20.7 | 3.7 | 264 | R | 117 | 84 | 99 | 33 |  |  | 0.1 | 99.9 | 600 | 716 | 684 | 692 | 119.3 | 3.3 | 3.3 | 27.3 | [12 empty] | 719.3 | 0.3 | 0.51 | 0.24
158 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN150 | 1S-DL-YP-ETC-DLNR-2503-MAN150 | ARYANAGAR CGHS,S/S-1.PPG:ID | TG-MAN150A-2 | 19504181 | 630 | 200 | 238 | 0.98 | 144 | 50 | 206 | 53 | 221 | 41 | 170 | 46 | 2019-06-11 22:30 | 27.1 | 3.7 | 257 | Y | 91 | 114 | 94 | 23 |  |  | 2.4 | 97.6 | 699.58 | 605.22 | 715.22 | 694.52 | 19.24 | 114 | 114 | 24.3 | [12 empty] | 719.22 | 0.38 | 0.5 | 0.23
159 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN151 | 1S-DL-YP-ETC-DLNR-2503-MAN151 | ARYANAGAR CGHS,S/S-2,PPG:ID | TG-MAN151A-1 | 19502528 | 630 | 200 | 237 | 0.98 | 98 | 30 | 128 | 51 | 216 | 17 | 72 | 126 | 2019-06-02 23:00 | 19.3 | 2.3 | 240 | Y | 82 | 150 | 69 | 81 | 0.1 | 3.9 | 55.5 | 40.6 | 719.3 | 683 | 719.3 | 719.3 |  | 36.3 | 36.3 | [13 empty] | 719.3 | 0.3 | 0.53 | 0.16
160 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN151 | 1S-DL-YP-ETC-DLNR-2503-MAN151 | ARYANAGAR CGHS,S/S-2,PPG:ID | TG-MAN151A-2 | 19501994 | 630 | 200 | 237 | 0.97 | 158 | 48 | 213 | 80 | 356 | 30 | 132 | 196 | 2019-06-29 23:30 | 46.5 | 5.5 | 356 | Y | 94 | 140 | 67 | 73 |  | 0.1 | 36.1 | 63.8 | 682.01 | 337.38 | 719.31 | 649.31 | 37.3 | 381.53 | 381.53 | 70 | [12 empty] | 719.31 | 0.29 | 0.59 | 0.25
161 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN152 | 1S-DL-YP-ETC-DLNR-2503-MAN152 | ARYANAGAR CGHS,S/S-3,PPG:ID | TG-MAN152A-1 | 19501992 | 630 | 200 | 237 | 0.99 | 151 | 47 | 199 | 65 | 271 | 39 | 166 | 93 | 2019-06-01 23:00 | 16.1 | 0.9 | 283 | Y | 92 | 133 | 75 | 58 |  |  | 0.3 | 99.7 | 704.31 | 558 | 718.01 | 698.31 | 15 | 161.31 | 161.31 | 21 | [12 empty] | 719.31 | 0.29 | 0.49 | 0.24
162 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN152 | 1S-DL-YP-ETC-DLNR-2503-MAN152 | ARYANAGAR CGHS,S/S-3,PPG:ID | TG-MAN152A-2 | 19501693 | 630 | 200 | 236 | 0.99 | 177 | 55 | 252 | 48 | 219 | 73 | 335 | 103 | 2019-06-10 23:30 | 23 | 3.7 | 335 | B | 93 | 86 | 121 | 35 |  |  | 0.4 | 99.6 | 612.21 | 685.01 | 520.3 | 612.21 | 107.1 | 34.3 | 34.3 | 107.1 | [12 empty] | 719.31 | 0.29 | 0.49 | 0.28
163 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN154 | 1S-DL-YP-ETC-DLNR-2503-MAN154 | VIDHI CGHS, PPG:ID | TG-MAN154A-1 | 19505372 | 400 | 120 | 240 | 0.98 | 105 | 51 | 221 | 24 | 104 | 29 | 127 | 108 | 2019-06-30 23:00 | 23.3 | 1.6 | 227 | R | 132 | 88 | 79 | 53 |  | 0.1 | 13.6 | 86.3 | 319.29 | 524.26 | 519.59 | 469.59 | 231.57 | 27.3 | 27.3 | 81.57 | 0.3 | [11 empty] | 551.56 | 0.04 | 0.56 | 0.26
164 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN154 | 1S-DL-YP-ETC-DLNR-2503-MAN154 | VIDHI CGHS, PPG:ID | TG-MAN154A-2 | 19504827 | 400 | 120 | 239 | 0.97 | 95 | 34 | 140 | 36 | 150 | 25 | 103 | 43 | 2019-06-15 23:30 | 21.5 | 2.5 | 200 | Y | 88 | 141 | 71 | 70 |  |  | 12.2 | 87.8 | 699.56 | 438.59 | 717.26 | 663.26 | 20 | 280.57 | 280.57 | 56.3 | [12 empty] | 719.56 | 0.04 | 0.55 | 0.24
165 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN155 | 1S-DL-YP-ETC-DLNR-2503-MAN155 | KURMANCHAL CGHS, PPG:ID | TG-MAN155A-1 | 19505414 | 400 | 120 | 240 | 0.98 | 102 | 33 | 144 | 35 | 150 | 35 | 151 | 7 | 2019-06-30 23:30 | 24.1 | 1.4 | 175 | B | 115 | 75 | 110 | 40 | 0.1 |  | 5.7 | 94.2 | 631.41 | 667.41 | 657.41 | 678.11 | 87 | 51 | 51 | 40.3 | [12 empty] | 718.41 | 1.19 | 0.44 | 0.26
166 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN155 | 1S-DL-YP-ETC-DLNR-2503-MAN155 | KURMANCHAL CGHS, PPG:ID | TG-MAN155A-2 | 19505335 | 400 | 120 | 241 | 0.98 | 117 | 46 | 203 | 31 | 134 | 40 | 173 | 60 | 2019-06-11 | 19.7 | 2.4 | 203 | R | 111 | 81 | 108 | 30 | 0.1 |  | 2.9 | 97 | 532.48 | 663.15 | 538.18 | 579.18 | 162.57 | 32.3 | 32.3 | 116.27 | [12 empty] | 695.45 | 24.15 | 0.47 | 0.29
167 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN156 | 1S-DL-YP-ETC-DLNR-2503-MAN156 | INDRA PRASTHA CGHS, PPG:ID | TG-MAN156A-1 | 19505424 | 630 | 200 | 246 | 0.98 | 217 | 71 | 286 | 84 | 336 | 62 | 246 | 78 | 2019-06-12 01:00 | 43.8 | 7.4 | 357 | Y | 94 | 112 | 94 | 18 | 0.1 |  | 3 | 96.9 | 508.29 | 428.29 | 529.29 | 500.29 | 211.27 | 287.27 | 287.27 | 219.27 |  | 4 | [10 empty] | 719.56 | 0.04 | 0.5 | 0.34
168 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN156 | 1S-DL-YP-ETC-DLNR-2503-MAN156 | INDRA PRASTHA CGHS, PPG:ID | TG-MAN156A-2 | 19505371 | 400 | 120 | 240 | 0.98 | 154 | 62 | 272 | 53 | 233 | 38 | 167 | 93 | 2019-06-09 23:30 | 31.8 | 3.7 | 284 | Y | 100 | 124 | 75 | 49 | 0.1 | 0.3 | 13.1 | 86.4 | 336.29 | 231.59 | 584.26 | 390.29 | 356.27 | 439.27 | 439.27 | 329.27 | 27 | 48.3 | [10 empty] | 719.56 | 0.04 | 0.53 | 0.38
169 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN157 | 1S-DL-YP-ETC-DLNR-2503-MAN157 | SAGAR CGHS, PPG:ID | TG-MAN157A-1 | 19505411 | 400 | 120 | 245 | 0.98 | 147 | 44 | 178 | 44 | 181 | 59 | 238 | 59 | 2019-06-15 | 28.6 | 5.2 | 259 | B | 91 | 98 | 112 | 21 | 0.1 | 0.1 | 20.2 | 79.7 | 478.29 | 456.59 | 365.59 | 446.29 | 235.27 | 257.27 | 257.27 | 267.57 | 0.3 |  | 15 | [9 empty] | 714.26 | 5.34 | 0.52 | 0.37
170 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN157 | 1S-DL-YP-ETC-DLNR-2503-MAN157 | SAGAR CGHS, PPG:ID | TG-MAN157A-2 | 19506849 | 400 | 120 | 240 | 0.97 | 63 | 2 | 10 | 32 | 136 | 29 | 123 | 120 | 2019-06-30 | 13.9 | 1.4 | 152 | Y | 7 | 138 | 155 | 148 |  |  | 4.9 | 95.1 | 696.26 | 674.56 | 679.26 | 696.26 |  | 21.3 | 21.3 | [13 empty] | 696.26 | 23.34 | 0.47 | 0.16
171 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN158 | 1S-DL-YP-ETC-DLNR-2503-MAN158 | KAYMES VRINDAVAN,CGHS PPJ:ID | TG-MAN158A-1 | 19501245 | 400 | 120 | 240 | 0.97 | 40 | 16 | 70 | 18 | 79 | 7 | 31 | 44 | 2019-06-02 22:00 | 8.3 | 0.3 | 79 | Y | 101 | 122 | 76 | 46 |  |  | 1.1 | 98.9 | 719.56 | 719.56 | 719.56 | 719.56 | [16 empty] | 719.56 | 0.04 | 0.49 | 0.1
172 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN158 | 1S-DL-YP-ETC-DLNR-2503-MAN158 | KAYMES VRINDAVAN,CGHS PPJ:ID | TG-MAN158A-2 | 19506661 | 400 | 120 | 240 | 0.99 | 82 | 33 | 136 | 34 | 140 | 15 | 61 | 77 | 2019-06-12 | 11.8 | 0.7 | 164 | Y | 129 | 115 | 55 | 74 | 0.1 | 0.2 | 15.3 | 84.4 | 657.56 | 629.56 | 696.26 | 695.26 | 38.3 | 66.3 | 66.3 | 1 | [12 empty] | 696.26 | 23.34 | 0.5 | 0.2
173 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN159 | 1S-DL-YP-ETC-DLNR-2503-MAN159 | NDMC (VIDYUT NIKUNJ),CGHS PPG:ID | TG-MAN159A-1 | 19503056 | 400 | 120 | 245 | 0.97 | 80 | 46 | 190 | 19 | 78 | 14 | 58 | 122 | 2019-06-02 23:30 | 17.7 | 2.2 | 212 | R | 154 | 74 | 71 | 83 |  | 0.1 | 24.8 | 75.1 | 499 | 719.57 | 719.57 | 719.57 | 220.57 | [15 empty] | 719.57 | 0.03 | 0.55 | 0.2
174 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN159 | 1S-DL-YP-ETC-DLNR-2503-MAN159 | NDMC (VIDYUT NIKUNJ),CGHS PPG:ID | TG-MAN159A-2 | 19504178 | 400 | 120 | 245 | 0.98 | 89 | 29 | 115 | 33 | 133 | 27 | 107 | 23 | 2019-06-13 23:00 | 21 | 1.7 | 151 | Y | 94 | 110 | 97 | 16 |  |  | 0.7 | 99.3 | 679.26 | 647.56 | 683.26 | 685.26 | 16.3 | 48 | 48 | 10.3 | [12 empty] | 695.56 | 0.04 | 0.5 | 0.22
175 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN160 | 1S-DL-YP-ETC-DLNR-2503-MAN160 | VIJAY LAXMI CGHS, PPG:ID | TG-MAN160A-1 | 19501922 | 400 | 120 | 246 | 0.97 | 67 | 20 | 83 | 33 | 136 | 14 | 57 | 70 | 2019-06-30 | 13.8 | 1.4 | 138 | Y | 91 | 129 | 81 | 48 |  |  | 0.2 | 99.8 | 719.04 | 707.04 | 719.04 | 719.04 |  | 12 | 12 | [13 empty] | 719.04 | 0.56 | 0.48 | 0.17
176 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN160 | 1S-DL-YP-ETC-DLNR-2503-MAN160 | VIJAY LAXMI CGHS, PPG:ID | TG-MAN160A-2 | 19501986 | 400 | 120 | 246 | 0.98 | 89 | 36 | 152 | 24 | 102 | 29 | 119 | 44 | 2019-06-11 23:30 | 17.4 | 2.2 | 168 | R | 118 | 87 | 95 | 31 |  |  | 0.8 | 99.2 | 627.35 | 718.35 | 711.35 | 708.35 | 91.3 | 0.3 | 0.3 | 10.3 | [12 empty] | 719.05 | 0.55 | 0.48 | 0.22
177 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN161 | 1S-DL-YP-ETC-DLNR-2503-MAN161 | JAI APARTMENT, JAI SANTOSHI PPG:ID | TG-MAN161A-1 | 19502529 | 630 | 200 | 237 | 0.98 | 157 | 65 | 266 | 31 | 129 | 61 | 249 | 129 | 2019-06-03 | 26.7 | 3.7 | 293 | R | 119 | 62 | 119 | 57 |  |  |  | 100 | 534.32 | 719.3 | 565.3 | 656.02 | 184.58 |  |  | 63.28 | [12 empty] | 719.3 | 0.3 | 0.53 | 0.25
178 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN161 | 1S-DL-YP-ETC-DLNR-2503-MAN161 | JAI APARTMENT, JAI SANTOSHI PPG:ID | TG-MAN161A-2 | 19504324 | 630 | 200 | 237 | 0.98 | 145 | 37 | 164 | 44 | 193 | 63 | 279 | 103 | 2019-06-30 | 26.7 | 2.3 | 284 | B | 87 | 82 | 131 | 49 |  |  | 0.4 | 99.6 | 712.01 | 709.31 | 552.3 | 687.01 | 7.3 | 10 | 10 | 32.3 | [12 empty] | 719.31 | 0.29 | 0.51 | 0.23
179 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN162 | 1S-DL-YP-ETC-DLNR-2503-MAN162 | HIMVARSHA CGHS, PPG:ID | TG-MAN162A-1 | 19501891 | 630 | 200 | 246 | 0.97 | 146 | 53 | 212 | 50 | 205 | 43 | 178 | 31 | 2019-06-13 23:00 | 32.7 | 5.1 | 247 | R | 116 | 90 | 94 | 26 | 99.3 | 0.7 |  |  | 595.58 | 700.58 | 703.28 | 686.58 | 124 | 19 | 19 | 33 | [12 empty] | 719.58 | 0.02 | 0.54 | 0.23
180 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN162 | 1S-DL-YP-ETC-DLNR-2503-MAN162 | HIMVARSHA CGHS, PPG:ID | TG-MAN162A-2 | 19506486 | 630 | 200 | 245 | 0.97 | 149 | 55 | 232 | 50 | 213 | 44 | 184 | 42 | 2019-06-30 00:30 | 27.2 | 5.6 | 287 | R | 116 | 78 | 106 | 38 | 0.1 | 2.1 | 36.9 | 60.9 | 609.3 | 715.28 | 640 | 680.58 | 110.28 | 4.3 | 4.3 | 39 | [12 empty] | 719.58 | 0.02 | 0.51 | 0.24
181 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN163 | 1S-DL-YP-ETC-DLNR-2503-MAN163 | SHIVALIK CGHS, PPG:ID | TG-MAN163A-1 | 19501471 | 630 | 200 | 251 | 0.98 | 190 | 74 | 310 | 39 | 164 | 77 | 319 | 151 | 2019-06-29 23:30 | 33.1 | 4.1 | 351 | B | 117 | 66 | 116 | 51 |  |  | 8.8 | 91.2 | 479.3 | 718.58 | 480.3 | 554 | 240.28 | 1 | 1 | 165.58 | [12 empty] | 719.58 | 0.02 | 0.5 | 0.3
182 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN163 | 1S-DL-YP-ETC-DLNR-2503-MAN163 | SHIVALIK CGHS, PPG:ID | TG-MAN163A-2 | 19502549 | 630 | 200 | 246 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [8 empty] | 100 | 719.58 | 719.58 | 719.58 | 719.58 | [16 empty] | 719.58 | 0.02 |  | 0
183 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN164 | 1S-DL-YP-ETC-DLNR-2503-MAN164 | NEETHI (NIDHI) CGHS, PPG:ID | TG-MAN164A-1 | 19501925 | 630 | 200 | 240 | 0.98 | 195 | 76 | 339 | 68 | 303 | 51 | 229 | 98 | 2019-06-30 23:30 | 32.7 | 5.1 | 339 | R | 115 | 93 | 92 | 23 |  |  | 0.1 | 99.9 | 493.59 | 583.46 | 618 | 563.46 | 225.31 | 135.44 | 135.44 | 155.44 | [12 empty] | 719.3 | 0.3 | 0.48 | 0.31
184 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN165 | 1S-DL-YP-ETC-DLNR-2503-MAN165 | MOON LIGHT CGHS, PPG:ID | TG-MAN165A-1 | 19501970 | 630 | 200 | 239 | 0.97 | 106 | 37 | 159 | 39 | 165 | 30 | 127 | 36 | 2019-06-11 00:30 | 24.4 | 5.1 | 184 | R | 118 | 102 | 80 | 38 | 0.2 | 16.7 | 55.3 | 27.8 | 718.28 | 719.58 | 719.58 | 719.58 | 1.3 | [15 empty] | 719.58 | 0.02 | 0.55 | 0.17
185 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN165 | 1S-DL-YP-ETC-DLNR-2503-MAN165 | MOON LIGHT CGHS, PPG:ID | TG-MAN165A-2 | 19506888 | 630 | 200 | 241 | 0.98 | 79 | 4 | 18 | 38 | 162 | 37 | 159 | 143 | 2019-06-01 23:30 | 21.2 | 2 | 206 | B | 11 | 137 | 152 | 141 | 0.1 |  | 3.3 | 96.6 | 710.28 | 710.28 | 705.58 | 710.28 | [16 empty] | 710.28 | 9.32 | 0.49 | 0.13
186 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN166 | 1S-DL-YP-ETC-DLNR-2503-MAN166 | SILVEROAK CGHS, PPG:ID | TG-MAN166A-1 | 19500773 | 630 | 200 | 245.3285 | 0.96731 | 136.3344 | 41.5963 | 171.4251 | 45.6537 | 186.9062 | 49.0844 | 200.0097 | 24.7835 | 2019-06-02 00:30 | [15 empty] | 709 |  |  |  | 11 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.53797 | 0.2164
187 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN167 | 1S-DL-YP-ETC-DLNR-2503-MAN167 | AZAD APARTMENT, PPG:ID | TG-MAN167A-1 | 19506727 | 630 | 200 | 246 | 0.98 | 177 | 78 | 309 | 49 | 196 | 50 | 210 | 106 | 2019-06-29 04:00 | 80.2 | 0.8 | 309 | R | 99 | 133 | 68 | 65 | 100 |  |  |  | 691.01 | 642.59 | 716.29 | 715.29 | 26.58 | 75 | 75 | 2.3 | [12 empty] | 717.59 | 2.01 | 0.36 | 0.28
188 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN167 | 1S-DL-YP-ETC-DLNR-2503-MAN167 | AZAD APARTMENT, PPG:ID | TG-MAN167A-2 | 19502514 | 630 | 200 | 246 | 0.95 | 97 | 26 | 106 | 37 | 154 | 34 | 138 | 43 | 2019-06-12 00:30 | 34 | 1.8 | 215 | Y | 82 | 156 | 62 | 94 |  |  | 1.4 | 98.6 | 717.13 | 703.13 | 717.13 | 717.13 |  | 14 | 14 | [13 empty] | 717.13 | 2.47 | 0.4 | 0.15
189 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN203 | 1S-DL-YP-ETC-DLNR-2503-MAN203 | SHIVANI CGHS, PPG:ID | TG-MAN203A-1 | 19505990 | 400 | 120 | 253 | 0.97 | 70 | 17 | 69 | 23 | 95 | 30 | 122 | 46 | 2019-06-05 00:30 | 17.8 | 2.2 | 128 | B | 73 | 99 | 127 | 54 | 0.1 | 0.2 | 42.3 | 57.3 | 715 | 715 | 699 | 715 | [16 empty] | 715 | 5 | 0.49 | 0.17
190 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN203 | 1S-DL-YP-ETC-DLNR-2503-MAN203 | SHIVANI CGHS, PPG:ID | TG-MAN203A-2 | 19501879 | 400 | 120 | 239 | 0.98 | 66 | 16 | 71 | 32 | 141 | 17 | 74 | 69 | 2019-06-01 23:00 | 11 | 0.3 | 150 | Y | 72 | 148 | 80 | 76 |  |  | 16.1 | 83.9 | 719.3 | 706.3 | 719.3 | 719.3 |  | 13 | 13 | [13 empty] | 719.3 | 0.3 | 0.48 | 0.16
191 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN209 | 1S-DL-YP-ETC-DLNR-2503-MAN209 | MILAN VIH SS I:ID | TG-MAN209A-1 | 19502511 | 630 | 200 | 245 | 0.98 | 194 | 58 | 237 | 69 | 281 | 67 | 273 | 41 | 2019-06-16 01:00 | 41.9 | 2.8 | 301 | Y | 90 | 105 | 106 | 16 |  |  | 0.6 | 99.4 | 600.01 | 522.04 | 501.04 | 557.01 | 119.28 | 197.25 | 197.25 | 162.28 | [12 empty] | 719.29 | 0.31 | 0.52 | 0.31
192 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN209 | 1S-DL-YP-ETC-DLNR-2503-MAN209 | MILAN VIH SS I:ID | TG-MAN209A-2 | 19502544 | 630 | 200 | 239.4878 | 0.98543 | 95.0804 | 38.8612 | 166.4646 | 19.1329 | 81.5554 | 37.0864 | 159.3332 | 81.5776 | 2019-06-30 00:30 | [15 empty] | 720 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.5061 | 0.15092
193 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN210 | 1S-DL-YP-ETC-DLNR-2503-MAN210 | MILAN VIH SS I:ID | TG-MAN210A-1 | 19506900 | 630 | 200 | 246 | 0.97 | 149 | 40 | 164 | 49 | 203 | 61 | 252 | 77 | 2019-06-28 23:30 | 27 | -31.2 | 278 | B | 85 | 96 | 119 | 34 | 0.1 |  | 3 | 96.8 | 707.29 | 702.59 | 667.59 | 697.29 | 0.3 | 5 | 5 | 10.3 | [12 empty] | 707.59 | 12.01 | 0.2 | 0.24
194 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN210 | 1S-DL-YP-ETC-DLNR-2503-MAN210 | MILAN VIH SS II:ID | TG-MAN210A-2 | 19506724 | 630 | 200 | 240 | 0.96 | 230 | 58 | 249 | 98 | 420 | 74 | 315 | 150 | 2019-06-30 20:30 | 91.2 | 3.8 | 420 | Y | 78 | 139 | 83 | 61 |  | 0.1 | 5.4 | 94.5 | 604.3 | 186.05 | 589.3 | 465.32 | 91.3 | 502.55 | 502.55 | 230.28 |  | 7 | [10 empty] | 696 | 24 | 0.48 | 0.37
195 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN211 | 1S-DL-YP-ETC-DLNR-2503-MAN211 | SUDARSHAN,PPG.:ID | TG-MAN211A-1 | 19501346 | 630 | 200 | 246 | 0.97 | 120 | 43 | 173 | 37 | 148 | 40 | 160 | 22 | 2019-06-10 23:30 | 27.6 | 2.3 | 202 | R | 119 | 92 | 89 | 30 |  |  | 3.1 | 96.9 | 689.56 | 719.56 | 718.56 | 719.56 | 30 | [15 empty] | 719.56 | 0.04 | 0.51 | 0.19
196 | 2019-06-16 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN211 | 1S-DL-YP-ETC-DLNR-2503-MAN211 | SUDARSHAN,PPG.:ID | TG-MAN211A-2 | 19501291 | 630 | 200 | 247 | 0.98 | 173 | 89 | 363 | 38 | 154 | 46 | 188 | 195 | 2019-06-30 23:30 | 26.2 | 2.3 | 363 | R | 148 | 64 | 88 | 84 |  |  | 0.4 | 99.6 | 227.3 | 359.57 | 345.57 | 328.57 | 131.27 |  |  | 31 | 1 | [11 empty] | 359.57 | 0.03 | 0.45 | 0.27
197 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN216 | 1S-DL-YP-ETC-DLNR-2503-MAN216 | DTC DEPOT GAZIPUR:ID | TG-MAN216A-1 | 19502566 | 100 | 40 | 245 | 0.96 | 85 | 27 | 109 | 22 | 90 | 36 | 151 | 54 | 2019-06-08 00:30 | 40.3 | -2.7 | 151 | B | 109 | 65 | 127 | 62 |  |  | 16 | 84 | 1 | 16 | 0.3 | 0.3 | 18.3 | 532.03 | 532.03 | 37.59 | 673.3 | 170.27 | 616.3 | 679.31 | 25.3 |  | 94.3 | 0.3 |  |  | 1 |  | 718.3 | 1.3 | 0.63 | 0.85
198 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN234 | 1S-DL-YP-ETC-DLNR-2503-MAN234 | AZAD APPTT. S/S NO. 2 CGHS PPG:ID | TG-MAN234A-2 | 19501219 | 630 | 200 | 245 | 0.98 | 183 | 57 | 233 | 56 | 229 | 70 | 287 | 56 | 2019-06-12 01:00 | 37.3 | 6.4 | 306 | B | 100 | 87 | 113 | 26 |  |  | 4.3 | 95.7 | 542.32 | 557.32 | 425.34 | 531.02 | 176.58 | 161.58 | 161.58 | 188.28 | [12 empty] | 719.3 | 0.3 | 0.58 | 0.29
199 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN237 | 1S-DL-YP-ETC-DLNR-2503-MAN237 | KANCHAN CHANGA APPT:ID | TG-MAN237A-1 | 19502565 | 400 | 120 | 239 | 0.98 | 105 | 49 | 214 | 18 | 78 | 39 | 171 | 121 | 2019-06-30 23:30 | 19.9 | 1.4 | 240 | B | 105 | 64 | 132 | 68 | 2.6 | 8.3 | 58.8 | 30.2 | 631.3 | 719.58 | 519 | 651 | 88.28 |  |  | 68.58 |  |  | 1 | [9 empty] | 719.58 | 0.02 | 0.47 | 0.26
200 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN237 | 1S-DL-YP-ETC-DLNR-2503-MAN237 | KANCHAN CHANGA APPT:ID | TG-MAN237A-2 | 19502952 | 400 | 120 | 240 | 0.96 | 73 | 20 | 87 | 24 | 107 | 29 | 127 | 35 | 2019-06-08 23:00 | 22.4 | 1.9 | 129 | B | 80 | 99 | 121 | 41 |  |  | 0.1 | 99.9 | 719.58 | 719.58 | 716.58 | 719.58 | [16 empty] | 719.58 | 0.02 | 0.5 | 0.18
201 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN238 | 1S-DL-YP-ETC-DLNR-2503-MAN238 | CNG PETROL PUMP:PM | TG-MAN238A-1 | 19505950 | 630 | 200 | 255 | 0.98 | 454 | 152 | 622 | 193 | 778 | 109 | 440 | 293 | 2019-06-12 10:30 | 89 | -3.4 | 778 | Y | 126 | 76 | 98 | 50 |  |  | 4.3 | 95.7 | 712.26 | 713.26 | 713.26 | 713.26 | 1 |  |  |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 | [6 empty] | 713.56 | 6.04 | 0.05 | 0.72
202 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN239 | 1S-DL-YP-ETC-DLNR-2503-MAN239 | S/STN.NO-4, GAZIPUR:ID | TG-MAN239A-1 | 19506125 | 630 | 200 | 245 | 0.96 | 353 | 121 | 493 | 119 | 492 | 114 | 468 | 24 | 2019-06-27 18:30 | 122.8 | 13.4 | 503 | B | 107 | 97 | 96 | 11 | 0.1 | 1 | 40.6 | 58.2 | 70 | 207 | 225.3 | 160.3 | 505 | 384 | 384 | 419.3 | 139.3 | 123.3 | 149.3 | 134.3 | [8 empty] | 714.3 | 5.3 | 0.52 | 0.56
203 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN239 | 1S-DL-YP-ETC-DLNR-2503-MAN239 | S/STN.NO-4, GAZIPUR:ID | TG-MAN239A-2 | 19505423 | 630 | 200 | 246.315 | 0.97052 | 224.4098 | 93.8674 | 392.7011 | 42.7425 | 177.79 | 87.8 | 367.3179 | 203.4109 | 2019-06-07 11:30 | [15 empty] | 618.5 |  |  |  | 101.5 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.22987 | 0.35621
204 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN240 | 1S-DL-YP-ETC-DLNR-2503-MAN240 | MILAN VIHAR SUB STN 3:ID | TG-MAN240A-1 | 19502513 | 630 | 200 | 240 | 0.98 | 154 | 73 | 302 | 41 | 172 | 40 | 172 | 130 | 2019-06-12 00:30 | 28.1 | 2.8 | 313 | R | 122 | 89 | 89 | 33 | 10.5 | 89.4 | 0.1 |  | 591.02 | 715.3 | 716 | 689 | 128.28 | 4 | 4 | 30.3 | [12 empty] | 719.3 | 0.3 | 0.49 | 0.24
205 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN240 | 1S-DL-YP-ETC-DLNR-2503-MAN240 | MILAN VIHAR SUB STN 3:ID | TG-MAN240A-2 | 19502515 | 630 | 200 | 246 | 0.97 | 122 | 27 | 111 | 54 | 224 | 41 | 171 | 98 | 2019-06-02 23:30 | 26.7 | 4.1 | 232 | Y | 81 | 131 | 88 | 50 |  | 0.2 | 11.6 | 88.2 | 719.3 | 629.32 | 719 | 719.3 |  | 89.58 | 89.58 | [13 empty] | 719.3 | 0.3 | 0.56 | 0.19
206 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN241 | 1S-DL-YP-ETC-DLNR-2503-MAN241 | MILAN VIHAR SUB STN 4:ID | TG-MAN241A-1 | 19502567 | 630 | 200 | 240 | 0.99 | 143 | 56 | 243 | 39 | 169 | 47 | 206 | 64 | 2019-06-30 23:30 | 17.5 | 1.8 | 251 | R | 96 | 103 | 101 | 7 |  |  | 4.8 | 95.2 | 672 | 708.3 | 711 | 710 | 47.3 | 11 | 11 | 9.3 | [12 empty] | 719.3 | 0.3 | 0.5 | 0.23
207 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN241 | 1S-DL-YP-ETC-DLNR-2503-MAN241 | MILAN VIHAR SUB STN 4:ID | TG-MAN241A-2 | 19506912 | 630 | 200 | 245.7263 | 0.93 | 193.6237 | 68.4655 | 290.6004 | 58.6941 | 247.3831 | 66.4641 | 280.2265 | 39.0771 | 2019-06-30 23:00 | [15 empty] | 652.5 |  |  |  | 67.5 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.34637 | 0.30734
208 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN246 | 1S-DL-YP-ETC-DLNR-2503-MAN246 | STORM W/PUMP STN. NR. MAYFAIR IP EXT.:ID | TG-MAN246A-1 | 19506123 | 400 | 120 | 242 | 0.94 | 138 | 46 | 188 | 45 | 181 | 47 | 190 | 8 | 2019-06-23 18:00 | 117.4 | -21.2 | 221 | R | 104 | 88 | 109 | 21 | 45.5 | 6 | 30.3 | 18.3 | 646.58 | 664.58 | 637.58 | 657.28 | 57 | 39 | 39 | 46.3 | [12 empty] | 708.58 | 11.02 | 0.2 | 0.34
209 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN250 | 1S-DL-YP-ETC-DLNR-2503-MAN250 | INSTITUTIONAL AREA S/STN NO-1 | TG-MAN250A-1 | 19504473 | 630 | 200 | 248 | 0.99 | 81 | 28 | 117 | 27 | 111 | 25 | 102 | 13 | 2019-06-09 16:00 | 17 | -2.8 | 117 | R | 116 | 110 | 74 | 42 |  |  | 1.4 | 98.6 | 719.56 | 719.56 | 719.56 | 719.56 | [16 empty] | 719.56 | 0.04 | 0.32 | 0.13
210 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN251 | 1S-DL-YP-ETC-DLNR-2503-MAN251 | INSTITUTIONAL AREA S/STN NO-3 | TG-MAN251A-1 | 19504487 | 630 | 200 | 247 | 0.95 | 244 | 73 | 295 | 79 | 319 | 93 | 377 | 73 | 2019-06-28 09:30 | 52 | -22.1 | 395 | B | 89 | 86 | 126 | 40 |  |  | 19.9 | 80.1 | 676.57 | 682.27 | 639.57 | 669.27 | 42.3 | 37.3 | 37.3 | 50.3 | 0.3 |  | 12 | [9 empty] | 719.57 | 0.03 | 0.23 | 0.39
211 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN252 | 1S-DL-YP-ETC-DLNR-2503-MAN252 | S/STN NO-10, CGHS, PPG | TG-MAN252A-1 | 19504304 | 630 | 200 | 241 | 0.98 | 113 | 45 | 191 | 39 | 167 | 29 | 120 | 62 | 2019-06-10 14:30 | 31.3 | -7.8 | 208 | R | 95 | 112 | 93 | 19 |  | 27.7 | 72.2 | 0.1 | 700.2 | 711.2 | 719.2 | 719.2 | 19 | 8 | 8 | [13 empty] | 719.2 | 0.4 | 0.56 | 0.18
212 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN252 | 1S-DL-YP-ETC-DLNR-2503-MAN252 | S/STN NO-10, CGHS, PPG | TG-MAN252A-2 | 19504305 | 630 | 200 | 236 | 0.97 | 714 | 210 | 953 | 276 | 1274 | 227 | 1037 | 289 | 2019-06-30 23:30 | 155.5 | 81.4 | 1274 | Y | 98 | 108 | 94 | 14 |  |  | 8.1 | 91.9 | [8 empty] | 468.21 | 353.2 | 513.51 | 442.21 | 231 | 257.31 | 201 | 255 | 20 | 108.3 | 4.3 | 22 | 719.21 | 0.39 | 0.68 | 1.13
213 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN277 | 1S-DL-YP-ETC-DLNR-2503-MAN277 | Takshila S/Stn Mtnl I.P. Extension | TG-MAN277A-1 | 19504577 | 100 | 40 | 241 | 0.98 | 55 | 15 | 63 | 14 | 62 | 26 | 113 | 50 | 2019-06-26 15:00 | 19.2 | -2.2 | 113 | B | 92 | 63 | 145 | 82 |  |  | 0.4 | 99.6 | 0.17 | 415.31 | 0.17 | 0.17 | 683.1 | 302.55 | 302.55 | 601.44 | 35.59 | 1 | 703.39 | 117.25 | [8 empty] | 719.26 | 0.34 | 0.6 | 0.55
214 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN278 | 1S-DL-YP-ETC-DLNR-2503-MAN278 | New Gazi Pur Vag Mkt.S/Stn | TG-MAN278A-1 | 19505922 | 630 | 200 | 247 | 0.96 | 307 | 125 | 512 | 54 | 220 | 128 | 522 | 297 | 2019-06-21 20:30 | 113.2 | 27.6 | 731 | B | 141 | 18 | 141 | 123 | 0.1 | 0.4 | 17.1 | 82.3 | 0.3 | 628 | 1 | 5.3 | 51.3 | 85.51 | 85.51 | 588 | 661.21 |  | 624.55 | 120.21 | 0.3 |  | 1 | [5 empty] | 713.51 | 6.09 | 0.73 | 0.49
215 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN278 | 1S-DL-YP-ETC-DLNR-2503-MAN278 | New Gazi Pur Vag Mkt.S/Stn | TG-MAN278A-2 | 19506322 | 630 | 200 | 250 | 0.99 | 65 | 31 | 123 | 15 | 60 | 19 | 76 | 57 | 2019-06-24 12:00 | 16 | 1.6 | 125 | B | 94 | 89 | 117 | 28 |  | 0.1 | 9.7 | 90.1 | 713.51 | 713.51 | 713.51 | 713.51 | [16 empty] | 713.51 | 6.09 | 0.66 | 0.1
216 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN292 | 1S-DL-YP-ETC-DLNR-2503-MAN292 | GAZIPUR PARK NEAR ASHOK DAIRY STN:OD | TG-MAN292A-1 | 19506443 | 990 | 320 | 247 | 0.99 | 868 | 265 | 1058 | 276 | 1113 | 328 | 1327 | 247 | 2019-06-29 16:00 | 230.7 | -15 | 1438 | B | 95 | 90 | 115 | 25 |  | 0.2 | 21.8 | 77.9 | [5 empty] | 5.34 | 5.34 |  | 679.21 | 682.31 | 408.21 | 659.18 | 11.44 | 3 | 269.44 | 31.47 |  |  | 13 |  | 691.05 | 28.55 | 0.78 | 0.88
217 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN298 | 1S-DL-YP-ETC-DLNR-2503-MAN298 | DCP OFFICE MANDAWALI | TG-MAN298A-1 | 19506362 | 400 | 120 | 248 | 0.97 | 69 | 30 | 120 | 20 | 82 | 20 | 79 | 40 | 2019-06-10 | 16.6 | 0.6 | 140 | R | 122 | 93 | 85 | 37 |  | 0.1 | 16.7 | 83.1 | 650.37 | 713.37 | 713.37 | 713.37 | 63 | [15 empty] | 713.37 | 6.23 | 0.54 | 0.17
218 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR027 | 1S-DL-YP-ETC-DLNR-2502-PVR027 | S/STN. NO.2 F.I.E., PPG:ID | TG-PVR027A-1 | 19505240 | 630 | 200 | 248 | 0.98 | 495 | 171 | 676 | 148 | 585 | 176 | 696 | 103 | 2019-06-29 17:30 | 165.2 | -68.2 | 928 | B | 100 | 89 | 111 | 22 |  | 0.1 | 3 | 96.9 | 367.14 | 376.44 | 345.14 | 364.44 | 85.19 | 96.49 | 96.49 | 82.19 | 252.32 | 232.02 | 260.32 | 258.32 | 0.3 |  | 9 |  |  |  | 0.3 |  | 705.35 | 14.25 | 0.4 | 0.79
219 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR027 | 1S-DL-YP-ETC-DLNR-2502-PVR027 | S/STN. NO.2 F.I.E., PPG:ID | TG-PVR027A-2 | 19500599 | 630 | 200 | 248 | 0.96 | 469 | 153 | 671 | 171 | 750 | 145 | 636 | 101 | 2019-06-10 12:00 | 116.4 | -44.2 | 755 | Y | 98 | 109 | 93 | 16 |  |  | 0.1 | 99.9 | 426.02 | 418.02 | 430.02 | 424.32 | 79.3 | 77 | 77 | 83.3 | 213.32 | 223.02 | 189.02 | 211.02 |  | 1 | [6 empty] | 719.04 | 0.56 | 0.31 | 0.74
220 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR028 | 1S-DL-YP-ETC-DLNR-2502-PVR028 | S/STN. NO.3 F.I.E., PPG:ID | TG-PVR028A-1 | 19502419 | 990 | 320 | 249 | 0.98 | 526 | 172 | 714 | 176 | 735 | 178 | 739 | 24 | 2019-06-15 10:30 | 146.5 | -30.2 | 765 | Y | 100 | 104 | 96 | 8 |  |  | 45.9 | 54.1 | 400.35 | 385.12 | 406.05 | 398.05 | 157.54 | 175.39 | 175.39 | 163.24 | 154.51 | 152.29 | 144.51 | 151.51 | [8 empty] | 713.2 | 6.4 | 0.43 | 0.53
221 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR029 | 1S-DL-YP-ETC-DLNR-2502-PVR029 | S/STN. NO.4 F.I.E., PPG:ID | TG-PVR029A-1 | 19504845 | 630 | 200 | 249 | 0.93 | 449 | 148 | 611 | 153 | 631 | 148 | 609 | 21 | 2019-06-26 15:30 | 135.7 | -45.5 | 666 | Y | 96 | 104 | 100 | 8 |  |  | 6.9 | 93.1 | 349.29 | 343.59 | 353.29 | 349.29 | 68.3 | 63 | 63 | 61 | 283.29 | 294.29 | 289.29 | 290.59 | [8 empty] | 701.28 | 18.32 | 0.42 | 0.71
222 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR030 | 1S-DL-YP-ETC-DLNR-2502-PVR030 | S/STN. NO.5 F.I.E., PPG:ID | TG-PVR030A-1 | 19500815 | 630 | 200 | 250 | 0.72 | 134 | 50 | 203 | 59 | 242 | 26 | 108 | 119 | 2019-06-27 11:30 | 34.5 | -46.9 | 250 | Y | 111 | 111 | 78 | 33 |  | 0.1 | 12.8 | 87.2 | 677.21 | 585.51 | 719.51 | 705.21 | 42.3 | 134 | 134 | 14.3 | [12 empty] | 719.51 | 0.09 | 0.43 | 0.21
223 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR031 | 1S-DL-YP-ETC-DLNR-2502-PVR031 | S/STN. NO.6 F.I.E., PPG:ID | TG-PVR031A-1 | 19506890 | 990 | 320 | 250 | 0.98 | 629 | 211 | 853 | 208 | 847 | 210 | 855 | 7 | 2019-06-26 10:30 | 196.2 | -104.3 | 901 | R | 98 | 94 | 108 | 14 | 0.1 | 0.1 | 18.7 | 81 | 387.53 | 397.53 | 368.53 | 384.53 | 109.29 | 101.59 | 101.59 | 110.59 | 206.56 | 204.26 | 214.26 | 208.26 | [8 empty] | 704.18 | 15.42 | 0.39 | 0.64
224 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR032 | 1S-DL-YP-ETC-DLNR-2502-PVR032 | S/STN. NO.7 F.I.E., PPG:ID | TG-PVR032A-1 | 19505236 | 990 | 300 | 249 | 0.98 | 841 | 220 | 923 | 306 | 1300 | 316 | 1328 | 392 | 2019-06-20 14:30 | 241.5 | -59.7 | 1328 | B | 96 | 102 | 101 | 6 |  |  | 10.1 | 89.9 | 335.01 | 301.08 | 247.08 | 301.08 | 117.58 | 147.51 | 147.51 | 149.21 | 232.19 | 226.51 | 237.21 | 234.51 | 2.3 | 11.58 | 0.28 | 2.28 |  |  |  |  | 687.48 | 32.12 | 0.39 | 0.85
225 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR032 | 1S-DL-YP-ETC-DLNR-2502-PVR032 | S/STN. NO.7 F.I.E., PPG:ID | TG-PVR032A-2 | 19506697 | 630 | 200 | 244 | 0.86 | 426 | 150 | 621 | 142 | 593 | 134 | 554 | 58 | 2019-06-29 12:00 | 164.2 | -91.4 | 621 | R | 103 | 99 | 98 | 5 |  | 0.1 | 14.7 | 85.2 | 409.53 | 421.53 | 424.53 | 413.53 | 152.56 | 132.59 | 132.59 | 149.56 | 156.17 | 164.14 | 139.47 | 155.17 | [8 empty] | 719.06 | 0.54 | 0.34 | 0.68
226 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR033 | 1S-DL-YP-ETC-DLNR-2502-PVR033 | S/STN. NO.10 F.I.E., PPG:ID | TG-PVR033A-1 | 19504880 | 630 | 200 | 250 | 0.97 | 301 | 95 | 392 | 110 | 448 | 97 | 396 | 54 | 2019-06-26 12:00 | 92.9 | -6.9 | 463 | Y | 94 | 116 | 90 | 26 |  |  | 0.4 | 99.6 | 451.55 | 397.27 | 443.57 | 432.57 | 243.28 | 185.56 | 185.56 | 224.26 | 24.3 | 136.3 | 26 | 62.3 | [8 empty] | 719.53 | 0.07 | 0.35 | 0.48
227 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR034 | 1S-DL-YP-ETC-DLNR-2502-PVR034 | S/STN. NO.8 F.I.E., PPG:ID | TG-PVR034A-1 | 19505921 | 630 | 200 | 248 | 0.99 | 577 | 191 | 806 | 190 | 798 | 195 | 820 | 19 | 2019-06-12 15:00 | 170 | -23.4 | 847 | Y | 102 | 96 | 102 | 6 |  | 0.1 | 3.4 | 96.5 | 41.57 | 67.27 | 26 | 40.57 | 334.3 | 328.56 | 328.56 | 336.56 | 266.55 | 270.29 | 299.59 | 282.59 | 61 | 37.3 | 42 | 43.3 |  |  |  |  | 704.22 | 15.38 | 0.48 | 0.92
228 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR034 | 1S-DL-YP-ETC-DLNR-2502-PVR034 | S/STN. NO.8 F.I.E., PPG:ID | TG-PVR034A-2 | 19500757 | 630 | 200 | 249 | 0.85 | 468 | 145 | 577 | 167 | 667 | 155 | 620 | 78 | 2019-06-24 15:30 | 106.3 | -136.6 | 715 | Y | 93 | 104 | 103 | 11 |  |  | 0.6 | 99.4 | 360.23 | 321.53 | 296.57 | 329.23 | 137.58 | 156.58 | 156.58 | 157.58 | 221.3 | 240.3 | 230 | 232.3 |  | 0.3 | [6 empty] | 719.51 | 0.09 | 0.43 | 0.74
229 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR034 | 1S-DL-YP-ETC-DLNR-2502-PVR034 | S/STN. NO.8 F.I.E., PPG:ID | TG-PVR034A-3 | 19505812 | 990 | 320 | 242 | 0.97 | 860 | 278 | 1148 | 290 | 1200 | 292 | 1211 | 59 | 2019-06-03 18:00 | 355.8 | -84.2 | 1236 | Y | 97 | 104 | 99 | 7 |  |  | 1.3 | 98.7 | 91.59 | 87.29 | 101.59 | 91.29 | 298.53 | 256.53 | 256.53 | 286.23 | 312 | 355.3 | 315.3 | 325 | 2.3 | 5.3 | 5 | 2.3 |  |  |  |  | 705.22 | 14.38 | 0.46 | 0.87
230 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR035 | 1S-DL-YP-ETC-DLNR-2502-PVR035 | S/STN. NO.9 F.I.E., PPG:ID | TG-PVR035A-1 | 19504874 | 990 | 320 | 249 | 0.96 | 799 | 250 | 1006 | 280 | 1129 | 268 | 1078 | 107 | 2019-06-27 12:30 | 153.8 | -72.9 | 1145 | Y | 92 | 107 | 101 | 15 |  |  | 1.1 | 98.9 | 394.55 | 363.25 | 381.55 | 378.25 | 102.29 | 114.59 | 114.59 | 107.29 | 216.15 | 225.15 | 221.45 | 225.45 |  | 10 | 4 | 2 |  |  |  |  | 713.39 | 6.21 | 0.37 | 0.81
231 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR036 | 1S-DL-YP-ETC-DLNR-2502-PVR036 | S/STN. NO.11 F.I.E., PPG:ID | TG-PVR036A-1 | 19503810 | 630 | 200 | 244 | 0.96 | 117 | 41 | 172 | 31 | 131 | 45 | 190 | 53 | 2019-06-03 15:00 | 30.8 | -4.1 | 194 | B | 102 | 83 | 115 | 32 |  |  | 0.1 | 99.9 | 719.22 | 719.52 | 712.52 | 719.52 | 0.3 | [15 empty] | 719.52 | 0.08 | 0.27 | 0.19
232 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR036 | 1S-DL-YP-ETC-DLNR-2502-PVR036 | S/STN. NO.11 F.I.E., PPG:ID | TG-PVR036A-2 | 19506906 | 630 | 200 | 243.9387 | 0.97195 | 305.3875 | 101.5175 | 426.2038 | 94.6938 | 395.6456 | 109.1762 | 459.7279 | 55.5167 | 2019-06-26 12:30 | [15 empty] | 432 |  |  |  | 254 |  |  |  | 34 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.39094 | 0.48474
233 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR037 | 1S-DL-YP-ETC-DLNR-2502-PVR037 | S/STN. NO.12 F.I.E., PPG:ID | TG-PVR037A-1 | 19506518 | 630 | 200 | 250 | 0.9 | 137 | 49 | 200 | 55 | 222 | 33 | 133 | 80 | 2019-06-28 16:00 | 55 | -43.2 | 302 | R | 120 | 115 | 65 | 55 |  | 0.2 | 7.5 | 92.3 | 680.52 | 552.52 | 712.52 | 703.22 | 32 | 160 | 160 | 9.3 | [12 empty] | 712.52 | 7.08 | 0.4 | 0.22
234 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR037 | 1S-DL-YP-ETC-DLNR-2502-PVR037 | S/STN. NO.12 F.I.E., PPG:ID | TG-PVR037A-2 | 19505476 | 990 | 320 | 251 | 0.78 | 427 | 158 | 630 | 135 | 538 | 135 | 536 | 93 | 2019-06-27 12:00 | 67.5 | -116.2 | 649 | R | 107 | 98 | 95 | 12 | 0.1 | 0.1 | 6.9 | 92.9 | 466.22 | 482.22 | 477.52 | 475.52 | 159 | 218.59 | 218.59 | 218.59 | 87.29 | 11.3 | 5 | 18 | [8 empty] | 712.51 | 7.09 | 0.43 | 0.43
235 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR038 | 1S-DL-YP-ETC-DLNR-2502-PVR038 | S/STN. NO.13 F.I.E., PPG:ID | TG-PVR038A-1 | 19505415 | 630 | 200 | 244 | 0.89 | 336 | 107 | 443 | 119 | 492 | 110 | 455 | 44 | 2019-06-08 11:30 | 124.4 | -66 | 638 | R | 104 | 110 | 87 | 23 | 0.1 |  | 7.4 | 92.6 | 442.52 | 433.52 | 460.52 | 447.22 | 155.3 | 129.3 | 129.3 | 168.3 | 115 | 150 | 30.3 | 97.3 | [8 empty] | 713.22 | 6.38 | 0.36 | 0.53
236 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR038 | 1S-DL-YP-ETC-DLNR-2502-PVR038 | S/STN. NO.13 F.I.E., PPG:ID | TG-PVR038A-2 | 19501454 | 400 | 120 | 243 | 0.92 | 262 | 90 | 389 | 88 | 382 | 84 | 364 | 22 | 2019-06-22 12:30 | 21 | -67.1 | 394 | R | 99 | 103 | 98 | 5 |  |  | 0.1 | 99.9 | 325.22 | 267.26 | 313.22 | 308.52 | 183 | 229.56 | 229.56 | 197.3 | 211.3 | 222.3 | 207 | 213.3 | [8 empty] | 719.52 | 0.08 | 0.45 | 0.65
237 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR039 | 1S-DL-YP-ETC-DLNR-2502-PVR039 | S/STN. NO.14 F.I.E., PPG:ID | TG-PVR039A-1 | 19505920 | 630 | 200 | 249 | 0.96 | 539 | 183 | 757 | 170 | 698 | 186 | 767 | 65 | 2019-06-28 17:00 | 203.2 | -22.6 | 767 | B | 103 | 93 | 104 | 11 |  |  | 2.4 | 97.6 | 287.31 | 288.31 | 288.31 | 288.31 | 105.3 | 111.3 | 111.3 | 88 | 319.2 | 313.5 | 371.5 | 336.5 | 2 | 0.3 | 5.3 | 1 |  |  |  |  | 714.21 | 5.39 | 0.41 | 0.85
238 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR039 | 1S-DL-YP-ETC-DLNR-2502-PVR039 | S/STN. NO.14 F.I.E., PPG:ID | TG-PVR039A-2 | 19506770 | 630 | 200 | 250 | 0.97 | 311 | 100 | 411 | 100 | 409 | 111 | 456 | 46 | 2019-06-26 11:00 | 127.8 | -20.8 | 456 | B | 91 | 100 | 109 | 18 |  | 0.2 | 10.8 | 89 | 435.22 | 380.52 | 301.23 | 389.52 | 250 | 251 | 251 | 248 | 29.3 | 83 | 116.3 | 77 | [8 empty] | 714.52 | 5.08 | 0.47 | 0.49
239 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR040 | 1S-DL-YP-ETC-DLNR-2502-PVR040 | S/STN. NO.15 F.I.E., PPG:ID | TG-PVR040A-1 | 19504935 | 990 | 320 | 249 | 0.91 | 616 | 216 | 890 | 205 | 848 | 195 | 809 | 70 | 2019-06-12 15:00 | 191.4 | -131 | 901 | R | 103 | 100 | 97 | 6 |  |  | 13.8 | 86.2 | 437.22 | 442.52 | 442.22 | 439.22 | 80 | 76 | 76 | 82 | 201.55 | 200.25 | 188.55 | 197.55 | [8 empty] | 719.17 | 0.43 | 0.38 | 0.62
240 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR040 | 1S-DL-YP-ETC-DLNR-2502-PVR040 | S/STN. NO.15 F.I.E., PPG:ID | TG-PVR040A-2 | 19504783 | 400 | 120 | 249 | 0.96 | 384 | 121 | 520 | 149 | 640 | 114 | 491 | 137 | 2019-06-06 11:30 | 93 | -64.9 | 661 | Y | 94 | 118 | 88 | 30 |  |  | 41.1 | 58.9 | 261.53 | 236.23 | 282.53 | 258.53 | 203.58 | 185.3 | 185.3 | 192.3 | 239.32 | 146.28 | 244.24 | 233 | 13.54 | 132.02 | 3.3 | 34.54 |  | 18.54 |  |  | 719.17 | 0.43 | 0.38 | 0.96
241 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR041 | 1S-DL-YP-ETC-DLNR-2502-PVR041 | S/STN. NO.16 F.I.E., PPG:ID | TG-PVR041A-1 | 19502418 | 630 | 200 | 249 | 0.94 | 288 | 100 | 417 | 95 | 398 | 93 | 388 | 25 | 2019-06-29 10:30 | 81.4 | -25.8 | 417 | R | 108 | 94 | 98 | 14 |  |  | 2.1 | 97.9 | 448.23 | 474.53 | 472.23 | 464.53 | 255.49 | 236.49 | 236.49 | 248.49 | 15.3 | 8 | 6.3 | 6 | [8 empty] | 719.42 | 0.18 | 0.31 | 0.46
242 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR041 | 1S-DL-YP-ETC-DLNR-2502-PVR041 | S/STN. NO.16 F.I.E., PPG:ID | TG-PVR041A-2 | 19502874 | 630 | 200 | 248 | 0.97 | 573 | 195 | 801 | 180 | 738 | 198 | 818 | 74 | 2019-06-29 13:00 | 158.7 | -65.8 | 856 | B | 102 | 93 | 106 | 13 |  |  | 6.8 | 93.2 | 235.26 | 297.55 | 242.56 | 256.26 | 220.56 | 173.27 | 173.27 | 200.26 | 231.3 | 238.3 | 224.3 | 237 | 32 | 10 | 49 | 26 |  |  |  |  | 719.52 | 0.08 | 0.4 | 0.91
243 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR042 | 1S-DL-YP-ETC-DLNR-2502-PVR042 | S/STN. NO.17 F.I.E., PPG:ID | TG-PVR042A-1 | 19504843 | 630 | 200 | 249 | 0.98 | 353 | 107 | 427 | 121 | 482 | 126 | 499 | 66 | 2019-06-27 15:30 | 90.6 | -4.1 | 555 | B | 86 | 102 | 112 | 26 |  |  | 30.3 | 69.7 | 461.23 | 424.23 | 414.54 | 438.53 | 148.3 | 128 | 128 | 113.3 | 109.55 | 167.25 | 201.55 | 167.25 | [8 empty] | 719.48 | 0.12 | 0.38 | 0.56
244 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR043 | 1S-DL-YP-ETC-DLNR-2502-PVR043 | S/STN. NO.18 F.I.E., PPG:ID | TG-PVR043A-1 | 19500814 | 990 | 320 | 249 | 0.98 | 608 | 200 | 859 | 208 | 901 | 200 | 867 | 39 | 2019-06-10 12:30 | 145.7 | -53 | 906 | Y | 95 | 105 | 100 | 10 |  |  | 12.4 | 87.6 | 392.23 | 256.56 | 276.56 | 287.56 | 133.29 | 265.56 | 265.56 | 238.56 | 193.55 | 196.55 | 187 | 192.55 | [8 empty] | 719.47 | 0.13 | 0.44 | 0.61
245 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR043 | 1S-DL-YP-ETC-DLNR-2502-PVR043 | S/STN. NO.18 F.I.E., PPG:ID | TG-PVR043A-2 | 19505742 | 630 | 200 | 249 | 0.95 | 462 | 164 | 693 | 150 | 637 | 148 | 627 | 62 | 2019-06-24 12:30 | 190.4 | -43 | 703 | R | 109 | 96 | 95 | 14 | 0.1 |  | 6.4 | 93.5 | 350.23 | 364.53 | 370.53 | 362.23 | 113.29 | 135.29 | 135.29 | 133.29 | 240.55 | 205.25 | 197.55 | 209.55 | 1 | [7 empty] | 705.47 | 14.13 | 0.37 | 0.73
246 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR044 | 1S-DL-YP-ETC-DLNR-2502-PVR044 | S/STN. NO.19 F.I.E., PPG:ID | TG-PVR044A-1 | 19505421 | 630 | 200 | 243 | 0.91 | 456 | 124 | 522 | 167 | 703 | 166 | 701 | 180 | 2019-06-26 12:00 | 94.8 | -61 | 714 | Y | 81 | 111 | 108 | 30 |  | 0.1 | 4.9 | 95 | 412.53 | 350.57 | 353.57 | 361.57 | 105.58 | 74.26 | 74.26 | 91.26 | 194.23 | 287.51 | 272.21 | 259.51 | [8 empty] | 713.14 | 6.46 | 0.41 | 0.72
247 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR044 | 1S-DL-YP-ETC-DLNR-2502-PVR044 | S/STN. NO.19 F.I.E., PPG:ID | TG-PVR044A-2 | 19500709 | 630 | 200 | 249 | 0.92 | 209 | 57 | 235 | 57 | 236 | 95 | 390 | 154 | 2019-06-14 14:00 | 65.3 | -15.6 | 400 | B | 87 | 82 | 130 | 48 |  |  |  | 100 | 572.21 | 566.51 | 501.21 | 535.51 | 147.3 | 153 | 153 | 184 |  |  | 30.3 | [9 empty] | 719.51 | 0.09 | 0.32 | 0.33
248 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR045 | 1S-DL-YP-ETC-DLNR-2502-PVR045 | S/STN. NO.20 F.I.E., PPG:ID | TG-PVR045A-1 | 19505036 | 400 | 120 | 248 | 0.96 | 351 | 121 | 516 | 117 | 503 | 113 | 488 | 24 | 2019-06-13 12:30 | 117.6 | 0.8 | 530 | Y | 106 | 100 | 94 | 12 |  |  | 8.7 | 91.3 | 281.53 | 318.23 | 313.53 | 305.23 | 137.3 | 101.3 | 101.3 | 114.41 | 254.08 | 269.08 | 294.28 | 279.57 | 46 | 30.3 | 4 | 19.3 |  |  |  |  | 719.31 | 0.29 | 0.41 | 0.88
249 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR045 | 1S-DL-YP-ETC-DLNR-2502-PVR045 | S/STN. NO.20 F.I.E., PPG:ID | TG-PVR045A-2 | 19505034 | 630 | 200 | 249 | 0.96 | 330 | 105 | 448 | 111 | 473 | 114 | 481 | 30 | 2019-06-13 11:00 | 108.6 | -21.2 | 481 | B | 100 | 98 | 102 | 4 |  |  | 15.2 | 84.8 | 425.52 | 424.33 | 417.52 | 423.52 | 210.1 | 224.59 | 224.59 | 205.1 | 83.3 | 70 | 110.3 | 90.3 | [8 empty] | 719.32 | 0.28 | 0.41 | 0.52
250 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR045 | 1S-DL-YP-ETC-DLNR-2502-PVR045 | S/STN. NO.20 F.I.E., PPG:ID | TG-PVR045A-3 | 19505035 | 630 | 200 | 248 | 0.97 | 589 | 199 | 827 | 216 | 903 | 174 | 724 | 156 | 2019-06-03 15:30 | 152.7 | -82.3 | 910 | Y | 103 | 99 | 97 | 6 |  |  | 0.5 | 99.5 | 39.3 | 71.3 | 50 | 51.3 | 367.23 | 373.51 | 373.51 | 382.53 | 245.07 | 198.09 | 266.07 | 228.37 | 67.3 | 72.3 | 15 | 56.3 |  | 3.3 |  |  | 719.3 | 0.3 | 0.47 | 0.94
251 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR046 | 1S-DL-YP-ETC-DLNR-2502-PVR046 | S/STN. NO.21 F.I.E., PPG:ID | TG-PVR046A-1 | 19506665 | 630 | 200 | 237 | 0.97 | 485 | 164 | 716 | 164 | 723 | 157 | 689 | 32 | 2019-06-07 16:00 | 151.6 | -36 | 723 | Y | 100 | 104 | 96 | 8 |  | 0.1 | 7.5 | 92.5 | 362.53 | 354.23 | 366.53 | 361.53 | 100.58 | 98.58 | 98.58 | 105.28 | 232.01 | 242.31 | 220.27 | 228.31 | [8 empty] | 695.52 | 24.08 | 0.36 | 0.77
252 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR046 | 1S-DL-YP-ETC-DLNR-2502-PVR046 | S/STN. NO.21 F.I.E., PPG:ID | TG-PVR046A-2 | 19504984 | 630 | 200 | 242 | 0.97 | 458 | 150 | 653 | 159 | 697 | 148 | 640 | 52 | 2019-06-26 14:30 | 152.3 | -40.9 | 714 | R | 104 | 106 | 90 | 16 |  |  | 4.4 | 95.6 | 288.55 | 217.25 | 355.22 | 279.25 | 193.24 | 276.24 | 276.24 | 223.24 | 234.01 | 223.01 | 193.01 | 214.01 | 0.3 | [7 empty] | 716.5 | 3.1 | 0.41 | 0.73
253 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR047 | 1S-DL-YP-ETC-DLNR-2502-PVR047 | S/STN. NO.22 F.I.E., PPG:ID | TG-PVR047A-1 | 19506769 | 630 | 200 | 248 | 0.98 | 782 | 271 | 1097 | 257 | 1032 | 254 | 1028 | 67 | 2019-06-06 17:00 | 182.8 | -80.2 | 1119 | R | 104 | 98 | 98 | 6 |  |  | 15.4 | 84.6 | 107.3 | 237.57 | 220.27 | 194.27 | 285.22 | 157.25 | 157.25 | 202.55 | 88.33 | 90.33 | 85.33 | 86.33 | 101.3 | 120 | 113.3 | 108.3 | 122.15 | 99.15 | 104.15 | 112.45 | 705.1 | 14.5 | 0.41 | 1.24
254 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR047 | 1S-DL-YP-ETC-DLNR-2502-PVR047 | S/STN. NO.22 F.I.E., PPG:ID | TG-PVR047A-2 | 19504981 | 630 | 200 | 248 | 0.94 | 643 | 193 | 799 | 228 | 956 | 222 | 925 | 144 | 2019-06-08 14:00 | 187.7 | -94.3 | 976 | B | 90 | 103 | 107 | 17 | 0.1 |  | 21.8 | 78.1 | 359.57 | 330.27 | 332.57 | 338.57 | 80.05 | 86.26 | 86.26 | 77.56 | 183.41 | 133.5 | 135.29 | 147.2 | 91.26 | 156.56 | 151.17 | 149.26 |  | 7.3 | 24 | 1.3 | 715.09 | 4.51 | 0.39 | 1.02
255 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR048 | 1S-DL-YP-ETC-DLNR-2502-PVR048 | S/STN. NO.23 F.I.E., PPG:ID | TG-PVR048A-1 | 19501513 | 630 | 200 | 243 | 0.96 | 380 | 130 | 534 | 125 | 521 | 125 | 519 | 14 | 2019-06-05 12:30 | 106.3 | -33.6 | 534 | R | 102 | 97 | 101 | 5 |  |  | 37.4 | 62.6 | 427.23 | 436.52 | 427.53 | 431.23 | 80.59 | 89.3 | 89.3 | 78.59 | 211.3 | 193.3 | 214 | 209.3 | [8 empty] | 719.52 | 0.08 | 0.37 | 0.6
256 | 2019-06-01 | 2019-06-10 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR048 | 1S-DL-YP-ETC-DLNR-2502-PVR048 | S/STN. NO.23 F.I.E., PPG:ID | TG-PVR048A-2 | 19502896 | 630 | 200 | 242 | 0.95 | 507 | 169 | 709 | 168 | 710 | 171 | 723 | 14 | 2019-06-04 14:30 | 126.5 | -64.4 | 745 | B | 102 | 99 | 99 | 3 |  | 0.2 | 23.3 | 76.5 | 68.29 | 75.59 | 86.25 | 73.29 | 86.56 | 79.56 | 79.56 | 81.56 | 75.01 | 75.01 | 73.31 | 75.01 | 1 | 0.3 | 1 | 1 |  |  |  |  | 231.26 | 8.34 | 0.42 | 0.81
257 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR049 | 1S-DL-YP-ETC-DLNR-2502-PVR049 | S/STN. NO.24 F.I.E., PPG:ID | TG-PVR049A-1 | 19505052 | 400 | 120 | 256 | 0.96 | 217 | 77 | 309 | 72 | 285 | 68 | 270 | 33 | 2019-06-28 10:30 | 80.9 | -44.2 | 309 | R | 102 | 104 | 94 | 10 |  |  | 27.7 | 72.3 | 464.34 | 445.04 | 475.04 | 465.04 | 111.3 | 155.3 | 155.3 | 126.3 | 143.29 | 118.59 | 110.29 | 127.59 | [8 empty] | 719.33 | 0.27 | 0.39 | 0.54
258 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR049 | 1S-DL-YP-ETC-DLNR-2502-PVR049 | S/STN. NO.24 F.I.E., PPG:ID | TG-PVR049A-2 | 19506489 | 630 | 200 | 243 | 0.98 | 576 | 190 | 808 | 174 | 745 | 212 | 911 | 145 | 2019-06-14 14:30 | 152.6 | -36.4 | 911 | B | 97 | 98 | 105 | 8 |  | 0.3 | 16.8 | 82.9 | 375.53 | 371.23 | 364.23 | 371.23 | 61.59 | 67.59 | 67.59 | 64.59 | 201.41 | 239.11 | 175.11 | 199.11 | 66.3 | 27.3 | 96 | 70.3 |  |  | 1 |  | 706.03 | 13.57 | 0.37 | 0.91
259 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR050 | 1S-DL-YP-ETC-DLNR-2502-PVR050 | ROAD NO. 56, ST. LTG:PM | TG-PVR050A-1 | 19505741 | 100 | 40 | 242 | 0.91 | 55 | 22 | 89 | 16 | 65 | 17 | 67 | 24 | 2019-06-15 21:00 | 31.2 | 1.3 | 91 | R | 113 | 91 | 96 | 22 |  | 0.1 | 8.8 | 91 | 100 | 196 | 134 | 104 | 517.22 | 490.56 | 490.56 | 579.52 | 91 | 21.26 | 22.26 | 24.3 | [8 empty] | 708.22 | 11.38 | 0.48 | 0.55
260 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR062 | 1S-DL-YP-ETC-DLNR-2502-PVR062 | DSIDC S/STN-1 PPG COMPLEX:ID | TG-PVR062A-1 | 19502569 | 630 | 200 | 250 | 0.95 | 151 | 51 | 209 | 45 | 181 | 55 | 224 | 38 | 2019-06-07 17:00 | 33.6 | -18.4 | 245 | B | 104 | 86 | 111 | 25 |  |  | 41.2 | 58.8 | 618.52 | 713.52 | 582.52 | 649.52 | 101 | 6 | 6 | 70 | [12 empty] | 719.52 | 0.08 | 0.36 | 0.24
261 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR062 | 1S-DL-YP-ETC-DLNR-2502-PVR062 | DSIDC S/STN-1 PPG COMPLEX:ID | TG-PVR062A-2 | 19502562 | 630 | 200 | 244 | 0.91 | 281 | 109 | 451 | 93 | 379 | 80 | 327 | 108 | 2019-06-29 16:00 | 48.8 | -30.4 | 454 | R | 113 | 98 | 89 | 24 |  |  | 12.3 | 87.7 | 464.22 | 483.22 | 478.52 | 473.22 | 140.3 | 206.3 | 206.3 | 233.3 | 115 | 30 |  | 13 | [8 empty] | 719.52 | 0.08 | 0.35 | 0.45
262 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR063 | 1S-DL-YP-ETC-DLNR-2502-PVR063 | DSIDC S/STN-2 PPG COMPLEX:ID | TG-PVR063A-1 | 19504844 | 400 | 120 | 244 | 0.97 | 236 | 85 | 357 | 73 | 308 | 77 | 321 | 44 | 2019-06-06 15:00 | 66.8 | -29.5 | 362 | B | 97 | 92 | 111 | 19 |  | 0.2 | 47.6 | 52.2 | 391.53 | 414.22 | 333.23 | 376.23 | 135.29 | 139 | 139 | 154.59 | 192.3 | 166.3 | 198 | 188.3 | [8 empty] | 719.52 | 0.08 | 0.44 | 0.59
263 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR063 | 1S-DL-YP-ETC-DLNR-2502-PVR063 | DSIDC S/STN-2 PPG COMPLEX:ID | TG-PVR063A-2 | 19504887 | 400 | 120 | 244 | 0.98 | 206 | 80 | 338 | 61 | 260 | 65 | 276 | 71 | 2019-06-29 11:00 | 30.9 | -22.4 | 338 | R | 110 | 91 | 99 | 19 |  |  | 25.2 | 74.8 | 461.22 | 450.22 | 454.22 | 457.52 | 74.3 | 252 | 252 | 144.3 | 184 | 17.3 | 115.3 | 117.3 | [8 empty] | 719.52 | 0.08 | 0.35 | 0.52
264 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR087 | 1S-DL-YP-ETC-DLNR-2502-PVR087 | ISBT Anand Vihar Outside | TG-PVR087A-1 | 19504989 | 400 | 120 | 250 | 0.86 | 45 | 21 | 79 | 12 | 46 | 12 | 48 | 32 | 2019-06-06 18:00 | 31.5 | -0.3 | 81 | R | 126 | 83 | 91 | 43 |  |  | 0.4 | 99.6 | 719.52 | 719.52 | 719.52 | 719.52 | [16 empty] | 719.52 | 0.08 | 0.36 | 0.11
265 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR001 | 1S-DL-YP-ETC-DLNR-2501-LGR001 | PRIYADARSHINI VIHAR:ID | TG-LGR001A-1 | 19505699 | 990 | 320 | 239.2952 | 0.97973 | 961.7521 | 302.3323 | 1368.8865 | 327.9906 | 1485.734 | 331.4292 | 1493.1933 | 120.7501 | 2019-06-27 | [15 empty] | 0 |  |  |  | 206.5 |  |  |  | 502.5 |  |  |  | 9 |  |  |  | 0 | 718 |  | 0.49918 | 0.97147
266 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR001 | 1S-DL-YP-ETC-DLNR-2501-LGR001 | PRIYADARSHINI VIHAR:ID | TG-LGR001A-2 | 19506908 | 990 | 320 | 247 | 0.97 | 896 | 277 | 1161 | 292 | 1213 | 328 | 1381 | 200 | 2019-06-10 11:30 | 282.6 | 28.8 | 1381 | B | 109 | 82 | 109 | 27 | 0.2 |  | 50.8 | 49 | 7.3 | 44.3 | 6.3 | 6 | 437.47 | 628.3 | 628.3 | 509.17 | 259.43 | 32 | 269.43 | 189.43 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | 705.3 | 14.3 | 0.39 | 0.91
267 | 2019-06-25 15:00 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR002 | 1S-DL-YP-ETC-DLNR-2501-LGR002 | PNB BANK ENCLAVE:ID | TG-LGR002A-1 | 19505159 | 990 | 320 | 245.6963 | 0.97806 | 619.2019 | 219.9527 | 913.1594 | 212.9155 | 887.0369 | 186.3337 | 764.4774 | 137.4946 | 2019-06-29 23:30 | [15 empty] | 0 |  |  |  | 63.5 |  |  |  | 65.5 |  |  |  | 0 |  |  |  | 0 | 129 |  | 0.65995 | 0.62546
268 | 2019-06-03 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR002 | 1S-DL-YP-ETC-DLNR-2501-LGR002 | PNB BANK ENCLAVE:ID | TG-LGR002A-2 | 19502526 | 990 | 320 | 240 | 0.98 | 650 | 164 | 678 | 272 | 1172 | 215 | 911 | 428 | 2019-06-30 | 112.6 | 14 | 1216 | Y | 79 | 121 | 99 | 42 | 99.9 | 0.1 |  |  | 146.17 | 28.3 | 55.02 | 59.3 | 442.26 | 331.47 | 331.47 | 423.12 | 56.18 | 281.14 | 152.48 | 162.19 |  | 3.3 | [6 empty] | 667.51 | 4.09 | 0.5 | 0.66
269 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR002 | 1S-DL-YP-ETC-DLNR-2501-LGR002 | PNB BANK ENCLAVE:ID | TG-LGR002A-3 | 19504436 | 990 | 320 | 240 | 0.98 | 1045 | 391 | 1644 | 320 | 1326 | 334 | 1396 | 289 | 2019-06-12 00:30 | 214.9 | 29.4 | 1694 | R | 104 | 105 | 91 | 14 |  | 1.2 | 72.2 | 26.6 |  | 0.12 | 0.42 | 0.12 | 55.12 | 30.3 | 30.3 | 52.3 | 489.42 | 514.12 | 493.22 | 515.12 | 121 | 112 | 75.54 | 109.3 | 23.24 | 32.24 | 3 | 11.54 | 689.18 | 6.42 | 0.58 | 1.06
270 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR003 | 1S-DL-YP-ETC-DLNR-2501-LGR003 | LNR COMPLAINT CENTER:ID | TG-LGR003A-1 | 19502778 | 630 | 200 | 245 | 0.98 | 523 | 239 | 988 | 145 | 586 | 139 | 569 | 410 | 2019-06-30 20:00 | 91.1 | 29.4 | 1020 | R | 125 | 96 | 79 | 46 |  | 0.3 | 52.3 | 47.4 |  |  | 2.3 |  | 37.25 | 104.24 | 104.24 | 106.24 | 451.5 | 614.27 | 461.06 | 607.57 | 199.06 | 0.3 |  | 5 | 31 |  |  |  | 719.21 | 0.39 | 0.67 | 0.83
271 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR003 | 1S-DL-YP-ETC-DLNR-2501-LGR003 | LNR COMPLAINT CENTER:ID | TG-LGR003A-2 | 19505889 | 990 | 320 | 246 | 0.99 | 766 | 368 | 1603 | 260 | 1110 | 138 | 592 | 876 | 2019-06-02 21:00 | 120.3 | 11.2 | 1627 | R | 145 | 106 | 49 | 96 | 0.1 | 0.8 | 53.2 | 45.9 |  |  | 232.48 |  | 15 | 137.32 | 137.32 | 195.02 | 459.44 | 561.42 | 14.3 | 508.42 | 222.3 | 4.3 |  |  | 6.3 |  |  |  | 703.44 | 16.16 | 0.63 | 0.77
272 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR003 | 1S-DL-YP-ETC-DLNR-2501-LGR003 | LNR COMPLAINT CENTER:ID | TG-LGR003A-3 | 19505700 | 990 | 320 | 247 | 0.99 | 462 | 131 | 540 | 96 | 388 | 235 | 989 | 541 | 2019-06-10 15:30 | 108.5 | 6.1 | 989 | B | 114 | 73 | 113 | 41 | 0.4 | 0.1 | 47.7 | 51.8 | 19.56 | 291.17 | 9 | 47.26 | 471.19 | 412.21 | 412.21 | 584.48 | 213.23 | 1 | 175.54 | 72.24 | [8 empty] | 704.38 | 15.22 | 0.66 | 0.47
273 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR004 | 1S-DL-YP-ETC-DLNR-2501-LGR004 | KISHAN KUNJ:K | TG-LGR004A-1 | 19505542 | 990 | 200 | 245 | 0.98 | 1036 | 355 | 1502 | 336 | 1409 | 345 | 1445 | 82 | 2019-06-30 00:30 | 185.2 | 40.4 | 1582 | R | 105 | 94 | 101 | 11 | 4.7 | 23.4 | 32.8 | 39.1 |  |  |  |  | 84.44 | 180.25 | 180.25 | 114.14 | 535.05 | 493.55 | 523.56 | 533.05 | 72.03 | 22.06 | 56.26 | 47.56 | 4.42 | 0.08 | 1.49 | 1.19 | 696.34 | 23.26 | 0.52 | 1.05
274 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR004 | 1S-DL-YP-ETC-DLNR-2501-LGR004 | KISHAN KUNJ:K | TG-LGR004A-2 | 19505955 | 990 | 320 | 244 | 0.98 | 1288 | 470 | 2013 | 417 | 1756 | 401 | 1689 | 296 | 2019-06-30 00:30 | 252.5 | 52.2 | 2026 | R | 113 | 92 | 95 | 21 | 0.6 | 1.7 | 41.2 | 56.5 |  |  |  |  | 25.53 | 113.25 | 113.25 | 54.53 | 460.58 | 466.52 | 521.24 | 491.54 | 116.06 | 105.41 | 106.12 | 120.4 | 94.56 | 11.55 | 6.54 | 30.26 | 697.53 | 22.07 | 0.49 | 1.3
275 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR004 | 1S-DL-YP-ETC-DLNR-2501-LGR004 | KISHAN KUNJ:K | TG-LGR004A-3 | 19506173 | 990 | 320 | 244 | 0.97 | 1313 | 476 | 2043 | 448 | 1904 | 389 | 1642 | 353 | 2019-06-30 00:30 | 270.4 | 14.1 | 2043 | R | 108 | 101 | 91 | 17 | 0.3 | 1.2 | 18.7 | 79.8 | 0.01 | 0.01 | 0.01 | 0.01 | 9 | 19.3 | 19.3 | 14.3 | 429.54 | 452.03 | 507.3 | 464.24 | 137.06 | 140.54 | 137.19 | 141.33 | 121.34 | 85.07 | 23.15 | 77.07 | 697.35 | 22.25 | 0.54 | 1.33
276 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR006 | 1S-DL-YP-ETC-DLNR-2501-LGR006 | J&K BLOCK HALWAI WALA:PL | TG-LGR006A-1 | 19506637 | 990 | 320 | 246 | 0.97 | 647 | 177 | 703 | 227 | 926 | 243 | 987 | 259 | 2019-06-05 03:30 | 147.2 | 38.1 | 1127 | B | 86 | 98 | 115 | 29 | 0.8 | 66.1 | 32.9 | 0.1 | 22 | 10.3 |  | 4 | 496.36 | 424.45 | 424.45 | 414.45 | 194.17 | 277.38 | 440.32 | 294.08 |  |  | 0.3 | [5 empty] | 712.53 | 7.07 | 0.6 | 0.65
277 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR007 | 1S-DL-YP-ETC-DLNR-2501-LGR007 | WALIA NURSHING HOME:PL | TG-LGR007A-1 | 19505671 | 990 | 320 | 240 | 0.98 | 658 | 180 | 777 | 231 | 992 | 247 | 1072 | 264 | 2019-06-08 16:00 | 162.2 | 20.2 | 1168 | R | 82 | 98 | 120 | 38 | 0.1 | 0.1 | 2.7 | 97.2 | 234.34 | 171.5 | 63.3 | 161.5 | 291.26 | 251.1 | 251.1 | 251.4 | 191.14 | 294.44 | 344.03 | 304.14 | 0.3 | [7 empty] | 717.44 | 2.16 | 0.54 | 0.66
278 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR007 | 1S-DL-YP-ETC-DLNR-2501-LGR007 | WALIA NURSHING HOME:PL | TG-LGR007A-2 | 19505459 | 630 | 200 | 238 | 0.98 | 631 | 208 | 906 | 207 | 912 | 215 | 940 | 32 | 2019-06-08 15:00 | 126.6 | 38.4 | 948 | Y | 101 | 97 | 102 | 5 | 0.1 | 0.1 | 11 | 88.9 |  |  |  |  | 28 | 75.3 | 75.3 | 18 | 555.04 | 548.04 | 624.31 | 590.04 | 120.43 | 80.43 | 68.3 | 96.27 | 1 | 0.3 | 0.16 | 0.16 | 704.47 | 15.13 | 0.62 | 1
279 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR008 | 1S-DL-YP-ETC-DLNR-2501-LGR008 | LALITA PARK:K | TG-LGR008A-1 | 19506683 | 990 | 320 | 239 | 0.98 | 825 | 272 | 1230 | 232 | 1033 | 320 | 1432 | 346 | 2019-06-28 23:30 | 186.2 | 41 | 1432 | B | 100 | 92 | 108 | 16 | 0.3 |  | 35.4 | 64.3 | 1.3 | 1 |  |  | 295.53 | 337.17 | 337.17 | 287.53 | 411.02 | 374.38 | 432.54 | 424.02 | 4.3 |  | 43.05 | 1 |  |  |  |  | 712.55 | 7.05 | 0.55 | 0.83
280 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR008 | 1S-DL-YP-ETC-DLNR-2501-LGR008 | LALITA PARK:K | TG-LGR008A-2 | 19505453 | 990 | 320 | 248 | 0.97 | 531 | 190 | 793 | 160 | 666 | 181 | 755 | 113 | 2019-06-30 23:00 | 122.6 | 38.7 | 883 | B | 104 | 100 | 97 | 7 | 0.1 |  | 15.8 | 84.2 | 32 | 29.3 | 53 | 33 | 487.3 | 516.52 | 516.52 | 507.25 | 176 | 149.08 | 137.38 | 155.05 | [8 empty] | 695.3 | 24.3 | 0.6 | 0.54
281 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR008 | 1S-DL-YP-ETC-DLNR-2501-LGR008 | LALITA PARK:K | TG-LGR008A-3 | 19506761 | 990 | 320 | 240 | 0.98 | 785 | 308 | 1371 | 191 | 842 | 286 | 1287 | 493 | 2019-06-28 23:30 | 175.7 | 41.6 | 1458 | R | 123 | 73 | 104 | 50 | 0.1 | 6 | 75.6 | 18.2 | 0.3 | 23.3 |  |  | 143.3 | 515.06 | 515.06 | 270.29 | 459.06 | 174.18 | 481.25 | 442.25 | 108.48 |  | 4.3 |  | 1 |  |  |  | 712.54 | 7.06 | 0.58 | 0.79
282 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR009 | 1S-DL-YP-ETC-DLNR-2501-LGR009 | RAMESH PARK AKHARA:PL | TG-LGR009A-1 | 19503006 | 990 | 320 | 240 | 0.97 | 855 | 273 | 1139 | 251 | 1040 | 332 | 1403 | 324 | 2019-06-01 04:30 | 167.8 | 58.9 | 1444 | B | 100 | 85 | 115 | 30 |  | 0.9 | 75 | 24.1 | 0.01 | 0.01 |  |  | 70 | 193.09 | 193.09 | 55.18 | 635.49 | 524.25 | 639.17 | 657.17 | 11.45 |  | 59.3 | 5 |  |  | 1 |  | 717.35 | 2.25 | 0.63 | 0.86
283 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR009 | 1S-DL-YP-ETC-DLNR-2501-LGR009 | RAMESH PARK AKHARA:PL | TG-LGR009A-2 | 19506036 | 990 | 320 | 241 | 0.98 | 917 | 363 | 1740 | 396 | 1763 | 158 | 673 | 1078 | 2019-06-01 19:00 | 302.4 | 25.6 | 1763 | Y | 89 | 123 | 88 | 35 | 0.5 | 0.1 | 11.5 | 88 | 48.35 | 6 | 30 | 10 | 397.32 | 154.57 | 154.57 | 359.27 | 269.32 | 484.22 | 253.3 | 344.42 |  | 70.2 | 1.3 | 1.54 | 0.24 | 0.24 |  |  | 716.03 | 3.57 | 0.47 | 0.93
284 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR010 | 1S-DL-YP-ETC-DLNR-2501-LGR010 | RAMESH PARK NEAR V-10:PL | TG-LGR010A-1 | 19503394 | 630 | 200 | 241 | 0.98 | 284 | 121 | 517 | 66 | 276 | 97 | 411 | 209 | 2019-06-30 00:30 | 47.8 | 11 | 540 | R | 128 | 68 | 104 | 60 |  | 0.8 | 67.1 | 32.1 | 8.3 | 450.36 | 85.29 | 73.3 | 518.34 | 265.05 | 265.05 | 628.11 | 188.37 |  | 57 | 14 | [8 empty] | 715.41 | 4.19 | 0.61 | 0.45
285 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR010 | 1S-DL-YP-ETC-DLNR-2501-LGR010 | RAMESH PARK NEAR V-10:PL | TG-LGR010A-2 | 19503400 | 630 | 200 | 247 | 0.97 | 436 | 177 | 726 | 151 | 613 | 108 | 439 | 251 | 2019-06-11 00:30 | 75.9 | 28.5 | 736 | R | 116 | 101 | 83 | 33 |  |  | 19.2 | 80.8 |  | 2 | 1.3 |  | 173.58 | 319.33 | 319.33 | 316.03 | 537.14 | 394.09 | 187.03 | 399.39 | 4.3 | [7 empty] | 715.42 | 4.18 | 0.62 | 0.69
286 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR011 | 1S-DL-YP-ETC-DLNR-2501-LGR011 | JAGAT RAM PARK:K | TG-LGR011A-1 | 19502822 | 990 | 320 | 244 | 0.97 | 934 | 359 | 1503 | 283 | 1197 | 292 | 1219 | 296 | 2019-06-30 00:30 | 192.1 | 53 | 1503 | R | 112 | 92 | 96 | 20 |  |  | 23.4 | 76.6 |  |  |  |  | 44 | 199.59 | 199.59 | 120 | 565.12 | 501.11 | 529.1 | 545.1 | 101.14 | 17.46 | 36.16 | 53.46 | 8.3 |  |  |  | 718.56 | 1.04 | 0.58 | 0.94
287 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR011 | 1S-DL-YP-ETC-DLNR-2501-LGR011 | JAGAT RAM PARK:K | TG-LGR011A-2 | 19502825 | 990 | 320 | 239 | 0.98 | 906 | 312 | 1349 | 302 | 1296 | 292 | 1269 | 70 | 2019-06-06 03:30 | 154.6 | 55.9 | 1439 | B | 100 | 95 | 104 | 9 |  | 6.6 | 81.8 | 11.6 |  |  |  |  | 112.57 | 196.56 | 196.56 | 138.26 | 590.55 | 497.27 | 531.28 | 547.27 | 14.26 | 23.55 | 58.24 | 32.25 |  |  | 0.3 |  | 718.18 | 1.42 | 0.57 | 0.91
288 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR011 | 1S-DL-YP-ETC-DLNR-2501-LGR011 | JAGAT RAM PARK:K | TG-LGR011A-3 | 19506037 | 990 | 320 | 244 | 0.97 | 928 | 365 | 1607 | 355 | 1510 | 207 | 885 | 679 | 2019-06-03 23:00 | 259.2 | 73 | 1607 | R | 98 | 103 | 99 | 5 | 0.3 | 0.3 | 17.8 | 81.6 |  |  |  |  | 113 | 78.3 | 78.3 | 88 | 580.22 | 614.22 | 608.27 | 615.22 | 25.3 | 25.3 | 12 | 16 | 0.3 | 1 |  |  | 719.22 | 0.38 | 0.57 | 0.94
289 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR011 | 1S-DL-YP-ETC-DLNR-2501-LGR011 | JAGAT RAM PARK:K | TG-LGR011A-4 | 19504472 | 630 | 200 | 236 | 0.98 | 480 | 163 | 731 | 180 | 810 | 137 | 611 | 174 | 2019-06-02 23:30 | 75.4 | 17.5 | 810 | Y | 108 | 107 | 85 | 23 |  |  | 0.4 | 99.6 | 13 | 24.3 | 109.27 | 26 | 399.27 | 383.55 | 383.55 | 439.25 | 307.15 | 309.17 | 157.47 | 254.17 |  | 2 | [6 empty] | 719.42 | 0.18 | 0.49 | 0.76
290 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR011 | 1S-DL-YP-ETC-DLNR-2501-LGR011 | JAGAT RAM PARK:K | TG-LGR011A-5 | 19506715 | 630 | 200 | 237 | 0.99 | 441 | 93 | 384 | 204 | 854 | 144 | 598 | 407 | 2019-06-18 01:30 | 141 | 7.2 | 854 | Y | 87 | 100 | 113 | 26 | 0.1 |  | 39.4 | 60.4 | 46 | 36 | 8.3 | 13.3 | 621.1 | 471.18 | 471.18 | 521.48 | 37.05 | 196.52 | 291.27 | 168.57 |  | 0.05 | [6 empty] | 704.15 | 15.45 | 0.49 | 0.7
291 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR012 | 1S-DL-YP-ETC-DLNR-2501-LGR012 | GURU RAM DASS NAGAR:PL | TG-LGR012A-1 | 19502826 | 990 | 320 | 244 | 0.97 | 891 | 298 | 1285 | 318 | 1368 | 276 | 1181 | 162 | 2019-06-30 23:30 | 159.7 | 47.1 | 1421 | Y | 98 | 110 | 92 | 18 | 0 |  | 0.1 | 99.8 | 0.07 |  | 0.07 |  | 184.5 | 101.2 | 101.2 | 163.27 | 515.35 | 521.01 | 469.17 | 525.05 | 17 | 93.11 | 8 | 29 |  | 2 |  |  | 717.32 | 2.28 | 0.57 | 0.9
292 | 2019-06-01 | 2019-06-21 12:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR012 | 1S-DL-YP-ETC-DLNR-2501-LGR012 | GURU RAM DASS NAGAR:PL | TG-LGR012A-2 | 19502829 | 990 | 320 | 243.4734 | 0.97614 | 1153.7459 | 364.1066 | 1501.9659 | 377.1575 | 1548.4561 | 412.4819 | 1714.531 | 193.5538 | 2019-06-12 | [15 empty] | 0 |  |  |  | 18 |  |  |  | 343 |  |  |  | 80.5 |  |  |  | 48.5 | 490 |  | 0.59274 | 1.1654
293 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR012 | 1S-DL-YP-ETC-DLNR-2501-LGR012 | GURU RAM DASS NAGAR:PL | TG-LGR012A-3 | 19505569 | 990 | 320 | 245 | 0.97 | 1059 | 395 | 1655 | 367 | 1557 | 297 | 1238 | 378 | 2019-06-30 01:30 | 218.2 | 68.2 | 1655 | R | 108 | 103 | 89 | 19 | 0.3 | 0.6 | 28.8 | 70.3 |  |  |  |  | 63.53 | 66.23 | 66.23 | 77.23 | 508.59 | 542.05 | 568.26 | 552.35 | 120.41 | 98.35 | 11.42 | 82.05 | 21.28 | 7.58 |  | 2.58 | 715.01 | 4.59 | 0.54 | 1.07
294 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR013 | 1S-DL-YP-ETC-DLNR-2501-LGR013 | GURU NANAK PURA:PL:K | TG-LGR013A-1 | 19502771 | 990 | 320 | 243 | 0.97 | 602 | 236 | 1017 | 182 | 776 | 184 | 796 | 231 | 2019-06-26 15:30 | 169.3 | 36.8 | 1045 | R | 107 | 106 | 87 | 20 |  |  | 8.9 | 91.1 | 4.3 | 2 | 19.32 | 3.3 | 428.29 | 409.39 | 409.39 | 498.21 | 281.32 | 302.52 | 88.42 | 212.4 | [8 empty] | 714.31 | 5.29 | 0.59 | 0.61
295 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR014 | 1S-DL-YP-ETC-DLNR-2501-LGR014 | TIKONA PARK:ID | TG-LGR014A-1 | 19502942 | 990 | 320 | 241 | 0.98 | 1007 | 257 | 1050 | 366 | 1516 | 384 | 1597 | 511 | 2019-06-11 23:30 | 172.2 | 67.7 | 1622 | B | 87 | 108 | 105 | 21 |  | 0.5 | 16.7 | 82.8 |  |  |  |  | 59.57 | 10 | 10 | 12 | 634.47 | 540.48 | 529.28 | 607.15 | 20 | 141.26 | 130.49 | 94.59 |  | 22.3 | 25.3 | 0.3 | 714.44 | 5.16 | 0.62 | 1.02
296 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR014 | 1S-DL-YP-ETC-DLNR-2501-LGR014 | TIKONA PARK:ID | TG-LGR014A-2 | 19505669 | 990 | 200 | 244 | 0.98 | 865 | 241 | 1049 | 362 | 1591 | 262 | 1145 | 501 | 2019-06-30 23:30 | 202.4 | 39.2 | 1591 | Y | 92 | 109 | 98 | 17 | 0.2 | 0.1 | 4.7 | 95 | 1 |  |  |  | 257.3 | 156.04 | 156.04 | 185.53 | 445.24 | 511.5 | 511.2 | 513.01 | 0.3 | 31 | 1 | 6 | 0.3 | 6 | 0.3 |  | 704.54 | 15.06 | 0.54 | 0.87
297 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR014 | 1S-DL-YP-ETC-DLNR-2501-LGR014 | TIKONA PARK:ID | TG-LGR014A-3 | 19505467 | 630 | 200 | 249 | 0.98 | 727 | 295 | 1191 | 198 | 794 | 234 | 935 | 349 | 2019-06-11 23:30 | 134.2 | 30 | 1206 | R | 119 | 83 | 98 | 36 | 0.2 | 0.1 | 36.5 | 63.2 |  |  |  |  | 0.3 | 113.05 | 113.05 | 18.3 | 390.27 | 525.36 | 516.26 | 546.47 | 208.44 | 65.3 | 108.24 | 103.24 | 104.3 |  | 39 | 35.3 | 704.11 | 15.49 | 0.58 | 1.15
298 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR014 | 1S-DL-YP-ETC-DLNR-2501-LGR014 | TIKONA PARK:ID | TG-LGR014A-4 | 19505750 | 630 | 200 | 244 | 0.97 | 505 | 232 | 949 | 134 | 545 | 139 | 561 | 396 | 2019-06-11 23:30 | 102.2 | 28.4 | 1106 | R | 130 | 88 | 82 | 48 | 0.1 | 0.5 | 48.4 | 51 |  | 7.56 | 22.23 |  | 134.19 | 426.11 | 426.11 | 341.37 | 476.41 | 270.23 | 221.24 | 362.23 | 83 |  |  | 0.3 | 10.3 |  |  |  | 704.3 | 15.3 | 0.54 | 0.8
299 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR016 | 1S-DL-YP-ETC-DLNR-2501-LGR016 | WEST GURU ANGAD NAGAR, SCHOOL WALA | TG-LGR016A-1 | 19502944 | 990 | 320 | 246 | 0.98 | 755 | 224 | 938 | 265 | 1126 | 265 | 1117 | 184 | 2019-06-10 00:30 | 134.7 | 30.9 | 1181 | B | 91 | 104 | 104 | 13 |  |  | 43.8 | 56.2 | 1 | 1 | 1 | 1 | 184.53 | 104.53 | 104.53 | 125.53 | 532.45 | 606.45 | 603.04 | 591.45 |  | 6 | 13.3 | [5 empty] | 718.38 | 1.22 | 0.67 | 0.76
300 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR017 | 1S-DL-YP-ETC-DLNR-2501-LGR017 | POLICE QTR SHAKARPUR:ID | TG-LGR017A-1 | 19505830 | 990 | 320 | 242 | 0.98 | 224 | 90 | 381 | 75 | 315 | 60 | 256 | 108 | 2019-06-30 | 61.8 | 13.4 | 618 | R | 117 | 93 | 90 | 27 | 0.3 | 0.1 | 40.8 | 58.7 | 575.23 | 708.53 | 711.23 | 686.23 | 139.3 | 6 | 6 | 28.3 | [12 empty] | 714.53 | 5.07 | 0.57 | 0.23
301 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR017 | 1S-DL-YP-ETC-DLNR-2501-LGR017 | POLICE QTR SHAKARPUR:ID | TG-LGR017A-2 | 19503391 | 990 | 320 | 233 | 0.97 | 784 | 283 | 1252 | 237 | 1049 | 264 | 1170 | 177 | 2019-06-30 00:30 | 140.6 | 69.9 | 1291 | R | 100 | 95 | 104 | 9 |  |  | 13.5 | 86.5 |  |  |  |  | 108.27 | 156.23 | 156.23 | 104.27 | 583.26 | 539.3 | 608.56 | 591.26 | 4 |  | 5 | [5 empty] | 695.53 | 0.07 | 0.64 | 0.79
302 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR018 | 1S-DL-YP-ETC-DLNR-2501-LGR018 | D BLOCK KHATTA VIKAS MARG:PL | TG-LGR018A-1 | 19506589 | 990 | 320 | 238 | 0.98 | 719 | 268 | 1224 | 225 | 1011 | 226 | 1012 | 212 | 2019-06-10 23:00 | 145 | 40.3 | 1312 | Y | 94 | 107 | 99 | 13 | 0.3 | 0.1 | 7.4 | 92.2 |  |  |  |  | 230 | 69.3 | 69.3 | 136 | 464.12 | 620.42 | 521.12 | 558.42 | 0.3 | 4.3 | [6 empty] | 694.42 | 25.18 | 0.67 | 0.73
303 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR018 | 1S-DL-YP-ETC-DLNR-2501-LGR018 | D BLOCK KHATTA VIKAS MARG:PL | TG-LGR018A-2 | 19504830 | 990 | 320 | 236 | 0.98 | 830 | 312 | 1363 | 283 | 1239 | 235 | 1038 | 284 | 2019-06-11 22:30 | 134.7 | 60.4 | 1480 | R | 114 | 97 | 90 | 24 |  |  | 47.1 | 52.9 |  |  |  |  | 1 | 10 | 10 | 6.3 | 524.1 | 686.37 | 697 | 706 | 193.5 | 22.53 |  | 7 | 0.3 |  |  |  | 719.3 | 0.3 | 0.75 | 0.84
304 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR018 | 1S-DL-YP-ETC-DLNR-2501-LGR018 | D BLOCK KHATTA VIKAS MARG:PL | TG-LGR018A-3 | 19506175 | 630 | 200 | 244 | 0.97 | 384 | 141 | 586 | 124 | 515 | 119 | 488 | 87 | 2019-06-25 16:00 | 148.2 | 14.4 | 709 | Y | 113 | 94 | 92 | 21 | 0.2 | 0.1 | 31.3 | 68.4 | 39.58 | 195.15 | 119.55 | 81 | 468.47 | 331 | 331 | 449.15 | 187.27 | 169.57 | 93 | 165.57 | [8 empty] | 696.12 | 23.48 | 0.51 | 0.61
305 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR019 | 1S-DL-YP-ETC-DLNR-2501-LGR019 | RAMESH PARK J & K BLOCK:PL | TG-LGR019A-1 | 19502336 | 1600 | 500 | 242 | 0.97 | 1286 | 421 | 1847 | 471 | 2103 | 393 | 1728 | 332 | 2019-06-01 | 203.6 | 88.6 | 2103 | Y | 95 | 114 | 91 | 23 |  | 0.9 | 93.3 | 5.8 |  |  | 1 |  | 269.27 | 83 | 83 | 202.57 | 450.09 | 604.17 | 391.09 | 516.09 |  | 32.19 |  | 0.3 |  |  |  |  | 719.36 | 0.24 | 0.6 | 0.8
306 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR020 | 1S-DL-YP-ETC-DLNR-2501-LGR020 | MASTER BLOCK SHAKARPUR:PL | TG-LGR020A-1 | 19502830 | 990 | 320 | 237 | 0.98 | 593 | 282 | 1243 | 169 | 768 | 142 | 650 | 544 | 2019-06-11 01:30 | 89.1 | 24.3 | 1259 | R | 135 | 85 | 80 | 55 | 99.7 | 0.3 |  |  |  | 30.3 | 78 | 1 | 169.3 | 594 | 594 | 490.3 | 521.3 | 71.3 | 43 | 204.3 | 5 | [7 empty] | 696 | 0 | 0.6 | 0.6
307 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR020 | 1S-DL-YP-ETC-DLNR-2501-LGR020 | MASTER BLOCK SHAKARPUR:PL | TG-LGR020A-2 | 19505481 | 630 | 200 | 237 | 0.98 | 546 | 158 | 698 | 154 | 673 | 234 | 1044 | 359 | 2019-06-28 23:00 | 92.6 | 27 | 1099 | B | 94 | 94 | 113 | 19 | 0.3 | 1.1 | 27.4 | 71.2 |  | 3 |  |  | 212.52 | 249.22 | 249.22 | 169.52 | 376 | 332 | 416.52 | 405.3 |  | 4.3 | 53 | 13.3 |  |  | 9 |  | 696.11 | 23.49 | 0.57 | 0.87
308 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR021 | 1S-DL-YP-ETC-DLNR-2501-LGR021 | G-BLOCK SHAKARPUR:K | TG-LGR021A-1 | 19504461 | 990 | 320 | 240 | 0.98 | 1055 | 367 | 1564 | 359 | 1533 | 330 | 1417 | 134 | 2019-06-12 | 175.9 | 61.1 | 1617 | Y | 105 | 100 | 95 | 10 |  |  | 23 | 77 |  |  |  |  | 31.11 | 57.16 | 57.16 | 48.1 | 501.22 | 494.5 | 503.4 | 507.26 | 125 | 107.54 | 102.53 | 116.45 | 29.18 | 26.51 | 0.3 | 14.3 | 686.51 | 33.09 | 0.58 | 1.07
309 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR021 | 1S-DL-YP-ETC-DLNR-2501-LGR021 | G-BLOCK SHAKARPUR:K | TG-LGR021A-2 | 19502945 | 990 | 320 | 240 | 0.98 | 1186 | 406 | 1720 | 384 | 1638 | 396 | 1690 | 72 | 2019-06-30 01:00 | 202.4 | 54.5 | 1931 | B | 92 | 95 | 113 | 21 |  | 1.3 | 45.9 | 52.8 |  |  |  |  | 121.3 | 100.46 | 100.46 | 75.16 | 512.02 | 511.33 | 471.55 | 501.33 | 70.48 | 96.01 | 90.08 | 120.43 | 8.51 | 4.51 | 99.52 | 15.39 | 713.11 | 6.49 | 0.51 | 1.2
310 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR022 | 1S-DL-YP-ETC-DLNR-2501-LGR022 | WB BLOCK SHAKARPUR:K | TG-LGR022A-1 | 19506691 | 990 | 320 | 242 | 0.97 | 1031 | 336 | 1432 | 331 | 1384 | 363 | 1540 | 139 | 2019-06-30 23:00 | 207 | 60.8 | 1569 | R | 100 | 98 | 102 | 4 | 0.1 | 2.2 | 49.6 | 48.1 |  |  |  |  | 94 | 119.3 | 119.3 | 92.3 | 521.2 | 493.5 | 518.5 | 518.2 | 93 | 98 | 97 | 98.3 | 5 | 2 | 9.3 | 4 | 713.2 | 6.4 | 0.55 | 1.04
311 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR022 | 1S-DL-YP-ETC-DLNR-2501-LGR022 | WB BLOCK SHAKARPUR:K | TG-LGR022A-2 | 19502950 | 990 | 320 | 241 | 0.97 | 984 | 348 | 1486 | 361 | 1563 | 274 | 1157 | 373 | 2019-06-30 23:30 | 160.4 | 57.4 | 1635 | Y | 96 | 112 | 92 | 20 |  | 2.4 | 57.5 | 40.1 |  |  |  |  | 154.27 | 40 | 40 | 95.27 | 475.47 | 528.14 | 543.17 | 530.17 | 85.3 | 124.3 | 31.3 | 92.3 | 2.3 | 25.3 |  |  | 718.14 | 1.46 | 0.57 | 0.99
312 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR022 | 1S-DL-YP-ETC-DLNR-2501-LGR022 | WB BLOCK SHAKARPUR:K | TG-LGR022A-3 | 19504770 | 990 | 320 | 242 | 0.98 | 870 | 258 | 1073 | 315 | 1320 | 298 | 1258 | 223 | 2019-06-29 23:30 | 138.4 | 16.9 | 1343 | Y | 94 | 104 | 102 | 10 |  |  | 33.8 | 66.2 | 2.3 | 1.3 | 1 | 1 | 260.45 | 182 | 182 | 214.27 | 423.51 | 488.36 | 464.39 | 469.09 | 6.3 | 21.3 | 18 | 9 |  |  |  |  | 693.36 | 2.24 | 0.56 | 0.88
313 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR022 | 1S-DL-YP-ETC-DLNR-2501-LGR022 | WB BLOCK SHAKARPUR:K | TG-LGR022A-4 | 19506276 | 630 | 200 | 242 | 0.98 | 639 | 187 | 800 | 213 | 908 | 240 | 1040 | 209 | 2019-06-03 00:30 | 142.8 | 10.6 | 1040 | B | 86 | 108 | 106 | 22 | 0.1 | 0.1 | 28.2 | 71.6 | 7 | 1.3 | 2.3 | 2.3 | 306.52 | 116.3 | 116.3 | 170 | 390.07 | 507.59 | 479.59 | 487.59 | 6.16 | 81.54 | 88.54 | 49.24 |  | 2.22 | 2.52 | 0.22 | 710.15 | 9.45 | 0.51 | 1.01
314 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR023 | 1S-DL-YP-ETC-DLNR-2501-LGR023 | ARA MACHINE SHAKARPUR:PM | TG-LGR023A-1 | 19505890 | 990 | 320 | 236 | 0.99 | 584 | 160 | 686 | 137 | 562 | 287 | 1308 | 692 | 2019-06-12 19:00 | 127.7 | 17.6 | 1308 | B | 104 | 77 | 119 | 42 | 0.2 | 1.4 | 56.8 | 41.6 |  | 13 |  |  | 264.3 | 610.51 | 610.51 | 295.3 | 455.21 | 96 | 582.51 | 424.21 |  |  | 0.3 | [5 empty] | 719.51 | 0.09 | 0.7 | 0.59
315 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR024 | 1S-DL-YP-ETC-DLNR-2501-LGR024 | SHAKARPUR SANJAY PARK | TG-LGR024A-1 | 19505154 | 990 | 320 | 242 | 0.98 | 1211 | 417 | 1835 | 489 | 2257 | 305 | 1329 | 804 | 2019-06-02 00:30 | 209.3 | 61.4 | 2257 | Y | 98 | 104 | 98 | 6 | 0.2 | 0.1 | 28.6 | 71.1 |  |  |  |  | 25 | 17.3 | 17.3 | 14.3 | 514.12 | 476.06 | 526.42 | 511.58 | 141.3 | 137.06 | 153 | 144.14 | 25.45 | 75.45 | 14.45 | 35.45 | 706.27 | 13.33 | 0.56 | 1.22
316 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR024 | 1S-DL-YP-ETC-DLNR-2501-LGR024 | SHAKARPUR SANJAY PARK | TG-LGR024A-2 | 19502827 | 990 | 320 | 232 | 0.98 | 1061 | 345 | 1568 | 374 | 1705 | 342 | 1563 | 139 | 2019-06-11 23:30 | 187.7 | 32.4 | 1841 | R | 114 | 91 | 95 | 23 |  |  | 25.4 | 74.6 |  | 1 | 0.3 | 0.3 | 8 | 94.18 | 94.18 | 43.23 | 507.33 | 542.15 | 521.42 | 551.57 | 147.3 | 70.15 | 94.43 | 106.43 | 53.15 | 8.3 | 7.45 | 13.45 | 716.18 | 3.42 | 0.58 | 1.07
317 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR025 | 1S-DL-YP-ETC-DLNR-2501-LGR025 | DALL MILL SHAKARPUR:PM | TG-LGR025A-1 | 19502941 | 990 | 320 | 242 | 0.98 | 892 | 316 | 1331 | 264 | 1098 | 313 | 1310 | 223 | 2019-06-29 23:30 | 141.3 | 53 | 1417 | R | 115 | 82 | 103 | 33 |  |  | 55 | 45 |  |  |  |  | 6.3 | 226.27 | 226.27 | 41 | 587.45 | 491.48 | 609.15 | 641.45 | 125 | 1 | 73 | 36.3 |  |  |  |  | 719.15 | 0.45 | 0.63 | 0.9
318 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR026 | 1S-DL-YP-ETC-DLNR-2501-LGR026 | POLICE BOOTH S. PUR, V. MARG:PL | TG-LGR026A-1 | 19506000 | 990 | 320 | 238 | 0.98 | 843 | 263 | 1204 | 209 | 939 | 371 | 1723 | 691 | 2019-06-10 23:30 | 191.4 | 27.2 | 1742 | B | 108 | 79 | 113 | 34 | 0.7 | 12.1 | 75.2 | 11.9 |  | 4 | 0.3 | 1.3 | 10.3 | 158.3 | 158.3 | 17 | 640.54 | 548.49 | 579.54 | 677.19 | 59.55 |  | 116.55 | 15.3 |  |  | 4 |  | 711.19 | 8.41 | 0.7 | 0.85
319 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR027 | 1S-DL-YP-ETC-DLNR-2501-LGR027 | U BLOCK SHAKARPUR, V. MARG:PL | TG-LGR027A-1 | 19506384 | 990 | 320 | 234 | 0.98 | 864 | 333 | 1516 | 236 | 1065 | 296 | 1350 | 395 | 2019-06-15 23:30 | 211.8 | 52.5 | 1516 | R | 114 | 77 | 109 | 37 | 0.6 | 12.3 | 20 | 67.1 |  |  |  |  | 12 | 343.51 | 343.51 | 44 | 686.09 | 367.48 | 677.39 | 667.09 | 13 |  | 5 | 0.3 | 0.3 |  |  |  | 711.39 | 8.21 | 0.59 | 0.87
320 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR027 | 1S-DL-YP-ETC-DLNR-2501-LGR027 | U BLOCK SHAKARPUR, V. MARG:PL | TG-LGR027A-2 | 19504762 | 990 | 320 | 243 | 0.98 | 840 | 310 | 1318 | 257 | 1111 | 273 | 1159 | 187 | 2019-06-29 16:00 | 170.8 | 43.4 | 1387 | R | 102 | 91 | 108 | 17 |  | 2.9 | 91.1 | 6.1 |  | 0.3 |  |  | 296.23 | 322.23 | 322.23 | 215.23 | 321.29 | 395.45 | 599.08 | 485.29 | 100.46 |  | 13.3 | 17.46 |  |  |  |  | 718.38 | 1.22 | 0.59 | 0.85
321 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR029 | 1S-DL-YP-ETC-DLNR-2501-LGR029 | SCHOOL BLOCK SHAKARPUR:PL | TG-LGR029A-1 | 19505466 | 990 | 320 | 238 | 0.97 | 524 | 157 | 673 | 223 | 965 | 143 | 618 | 323 | 2019-06-30 23:30 | 117.4 | 42.6 | 984 | Y | 94 | 125 | 81 | 44 | 0.1 |  | 8.6 | 91.3 | 9 |  | 61.4 | 2 | 614.12 | 311.09 | 311.09 | 566.42 | 72.3 | 384.33 | 10.3 | 127 | [8 empty] | 695.42 | 24.18 | 0.63 | 0.53
322 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR029 | 1S-DL-YP-ETC-DLNR-2501-LGR029 | SCHOOL BLOCK SHAKARPUR:PL | TG-LGR029A-2 | 19506483 | 990 | 320 | 245 | 0.98 | 695 | 163 | 688 | 184 | 782 | 348 | 1489 | 758 | 2019-06-05 23:30 | 194.2 | 21.4 | 1489 | B | 92 | 112 | 96 | 20 | 0.1 | 0.1 | 7.6 | 92.2 | 1.3 | 1.3 | 1.3 | 1.3 | 427.5 | 166.3 | 166.3 | 301.28 | 284.29 | 545.49 | 358.26 | 410.51 | [6 empty] | 0.3 |  | 713.49 | 6.11 | 0.59 | 0.7
323 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR030 | 1S-DL-YP-ETC-DLNR-2501-LGR030 | BODH VIHAR LAXMI NAGAR:K | TG-LGR030A-1 | 19503402 | 990 | 320 | 238 | 0.98 | 815 | 229 | 1030 | 308 | 1413 | 278 | 1260 | 333 | 2019-06-01 | 159 | 45.6 | 1424 | Y | 88 | 115 | 98 | 27 |  | 0.5 | 34.6 | 64.9 | 3.3 |  |  |  | 318.51 | 102.3 | 102.3 | 202.24 | 396.03 | 532.37 | 496.32 | 511.32 |  | 83.17 | 2.28 | 4.28 |  |  |  |  | 718.24 | 1.36 | 0.6 | 0.82
324 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR030 | 1S-DL-YP-ETC-DLNR-2501-LGR030 | BODH VIHAR LAXMI NAGAR:K | TG-LGR030A-2 | 19504644 | 630 | 200 | 244 | 0.97 | 580 | 189 | 766 | 215 | 884 | 175 | 719 | 148 | 2019-06-05 03:30 | 122.8 | 32.2 | 973 | Y | 95 | 110 | 95 | 15 |  | 0.6 | 51.8 | 47.6 |  |  |  |  | 177.57 | 101.3 | 101.3 | 136.3 | 514.52 | 510.37 | 544.25 | 540.53 | 25.35 | 103.47 | 9.3 | 41.01 |  | 2.3 |  |  | 718.24 | 1.36 | 0.58 | 0.92
325 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR031 | 1S-DL-YP-ETC-DLNR-2501-LGR031 | MANGAL BAZAR LAXMI NAGAR:PL | TG-LGR031A-1 | 19504511 | 990 | 320 | 244 | 0.98 | 1213 | 387 | 1620 | 461 | 1944 | 364 | 1536 | 373 | 2019-06-12 00:30 | 228.2 | 63.3 | 1944 | Y | 99 | 111 | 91 | 20 |  |  | 3.3 | 96.7 |  |  |  |  | 8.5 | 0.3 | 0.3 | 6 | 528.49 | 419.4 | 557.08 | 516.25 | 155.15 | 207.28 | 108 | 166.18 | 21.49 | 87.05 | 7.3 | 26 | 714.43 | 5.17 | 0.57 | 1.22
326 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR031 | 1S-DL-YP-ETC-DLNR-2501-LGR031 | MANGAL BAZAR LAXMI NAGAR:PL | TG-LGR031A-2 | 19502775 | 990 | 200 | 246 | 0.98 | 691 | 258 | 1082 | 192 | 800 | 240 | 1011 | 254 | 2019-06-11 23:30 | 118.2 | 49.2 | 1121 | B | 106 | 91 | 103 | 15 |  |  | 4.2 | 95.8 |  | 1.3 | 1 |  | 240.07 | 381.37 | 381.37 | 302.37 | 478.04 | 335.04 | 435.04 | 415.34 | [8 empty] | 718.11 | 1.49 | 0.62 | 0.7
327 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR031 | 1S-DL-YP-ETC-DLNR-2501-LGR031 | MANGAL BAZAR LAXMI NAGAR:PL | TG-LGR031A-3 | 19506025 | 990 | 320 | 249 | 0.97 | 830 | 319 | 1367 | 256 | 1094 | 255 | 1098 | 271 | 2019-06-10 23:30 | 191 | 57.6 | 1537 | R | 110 | 95 | 95 | 15 | 0.3 |  | 3.6 | 96.1 |  |  |  |  | 115.21 | 236.09 | 236.09 | 186.39 | 554.55 | 480.37 | 469.37 | 525.07 | 46.3 | 0.3 | 3.3 | 5.3 | 0.3 |  |  |  | 717.16 | 2.44 | 0.59 | 0.84
328 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR032 | 1S-DL-YP-ETC-DLNR-2501-LGR032 | KULDEEP NURSING HOME LNG:K | TG-LGR032A-1 | 19502461 | 990 | 320 | 244 | 0.97 | 902 | 287 | 1171 | 298 | 1227 | 318 | 1304 | 116 | 2019-06-11 21:30 | 171.5 | 56.7 | 1344 | B | 93 | 102 | 105 | 12 |  | 0.3 | 22.1 | 77.7 |  |  |  |  | 110.23 | 91.01 | 91.01 | 91.01 | 592.55 | 564.47 | 554.23 | 576.47 | 10 | 57.3 | 82.43 | 45.3 |  |  |  |  | 713.18 | 6.42 | 0.62 | 0.91
329 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR032 | 1S-DL-YP-ETC-DLNR-2501-LGR032 | KULDEEP NURSING HOME LNG:K | TG-LGR032A-2 | 19502463 | 990 | 320 | 245 | 0.98 | 917 | 310 | 1253 | 284 | 1148 | 323 | 1315 | 146 | 2019-06-12 00:30 | 153.1 | 36.8 | 1355 | R | 102 | 97 | 101 | 5 |  | 0.1 | 14.6 | 85.3 |  |  |  |  | 169.55 | 205 | 205 | 191.25 | 491.18 | 498.3 | 447.35 | 484.05 | 58 | 15.43 | 60.43 | 43.43 |  |  |  |  | 719.13 | 0.47 | 0.55 | 0.93
330 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR032 | 1S-DL-YP-ETC-DLNR-2501-LGR032 | KULDEEP NURSING HOME LNG:K | TG-LGR032A-3 | 19505951 | 990 | 320 | 246 | 0.97 | 727 | 264 | 1149 | 225 | 985 | 238 | 1041 | 145 | 2019-06-28 23:00 | 170.9 | 40.3 | 1255 | B | 103 | 102 | 95 | 8 | 0.4 | 0.1 | 18.9 | 80.6 |  | 9 | 12.3 | 1 | 350.24 | 318.48 | 318.48 | 366.18 | 355.08 | 378.14 | 298.17 | 338.44 | 0.3 |  | 0.3 | [5 empty] | 706.02 | 13.58 | 0.57 | 0.73
331 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR033 | 1S-DL-YP-ETC-DLNR-2501-LGR033 | U BLOCK SHAKARPUR:PM | TG-LGR033A-1 | 19502818 | 1600 | 500 | 242 | 0.98 | 1181 | 405 | 1727 | 363 | 1563 | 413 | 1766 | 187 | 2019-06-12 14:30 | 245 | 79.4 | 1766 | B | 102 | 96 | 102 | 6 |  |  | 8 | 92 |  |  |  |  | 45 | 109.01 | 109.01 | 57.33 | 671.35 | 607.34 | 665.32 | 659.02 | [8 empty] | 716.35 | 3.25 | 0.69 | 0.74
332 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR034 | 1S-DL-YP-ETC-DLNR-2501-LGR034 | MOHAN PARK LAXMI NAGAR:K | TG-LGR034A-1 | 19502470 | 990 | 320 | 239 | 0.98 | 910 | 305 | 1298 | 293 | 1254 | 312 | 1330 | 66 | 2019-06-11 19:30 | 155.3 | 53 | 1413 | B | 97 | 95 | 108 | 13 |  |  | 17.8 | 82.2 |  |  |  |  | 11 | 19.3 | 19.3 | 7.3 | 660.42 | 667.42 | 600.17 | 659.58 | 46 | 30.3 | 111.55 | 50.14 |  |  |  |  | 717.42 | 2.18 | 0.68 | 0.92
333 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR035 | 1S-DL-YP-ETC-DLNR-2501-LGR035 | N.GANESH NAGAR SHAKARPUR:PL | TG-LGR035A-1 | 19502820 | 630 | 200 | 229 | 0.98 | 563 | 151 | 668 | 205 | 922 | 208 | 917 | 251 | 2019-06-30 | 84.2 | 23.5 | 1027 | B | 81 | 109 | 110 | 29 |  | 1.8 | 62 | 36.2 | 5.59 |  | 3 | 1 | 340.36 | 94 | 94 | 151.21 | 372 | 551.35 | 512.35 | 530.44 |  | 73 | 95.3 | 35.3 |  |  | 6.3 |  | 718.35 | 1.25 | 0.59 | 0.89
334 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR036 | 1S-DL-YP-ETC-DLNR-2501-LGR036 | SHIROMANI SCHOOL, SHAKARPUR:PL | TG-LGR036A-1 | 19506252 | 990 | 320 | 240 | 0.95 | 1033 | 357 | 1551 | 242 | 1048 | 433 | 1908 | 748 | 2019-06-30 23:30 | 327 | 83.8 | 1908 | B | 101 | 84 | 115 | 31 | 0.1 | 0.1 | 25.5 | 74.3 | 5.09 | 5.3 |  |  | 179.45 | 276.5 | 276.5 | 128.2 | 407.09 | 410.42 | 524.24 | 496.43 | 92.59 | 2.3 | 119.59 | 69.59 | 10.3 |  | 22 | 0.3 | 695.32 | 24.28 | 0.52 | 1.04
335 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR036 | 1S-DL-YP-ETC-DLNR-2501-LGR036 | SHIROMANI SCHOOL, SHAKARPUR:PL | TG-LGR036A-2 | 19504467 | 990 | 320 | 248 | 0.97 | 597 | 145 | 602 | 242 | 998 | 211 | 874 | 351 | 2019-06-30 | 106.7 | 45.6 | 1007 | Y | 80 | 114 | 106 | 34 |  | 0.6 | 24.5 | 74.8 | 28.56 |  | 1 |  | 412.25 | 258.07 | 258.07 | 339.33 | 35.17 | 218.31 | 173.15 | 137.05 | [8 empty] | 476.38 | 147.22 | 0.61 | 0.6
336 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR037 | 1S-DL-YP-ETC-DLNR-2501-LGR037 | NEHRU ENCLAVE SHAKARPUR:K | TG-LGR037A-1 | 19502517 | 990 | 320 | 234 | 0.99 | 621 | 205 | 908 | 176 | 777 | 240 | 1057 | 243 | 2019-06-10 23:30 | 80.2 | 19.1 | 1071 | B | 106 | 87 | 106 | 19 |  |  | 40.8 | 59.2 | 1 | 19.3 | 5 | 4 | 436.3 | 548.55 | 548.55 | 483 | 282.21 | 151.26 | 278.21 | 232.51 | [8 empty] | 719.51 | 0.09 | 0.59 | 0.63
337 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR037 | 1S-DL-YP-ETC-DLNR-2501-LGR037 | NEHRU ENCLAVE SHAKARPUR:K | TG-LGR037A-2 | 19506185 | 990 | 320 | 248 | 0.97 | 691 | 229 | 953 | 212 | 881 | 250 | 1045 | 142 | 2019-06-30 23:00 | 166.4 | 41.6 | 1045 | B | 98 | 96 | 106 | 10 | 0.1 |  | 10.2 | 89.7 | 8.3 | 5 | 0.3 | 4 | 438.3 | 464 | 464 | 436 | 266.51 | 244.51 | 334.21 | 273.51 | [8 empty] | 713.51 | 6.09 | 0.56 | 0.7
338 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR038 | 1S-DL-YP-ETC-DLNR-2501-LGR038 | PWD KIOSK LAXMI NAGAR:K | TG-LGR038A-1 | 19504464 | 990 | 320 | 244 | 0.98 | 537 | 178 | 728 | 175 | 714 | 185 | 762 | 42 | 2019-06-14 11:30 | 83.2 | 15.5 | 857 | R | 99 | 99 | 102 | 3 |  |  | 12.3 | 87.7 | 266.23 | 252.23 | 183.55 | 225.23 | 295.57 | 304.3 | 304.3 | 330.3 | 157.3 | 162.57 | 159.27 | 163.57 | [8 empty] | 719.5 | 0.1 | 0.51 | 0.54
339 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR038 | 1S-DL-YP-ETC-DLNR-2501-LGR038 | PWD KIOSK LAXMI NAGAR:K | TG-LGR038A-2 | 19506172 | 630 | 200 | 247 | 0.98 | 422 | 144 | 587 | 103 | 421 | 175 | 720 | 260 | 2019-06-12 16:00 | 88.8 | 18.2 | 754 | B | 94 | 93 | 113 | 20 | 0.1 |  | 25.2 | 74.7 | 13 | 1 |  | 1 | 409.43 | 401.22 | 401.22 | 386.26 | 273 | 293.21 | 419.36 | 308.17 |  |  | 1 | [5 empty] | 695.43 | 24.17 | 0.62 | 0.67
340 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR040 | 1S-DL-YP-ETC-DLNR-2501-LGR040 | J EXTN. LAXMI NAGAR:PM | TG-LGR040A-1 | 19503409 | 990 | 320 | 229 | 0.98 | 1156 | 351 | 1489 | 365 | 1626 | 440 | 1926 | 387 | 2019-06-30 01:30 | 214.9 | 67 | 2005 | B | 90 | 95 | 115 | 25 | 74.4 | 10 | 7 | 8.7 |  |  |  |  | 20.23 | 70.16 | 70.16 | 31.23 | 601.11 | 518.37 | 453.3 | 527.06 | 85.33 | 114.14 | 181.38 | 143.48 | 1.29 | 5.29 | 62.58 | 6.19 | 708.36 | 11.24 | 0.56 | 1.17
341 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR041 | 1S-DL-YP-ETC-DLNR-2501-LGR041 | KUNDAN NAGAR, LAXMI NAGAR:K | TG-LGR041A-1 | 19505457 | 990 | 320 | 236 | 0.98 | 1052 | 348 | 1512 | 313 | 1354 | 391 | 1710 | 308 | 2019-06-11 01:00 | 202.6 | 64.6 | 1729 | R | 101 | 87 | 112 | 25 | 0.2 |  | 14 | 85.7 |  |  |  |  | 35.3 | 100.03 | 100.03 | 37.3 | 513.24 | 515.07 | 479.54 | 519.54 | 76.31 | 11.15 | 106.46 | 68.31 | 1 |  | 21.45 | 0.3 | 626.25 | 45.35 | 0.55 | 1.06
342 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR042 | 1S-DL-YP-ETC-DLNR-2501-LGR042 | V. SAVARKAR BLOCK, SHAKARPUR:PL | TG-LGR042A-1 | 19506382 | 990 | 320 | 244 | 0.98 | 975 | 304 | 1266 | 339 | 1415 | 332 | 1401 | 143 | 2019-06-10 15:00 | 267.5 | 14.1 | 2020 | Y | 98 | 115 | 86 | 29 | 0.4 |  | 15.9 | 83.7 | 372.52 | 357.52 | 413.52 | 374.52 | 103.57 | 104.57 | 104.57 | 103.27 | 169.47 | 113.53 | 211.29 | 186.04 | 62.4 | 124.33 | 0.3 | 45.22 | 0.29 | 8.3 | 0.3 |  | 709.45 | 10.15 | 0.34 | 0.98
343 | 2019-06-01 | 2019-06-30 21:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR043 | 1S-DL-YP-ETC-DLNR-2501-LGR043 | SUNDER BLOCK, SHAKARPUR:PL | TG-LGR043A-1 | 19502815 | 1600 | 500 | 243.3516 | 0.98012 | 1768.3862 | 380.2798 | 1630.5626 | 397.481 | 1707.686 | 990.6254 | 4230.9105 | 2562.6567 | 2019-06-30 01:30 | [15 empty] | 0 |  |  |  | 67.5 |  |  |  | 500.5 |  |  |  | 82.5 |  |  |  | 16.5 | 667 |  | 0.53799 | 1.1052
344 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR044 | 1S-DL-YP-ETC-DLNR-2501-LGR044 | N. ENCL. HARIZON BASTI, S PUR:PL | TG-LGR044A-1 | 19505887 | 990 | 320 | 247 | 0.97 | 712 | 255 | 1071 | 235 | 983 | 222 | 927 | 126 | 2019-06-30 23:30 | 187.8 | 53.4 | 1085 | R | 110 | 100 | 89 | 21 | 0.1 |  | 8 | 91.9 |  |  |  |  | 176 | 299 | 299 | 298.3 | 543.46 | 420.46 | 290.46 | 421.16 | [8 empty] | 719.46 | 0.14 | 0.62 | 0.72
345 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR045 | 1S-DL-YP-ETC-DLNR-2501-LGR045 | INST. OF COMMERCIAL PRACTICE:ID | TG-LGR045A-1 | 19502816 | 400 | 120 | 231 | 0.96 | 164 | 47 | 213 | 56 | 250 | 62 | 278 | 57 | 2019-06-30 23:30 | 51.3 | 6.3 | 310 | B | 88 | 106 | 107 | 19 |  |  | 17.4 | 82.6 | 268.3 | 183.3 | 197 | 172 | 451.3 | 512 | 512 | 546.3 |  | 24.3 | 62 | 1.3 | [8 empty] | 720 | 0 | 0.6 | 0.41
346 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR046 | 1S-DL-YP-ETC-DLNR-2501-LGR046 | VISHWAKARMA PARK:K | TG-LGR046A-1 | 19504599 | 990 | 320 | 244 | 0.97 | 564 | 209 | 893 | 212 | 897 | 143 | 608 | 287 | 2019-06-06 03:30 | 92.7 | 32.4 | 897 | Y | 110 | 108 | 83 | 27 |  |  | 51.2 | 48.8 | 42.29 | 44.59 | 221.16 | 77.56 | 488.07 | 491.37 | 491.37 | 494.4 | 186.04 | 180.04 | 26.53 | 144.04 | [8 empty] | 716.4 | 3.2 | 0.54 | 0.57
347 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR046 | 1S-DL-YP-ETC-DLNR-2501-LGR046 | VISHWAKARMA PARK:K | TG-LGR046A-2 | 19502821 | 990 | 320 | 244 | 0.98 | 521 | 173 | 708 | 180 | 731 | 167 | 684 | 41 | 2019-06-12 01:00 | 92 | 21.3 | 843 | B | 93 | 100 | 107 | 14 |  |  | 47.3 | 52.7 | 15.3 | 24.29 | 3 | 3 | 591.15 | 504.57 | 504.57 | 553.19 | 109.56 | 187.15 | 205.15 | 160.22 | [8 empty] | 716.41 | 3.19 | 0.65 | 0.53
348 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR049 | 1S-DL-YP-ETC-DLNR-2501-LGR049 | R BLOCK SHAKARPUR:PL | TG-LGR049A-1 | 19504568 | 990 | 320 | 236 | 0.99 | 441 | 134 | 593 | 119 | 516 | 188 | 814 | 268 | 2019-06-01 15:00 | 67 | 14 | 814 | B | 79 | 102 | 119 | 40 | 32.4 | 41 | 26 | 0.6 | 240 | 46 | 9.3 | 35.3 | 478.18 | 614.07 | 614.07 | 651.48 | 1 | 59.11 | 180.18 | 32 | [8 empty] | 719.18 | 0.42 | 0.66 | 0.45
349 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR049 | 1S-DL-YP-ETC-DLNR-2501-LGR049 | R BLOCK SHAKARPUR:PL | TG-LGR049A-2 | 19504448 | 630 | 200 | 231 | 0.98 | 544 | 205 | 896 | 205 | 891 | 134 | 578 | 315 | 2019-06-29 23:30 | 91.5 | 33.6 | 928 | B | 102 | 105 | 93 | 12 |  | 0.3 | 30.9 | 68.7 |  |  |  |  | 16.3 | 4.3 | 4.3 | 15 | 659.5 | 657.24 | 520.2 | 697.5 | 43.24 | 57.5 | 44.54 | 6.54 |  |  |  |  | 719.44 | 0.16 | 0.69 | 0.86
350 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR051 | 1S-DL-YP-ETC-DLNR-2501-LGR051 | H BLOCK LAXMI NAGAR:PL | TG-LGR051A-1 | 19502010 | 990 | 320 | 237 | 0.98 | 552 | 225 | 1025 | 202 | 916 | 125 | 562 | 419 | 2019-06-08 15:30 | 126.6 | 38.3 | 1025 | R | 124 | 100 | 77 | 47 |  |  | 36.4 | 63.6 |  | 2.3 | 62.3 | 2.3 | 176.3 | 386.53 | 386.53 | 373.23 | 541.44 | 328.51 | 20.11 | 342.21 | [8 empty] | 718.14 | 1.46 | 0.69 | 0.56
351 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR051 | 1S-DL-YP-ETC-DLNR-2501-LGR051 | H BLOCK LAXMI NAGAR:PL | TG-LGR051A-2 | 19504765 | 630 | 200 | 242 | 0.99 | 696 | 206 | 893 | 280 | 1226 | 210 | 904 | 327 | 2019-06-26 14:30 | 75.4 | -6.9 | 1230 | Y | 90 | 113 | 96 | 23 |  |  | 16.9 | 83.1 |  |  |  |  | 87.28 | 33 | 33 | 45.58 | 502.13 | 386.23 | 481.46 | 475.55 | 127.45 | 156.24 | 154.27 | 162.03 | 1 | 142.39 | 9.15 | 34.3 | 718.26 | 1.34 | 0.59 | 1.1
352 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR052 | 1S-DL-YP-ETC-DLNR-2501-LGR052 | RAMESH PARK, G NO.12, LN:PL | TG-LGR052A-1 | 19504589 | 990 | 320 | 235 | 0.98 | 903 | 283 | 1203 | 368 | 1576 | 253 | 1085 | 444 | 2019-06-30 00:30 | 159 | 64 | 1576 | Y | 103 | 108 | 89 | 19 |  |  | 1.2 | 98.8 |  |  |  |  | 22.3 | 15.3 | 15.3 | 28.3 | 642.2 | 580.33 | 622.06 | 642.03 | 52.13 | 118 | 2.3 | 48.3 | 2 | 5 |  |  | 719.03 | 0.57 | 0.65 | 0.91
353 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR052 | 1S-DL-YP-ETC-DLNR-2501-LGR052 | RAMESH PARK, G NO.12, LN:PL | TG-LGR052A-2 | 19506150 | 990 | 320 | 237 | 0.97 | 799 | 270 | 1183 | 262 | 1134 | 267 | 1165 | 43 | 2019-06-03 01:00 | 169.3 | 53.4 | 1293 | R | 104 | 97 | 99 | 7 | 0.2 | 0.2 | 13.7 | 85.9 |  |  |  |  | 78 | 126.3 | 126.3 | 101.3 | 611.34 | 577.34 | 586.04 | 602.04 | 15 | 0.3 | 1 | 1 |  |  |  |  | 704.34 | 15.26 | 0.64 | 0.81
354 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR053 | 1S-DL-YP-ETC-DLNR-2501-LGR053 | RAMESH PARK, JJ CLUSTER:PL | TG-LGR053A-1 | 19506253 | 630 | 200 | 240 | 0.97 | 332 | 150 | 646 | 72 | 308 | 110 | 473 | 293 | 2019-06-30 | 108 | 30.2 | 646 | R | 118 | 80 | 102 | 38 | 0.4 |  | 1.3 | 98.4 |  | 8.3 | 0.3 |  | 296.27 | 702.22 | 702.22 | 510.04 | 417.25 | 3 | 270.48 | 203.48 | [8 empty] | 713.52 | 6.08 | 0.7 | 0.53
355 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR054 | 1S-DL-YP-ETC-DLNR-2501-LGR054 | KISHAN KUNJ ENTN.:PL | TG-LGR054A-1 | 19503404 | 990 | 320 | 240 | 0.97 | 793 | 251 | 1013 | 238 | 969 | 304 | 1237 | 249 | 2019-06-02 23:30 | 187.7 | 58.1 | 1237 | B | 100 | 99 | 101 | 2 |  |  | 5.3 | 94.7 |  |  | 0.3 |  | 149.27 | 186.27 | 186.27 | 189.53 | 570.18 | 533.18 | 470.22 | 529.22 |  |  | 20.3 | 0.3 |  |  |  |  | 719.45 | 0.15 | 0.63 | 0.8
356 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR054 | 1S-DL-YP-ETC-DLNR-2501-LGR054 | KISHAN KUNJ ENTN.:PL | TG-LGR054A-2 | 19506147 | 630 | 200 | 240 | 0.97 | 579 | 164 | 710 | 208 | 987 | 208 | 949 | 260 | 2019-06-11 01:00 | 127 | 34.2 | 995 | B | 99 | 81 | 120 | 39 | 0.3 | 0.1 | 11.6 | 88 |  | 5.3 |  |  | 179.23 | 328.52 | 328.52 | 131.53 | 504.52 | 384.53 | 557.15 | 565.52 | 35.3 | 0.3 | 123.3 | 22 |  |  | 10 |  | 719.45 | 0.15 | 0.57 | 0.92
357 | 2019-06-03 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR056 | 1S-DL-YP-ETC-DLNR-2501-LGR056 | PUSHTA NEAR POLICE QTR.:PM | TG-LGR056A-1 | 19504416 | 100 | 40 | 241.2671 | 0.98842 | 72.1138 | 14.5982 | 62.594 | 21.9064 | 92.7414 | 35.6092 | 157.1804 | 83.6895 | 2019-06-11 12:30 | [15 empty] | 108 |  |  |  | 377.5 |  |  |  | 185.5 |  |  |  | 0 |  |  |  | 0 | 671 |  | 0.43875 | 0.72114
358 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR057 | 1S-DL-YP-ETC-DLNR-2501-LGR057 | RENNY WELL NO. V-8:PM | TG-LGR057A-1 | 19505909 | 400 | 120 | 206 | 0.95 | 268 | 99 | 429 | 92 | 410 | 77 | 387 | 37 | 2019-06-05 20:30 | 206 | -11.8 | 451 | Y | 104 | 102 | 93 | 11 | 65.1 | 6 | 5.8 | 23 | 49.3 | 41.3 | 134.29 | 74.3 | 152.3 | 163 | 163 | 136 | 38.59 | 36.29 | 18 | 30.29 | [8 empty] | 713.54 | 6.06 | 0.4 | 0.67
359 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR080 | 1S-DL-YP-ETC-DLNR-2501-LGR080 | GALI MASJID ANAR WALI | TG-LGR080A-1 | 19506548 | 990 | 320 | 239 | 0.97 | 1118 | 370 | 1595 | 396 | 1704 | 352 | 1499 | 178 | 2019-06-30 01:00 | 339.5 | 70.1 | 1911 | Y | 102 | 104 | 94 | 10 | 0.2 | 0.1 | 60.2 | 39.5 |  |  | 33.3 |  | 5.3 | 1.3 | 1.3 | 29.3 | 444.27 | 436.27 | 463.27 | 437.27 | 176.1 | 187.32 | 173.1 | 174.32 | 73.38 | 74.16 | 29.38 | 58.16 | 699.45 | 20.15 | 0.64 | 1.13
360 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR082 | 1S-DL-YP-ETC-DLNR-2501-LGR082 | E BLOCK ,VIKAS MARG | TG-LGR082A-1 | 19506667 | 990 | 320 | 238 | 0.98 | 1152 | 389 | 1684 | 407 | 1762 | 356 | 1539 | 196 | 2019-06-08 16:00 | 279.4 | 65 | 2038 | R | 99 | 107 | 94 | 13 | 0.2 |  | 0.3 | 99.5 |  |  |  |  | 60.3 | 25.3 | 25.3 | 51.3 | 443.3 | 450.58 | 387.11 | 447.18 | 136.46 | 115.1 | 136.36 | 127.28 | 62.43 | 111.51 | 51.42 | 77.13 | 703.29 | 16.31 | 0.58 | 1.16
361 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR082 | 1S-DL-YP-ETC-DLNR-2501-LGR082 | E BLOCK ,VIKAS MARG | TG-LGR082A-2 | 19502776 | 990 | 320 | 245 | 0.98 | 685 | 178 | 753 | 223 | 946 | 284 | 1206 | 393 | 2019-06-08 15:30 | 127.3 | 29.4 | 1206 | B | 93 | 90 | 117 | 27 |  |  | 0.2 | 99.8 | 54 | 166.41 | 12 | 52 | 424.43 | 312.48 | 312.48 | 375.13 | 238.34 | 237.48 | 376.02 | 290.04 |  |  | 1.12 | [5 empty] | 717.17 | 2.43 | 0.54 | 0.69
362 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR082 | 1S-DL-YP-ETC-DLNR-2501-LGR082 | E BLOCK ,VIKAS MARG | TG-LGR082A-3 | 19506528 | 990 | 320 | 246 | 0.97 | 719 | 236 | 990 | 293 | 1252 | 190 | 800 | 393 | 2019-06-06 14:30 | 249.3 | 35.2 | 1252 | Y | 99 | 106 | 95 | 11 |  | 0.1 | 11.7 | 88.2 | 5 | 8 | 11.3 | 7.3 | 441.31 | 391.26 | 391.26 | 417.56 | 255.38 | 302.4 | 221.46 | 276.43 |  | 0.03 | [6 empty] | 702.09 | 17.51 | 0.53 | 0.73
363 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR083 | 1S-DL-YP-ETC-DLNR-2501-LGR083 | EK MINAR MASID | TG-LGR083A-1 | 19506852 | 990 | 320 | 247 | 0.97 | 1349 | 452 | 1858 | 431 | 1757 | 467 | 1921 | 144 | 2019-06-08 | 315.2 | 91.2 | 1921 | B | 102 | 101 | 97 | 5 | 0.1 | 0.1 | 25.1 | 74.6 | [8 empty] | 383.23 | 402 | 445.53 | 415.23 | 193.47 | 177.1 | 140.17 | 170.17 | 130.4 | 128.4 | 116.4 | 122.1 | 707.5 | 12.1 | 0.58 | 1.36
364 | 2019-06-12 07:30 | 2019-06-20 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR083 | 1S-DL-YP-ETC-DLNR-2501-LGR083 | EK MINAR MASID | TG-LGR083A-2 | 19504438 | 990 | 320 | 246.2155 | 0.97855 | 611.7957 | 196.6333 | 819.6809 | 216.8354 | 904.7626 | 198.3271 | 822.013 | 83.9399 | 2019-06-13 23:30 | [15 empty] | 0 |  |  |  | 79 |  |  |  | 129.5 |  |  |  | 0 |  |  |  | 0 | 208.5 |  | 0.69872 | 0.61798
365 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR084 | 1S-DL-YP-ETC-DLNR-2501-LGR084 | WEST GURU ANGAD NAGER GALI NO-2 | TG-LGR084A-1 | 19502464 | 990 | 320 | 246 | 0.97 | 904 | 329 | 1359 | 268 | 1114 | 307 | 1271 | 215 | 2019-06-12 | 151.6 | 58.1 | 1420 | R | 114 | 91 | 94 | 23 |  |  | 9.6 | 90.4 |  |  |  |  | 46 | 231.3 | 231.3 | 158 | 573.04 | 485.04 | 449.04 | 531.34 | 99 | 2.3 | 20.3 | 29.3 | 1 |  |  |  | 719.04 | 0.56 | 0.57 | 0.91
366 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR090 | 1S-DL-YP-ETC-DLNR-2501-LGR090 | SCHOOL BLOCK,PARK WALA S/S NEAR MANDIR | TG-LGR090A-1 | 19504463 | 990 | 320 | 247 | 0.98 | 968 | 321 | 1329 | 295 | 1221 | 353 | 1462 | 209 | 2019-06-10 13:00 | 163.4 | 50 | 1510 | B | 103 | 96 | 100 | 7 |  |  | 22.5 | 77.5 |  |  |  |  | 63 | 152.27 | 152.27 | 112.55 | 547.36 | 497.09 | 467.14 | 501.11 | 108 | 69.3 | 112 | 105 | 0.3 |  | 6 |  | 719.06 | 0.54 | 0.57 | 0.98
367 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR090 | 1S-DL-YP-ETC-DLNR-2501-LGR090 | SCHOOL BLOCK,PARK WALA S/S NEAR MANDIR | TG-LGR090A-2 | 19503652 | 630 | 200 | 245 | 0.97 | 617 | 188 | 769 | 186 | 755 | 244 | 996 | 234 | 2019-06-03 | 118.2 | 46 | 996 | B | 89 | 103 | 108 | 19 |  | 2.8 | 35.9 | 61.3 | 0.3 | 0.3 | 0.3 | 0.3 | 59 | 9.3 | 9.3 | 12 | 638.13 | 596.43 | 548.52 | 635.13 | 21.21 | 112.21 | 140.51 | 71.21 |  |  | 23.21 |  | 719.04 | 0.56 | 0.65 | 0.98
368 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR092 | 1S-DL-YP-ETC-DLNR-2501-LGR092 | New S/Stn Nehru Enclave. Nehru Enclave | TG-LGR092A-1 | 19504574 | 630 | 200 | 240 | 0.98 | 438 | 149 | 635 | 140 | 595 | 150 | 644 | 45 | 2019-06-29 23:00 | 68.5 | 19.3 | 703 | B | 100 | 92 | 109 | 17 |  |  | 16.2 | 83.8 | 2 | 5.3 |  |  | 350.3 | 431.3 | 431.3 | 363.3 | 367.22 | 282.52 | 441.22 | 356.22 | [8 empty] | 719.52 | 0.08 | 0.61 | 0.7
369 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR093 | 1S-DL-YP-ETC-DLNR-2501-LGR093 | SURANA DHARAMSHALA S/S | TG-LGR093A-1 | 19504131 | 990 | 320 | 237 | 0.98 | 431 | 126 | 540 | 137 | 592 | 167 | 720 | 160 | 2019-06-12 15:30 | 62.6 | 25.8 | 724 | B | 92 | 98 | 109 | 17 |  |  | 2.3 | 97.7 | 41 | 12.28 | 21.3 | 13.28 | 676.51 | 706.23 | 706.23 | 701.23 | 2 | 1 | 110 | 5 | [8 empty] | 719.51 | 0.09 | 0.65 | 0.43
370 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR093 | 1S-DL-YP-ETC-DLNR-2501-LGR093 | SURANA DHARAMSHALA S/S | TG-LGR093A-2 | 19506459 | 990 | 320 | 238 | 0.98 | 828 | 249 | 1062 | 271 | 1161 | 308 | 1347 | 251 | 2019-06-30 23:30 | 175 | 33 | 1441 | Y | 97 | 105 | 98 | 8 | 0.1 | 4.1 | 59.3 | 36.5 | 0.3 |  | 1 | 0.3 | 113.3 | 122.3 | 122.3 | 108.3 | 600.14 | 540.14 | 556.14 | 603.44 |  | 51.3 | 7 | 1.3 |  |  |  |  | 714.14 | 5.46 | 0.6 | 0.84
371 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR095 | 1S-DL-YP-ETC-DLNR-2501-LGR095 | DMRC STAFF QUARTERS | TG-LGR095A-1 | 19504745 | 990 | 320 | 244 | 0.99 | 79 | 34 | 136 | 19 | 77 | 26 | 104 | 51 | 2019-06-12 01:30 | 9.6 | -0.7 | 141 | R | 137 | 74 | 89 | 63 |  |  | 8.5 | 91.5 | 716.31 | 716.31 | 716.31 | 716.31 | [16 empty] | 716.31 | 3.29 | 0.49 | 0.08
372 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR095 | 1S-DL-YP-ETC-DLNR-2501-LGR095 | DMRC STAFF QUARTERS | TG-LGR095A-2 | 19504750 | 630 | 200 | 243 | 0.88 | 61 | 21 | 87 | 19 | 78 | 21 | 86 | 9 | 2019-06-30 17:30 | 34.5 | 1.4 | 92 | B | 107 | 94 | 99 | 13 |  |  | 8.1 | 91.9 | 719.24 | 719.24 | 719.24 | 719.24 | [16 empty] | 719.24 | 0.36 | 0.57 | 0.1
373 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR097 | 1S-DL-YP-ETC-DLNR-2501-LGR097 | A BLK P,D.VIHAR PARK NR. O/H WATER TANK | TG-LGR097A-1 | 19505222 | 630 | 200 | 246 | 0.98 | 550 | 205 | 833 | 135 | 544 | 211 | 857 | 302 | 2019-06-11 23:30 | 186.6 | 31 | 1240 | B | 108 | 82 | 109 | 27 | 0.3 | 0.1 | 23.7 | 75.8 |  |  |  |  | 18.32 | 127.53 | 127.53 | 30.32 | 567.58 | 565.44 | 537 | 636.27 | 107.37 | 0.3 | 125.57 | 27.08 |  |  | 3.08 |  | 694.07 | 25.53 | 0.68 | 0.87
374 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR100 | 1S-DL-YP-ETC-DLNR-2501-LGR100 | GYAN KUNJ | TG-LGR100A-1 | 19505137 | 990 | 320 | 246.8554 | 0.97873 | 1052.5105 | 352.113 | 1413.0869 | 315.8192 | 1266.8241 | 384.5782 | 1544.4289 | 240.5285 | 2019-06-11 01:30 | [15 empty] | 0 |  |  |  | 243 |  |  |  | 464 |  |  |  | 9.5 |  |  |  | 1 | 717.5 |  | 0.44942 | 1.0631
375 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR101 | 1S-DL-YP-ETC-DLNR-2501-LGR101 | VEER SAVARKAR BLOCK VIKAS MARG | TG-LGR101A-1 | 19504960 | 990 | 320 | 225 | 0.98 | 907 | 235 | 1071 | 328 | 1506 | 344 | 1597 | 487 | 2019-06-27 14:00 | 131 | 9.6 | 1597 | B | 88 | 101 | 112 | 24 |  | 0.3 | 36.5 | 63.2 | 358.3 | 369.3 | 361.3 | 362 | 137.3 | 103.3 | 103.3 | 116.3 | 220.24 | 159.11 | 132.2 | 207.35 |  | 84.13 | 114.34 | 30.19 |  |  | 1 |  | 716.24 | 3.36 | 0.37 | 0.92
376 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR103 | 1S-DL-YP-ETC-DLNR-2501-LGR103 | NEW WB BLOCK (NEAR AGGARWAL SWEETS) | TG-LGR103A-1 | 19505891 | 990 | 320 | 243 | 0.98 | 910 | 281 | 1163 | 314 | 1318 | 314 | 1307 | 150 | 2019-06-30 | 190.4 | 75.5 | 1472 | Y | 94 | 108 | 98 | 14 | 0.1 |  | 37.2 | 62.6 |  |  |  |  | 19.3 | 6 | 6 | 11 | 695.08 | 582.42 | 661.5 | 660.42 | 5 | 127.56 | 46.18 | 47.56 |  | 3 |  |  | 719.38 | 0.22 | 0.69 | 0.92
377 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR104 | 1S-DL-YP-ETC-DLNR-2501-LGR104 | NARAIN NAGAR (NEAR GARHWALI MOHALLA) | TG-LGR104A-1 | 19505680 | 630 | 200 | 247 | 0.97 | 521 | 188 | 773 | 154 | 639 | 178 | 741 | 121 | 2019-06-29 23:30 | 166.2 | 36 | 823 | B | 113 | 84 | 103 | 29 | 0.1 |  | 21.4 | 78.5 |  |  |  |  | 16.3 | 287.03 | 287.03 | 76.01 | 659 | 410.57 | 579.3 | 620.29 | 22.3 |  | 23 | 1.3 |  |  |  |  | 698 | 22 | 0.64 | 0.83
378 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR107 | 1S-DL-YP-ETC-DLNR-2501-LGR107 | SHAKARPUR RAILWAY UNDERPASS | TG-LGR107A-1 | 19505952 | 630 | 200 | 237 | 0.97 | 478 | 106 | 454 | 200 | 869 | 172 | 742 | 368 | 2019-06-30 00:30 | 95.2 | 32.2 | 869 | Y | 82 | 103 | 115 | 33 | 0.3 | 0.4 | 23.8 | 75.6 | 16.34 | 2.35 |  |  | 476.47 | 301.19 | 301.19 | 325.57 | 211 | 397.27 | 511.49 | 378.24 |  | 3 | 5 | [5 empty] | 704.21 | 15.39 | 0.56 | 0.76
379 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR108 | 1S-DL-YP-ETC-DLNR-2501-LGR108 | COMMUNITY CENTER SHAKARPUR | TG-LGR108A-1 | 19505626 | 630 | 200 | 246 | 0.97 | 533 | 185 | 781 | 190 | 801 | 158 | 659 | 133 | 2019-06-30 23:30 | 139.2 | 28.2 | 982 | Y | 94 | 109 | 96 | 15 | 0.1 | 0.1 | 8 | 91.8 |  |  |  |  | 203 | 78 | 78 | 146.3 | 508.35 | 587.22 | 494.06 | 558.35 | 1.3 | 47.13 | 3.59 | 8 |  | 0.3 |  |  | 713.05 | 6.55 | 0.6 | 0.85
380 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR109 | 1S-DL-YP-ETC-DLNR-2501-LGR109 | GURU NANAK PURA EXT. | TG-LGR109A-1 | 19506818 | 990 | 320 | 242 | 0.98 | 556 | 166 | 716 | 217 | 934 | 173 | 743 | 206 | 2019-06-01 13:00 | 121.6 | 3.8 | 1044 | Y | 106 | 98 | 96 | 10 | 0.1 |  | 1.6 | 98.3 | 111.11 | 180.29 | 237.22 | 184.59 | 355.48 | 336.3 | 336.3 | 301 | 231.36 | 181.36 | 206.32 | 212.36 | [8 empty] | 698.35 | 21.25 | 0.55 | 0.56
381 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | PVR008 | 1S-DL-YP-ETC-DLNR-2502-PVR008 | DDA FLAT NIRMAN VIHAR:ID | TG-PVR008A-1 | 19501093 | 990 | 320 | 234.2274 | 0.98064 | 805.617 | 228.2324 | 1003.3517 | 244.8038 | 1087.1956 | 332.5808 | 1474.0097 | 434.8413 | 2019-06-01 | [15 empty] | 0 |  |  |  | 187.5 |  |  |  | 531 |  |  |  | 1.5 |  |  |  | 0 | 720 |  | 0.60048 | 0.81375
382 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | PVR008 | 1S-DL-YP-ETC-DLNR-2502-PVR008 | DDA FLAT NIRMAN VIHAR:ID | TG-PVR008A-2 | 19504486 | 990 | 320 | 234 | 0.98 | 857 | 282 | 1257 | 270 | 1195 | 305 | 1356 | 141 | 2019-06-11 23:30 | 136.9 | 39 | 1384 | B | 106 | 91 | 103 | 15 |  |  | 7.9 | 92.1 |  |  |  |  | 65 | 199 | 199 | 110 | 606.23 | 517.53 | 550.23 | 587.53 | 48.3 | 3 | 53 | 22 |  |  |  |  | 719.53 | 0.07 | 0.61 | 0.87
383 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN002 | 1S-DL-YP-ETC-DLNR-2503-MAN002 | RAS VIHAR CGHS PPG:ID | TG-MAN002A-1 | 19502367 | 630 | 200 | 234 | 0.98 | 190 | 45 | 205 | 83 | 378 | 61 | 277 | 151 | 2019-06-30 23:00 | 25.8 | 5.1 | 381 | Y | 70 | 127 | 103 | 57 |  |  | 0.3 | 99.7 | 705.36 | 453.55 | 546.28 | 571.32 | 13 | 264.41 | 264.41 | 147.04 | [12 empty] | 718.36 | 1.24 | 0.49 | 0.3
384 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN002 | 1S-DL-YP-ETC-DLNR-2503-MAN002 | RAS VIHAR CGHS PPG:ID | TG-MAN002A-2 | 19502370 | 630 | 200 | 246 | 0.98 | 165 | 41 | 172 | 52 | 219 | 73 | 306 | 118 | 2019-06-11 23:30 | 28.1 | 5.5 | 317 | B | 80 | 95 | 125 | 45 |  |  | 1.5 | 98.5 | 715.06 | 662.42 | 497.35 | 630.42 | 3.3 | 55.54 | 55.54 | 87.54 | [12 empty] | 718.36 | 1.24 | 0.52 | 0.26
385 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN003 | 1S-DL-YP-ETC-DLNR-2503-MAN003 | SOUTH GANESH NAGAR:PM | TG-MAN003A-1 | 19505687 | 400 | 120 | 234 | 0.98 | 588 | 183 | 823 | 190 | 864 | 216 | 982 | 143 | 2019-06-30 | 126.6 | 34 | 982 | B | 94 | 103 | 103 | 9 | 0.1 | 0.1 | 29.1 | 70.6 | [8 empty] | 417.59 | 336.3 | 361.29 | 373.59 | 180.57 | 200.59 | 143.57 | 175.27 | 107.56 | 169.23 | 199.56 | 157.26 | 706.52 | 13.08 | 0.56 | 1.47
386 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN004 | 1S-DL-YP-ETC-DLNR-2503-MAN004 | SOUTH GANESH NAGAR EXTN.:ID | TG-MAN004A-1 | 19505658 | 990 | 200 | 231 | 0.98 | 538 | 186 | 851 | 200 | 912 | 152 | 696 | 193 | 2019-06-30 | 110.6 | 32.4 | 912 | Y | 100 | 112 | 88 | 24 | 0.1 | 0.6 | 52.3 | 47 | 12 |  | 46 | 8.3 | 599.26 | 513.26 | 513.26 | 604.26 | 107.56 | 205.56 | 32.26 | 106.26 | [8 empty] | 719.22 | 0.38 | 0.59 | 0.54
387 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN004 | 1S-DL-YP-ETC-DLNR-2503-MAN004 | SOUTH GANESH NAGAR EXTN.:ID | TG-MAN004A-2 | 19506133 | 630 | 200 | 229 | 0.98 | 711 | 231 | 1065 | 223 | 1024 | 258 | 1201 | 160 | 2019-06-30 | 141.6 | 41.6 | 1299 | B | 100 | 93 | 107 | 14 | 0.2 | 0.1 | 5.4 | 94.3 |  |  |  |  | 60.3 | 98 | 98 | 46.3 | 518.56 | 529.26 | 519.56 | 538.56 | 114.26 | 77.56 | 110.3 | 112 | 13 | 1.3 | 49.56 | 9.26 | 706.52 | 13.08 | 0.54 | 1.13
388 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN005 | 1S-DL-YP-ETC-DLNR-2503-MAN005 | MOTHER DAIRY STAFF QUARTOR:ID | TG-MAN005A-1 | 19504306 | 630 | 200 | 231 | 0.97 | 77 | 20 | 93 | 28 | 129 | 29 | 130 | 37 | 2019-06-07 23:00 | 13.8 | 3.2 | 139 | Y | 79 | 114 | 107 | 35 |  |  | 0.3 | 99.7 | 718.59 | 718.59 | 718.59 | 718.59 | [16 empty] | 718.59 | 1.01 | 0.52 | 0.12
389 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN006 | 1S-DL-YP-ETC-DLNR-2503-MAN006 | PANDAV NAGAR D PARK:K | TG-MAN006A-1 | 19505744 | 990 | 320 | 239 | 0.98 | 1034 | 340 | 1441 | 383 | 1639 | 312 | 1335 | 267 | 2019-06-05 01:00 | 239 | 64.3 | 1869 | Y | 101 | 110 | 89 | 21 | 0.3 | 0.4 | 52.2 | 47.1 |  |  |  |  | 63.28 | 50.3 | 50.3 | 75.28 | 534.52 | 490.2 | 525.54 | 517.22 | 103.4 | 106 | 43.01 | 115.1 | 15.21 | 70.31 |  | 9.21 | 717.21 | 2.39 | 0.57 | 1.04
390 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN006 | 1S-DL-YP-ETC-DLNR-2503-MAN006 | PANDAV NAGAR D PARK:K | TG-MAN006A-2 | 19501944 | 990 | 320 | 242 | 0.97 | 965 | 324 | 1357 | 345 | 1439 | 296 | 1224 | 188 | 2019-06-05 00:30 | 211.2 | 78 | 1537 | Y | 96 | 107 | 97 | 11 |  | 0.1 | 38 | 61.9 |  |  |  |  | 55 | 21.3 | 21.3 | 31 | 587.58 | 572.43 | 631.13 | 607.43 | 73.38 | 118.56 | 52.23 | 77.53 |  | 3.27 |  |  | 716.36 | 3.24 | 0.63 | 0.97
391 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN006 | 1S-DL-YP-ETC-DLNR-2503-MAN006 | PANDAV NAGAR D PARK:K | TG-MAN006A-3 | 19505981 | 990 | 320 | 238 | 0.98 | 917 | 297 | 1366 | 349 | 1604 | 271 | 1250 | 312 | 2019-06-07 23:30 | 186.9 | 59.5 | 1604 | Y | 96 | 110 | 94 | 16 | 0.2 |  | 23.6 | 76.1 |  |  |  |  | 109.3 | 48 | 48 | 76 | 577.52 | 564.24 | 570.59 | 590.52 | 29.09 | 97.25 | 22.32 | 49.39 |  | 6.42 |  |  | 716.31 | 3.29 | 0.6 | 0.93
392 | 2019-06-01 | 2019-06-12 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN006 | 1S-DL-YP-ETC-DLNR-2503-MAN006 | PANDAV NAGAR D PARK:K | TG-MAN006A-4 | 19502899 | 630 | 200 | 235.1551 | 0.98535 | 376.3541 | 134.3932 | 575.6832 | 144.8007 | 626.4359 | 97.1602 | 417.8396 | 188.4183 | 2019-06-01 | [15 empty] | 1.5 |  |  |  | 180 |  |  |  | 105.5 |  |  |  | 0 |  |  |  | 0 | 287 |  | 0.64136 | 0.59739
393 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN006 | 1S-DL-YP-ETC-DLNR-2503-MAN006 | PANDAV NAGAR D PARK:K | TG-MAN006A-5 | 19506626 | 630 | 200 | 240 | 0.98 | 423 | 129 | 535 | 162 | 670 | 132 | 548 | 129 | 2019-06-02 23:30 | 95.2 | 17.8 | 728 | Y | 92 | 110 | 99 | 18 | 0.2 | 0.1 | 43.5 | 56.1 | 17.58 | 7.3 | 5 | 4.3 | 493.43 | 386.53 | 386.53 | 460.23 | 191.2 | 308.08 | 230.08 | 238.08 |  | 0.3 | [6 empty] | 703.01 | 16.59 | 0.56 | 0.67
394 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN007 | 1S-DL-YP-ETC-DLNR-2503-MAN007 | PANDAV NAGAR S BLOCK:ID | TG-MAN007A-1 | 19501803 | 990 | 320 | 235 | 0.97 | 874 | 274 | 1152 | 287 | 1212 | 314 | 1319 | 146 | 2019-06-06 03:00 | 192.1 | 56.7 | 1505 | B | 95 | 92 | 112 | 20 |  |  | 10.2 | 89.8 |  |  |  |  | 207.23 | 249.53 | 249.53 | 154.57 | 502.21 | 457.21 | 566.33 | 536.17 | 7.55 | 10.25 | 90.09 | 26.25 |  |  |  |  | 717.39 | 2.21 | 0.59 | 0.88
395 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN008 | 1S-DL-YP-ETC-DLNR-2503-MAN008 | PANDAV NAGAR S BLOCK NEAR PETROL PUMP:PM | TG-MAN008A-1 | 19506364 | 990 | 300 | 230 | 0.98 | 791 | 256 | 1172 | 287 | 1314 | 249 | 1137 | 162 | 2019-06-30 23:00 | 175.2 | 37.5 | 1340 | Y | 100 | 102 | 98 | 4 | 0.1 |  | 1.9 | 98 | 3 |  | 0.3 |  | 332.5 | 315.5 | 315.5 | 338.5 | 366.1 | 383.1 | 344.44 | 364.4 | 1.3 | 4.3 | 2 | [5 empty] | 703.3 | 16.3 | 0.55 | 0.8
396 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN008 | 1S-DL-YP-ETC-DLNR-2503-MAN008 | PANDAV NAGAR S BLOCK NEAR PETROL PUMP:PM | TG-MAN008A-2 | 19505534 | 630 | 200 | 229 | 0.99 | 420 | 131 | 604 | 155 | 718 | 135 | 629 | 104 | 2019-06-26 23:00 | 72.2 | 15.8 | 721 | Y | 92 | 106 | 102 | 14 | 0.2 |  | 0.2 | 99.7 | 5.3 | 4 | 1.3 | 1.3 | 237.59 | 195.29 | 195.29 | 215.59 | 78.32 | 122.32 | 110.02 | 104.32 | [8 empty] | 703.3 | 16.3 | 0.55 | 0.67
397 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN009 | 1S-DL-YP-ETC-DLNR-2503-MAN009 | J PARK PANDAV NAGAR:K | TG-MAN009A-1 | 19502964 | 990 | 320 | 239 | 0.98 | 1094 | 368 | 1588 | 397 | 1713 | 330 | 1407 | 266 | 2019-06-29 23:00 | 172.2 | 63.3 | 1810 | Y | 99 | 109 | 92 | 17 |  |  | 49.8 | 50.2 |  |  |  |  | 91.28 | 48.3 | 48.3 | 80.28 | 481.37 | 465.08 | 462.08 | 478.07 | 109.49 | 122.57 | 101.49 | 120.49 | 19.52 | 66.11 | 4.22 | 23.22 | 702.46 | 17.14 | 0.55 | 1.11
398 | 2019-06-10 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN010 | 1S-DL-YP-ETC-DLNR-2503-MAN010 | GANESH NAGAR COM. E BLCK.:PL | TG-MAN010A-1 | 19506916 | 990 | 320 | 238 | 0.98 | 1131 | 341 | 1514 | 427 | 1915 | 362 | 1608 | 364 | 2019-06-30 | 298.6 | 81.9 | 1915 | Y | 93 | 105 | 101 | 12 | 0.1 | 0.2 | 8.2 | 91.5 |  |  |  |  | 36.27 | 6.27 | 6.27 | 14.27 | 381.07 | 371.02 | 367.31 | 376.34 | 77.26 | 81.35 | 91.33 | 88.03 | 5.59 | 41.55 | 25.25 | 21.55 | 500.59 | 3.01 | 0.56 | 1.14
399 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN010 | 1S-DL-YP-ETC-DLNR-2503-MAN010 | GANESH NAGAR COM. E BLCK.:PL | TG-MAN010A-2 | 19500753 | 990 | 320 | 246.1418 | 0.9807 | 1023.2342 | 334.4389 | 1395.4724 | 352.5955 | 1523.8805 | 336.1998 | 1447.2655 | 111.8951 | 2019-06-30 00:30 | [15 empty] | 0 |  |  |  | 15 |  |  |  | 570.5 |  |  |  | 126.5 |  |  |  | 6 | 718 |  | 0.61468 | 1.0336
400 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN011 | 1S-DL-YP-ETC-DLNR-2503-MAN011 | GANESH NAGAR COM. C BLCK.:PL | TG-MAN011A-1 | 19500759 | 1600 | 500 | 236.1626 | 0.98463 | 1503.0792 | 476.6178 | 2165.3617 | 576.61 | 2608.7411 | 449.8514 | 2026.8143 | 526.5071 | 2019-06-30 23:30 | [15 empty] | 0 |  |  |  | 51.5 |  |  |  | 601.5 |  |  |  | 66.5 |  |  |  | 0 | 719.5 |  | 0.61074 | 0.93942
401 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN011 | 1S-DL-YP-ETC-DLNR-2503-MAN011 | GANESH NAGAR COM. C BLCK.:PL | TG-MAN011A-2 | 19504615 | 990 | 200 | 230 | 0.98 | 540 | 154 | 681 | 182 | 809 | 204 | 913 | 201 | 2019-06-10 23:30 | 96.6 | 32.7 | 913 | B | 86 | 105 | 109 | 23 |  |  | 3.8 | 96.2 | 5 | 1 | 0.3 | 1 | 631.17 | 433.45 | 433.45 | 508.15 | 82.34 | 284.06 | 325.05 | 209.36 | [8 empty] | 718.51 | 1.09 | 0.67 | 0.55
402 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN012 | 1S-DL-YP-ETC-DLNR-2503-MAN012 | TRUCK MARKET PANDAV NGR.:PL | TG-MAN012A-1 | 19503807 | 630 | 200 | 236 | 0.96 | 229 | 58 | 250 | 82 | 351 | 89 | 378 | 117 | 2019-06-02 12:30 | 81 | 7.4 | 378 | B | 76 | 120 | 104 | 44 |  |  | 37.4 | 62.6 | 453.3 | 385 | 396 | 398.3 | 265.08 | 333.38 | 333.38 | 320.08 |  |  | 2 | [9 empty] | 718.38 | 1.22 | 0.55 | 0.36
403 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN012 | 1S-DL-YP-ETC-DLNR-2503-MAN012 | TRUCK MARKET PANDAV NGR.:PL | TG-MAN012A-2 | 19504728 | 990 | 320 | 236 | 0.97 | 470 | 147 | 608 | 170 | 700 | 153 | 631 | 84 | 2019-06-03 11:00 | 127.3 | 2.9 | 880 | Y | 86 | 121 | 92 | 35 |  |  | 0.1 | 99.9 | 382.3 | 334 | 381.3 | 370.3 | 328.09 | 148.22 | 148.22 | 212.09 | 7.59 | 236.16 | 70.29 | 135.59 | [8 empty] | 718.38 | 1.22 | 0.51 | 0.48
404 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN012 | 1S-DL-YP-ETC-DLNR-2503-MAN012 | TRUCK MARKET PANDAV NGR.:PL | TG-MAN012A-3 | 19504873 | 630 | 200 | 229 | 0.97 | 437 | 123 | 546 | 156 | 696 | 158 | 695 | 150 | 2019-06-06 15:30 | 107.2 | 22.5 | 796 | Y | 75 | 125 | 100 | 50 |  | 0.1 | 58.2 | 41.7 | 33.32 |  |  |  | 519.53 | 45.02 | 45.02 | 275.32 | 165.13 | 669.36 | 410.36 | 443.06 |  | 4 | [6 empty] | 718.38 | 1.22 | 0.64 | 0.69
405 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN013 | 1S-DL-YP-ETC-DLNR-2503-MAN013 | MANDAWALI A BLOCK SHIV MANDIR MARG:PL | TG-MAN013A-1 | 19506457 | 990 | 320 | 248 | 0.97 | 1135 | 413 | 1753 | 358 | 1510 | 364 | 1524 | 236 | 2019-06-30 23:30 | 219.2 | 81.9 | 1753 | R | 98 | 100 | 102 | 4 | 0.1 |  | 4 | 95.9 |  |  |  |  | 25 | 9.3 | 9.3 | 12 | 516.34 | 523.34 | 508.04 | 519.34 | 130.52 | 130.22 | 138.18 | 137.52 | 19.3 | 28.3 | 31.04 | 22.3 | 691.56 | 28.04 | 0.57 | 1.15
406 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN013 | 1S-DL-YP-ETC-DLNR-2503-MAN013 | MANDAWALI A BLOCK SHIV MANDIR MARG:PL | TG-MAN013A-2 | 19502779 | 990 | 320 | 238 | 0.97 | 1242 | 438 | 1889 | 398 | 1731 | 405 | 1772 | 142 | 2019-06-29 23:30 | 222.3 | 64 | 1976 | B | 105 | 93 | 102 | 12 | 1 | 4.5 | 90.4 | 4.2 |  |  |  |  | 5.3 | 15.3 | 15.3 | 10.3 | 346.37 | 416.35 | 369.05 | 379.35 | 125 | 110.55 | 100.3 | 107.32 | 100.34 | 34.41 | 95.36 | 80.04 | 715.5 | 4.1 | 0.58 | 1.25
407 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN014 | 1S-DL-YP-ETC-DLNR-2503-MAN014 | MANDAWALI DISPANSARY:PL | TG-MAN014A-1 | 19500810 | 990 | 320 | 234 | 0.98 | 693 | 239 | 1081 | 228 | 1024 | 225 | 1006 | 68 | 2019-06-30 23:00 | 113.3 | 47.1 | 1098 | R | 102 | 102 | 96 | 6 |  |  | 71.5 | 28.5 |  |  |  |  | 73.3 | 58.3 | 58.3 | 79 | 646.3 | 661.3 | 585 | 641 | [8 empty] | 720 | 0 | 0.71 | 0.7
408 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN015 | 1S-DL-YP-ETC-DLNR-2503-MAN015 | MANDAWALI ( POST OFFICE):PL | TG-MAN015A-1 | 19505934 | 2000 | 640 | 245 | 0.97 | 1440 | 458 | 1959 | 494 | 2107 | 488 | 2096 | 142 | 2019-06-30 | 429.4 | 119 | 2136 | Y | 99 | 103 | 98 | 5 | 0.1 |  | 1.2 | 98.7 |  |  |  |  | 239.1 | 232.4 | 232.4 | 250.1 | 466.19 | 472.49 | 418.52 | 455.19 | [8 empty] | 705.29 | 14.31 | 0.63 | 0.72
409 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN016 | 1S-DL-YP-ETC-DLNR-2503-MAN016 | MANDAWALI PRIMARY SCHOOL:PL | TG-MAN016A-1 | 19506407 | 990 | 320 | 243 | 0.97 | 1132 | 393 | 1678 | 339 | 1439 | 400 | 1714 | 259 | 2019-06-29 23:30 | 279.4 | 88.3 | 1889 | R | 109 | 89 | 102 | 20 | 0.1 | 0.1 | 10.6 | 89.1 |  |  |  |  | 1 | 47.36 | 47.36 | 6.53 | 472.35 | 553.34 | 512.29 | 530.12 | 158.05 | 113.25 | 164.05 | 146.35 | 86.25 | 3.3 | 34.55 | 34.25 | 718.05 | 1.55 | 0.6 | 1.14
410 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN016 | 1S-DL-YP-ETC-DLNR-2503-MAN016 | MANDAWALI PRIMARY SCHOOL:PL | TG-MAN016A-2 | 19505523 | 990 | 320 | 239 | 0.97 | 613 | 226 | 991 | 188 | 822 | 199 | 875 | 150 | 2019-06-30 23:30 | 187.5 | 38.1 | 1030 | R | 106 | 96 | 99 | 10 | 0.1 | 0.1 | 0.6 | 99.3 | 0.3 | 20 | 6 | 5.3 | 404 | 451.3 | 451.3 | 444.3 | 302.31 | 235.31 | 247.31 | 257.01 | [8 empty] | 707.01 | 12.59 | 0.61 | 0.62
411 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN016 | 1S-DL-YP-ETC-DLNR-2503-MAN016 | MANDAWALI PRIMARY SCHOOL:PL | TG-MAN016A-3 | 19506597 | 630 | 200 | 237 | 0.98 | 670 | 209 | 913 | 201 | 881 | 260 | 1143 | 247 | 2019-06-11 | 189.2 | 46.2 | 1143 | B | 93 | 91 | 116 | 25 | 0.1 | 0.1 | 6.8 | 92.9 |  |  |  |  | 70 | 43 | 43 | 16.3 | 545.2 | 605.2 | 476.3 | 559.2 | 89.3 | 58 | 155.5 | 128 | 1.3 |  | 74 | 2.3 | 706.2 | 13.4 | 0.6 | 1.06
412 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN017 | 1S-DL-YP-ETC-DLNR-2503-MAN017 | SCHOOL KHATTA-1, MANDAWALI:PL | TG-MAN017A-1 | 19500781 | 990 | 120 | 241.4951 | 0.9772 | 1141.9346 | 355.0863 | 1542.3112 | 385.3779 | 1680.5981 | 401.4703 | 1750.7756 | 183.7192 | 2019-06-29 23:30 | [15 empty] | 0 |  |  |  | 8.5 |  |  |  | 504.5 |  |  |  | 161.5 |  |  |  | 44 | 718.5 |  | 0.6075 | 1.1535
413 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN017 | 1S-DL-YP-ETC-DLNR-2503-MAN017 | SCHOOL KHATTA-1, MANDAWALI:PL | TG-MAN017A-2 | 19505686 | 630 | 200 | 239 | 0.98 | 540 | 174 | 770 | 179 | 795 | 187 | 825 | 48 | 2019-06-30 23:30 | 114 | 19.6 | 843 | B | 103 | 100 | 97 | 6 | 0.1 | 0.1 | 2.3 | 97.5 | 1 | 2 | 10.3 | 1.3 | 286.09 | 293.52 | 293.52 | 307.39 | 423.04 | 416.03 | 350.39 | 402.34 | 4 | 2.18 | 9 | 2.3 |  |  |  |  | 714.13 | 5.47 | 0.52 | 0.86
414 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN018 | 1S-DL-YP-ETC-DLNR-2503-MAN018 | SCHOOL KHATTA-II,MANDAWALI:PM | TG-MAN018A-1 | 19500784 | 990 | 320 | 243.3387 | 0.97121 | 945.2505 | 322.5007 | 1399.3783 | 347.5744 | 1529.5476 | 275.1754 | 1197.6125 | 289.6846 | 2019-06-30 23:30 | [15 empty] | 0 |  |  |  | 64.5 |  |  |  | 597 |  |  |  | 57 |  |  |  | 0 | 718.5 |  | 0.60419 | 0.9548
415 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN019 | 1S-DL-YP-ETC-DLNR-2503-MAN019 | MANDAWALI UNCHEPAR;PL | TG-MAN019A-1 | 19501990 | 990 | 320 | 241 | 0.97 | 1093 | 353 | 1547 | 387 | 1699 | 353 | 1528 | 162 | 2019-06-29 23:30 | 193.6 | 69.2 | 1813 | Y | 97 | 109 | 95 | 14 |  | 0.1 | 9.2 | 90.7 |  |  |  |  | 97.56 | 37 | 37 | 88.26 | 537.23 | 515.56 | 459.23 | 511.53 | 81.57 | 133.23 | 104.58 | 106.37 | 2 | 32.57 | 5.29 | 12.2 | 719.16 | 0.44 | 0.54 | 1.1
416 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN019 | 1S-DL-YP-ETC-DLNR-2503-MAN019 | MANDAWALI UNCHEPAR;PL | TG-MAN019A-2 | 19505664 | 630 | 200 | 245 | 0.97 | 508 | 182 | 779 | 183 | 786 | 143 | 606 | 177 | 2019-06-29 23:30 | 133.4 | 39.2 | 938 | Y | 99 | 112 | 89 | 23 | 0.2 | 0.1 | 0.3 | 99.4 |  |  | 1 |  | 234.26 | 114.56 | 114.56 | 221.26 | 482.2 | 589.01 | 394.5 | 497.2 | 2.3 | 14.49 |  | 0.3 |  | 0.3 |  |  | 719.16 | 0.44 | 0.58 | 0.81
417 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN021 | 1S-DL-YP-ETC-DLNR-2503-MAN021 | MANDAWALI SUBJI MANDI:PL | TG-MAN021A-1 | 19504821 | 990 | 320 | 243 | 0.97 | 939 | 324 | 1402 | 301 | 1309 | 315 | 1369 | 81 | 2019-06-30 23:00 | 159.7 | 68.4 | 1487 | R | 107 | 96 | 98 | 11 |  |  | 1.2 | 98.8 |  |  | 0.3 |  | 14 | 83.5 | 83.5 | 38 | 620.51 | 603.01 | 616.3 | 633.51 | 81.3 | 32.3 | 39.3 | 47.3 | 3 |  |  |  | 719.21 | 0.39 | 0.61 | 0.95
418 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN021 | 1S-DL-YP-ETC-DLNR-2503-MAN021 | MANDAWALI TRY POLE:PM | TG-MAN021A-2 | 19504828 | 990 | 320 | 244 | 0.97 | 1069 | 345 | 1485 | 370 | 1589 | 354 | 1523 | 91 | 2019-06-29 23:00 | 208.3 | 62.6 | 1617 | Y | 98 | 102 | 100 | 4 |  |  | 1.4 | 98.6 |  |  |  |  | 9 | 3.3 | 3.3 | 4 | 590.21 | 553.53 | 565.53 | 570.53 | 114.3 | 148.28 | 145.28 | 139.28 | 4.3 | 12.3 | 4 | 4 | 718.21 | 1.39 | 0.63 | 1.08
419 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN023 | 1S-DL-YP-ETC-DLNR-2503-MAN023 | UTTARY SCHOOL BLOCK:K | TG-MAN023A-1 | 19502766 | 990 | 320 | 244 | 0.97 | 1159 | 407 | 1693 | 384 | 1608 | 368 | 1538 | 134 | 2019-06-30 23:30 | 237 | 98.6 | 1727 | R | 103 | 100 | 97 | 6 |  |  | 1.3 | 98.7 |  |  |  |  | 6.3 | 12 | 12 | 8 | 487.14 | 498.14 | 531.44 | 505.44 | 137.27 | 158.57 | 149.23 | 146.57 | 87.01 | 49.01 | 31.35 | 57.31 | 718.12 | 1.48 | 0.6 | 1.17
420 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN023 | 1S-DL-YP-ETC-DLNR-2503-MAN023 | UTTARY SCHOOL BLOCK:K | TG-MAN023A-2 | 19502768 | 630 | 200 | 242 | 0.99 | 720 | 283 | 1170 | 218 | 911 | 220 | 911 | 259 | 2019-06-29 23:00 | 40.5 | -89.7 | 1206 | R | 111 | 95 | 95 | 16 |  |  | 18.2 | 81.8 |  |  |  |  | 17 | 34 | 34 | 21.3 | 480 | 561.12 | 557.12 | 534.15 | 121.27 | 116.33 | 121.14 | 134.11 | 99.18 | 6 | 6.19 | 27.49 | 717.45 | 2.15 | 0.57 | 1.14
421 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN023 | 1S-DL-YP-ETC-DLNR-2503-MAN023 | UTTARY SCHOOL BLOCK:K | TG-MAN023A-3 | 19504321 | 630 | 200 | 236 | 0.97 | 609 | 222 | 965 | 215 | 937 | 171 | 742 | 210 | 2019-06-30 23:00 | 123.3 | 29.4 | 974 | R | 107 | 101 | 92 | 15 | 0.2 | 0.1 | 2.1 | 97.6 |  | 0.3 | 0.3 | 0.3 | 16.3 | 12.3 | 12.3 | 15 | 397.17 | 468.47 | 494.17 | 462.47 | 120.5 | 67.23 | 18.53 | 72.23 | 16.03 | 1.3 |  |  | 716.58 | 3.02 | 0.63 | 0.97
422 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN024 | 1S-DL-YP-ETC-DLNR-2503-MAN024 | CHANDERVIHAR SS-1:ID | TG-MAN024A-1 | 19500843 | 630 | 200 | 235.7614 | 0.97717 | 452.7075 | 129.538 | 573.5322 | 172.0849 | 765.8088 | 151.0846 | 664.8681 | 166.5856 | 2019-06-29 23:00 | [15 empty] | 0 |  |  |  | 323.5 |  |  |  | 396.5 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.60766 | 0.71858
423 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN024 | 1S-DL-YP-ETC-DLNR-2503-MAN024 | CHANDERVIHAR SS-1:ID | TG-MAN024A-2 | 19500076 | 990 | 320 | 243 | 0.97 | 1018 | 354 | 1525 | 325 | 1403 | 339 | 1461 | 105 | 2019-06-29 23:00 | 211.2 | 77.3 | 1538 | R | 99 | 100 | 101 | 2 | 0.1 | 0.1 | 2.6 | 97.2 |  |  |  |  | 94.3 | 101.29 | 101.29 | 80.3 | 543.56 | 522.27 | 590.26 | 556.26 | 77.3 | 93.3 | 72 | 81 | 4 | 2.3 | 0.3 | 2 | 719.56 | 0.04 | 0.56 | 1.03
424 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN025 | 1S-DL-YP-ETC-DLNR-2503-MAN025 | CHANDERVIHAR SS-II:ID | TG-MAN025A-1 | 19500845 | 630 | 200 | 242 | 0.97 | 751 | 254 | 1085 | 250 | 1063 | 247 | 1057 | 25 | 2019-06-15 23:00 | 167.9 | 9.2 | 1138 | R | 100 | 96 | 104 | 8 |  |  | 33.7 | 66.3 | 0.3 | 0.3 | 0.3 | 0.3 | 11 | 13 | 13 | 6.3 | 527.28 | 556.28 | 491.28 | 528.28 | 139 | 123.27 | 174.27 | 146.57 | 41.57 | 26.3 | 50.3 | 37.3 | 719.55 | 0.05 | 0.57 | 1.19
425 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN025 | 1S-DL-YP-ETC-DLNR-2503-MAN025 | CHANDERVIHAR SS-II:ID | TG-MAN025A-2 | 19504725 | 630 | 200 | 237 | 0.98 | 675 | 245 | 1072 | 231 | 1004 | 199 | 861 | 186 | 2019-06-29 23:00 | 118.7 | 8.3 | 1097 | R | 110 | 99 | 91 | 19 |  |  | 24 | 76 | 0.3 | 0.3 | 1 | 0.3 | 36.3 | 97 | 97 | 68 | 533.59 | 513.59 | 572.59 | 547.59 | 114 | 95 | 49 | 95 | 34.3 | 13 |  | 8 | 719.29 | 0.31 | 0.56 | 1.07
426 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN026 | 1S-DL-YP-ETC-DLNR-2503-MAN026 | WESTVINOD NAGAR NEAR MANGLAM:PL | TG-MAN026A-1 | 19506612 | 990 | 320 | 238 | 0.97 | 943 | 293 | 1232 | 330 | 1392 | 319 | 1345 | 142 | 2019-06-02 23:30 | 256.3 | 50.2 | 1456 | Y | 94 | 108 | 99 | 14 | 0.1 | 0.1 | 0.7 | 99.2 | 3.3 |  |  |  | 337.57 | 226.55 | 226.55 | 282.54 | 343.03 | 418.39 | 371.55 | 386.36 | 18 | 54.26 | 30.3 | 33 |  | 2.3 | 0.3 |  | 702.3 | 17.3 | 0.5 | 0.95
427 | 2019-06-01 | 2019-06-30 22:00 | LAXMI NAGAR | MANDAWALI | 1230 | MAN026 | 1S-DL-YP-ETC-DLNR-2503-MAN026 | WESTVINOD NAGAR NEAR MANGLAM:PL | TG-MAN026A-2 | 19506134 | 990 | 320 | 242.8441 | 0.97259 | 1698.2957 | 553.9903 | 2289.3109 | 568.7532 | 2360.4614 | 575.5522 | 2381.6609 | 83.7865 | 2019-06-27 00:30 | [15 empty] | 0 |  |  |  | 0 |  |  |  | 274.5 |  |  |  | 182.5 |  |  |  | 241 | 698 |  | 0.54355 | 1.7155
428 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN026 | 1S-DL-YP-ETC-DLNR-2503-MAN026 | WESTVINOD NAGAR NEAR MANGLAM:PL | TG-MAN026A-3 | 19505743 | 990 | 320 | 244 | 0.97 | 1060 | 331 | 1380 | 333 | 1382 | 396 | 1650 | 269 | 2019-06-26 23:00 | 329.3 | 28.2 | 1905 | B | 92 | 97 | 111 | 19 | 0.1 |  | 2.6 | 97.2 | 0.3 | 0.3 | 0.3 | 0.3 | 166.55 | 105.4 | 105.4 | 112.37 | 481.44 | 539.59 | 460.02 | 488.1 | 50.44 | 52.13 | 97.02 | 92.36 | 1.29 | 3 | 66.13 | 7.29 | 701.22 | 18.38 | 0.53 | 1.07
429 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN027 | 1S-DL-YP-ETC-DLNR-2503-MAN027 | WESTVINOD NAGAR D BLOCK:ID | TG-MAN027A-1 | 19506140 | 990 | 320 | 245 | 0.96 | 742 | 228 | 967 | 267 | 1135 | 247 | 1055 | 145 | 2019-06-29 23:00 | 210.6 | 58.2 | 1192 | Y | 103 | 96 | 102 | 7 | 0.1 | 0.1 | 1.8 | 98 |  |  |  |  | 251.49 | 338.49 | 338.49 | 282.19 | 466.1 | 378.1 | 448.1 | 435.4 |  | 1 | [6 empty] | 717.59 | 2.01 | 0.59 | 0.75
430 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN027 | 1S-DL-YP-ETC-DLNR-2503-MAN027 | WESTVINOD NAGAR D BLOCK:ID | TG-MAN027A-2 | 19505858 | 990 | 320 | 243 | 0.97 | 1271 | 421 | 1841 | 446 | 1954 | 404 | 1758 | 170 | 2019-06-30 23:30 | 429.8 | 95.7 | 1954 | Y | 98 | 107 | 95 | 12 | 0.1 | 0.1 | 4.8 | 95 |  |  |  |  | 10 | 5 | 5 | 8.3 | 475.49 | 387.49 | 492.19 | 462.19 | 149.46 | 185.3 | 153.16 | 156.16 | 70.15 | 127.31 | 47.15 | 78.45 | 705.5 | 14.1 | 0.57 | 1.28
431 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN029 | 1S-DL-YP-ETC-DLNR-2503-MAN029 | A BLOCK WESTVINOD NAGAR | TG-MAN029A-1 | 19504659 | 990 | 320 | 243 | 0.97 | 1213 | 384 | 1682 | 446 | 1966 | 383 | 1685 | 282 | 2019-06-30 23:30 | 212 | 78.8 | 1966 | Y | 96 | 105 | 99 | 9 |  |  | 0.8 | 99.2 |  |  |  |  | 43 | 25 | 25 | 27 | 538.58 | 492.57 | 535.28 | 528.58 | 117 | 135.31 | 127 | 128.3 | 19 | 64.3 | 26.3 | 33.3 | 717.58 | 2.02 | 0.54 | 1.22
432 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN029 | 1S-DL-YP-ETC-DLNR-2503-MAN029 | A BLOCK WEST VINOD NAGAR | TG-MAN029A-2 | 19501888 | 990 | 320 | 249 | 0.97 | 1185 | 360 | 1530 | 401 | 1700 | 424 | 1813 | 246 | 2019-06-30 23:30 | 221.5 | 88.3 | 1897 | B | 89 | 105 | 106 | 17 |  |  | 4.4 | 95.6 |  |  |  |  | 34.3 | 7 | 7 | 12 | 566.22 | 481.03 | 471.33 | 507.33 | 113.42 | 137.49 | 155.3 | 147.19 | 4 | 92.42 | 82.31 | 51.42 | 718.34 | 1.26 | 0.58 | 1.2
433 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN030 | 1S-DL-YP-ETC-DLNR-2503-MAN030 | E BLOCK WESTVINOD NAGAR:ID | TG-MAN030A-1 | 19505814 | 990 | 200 | 239.8024 | 0.97307 | 826.9265 | 269.7131 | 1166.1252 | 334.0345 | 1470.8048 | 223.1789 | 965.4321 | 440.7431 | 2019-06-30 23:00 | [15 empty] | 0 |  |  |  | 223 |  |  |  | 493.5 |  |  |  | 2 |  |  |  | 0 | 718.5 |  | 0.57448 | 0.83528
434 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN030 | 1S-DL-YP-ETC-DLNR-2503-MAN030 | E BLOCK WESTVINOD NAGAR:ID | TG-MAN030A-2 | 19505463 | 990 | 320 | 241 | 0.97 | 927 | 272 | 1197 | 353 | 1559 | 301 | 1321 | 319 | 2019-06-26 23:00 | 347.5 | 81 | 1587 | Y | 92 | 111 | 97 | 19 | 0.1 | 0.1 | 0.1 | 99.7 |  |  |  |  | 98.44 | 20.14 | 20.14 | 37.44 | 604.01 | 563.24 | 643.01 | 628.01 | 14.26 | 128.37 | 26.56 | 51.26 |  | 4.56 |  |  | 717.11 | 2.49 | 0.63 | 0.94
435 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN031 | 1S-DL-YP-ETC-DLNR-2503-MAN031 | MOHAN BABA MANDIR MANDAWALI:PL | TG-MAN031A-1 | 19506135 | 990 | 320 | 243 | 0.98 | 1290 | 448 | 1956 | 447 | 1951 | 395 | 1723 | 231 | 2019-06-30 23:30 | 336.3 | 71.7 | 2118 | Y | 103 | 106 | 91 | 15 | 0.1 |  | 0.3 | 99.6 | [8 empty] | 254.31 | 235.18 | 380.36 | 276.48 | 230.52 | 212.05 | 241.06 | 239.35 | 215.3 | 253.3 | 79.11 | 184.3 | 700.53 | 19.07 | 0.66 | 1.3
436 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN031 | 1S-DL-YP-ETC-DLNR-2503-MAN031 | MOHAN BABA MANDIR MANDAWALI:PL | TG-MAN031A-2 | 19504139 | 630 | 200 | 237 | 0.98 | 330 | 86 | 376 | 137 | 608 | 107 | 470 | 202 | 2019-06-29 23:00 | 52.9 | 18.9 | 612 | Y | 86 | 115 | 98 | 29 | 0.1 | 0.3 | 88.6 | 11.1 | 35 | 3 | 14.3 | 8 | 672.51 | 473.51 | 473.51 | 601.27 | 9 | 240 | 109.24 | 107.24 | [8 empty] | 716.51 | 3.09 | 0.61 | 0.52
437 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN032 | 1S-DL-YP-ETC-DLNR-2503-MAN032 | SONIYA VIHAR MANDAWALI:PL | TG-MAN032A-1 | 19505665 | 400 | 120 | 233 | 0.98 | 430 | 151 | 683 | 136 | 612 | 143 | 641 | 62 | 2019-06-11 23:00 | 96 | 27.8 | 772 | R | 106 | 100 | 94 | 12 | 0.1 | 0.6 | 12.9 | 86.4 | [5 empty] | 1 | 1 |  | 424.28 | 470.42 | 503.28 | 472.58 | 221.3 | 212.46 | 197.3 | 218 | 59.3 | 21 | 4 | 14.3 | 705.28 | 14.32 | 0.69 | 1.07
438 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN033 | 1S-DL-YP-ETC-DLNR-2503-MAN033 | B BLOCK MANDAWALI:ID | TG-MAN033A-1 | 19506545 | 990 | 320 | 240 | 0.97 | 1105 | 394 | 1767 | 366 | 1644 | 344 | 1544 | 194 | 2019-06-30 23:30 | 318.1 | 83.2 | 1777 | R | 105 | 103 | 92 | 13 | 0.1 | 0.4 | 29.1 | 70.4 |  |  |  |  | 15 | 31.3 | 31.3 | 32 | 512.38 | 495.13 | 559.13 | 526.13 | 144.05 | 153.3 | 73.25 | 132 | 31.55 | 23.25 | 2 | 13.25 | 703.38 | 16.22 | 0.57 | 1.12
439 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN033 | 1S-DL-YP-ETC-DLNR-2503-MAN033 | B BLOCK MANDAWALI:ID | TG-MAN033A-2 | 19506320 | 990 | 320 | 236 | 0.97 | 637 | 199 | 898 | 238 | 1077 | 200 | 901 | 178 | 2019-06-30 23:30 | 184.3 | 45.1 | 1095 | Y | 95 | 110 | 96 | 15 | 0.1 |  | 0.6 | 99.2 | 12.3 | 2.3 | 11.3 | 7 | 518.42 | 388.07 | 388.07 | 473.37 | 187.25 | 328 | 191 | 238 | [8 empty] | 718.37 | 1.23 | 0.56 | 0.64
440 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN033 | 1S-DL-YP-ETC-DLNR-2503-MAN033 | B BLOCK MANDAWALI:ID | TG-MAN033A-3 | 19506881 | 990 | 320 | 243 | 0.97 | 330 | 123 | 540 | 131 | 574 | 76 | 330 | 228 | 2019-06-30 23:30 | 94.7 | 22.1 | 626 | Y | 103 | 115 | 81 | 34 | 0.1 | 0.1 | 0.4 | 99.4 | 387.37 | 301.37 | 601.42 | 411.07 | 316 | 401.3 | 401.3 | 292.3 |  | 0.3 | [10 empty] | 703.37 | 16.23 | 0.58 | 0.33
441 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN034 | 1S-DL-YP-ETC-DLNR-2503-MAN034 | C BLOCK WESTVINOD NAGAR:PL | TG-MAN034A-1 | 19505260 | 990 | 320 | 244 | 0.96 | 1068 | 368 | 1536 | 326 | 1358 | 374 | 1573 | 200 | 2019-06-26 23:30 | 273.3 | 54.7 | 1650 | B | 100 | 94 | 106 | 12 | 0.1 | 0.1 | 2.3 | 97.5 |  |  |  |  | 79 | 95 | 95 | 55 | 504.42 | 542.12 | 542.11 | 539.12 | 113.3 | 68.21 | 116.01 | 107 | 8.21 |  | 18.51 | 4.21 | 705.33 | 14.27 | 0.56 | 1.08
442 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN034 | 1S-DL-YP-ETC-DLNR-2503-MAN034 | C BLOCK WESTVINOD NAGAR:PL | TG-MAN034A-2 | 19506137 | 630 | 200 | 257 | 0.96 | 669 | 150 | 595 | 245 | 980 | 275 | 1121 | 472 | 2019-06-26 23:00 | 209.6 | 32.6 | 1134 | B | 100 | 88 | 112 | 24 | 0.1 | 1 | 0.8 | 98.1 | 2.3 | 9.3 | 2.3 | 2.3 | 275.26 | 342.11 | 342.11 | 290.11 | 248.44 | 174.59 | 246.18 | 229.03 | 0.3 |  | 30 | 4.56 |  | 0.3 | 6.56 | 0.3 | 527.1 | 0.5 | 0.39 | 1.06
443 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN035 | 1S-DL-YP-ETC-DLNR-2503-MAN035 | LSC-II, MANDAWALI:ID | TG-MAN035A-1 | 19501890 | 630 | 200 | 240 | 0.98 | 97 | 40 | 167 | 28 | 118 | 29 | 122 | 47 | 2019-06-09 13:30 | 22.1 | 4.6 | 183 | R | 134 | 84 | 82 | 52 |  |  |  | 100 | 717.05 | 719.05 | 719.05 | 719.05 | 2 | [15 empty] | 719.05 | 0.55 | 0.51 | 0.15
444 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN035 | 1S-DL-YP-ETC-DLNR-2503-MAN035 | LSC-II, MANDAWALI:ID | TG-MAN035A-2 | 19505525 | 630 | 200 | 241 | 0.96 | 97 | 32 | 130 | 36 | 144 | 29 | 119 | 22 | 2019-06-27 12:30 | 52.8 | 0.6 | 172 | B | 90 | 107 | 103 | 17 | 0.1 |  | 0.2 | 99.7 | 719.05 | 719.05 | 719.05 | 719.05 | [16 empty] | 719.05 | 0.55 | 0.43 | 0.15
445 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN036 | 1S-DL-YP-ETC-DLNR-2503-MAN036 | SWAMINARAIN TEMPLE YAMUNA PUSTA | TG-MAN036A-1 | 19505948 | 400 | 120 | 245 | 0.88 | 40 | 12 | 46 | 14 | 54 | 14 | 57 | 9 | 2019-06-06 06:30 | 21.8 | -36.7 | 71 | B | 102 | 91 | 107 | 16 |  |  | 4.2 | 95.8 | 717.55 | 717.55 | 717.55 | 717.55 | [16 empty] | 717.55 | 2.05 | 0.58 | 0.1
446 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN037 | 1S-DL-YP-ETC-DLNR-2503-MAN037 | SHANKAR MARG MANDAWALI:PL | TG-MAN037A-1 | 19506836 | 990 | 320 | 244 | 0.97 | 1290 | 420 | 1822 | 386 | 1678 | 484 | 2131 | 400 | 2019-06-30 23:30 | 354.9 | 95.4 | 2131 | B | 102 | 95 | 103 | 8 | 0.1 | 0.1 | 2.8 | 97 |  |  |  |  | 11 | 24 | 24 | 15 | 450 | 485 | 455.3 | 466 | 130 | 125.05 | 115.3 | 120.35 | 113.31 | 70.26 | 121.01 | 102.56 | 704.31 | 15.29 | 0.56 | 1.3
447 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN038 | 1S-DL-YP-ETC-DLNR-2503-MAN038 | KRISHNA PURI MANDAWALI:PL | TG-MAN038A-1 | 19504301 | 630 | 200 | 233 | 0.97 | 589 | 208 | 954 | 192 | 865 | 189 | 855 | 94 | 2019-06-30 23:30 | 92.9 | 46.5 | 1097 | B | 107 | 84 | 109 | 25 | 0.5 | 21.1 | 74.9 | 3.5 |  |  |  |  | 40 | 183.33 | 183.33 | 53.48 | 554.33 | 527.3 | 526.09 | 599.15 | 122.3 | 7.3 | 89 | 65.3 | 1.3 |  | 39.3 |  | 718.33 | 1.27 | 0.61 | 0.93
448 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN039 | 1S-DL-YP-ETC-DLNR-2503-MAN039 | ALLAH COLONY MANDAWALI:PL | TG-MAN039A-1 | 19506415 | 630 | 200 | 244 | 0.96 | 616 | 194 | 840 | 212 | 923 | 210 | 913 | 78 | 2019-06-29 23:30 | 185.2 | 47.2 | 923 | Y | 99 | 103 | 97 | 6 | 0.1 | 0.4 | 5.9 | 93.6 |  |  |  |  | 53 | 47.3 | 47.3 | 54.3 | 619.06 | 601.36 | 558.36 | 613.06 | 24 | 46 | 23.3 | 28.3 |  | 1 | 0.3 |  | 696.06 | 23.54 | 0.57 | 0.98
449 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN050 | 1S-DL-YP-ETC-DLNR-2503-MAN050 | NOIDA MORE FLYOVER:PM | TG-MAN050A-1 | 19506321 | 400 | 120 | 245 | 0.99 | 69 | 26 | 103 | 22 | 88 | 21 | 83 | 18 | 2019-06-21 18:30 | 9.4 | -5.4 | 103 | R | 103 | 95 | 102 | 8 |  |  | 0.6 | 99.4 | 647.12 | 647.12 | 647.12 | 647.12 | [16 empty] | 647.12 | 48.48 | 0.33 | 0.17
450 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN059 | 1S-DL-YP-ETC-DLNR-2503-MAN059 | S/STN.NO-2, PPG CGHS:ID | TG-MAN059A-1 | 19501860 | 630 | 200 | 233 | 0.98 | 635 | 225 | 1040 | 202 | 918 | 208 | 947 | 110 | 2019-06-30 23:00 | 112.2 | 41.9 | 1059 | R | 100 | 95 | 105 | 10 |  | 2 | 26.3 | 71.7 |  |  |  |  | 12.3 | 31.3 | 31.3 | 8 | 609.25 | 603.26 | 594.25 | 623.49 | 91.31 | 81.19 | 120.2 | 84.37 | 3.19 | 0.3 |  | 0.19 | 716.45 | 3.15 | 0.63 | 1.01
451 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN060 | 1S-DL-YP-ETC-DLNR-2503-MAN060 | S/STN.NO-3, PPG CGHS:ID | TG-MAN060A-1 | 19506319 | 400 | 120 | 237 | 0.98 | 87 | 51 | 229 | 22 | 100 | 14 | 62 | 152 | 2019-06-30 14:30 | 26.3 | 1.9 | 229 | R | 107 | 94 | 100 | 13 | 0.1 | 0.3 | 13.9 | 85.7 | 678.52 | 688.52 | 681.16 | 694.52 | 16.3 | 6.3 | 6.3 | 0.3 | [12 empty] | 695.22 | 24.38 | 0.55 | 0.22
452 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN060 | 1S-DL-YP-ETC-DLNR-2503-MAN060 | S/STN.NO-3, PPG CGHS:ID | TG-MAN060A-2 | 19506318 | 400 | 120 | 238 | 0.98 | 79 | 20 | 92 | 38 | 172 | 21 | 95 | 79 | 2019-06-10 23:00 | 16 | 2.5 | 172 | Y | 84 | 130 | 86 | 46 | 0.1 |  | 1 | 98.9 | 718.52 | 629.58 | 716.52 | 718.52 |  | 88.54 | 88.54 | [13 empty] | 718.52 | 1.08 | 0.52 | 0.2
453 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN061 | 1S-DL-YP-ETC-DLNR-2503-MAN061 | S/STN.NO-4, PPG CGHS:ID | TG-MAN061A-1 | 19506534 | 400 | 120 | 243 | 0.97 | 304 | 65 | 275 | 97 | 415 | 142 | 600 | 283 | 2019-06-26 12:00 | 67.4 | 0.7 | 600 | B | 128 | 68 | 104 | 60 |  |  | 0.9 | 99.1 | 576.47 | 688.37 | 621.47 | 650.37 | 115.5 | 6 | 6 | 44 | 2.3 | 0.3 |  | 0.3 | [6 empty] | 0.3 |  | 695.07 | 24.53 | 0.13 | 0.76
454 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN062 | 1S-DL-YP-ETC-DLNR-2503-MAN062 | S/STN.NO-5, PPG CGHS:ID | TG-MAN062A-1 | 19504610 | 400 | 120 | 246 | 0.97 | 64 | 35 | 141 | 21 | 85 | 7 | 28 | 98 | 2019-06-10 11:00 | 16.8 | -1.7 | 147 | R | 155 | 100 | 45 | 110 |  |  |  | 100 | 616.01 | 719.31 | 719.31 | 719.31 | 103.3 | [15 empty] | 719.31 | 0.29 | 0.3 | 0.16
455 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN063 | 1S-DL-YP-ETC-DLNR-2503-MAN063 | S/STN.NO-6, PPG CGHS:ID | TG-MAN063A-1 | 19506873 | 400 | 120 | 240 | 0.95 | 280 | 126 | 550 | 29 | 124 | 124 | 525 | 414 | 2019-06-06 15:30 | 71.2 | 2 | 550 | R | 104 | 88 | 109 | 21 | 0.1 |  | 2.6 | 97.2 | 449.35 | 570.36 | 362.03 | 422.35 | 252 | 132.59 | 132.59 | 280 | 1 |  | 1.3 | 1 | 1 |  | 0.3 | [5 empty] | 703.35 | 16.25 | 0.25 | 0.7
456 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN064 | 1S-DL-YP-ETC-DLNR-2503-MAN064 | S/STN.NO-7, PPG CGHS:ID | TG-MAN064A-1 | 19502395 | 400 | 120 | 240 | 0.98 | 161 | 50 | 211 | 54 | 231 | 57 | 241 | 27 | 2019-06-06 13:00 | 26.5 | 4.7 | 255 | Y | 90 | 106 | 104 | 16 |  |  | 0.7 | 99.3 | 523.31 | 480.31 | 475.31 | 491.01 | 193.05 | 227.05 | 227.05 | 227.05 | 2.3 | 11.3 | 20.3 | 1 | [8 empty] | 719.06 | 0.54 | 0.4 | 0.4
457 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN110 | 1S-DL-YP-ETC-DLNR-2503-MAN110 | BATLA CGHS,PPG,S/STN-1:ID | TG-MAN110A-1 | 19500971 | 400 | 120 | 243 | 0.98 | 68 | 44 | 189 | 24 | 106 | 0 | 0 | 164 | 2019-06-11 00:30 | 13.2 | 1.9 | 199 | R | 201 | 99 | 0 | 201 |  |  | 0.1 | 99.9 | 486.3 | 719.3 | 719.3 | 719.3 | 233 | [15 empty] | 719.3 | 0.3 | 0.51 | 0.17
458 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN110 | 1S-DL-YP-ETC-DLNR-2503-MAN110 | BATLA CGHS,PPG,S/STN-1:ID | TG-MAN110A-2 | 19500972 | 400 | 120 | 243 | 0.98 | 149 | 57 | 250 | 54 | 237 | 38 | 169 | 76 | 2019-06-11 | 28.7 | 6.1 | 260 | R | 111 | 111 | 78 | 33 |  |  | 0.1 | 99.9 | 362.3 | 353 | 572 | 419 | 341.16 | 357.01 | 357.01 | 300.31 | 15.45 | 9.3 | [10 empty] | 719.31 | 0.29 | 0.53 | 0.37
459 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN111 | 1S-DL-YP-ETC-DLNR-2503-MAN111 | BATLA CGHS,PPG,S/STN-2:ID | TG-MAN111A-1 | 19500888 | 990 | 320 | 242.4675 | 0.98069 | 174.8764 | 54.959 | 234.4969 | 46.2217 | 196.8306 | 73.6956 | 313.8254 | 103.4397 | 2019-06-11 23:00 | [15 empty] | 720 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.53454 | 0.17664
460 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN111 | 1S-DL-YP-ETC-DLNR-2503-MAN111 | BATLA CGHS,PPG,S/STN-2:ID | TG-MAN111A-2 | 19500887 | 990 | 300 | 242.719 | 0.95278 | 161.0172 | 43.0352 | 181.1322 | 49.5745 | 208.8577 | 68.4075 | 287.9225 | 95.9794 | 2019-06-11 23:30 | [15 empty] | 720 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.56847 | 0.16264
461 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN112 | 1S-DL-YP-ETC-DLNR-2503-MAN112 | KARISHMA APTT. PPG S/S-1:ID | TG-MAN112A-1 | 19500976 | 630 | 200 | 242 | 0.98 | 178 | 54 | 243 | 68 | 303 | 56 | 254 | 56 | 2019-06-10 23:00 | 28.1 | 6.4 | 306 | Y | 79 | 131 | 90 | 52 |  |  | 16.1 | 83.9 | 681.31 | 459.3 | 630.01 | 599.46 | 38 | 260.01 | 260.01 | 119.45 | [12 empty] | 719.31 | 0.29 | 0.49 | 0.28
462 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN112 | 1S-DL-YP-ETC-DLNR-2503-MAN112 | KARISHMA APTT. PPG S/S-1:ID | TG-MAN112A-2 | 19500973 | 630 | 200 | 237 | 0.97 | 103 | 34 | 142 | 45 | 184 | 24 | 98 | 75 | 2019-06-02 23:30 | 20.7 | 2.3 | 221 | Y | 97 | 120 | 83 | 37 |  |  | 0.1 | 99.9 | 719.31 | 707.01 | 719.31 | 719.31 |  | 12.3 | 12.3 | [13 empty] | 719.31 | 0.29 | 0.55 | 0.16
463 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN113 | 1S-DL-YP-ETC-DLNR-2503-MAN113 | KARISHMA APTT. PPG S/S-2:ID | TG-MAN113A-1 | 19500988 | 630 | 200 | 243 | 0.97 | 129 | 44 | 185 | 43 | 179 | 42 | 175 | 8 | 2019-06-12 | 25.3 | 4.1 | 204 | Y | 93 | 107 | 100 | 14 |  |  | 0.1 | 99.9 | 717.01 | 705.01 | 716.01 | 719.01 | 2.3 | 14.3 | 14.3 | 0.3 | [12 empty] | 719.31 | 0.29 | 0.46 | 0.2
464 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN113 | 1S-DL-YP-ETC-DLNR-2503-MAN113 | KARISHMA APTT. PPG S/S-2:ID | TG-MAN113A-2 | 19504822 | 630 | 200 | 243 | 0.97 | 165 | 66 | 292 | 42 | 185 | 56 | 248 | 94 | 2019-06-11 | 35 | 5.1 | 307 | R | 133 | 75 | 92 | 58 |  |  | 19.1 | 80.9 | 515.3 | 713.01 | 686.04 | 648.04 | 204.01 | 6.3 | 6.3 | 71.27 | [12 empty] | 719.31 | 0.29 | 0.47 | 0.26
465 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN114 | 1S-DL-YP-ETC-DLNR-2503-MAN114 | KRIPAL CGHS, PPG:ID | TG-MAN114A-1 | 19500977 | 630 | 200 | 242 | 0.97 | 138 | 59 | 254 | 27 | 114 | 53 | 229 | 129 | 2019-06-30 | 28.1 | 5.1 | 255 | B | 119 | 63 | 119 | 56 |  |  | 0.2 | 99.8 | 639.3 | 719.3 | 651.3 | 707.3 | 80 |  |  | 12 | [12 empty] | 719.3 | 0.3 | 0.51 | 0.22
466 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN114 | 1S-DL-YP-ETC-DLNR-2503-MAN114 | KRIPAL CGHS, PPG:ID | TG-MAN114A-2 | 19500823 | 630 | 200 | 236.8045 | 0.98904 | 175.5617 | 64.2816 | 280.6077 | 47.1023 | 205.615 | 64.1778 | 280.4362 | 74.9071 | 2019-06-11 23:30 | [15 empty] | 587.5 |  |  |  | 132.5 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.5434 | 0.27867
467 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN115 | 1S-DL-YP-ETC-DLNR-2503-MAN115 | BHARAT CGHS, PPG, KOHINOOR:ID | TG-MAN115A-1 | 19500978 | 630 | 200 | 239 | 0.98 | 183 | 60 | 266 | 76 | 336 | 47 | 209 | 110 | 2019-06-30 23:00 | 26.7 | 5.1 | 336 | Y | 111 | 109 | 80 | 31 |  |  |  | 100 | 505.35 | 496.57 | 696.54 | 566.4 | 212.49 | 221.27 | 221.27 | 151.44 | [12 empty] | 718.24 | 1.36 | 0.52 | 0.29
468 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN116 | 1S-DL-YP-ETC-DLNR-2503-MAN116 | ORIENTAL CGHS, PPG:ID | TG-MAN116A-1 | 19500994 | 400 | 120 | 246 | 0.98 | 109 | 30 | 126 | 46 | 192 | 33 | 139 | 61 | 2019-06-10 | 17.4 | 2.5 | 199 | Y | 86 | 130 | 83 | 47 |  | 0.1 | 0.7 | 99.2 | 677.35 | 495.39 | 669.05 | 608.35 | 41.3 | 223.26 | 223.26 | 110.3 | [12 empty] | 719.05 | 0.55 | 0.48 | 0.27
469 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN116 | 1S-DL-YP-ETC-DLNR-2503-MAN116 | ORIENTAL CGHS, PPG:ID | TG-MAN116A-2 | 19500984 | 400 | 120 | 246 | 0.97 | 17 | 0 | 0 | 17 | 69 | 0 | 0 | 69 | 2019-06-06 06:30 | 6.3 | 0.3 | 74 | Y | 0 | 300 | 0 | 300 |  |  | 0.2 | 99.8 | 719.04 | 719.04 | 719.04 | 719.04 | [16 empty] | 719.04 | 0.56 | 0.49 | 0.04
470 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN117 | 1S-DL-YP-ETC-DLNR-2503-MAN117 | AJANTA CGHS, PPG:ID | TG-MAN117A-1 | 19500995 | 630 | 200 | 246 | 0.98 | 129 | 59 | 237 | 47 | 189 | 23 | 92 | 127 | 2019-06-03 | 20.7 | 2.8 | 249 | R | 134 | 107 | 59 | 75 |  |  | 0.3 | 99.7 | 637.27 | 698.57 | 718.57 | 717.27 | 81.3 | 20 | 20 | 1.3 | [12 empty] | 718.57 | 1.03 | 0.42 | 0.2
471 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN117 | 1S-DL-YP-ETC-DLNR-2503-MAN117 | AJANTA CGHS, PPG:ID | TG-MAN117A-2 | 19500987 | 630 | 200 | 246 | 0.97 | 135 | 54 | 223 | 48 | 199 | 32 | 133 | 81 | 2019-06-13 23:30 | 27.1 | 2.8 | 223 | R | 120 | 112 | 69 | 51 |  |  | 0.5 | 99.5 | 666.06 | 666.06 | 719.06 | 712.36 | 53 | 53 | 53 | 6.3 | [12 empty] | 719.06 | 0.54 | 0.49 | 0.21
472 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN118 | 1S-DL-YP-ETC-DLNR-2503-MAN118 | VANDANA CGHS, PPG:ID | TG-MAN118A-1 | 19506734 | 400 | 120 | 240 | 0.98 | 168 | 65 | 266 | 46 | 189 | 58 | 239 | 68 | 2019-06-03 | 54 | 4.7 | 307 | B | 110 | 84 | 106 | 26 | 0.2 | 0.1 | 0.3 | 99.4 | 170.35 | 398.05 | 244 | 267.3 | 496.04 | 303.29 | 303.29 | 425.04 | 37.55 | 3 | 50 | 12 | [8 empty] | 704.34 | 15.26 | 0.56 | 0.42
473 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN118 | 1S-DL-YP-ETC-DLNR-2503-MAN118 | VANDANA CGHS, PPG:ID | TG-MAN118A-2 | 19506910 | 400 | 120 | 241 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [7 empty] | 0.4 | 99.6 | 707.04 | 707.04 | 707.04 | 707.04 | [16 empty] | 707.04 | 12.56 |  | 0
474 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN119 | 1S-DL-YP-ETC-DLNR-2503-MAN119 | MIRTRADEEP CGHS, PPG:ID | TG-MAN119A-1 | 19504367 | 630 | 200 | 237 | 0.98 | 148 | 52 | 216 | 36 | 151 | 60 | 248 | 86 | 2019-06-11 23:00 | 23.5 | 2.3 | 286 | B | 103 | 80 | 117 | 37 |  |  | 0.1 | 99.9 | 694.01 | 719.01 | 622.01 | 694.01 | 25.3 | 0.3 | 0.3 | 25.3 | [12 empty] | 719.31 | 0.29 | 0.5 | 0.23
475 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN125 | 1S-DL-YP-ETC-DLNR-2503-MAN125 | SAVARKAR CGHS, PPG:ID | TG-MAN125A-1 | 19505977 | 630 | 200 | 246 | 0.97 | 188 | 78 | 319 | 57 | 232 | 53 | 216 | 96 | 2019-06-02 | 49.6 | 7.6 | 346 | R | 117 | 94 | 89 | 28 | 0.1 |  | 0.3 | 99.6 | 426 | 551.39 | 599.31 | 522.09 | 269.31 | 144.22 | 144.22 | 173.52 | 0.3 | [11 empty] | 696.01 | 23.59 | 0.54 | 0.3
476 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN125 | 1S-DL-YP-ETC-DLNR-2503-MAN125 | SAVARKAR CGHS, PPG:ID | TG-MAN125A-2 | 19500975 | 630 | 200 | 246 | 0.98 | 93 | 31 | 126 | 27 | 109 | 35 | 145 | 31 | 2019-06-26 23:30 | 16.1 | 1.4 | 188 | B | 94 | 81 | 126 | 45 |  |  | 0.3 | 99.7 | 719.05 | 719.05 | 712.05 | 719.05 | [16 empty] | 719.05 | 0.55 | 0.51 | 0.15
477 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN126 | 1S-DL-YP-ETC-DLNR-2503-MAN126 | PRASHANT CGHS, PPG:ID | TG-MAN126A-1 | 19500889 | 400 | 120 | 245.8243 | 0.97137 | 113.032 | 40.8825 | 168.9638 | 43.5626 | 180.5552 | 28.587 | 117.0351 | 58.5908 | 2019-06-30 00:30 | [15 empty] | 600.5 |  |  |  | 119.5 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.48601 | 0.28258
478 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN126 | 1S-DL-YP-ETC-DLNR-2503-MAN126 | PRASHANT CGHS, PPG:ID | TG-MAN126A-2 | 19500890 | 400 | 120 | 245.8826 | 0.9817 | 113.241 | 11.868 | 52.9774 | 45.3749 | 203.8041 | 55.9981 | 251.2589 | 179.3268 | 2019-06-10 23:30 | [15 empty] | 596.5 |  |  |  | 123.5 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.49309 | 0.2831
479 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN153 | 1S-DL-YP-ETC-DLNR-2503-MAN153 | BROTHERS CGHS, PPG:ID | TG-MAN153A-1 | 19506889 | 400 | 120 | 246 | 0.97 | 96 | 22 | 90 | 25 | 103 | 49 | 204 | 108 | 2019-06-02 22:30 | 35.2 | 3.5 | 204 | B | 87 | 88 | 125 | 38 | 0.1 |  | 0.3 | 99.6 | 688.05 | 649.35 | 500.4 | 647.35 | 17 | 55.3 | 55.3 | 57.3 | [12 empty] | 705.05 | 14.55 | 0.58 | 0.24
480 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN153 | 1S-DL-YP-ETC-DLNR-2503-MAN153 | BROTHERS CGHS, PPG:ID | TG-MAN153A-2 | 19500901 | 400 | 120 | 245.7147 | 0.97548 | 97.8341 | 31.1526 | 127.5385 | 29.7171 | 121.6619 | 36.9644 | 150.6232 | 26.5159 | 2019-06-15 | [15 empty] | 671 |  |  |  | 49 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.48624 | 0.24459
481 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN168 | 1S-DL-YP-ETC-DLNR-2503-MAN168 | PANCH MAHAL,PPG CGHS:ID | TG-MAN168A-1 | 19500993 | 400 | 120 | 240 | 0.99 | 81 | 17 | 78 | 32 | 144 | 32 | 144 | 66 | 2019-06-30 23:30 | 9.4 | 0.6 | 150 | Y | 80 | 107 | 113 | 33 |  |  | 1.5 | 98.5 | 718.36 | 698.06 | 682.06 | 717.36 |  | 20.3 | 20.3 | 1 | [12 empty] | 718.36 | 1.24 | 0.46 | 0.2
482 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN168 | 1S-DL-YP-ETC-DLNR-2503-MAN168 | PANCH MAHAL,PPG CGHS:ID | TG-MAN168A-2 | 19506138 | 400 | 120 | 240 | 0.98 | 102 | 29 | 125 | 46 | 194 | 27 | 114 | 75 | 2019-06-02 23:00 | 21.2 | 2.2 | 211 | Y | 81 | 138 | 81 | 57 | 0.1 |  | 0.1 | 99.9 | 678.36 | 463.06 | 691.06 | 636.12 | 16.3 | 232 | 232 | 58.54 | [12 empty] | 695.06 | 24.54 | 0.46 | 0.26
483 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN169 | 1S-DL-YP-ETC-DLNR-2503-MAN169 | SARASWATI KUNJ CGHS S/S-1:ID | TG-MAN169A-1 | 19500950 | 630 | 200 | 243 | 0.98 | 136 | 51 | 206 | 35 | 141 | 50 | 203 | 63 | 2019-06-03 | 23 | 3.7 | 244 | R | 114 | 94 | 92 | 22 |  |  | 2.6 | 97.4 | 617 | 708.3 | 707.3 | 702.3 | 102.3 | 11 | 11 | 17 | [12 empty] | 719.3 | 0.3 | 0.53 | 0.22
484 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN169 | 1S-DL-YP-ETC-DLNR-2503-MAN169 | SARASWATI KUNJ CGHS S/S-1:ID | TG-MAN169A-2 | 19506456 | 630 | 200 | 244 | 0.96 | 120 | 38 | 147 | 33 | 137 | 48 | 197 | 56 | 2019-06-02 23:30 | 39 | 5.2 | 197 | B | 98 | 98 | 104 | 6 | 100 |  |  |  | 719.3 | 719.3 | 718.3 | 719.3 | [16 empty] | 719.3 | 0.3 | 0.46 | 0.19
485 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN170 | 1S-DL-YP-ETC-DLNR-2503-MAN170 | SARSWATI KUNJ CGHS S/S-2:ID | TG-MAN170A-1 | 19500904 | 630 | 200 | 249 | 0.97 | 187 | 54 | 216 | 70 | 281 | 62 | 243 | 57 | 2019-06-02 23:00 | 41.4 | 9.2 | 304 | Y | 96 | 112 | 92 | 20 | 1.5 | 3.7 | 34.1 | 60.7 | 569 | 487.3 | 559 | 543.3 | 150.3 | 232 | 232 | 176 | [12 empty] | 719.3 | 0.3 | 0.51 | 0.3
486 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN170 | 1S-DL-YP-ETC-DLNR-2503-MAN170 | SARSWATI KUNJ CGHS S/S-2:ID | TG-MAN170A-2 | 19500903 | 630 | 200 | 249 | 0.97 | 181 | 60 | 262 | 71 | 311 | 50 | 215 | 83 | 2019-06-10 23:30 | 38.2 | 6.9 | 311 | Y | 102 | 104 | 94 | 10 |  |  | 6.7 | 93.3 | 561.34 | 533 | 598.3 | 558.3 | 157.56 | 186.3 | 186.3 | 161 | [12 empty] | 719.3 | 0.3 | 0.51 | 0.29
487 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN171 | 1S-DL-YP-ETC-DLNR-2503-MAN171 | AKASH BHARTI CGHS PPG:ID | TG-MAN171A-1 | 19500953 | 400 | 120 | 240 | 0.97 | 177 | 71 | 302 | 38 | 160 | 68 | 285 | 135 | 2019-06-11 23:30 | 34.8 | 7.5 | 342 | R | 117 | 67 | 115 | 50 |  |  | 7.7 | 92.3 | 148.46 | 509.51 | 135.46 | 204.51 | 437.38 | 208.3 | 208.3 | 485 | 131.57 |  | 124.3 | 28.3 | [8 empty] | 718.21 | 1.39 | 0.57 | 0.44
488 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN171 | 1S-DL-YP-ETC-DLNR-2503-MAN171 | AKASH BHARTI CGHS PPG:ID | TG-MAN171A-2 | 19500951 | 630 | 200 | 240 | 0.98 | 153 | 46 | 204 | 54 | 238 | 52 | 228 | 31 | 2019-06-30 23:00 | 28.5 | 5.1 | 243 | Y | 102 | 102 | 96 | 6 |  |  | 8.2 | 91.8 | 682.22 | 650.22 | 649.42 | 673.52 | 36 | 68 | 68 | 44.3 | [12 empty] | 718.22 | 1.38 | 0.51 | 0.24
489 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN172 | 1S-DL-YP-ETC-DLNR-2503-MAN172 | PRESS APPARTMENT CGHS PPG:ID | TG-MAN172A-1 | 19500955 | 630 | 200 | 247 | 0.98 | 46 | 26 | 104 | 0 | 0 | 19 | 76 | 93 | 2019-06-03 06:00 | 11 | 0.9 | 112 | R | 165 | 0 | 135 | 165 |  |  | 2.3 | 97.7 | 718.21 | 718.21 | 718.21 | 718.21 | [16 empty] | 718.21 | 1.39 | 0.55 | 0.07
490 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN172 | 1S-DL-YP-ETC-DLNR-2503-MAN172 | PRESS APPARTMENT CGHS PPG:ID | TG-MAN172A-2 | 19500952 | 630 | 200 | 247 | 0.98 | 98 | 32 | 140 | 30 | 132 | 35 | 148 | 14 | 2019-06-02 22:30 | 18.9 | 2.3 | 168 | B | 89 | 94 | 117 | 28 |  |  | 29.6 | 70.4 | 718.21 | 718.21 | 718.21 | 718.21 | [16 empty] | 718.21 | 1.39 | 0.52 | 0.15
491 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN173 | 1S-DL-YP-ETC-DLNR-2503-MAN173 | RETREET CGHS PPG S/S-1:ID | TG-MAN173A-1 | 19502053 | 630 | 200 | 246 | 0.97 | 70 | 16 | 67 | 23 | 96 | 31 | 127 | 52 | 2019-06-09 23:00 | 13.3 | 1.8 | 137 | B | 61 | 104 | 135 | 74 |  | 0.1 | 58.1 | 41.7 | 718.21 | 718.21 | 718.21 | 718.21 | [16 empty] | 718.21 | 1.39 | 0.47 | 0.11
492 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN173 | 1S-DL-YP-ETC-DLNR-2503-MAN173 | RETREET CGHS PPG S/S-1:ID | TG-MAN173A-2 | 19505533 | 630 | 200 | 241 | 0.98 | 139 | 67 | 296 | 20 | 83 | 52 | 225 | 188 | 2019-06-30 14:30 | 45 | 2.4 | 296 | R | 89 | 112 | 98 | 23 | 0.1 | 0.1 | 5.5 | 94.3 | 717.51 | 713.51 | 717.51 | 717.51 | 0.3 | 4.3 | 4.3 | 0.3 | [12 empty] | 718.21 | 1.39 | 0.43 | 0.22
493 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN174 | 1S-DL-YP-ETC-DLNR-2503-MAN174 | RETREET CGHS PPG S/S-2:ID | TG-MAN174A-1 | 19502056 | 630 | 200 | 241 | 0.94 | 135 | 47 | 203 | 31 | 133 | 57 | 248 | 101 | 2019-06-30 23:30 | 45.1 | 10.6 | 271 | B | 92 | 85 | 124 | 39 |  |  | 0.1 | 99.9 | 717.21 | 716.21 | 571.51 | 714.51 | 1 | 2 | 2 | 3.3 | [12 empty] | 718.21 | 1.39 | 0.6 | 0.21
494 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN174 | 1S-DL-YP-ETC-DLNR-2503-MAN174 | RETREET CGHS PPG S/S-2:ID | TG-MAN174A-2 | 19502055 | 630 | 200 | 241 | 0.97 | 101 | 9 | 39 | 40 | 165 | 52 | 219 | 160 | 2019-06-16 00:30 | 17.9 | 2.3 | 219 | B | 49 | 120 | 130 | 81 |  |  | 4.1 | 95.9 | 718.22 | 718.22 | 707.22 | 718.22 | [16 empty] | 718.22 | 1.38 | 0.47 | 0.16
495 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN175 | 1S-DL-YP-ETC-DLNR-2503-MAN175 | TARANG CGHS PPG S/S-1:ID | TG-MAN175A-1 | 19502059 | 630 | 200 | 237 | 0.98 | 139 | 66 | 296 | 45 | 200 | 29 | 128 | 146 | 2019-06-10 22:30 | 25.8 | 1.8 | 309 | R | 129 | 97 | 74 | 55 |  |  | 0.2 | 99.8 | 584.27 | 693.38 | 718.38 | 704.08 | 134.11 | 25 | 25 | 14.3 | [12 empty] | 718.38 | 1.22 | 0.52 | 0.22
496 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN175 | 1S-DL-YP-ETC-DLNR-2503-MAN175 | TARANG CGHS PPG S/S-1:ID | TG-MAN175A-2 | 19502057 | 630 | 200 | 237 | 0.96 | 148 | 56 | 245 | 42 | 183 | 50 | 222 | 54 | 2019-06-12 23:30 | 29.9 | 4.6 | 245 | R | 96 | 95 | 109 | 14 |  |  | 1 | 99 | 697.07 | 687.07 | 668.42 | 693.07 | 21.3 | 31.3 | 31.3 | 25.3 | [12 empty] | 718.37 | 1.23 | 0.47 | 0.23
497 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN176 | 1S-DL-YP-ETC-DLNR-2503-MAN176 | TARANG CGHS PPG S/S-2:ID | TG-MAN176A-1 | 19502058 | 400 | 120 | 242 | 0.98 | 99 | 25 | 103 | 18 | 77 | 56 | 234 | 146 | 2019-06-15 01:00 | 17.1 | 2.2 | 234 | B | 81 | 71 | 149 | 78 |  |  | 1.1 | 98.9 | 688.08 | 718.38 | 403.37 | 663.08 | 30.3 |  |  | 55.3 |  |  | 0.3 | [9 empty] | 718.38 | 1.22 | 0.54 | 0.25
498 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN176 | 1S-DL-YP-ETC-DLNR-2503-MAN176 | TARANG CGHS PPG S/S-2:ID | TG-MAN176A-2 | 19505527 | 400 | 120 | 243 | 0.98 | 79 | 35 | 145 | 25 | 104 | 20 | 82 | 55 | 2019-06-09 22:00 | 19.7 | 1.6 | 153 | R | 110 | 99 | 91 | 19 | 0.1 |  | 0.7 | 99.2 | 675.08 | 717.08 | 718.38 | 718.38 | 43.3 | 1.3 | 1.3 | [13 empty] | 718.38 | 1.22 | 0.51 | 0.2
499 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN177 | 1S-DL-YP-ETC-DLNR-2503-MAN177 | PRIYADARSHANI CGHS PPG:ID | TG-MAN177A-1 | 19500915 | 400 | 120 | 236 | 0.96 | 64 | 23 | 99 | 31 | 136 | 11 | 46 | 79 | 2019-06-03 22:30 | 21.3 | 1.7 | 158 | Y | 99 | 135 | 66 | 69 |  | 0.1 | 67.8 | 32.1 | 718.38 | 674.08 | 718.38 | 718.38 |  | 44.3 | 44.3 | [13 empty] | 718.38 | 1.22 | 0.57 | 0.16
500 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN177 | 1S-DL-YP-ETC-DLNR-2503-MAN177 | PRIYADARSHANI CGHS PPG:ID | TG-MAN177A-2 | 19505857 | 400 | 120 | 237 | 0.98 | 102 | 51 | 227 | 24 | 104 | 27 | 121 | 115 | 2019-06-30 | 15.8 | 1.7 | 231 | R | 152 | 55 | 93 | 97 |  | 0.2 | 67.6 | 32.2 | 373.37 | 718.08 | 663.08 | 667.38 | 345.01 | 0.3 | 0.3 | 51 | [12 empty] | 718.38 | 1.22 | 0.52 | 0.26
501 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN178 | 1S-DL-YP-ETC-DLNR-2503-MAN178 | EKTA GARDEN CGHS S/S-1, PPG:ID | TG-MAN178A-1 | 19500922 | 630 | 200 | 242 | 0.97 | 169 | 46 | 198 | 74 | 323 | 49 | 214 | 118 | 2019-06-29 23:30 | 35 | 6 | 323 | Y | 86 | 106 | 108 | 22 |  |  | 0.3 | 99.7 | 696.37 | 576.07 | 600.07 | 635.37 | 22 | 142.3 | 142.3 | 83 | [12 empty] | 718.37 | 1.23 | 0.51 | 0.27
502 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN178 | 1S-DL-YP-ETC-DLNR-2503-MAN178 | EKTA GARDEN CGHS S/S-1, PPG:ID | TG-MAN178A-2 | 19500923 | 630 | 200 | 242 | 0.98 | 175 | 42 | 168 | 60 | 236 | 73 | 293 | 109 | 2019-06-03 01:00 | 39.1 | 6.4 | 365 | B | 65 | 92 | 143 | 78 |  |  | 0.4 | 99.6 | 711.38 | 616.28 | 302.11 | 557.44 | 7 | 102.1 | 102.1 | 160.54 |  |  | 2 | [9 empty] | 718.38 | 1.22 | 0.56 | 0.28
503 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN179 | 1S-DL-YP-ETC-DLNR-2503-MAN179 | EKTA GARDEN CGHS PPG S/S-2:ID | TG-MAN179A-1 | 19500921 | 630 | 200 | 242 | 0.91 | 136 | 47 | 199 | 46 | 191 | 43 | 180 | 17 | 2019-06-30 19:30 | 67.6 | 15.2 | 212 | Y | 98 | 103 | 98 | 5 |  |  | 0.1 | 99.9 | 702.38 | 690.08 | 700.08 | 715.08 | 16 | 28.3 | 28.3 | 3.3 | [12 empty] | 718.38 | 1.22 | 0.67 | 0.22
504 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN179 | 1S-DL-YP-ETC-DLNR-2503-MAN179 | EKTA GARDEN CGHS PPG S/S-2:ID | TG-MAN179A-2 | 19500924 | 630 | 200 | 242 | 0.98 | 170 | 52 | 209 | 57 | 232 | 61 | 249 | 35 | 2019-06-11 23:00 | 28.5 | 4.1 | 284 | Y | 91 | 103 | 106 | 15 |  |  | 0.3 | 99.7 | 655.07 | 582.37 | 608.19 | 617.07 | 63.3 | 136 | 136 | 101.3 | [12 empty] | 718.37 | 1.23 | 0.5 | 0.27
505 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN180 | 1S-DL-YP-ETC-DLNR-2503-MAN180 | NAVKUNJ CGHS PPG S/S-1:ID | TG-MAN180A-1 | 19500912 | 630 | 200 | 240 | 0.97 | 204 | 87 | 375 | 53 | 228 | 64 | 275 | 130 | 2019-06-11 23:30 | 40.5 | 9.7 | 375 | R | 109 | 95 | 96 | 14 |  |  | 0.1 | 99.9 | 426.37 | 515.22 | 508.03 | 480.52 | 291.32 | 203.17 | 203.17 | 237.47 | 0.3 | [11 empty] | 718.39 | 1.21 | 0.55 | 0.32
506 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN180 | 1S-DL-YP-ETC-DLNR-2503-MAN180 | NAVKUNJ CGHS PPG S/S-1:ID | TG-MAN180A-2 | 19505855 | 630 | 200 | 242 | 0.93 | 121 | 29 | 121 | 55 | 228 | 37 | 154 | 95 | 2019-06-30 16:30 | 66.6 | 6.6 | 228 | Y | 80 | 127 | 93 | 47 |  | 0.1 | 0.2 | 99.7 | 718.38 | 682.19 | 718.38 | 718.38 |  | 36.19 | 36.19 | [13 empty] | 718.38 | 1.22 | 0.62 | 0.19
507 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN181 | 1S-DL-YP-ETC-DLNR-2503-MAN181 | NAVKUNJ CGHS PPG S/S-2:ID | TG-MAN181A-1 | 19500897 | 630 | 200 | 236.9165 | 0.98825 | 57.1085 | 13.3717 | 60.1218 | 23.165 | 104.4787 | 20.5718 | 91.9247 | 39.6015 | 2019-06-30 23:30 | [15 empty] | 720 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.45565 | 0.090648
508 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN181 | 1S-DL-YP-ETC-DLNR-2503-MAN181 | NAVKUNJ CGHS PPG S/S-2:ID | TG-MAN181A-2 | 19500899 | 630 | 200 | 236.7592 | 0.97956 | 111.8076 | 42.1647 | 186.3057 | 42.5693 | 187.7117 | 27.0736 | 119.7472 | 67.2725 | 2019-06-29 23:00 | [15 empty] | 720 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.52198 | 0.17747
509 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN182 | 1S-DL-YP-ETC-DLNR-2503-MAN182 | LINK HOUSE CGHS PPG:ID | TG-MAN182A-1 | 19500896 | 630 | 200 | 243.3945 | 0.98819 | 45.4838 | 21.7955 | 93.8246 | 11.5092 | 49.3491 | 12.1791 | 52.2733 | 43.0879 | 2019-06-27 | [15 empty] | 720 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.5085 | 0.072197
510 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN182 | 1S-DL-YP-ETC-DLNR-2503-MAN182 | LINK HOUSE CGHS PPG:ID | TG-MAN182A-2 | 19500913 | 630 | 200 | 242 | 0.97 | 73 | 31 | 131 | 21 | 92 | 20 | 87 | 42 | 2019-06-14 23:30 | 13.8 | 0.5 | 131 | R | 118 | 99 | 83 | 35 |  |  |  | 100 | 718.37 | 718.37 | 718.37 | 718.37 | [16 empty] | 718.37 | 1.23 | 0.53 | 0.12
511 | 2019-06-17 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN183 | 1S-DL-YP-ETC-DLNR-2503-MAN183 | ADITI CGHS PPG:ID | TG-MAN183A-1 | 19506927 | 400 | 120 | 239 | 0.99 | 11 | 2 | 10 | 1 | 3 | 8 | 35 | 30 | 2019-06-25 11:00 | -0.1 | -11.4 | 35 | B | 134 | 24 | 142 | 118 |  |  |  | 100 | 321.53 | 321.53 | 321.53 | 321.53 | [16 empty] | 321.53 | 14.07 | 0.42 | 0.03
512 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN183 | 1S-DL-YP-ETC-DLNR-2503-MAN183 | ADITI CGHS PPG:ID | TG-MAN183A-2 | 19502039 | 400 | 120 | 238 | 0.96 | 64 | 23 | 101 | 23 | 101 | 18 | 82 | 19 | 2019-06-02 21:00 | 3.3 | -20.4 | 136 | R | 132 | 93 | 75 | 57 |  |  | 1.7 | 98.3 | 713.11 | 716.41 | 716.41 | 716.41 | 3.3 | [15 empty] | 716.41 | 3.19 | 0.49 | 0.16
513 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN185 | 1S-DL-YP-ETC-DLNR-2503-MAN185 | DEEPA CGHS PPG:ID | TG-MAN185A-1 | 19502428 | 630 | 200 | 240 | 0.97 | 111 | 37 | 155 | 34 | 140 | 40 | 167 | 24 | 2019-06-02 23:30 | 23 | 5.1 | 185 | B | 88 | 90 | 122 | 34 |  |  | 0.1 | 99.9 | 718.59 | 718.59 | 717.59 | 718.59 | [16 empty] | 718.59 | 1.01 | 0.52 | 0.18
514 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN185 | 1S-DL-YP-ETC-DLNR-2503-MAN185 | DEEPA CGHS PPG:ID | TG-MAN185A-2 | 19502427 | 630 | 200 | 240 | 0.97 | 121 | 33 | 139 | 45 | 187 | 42 | 176 | 43 | 2019-06-08 23:00 | 22.5 | 4.1 | 197 | B | 88 | 103 | 109 | 21 |  |  |  | 100 | 695.28 | 690.58 | 688.58 | 695.28 |  | 4.3 | 4.3 | [13 empty] | 718.34 | 1.26 | 0.51 | 0.19
515 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN186 | 1S-DL-YP-ETC-DLNR-2503-MAN186 | CHETNA CGHS PPG:ID | TG-MAN186A-1 | 19502426 | 400 | 120 | 240 | 0.97 | 158 | 82 | 351 | 33 | 143 | 43 | 191 | 189 | 2019-06-11 23:00 | 29.8 | 5.8 | 352 | R | 143 | 67 | 89 | 76 | 96.9 | 3.1 |  |  | 222.4 | 642.22 | 493.39 | 442.39 | 356.42 | 76.47 | 76.47 | 276.3 | 139.47 | [11 empty] | 719.09 | 0.51 | 0.48 | 0.39
516 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN187 | 1S-DL-YP-ETC-DLNR-2503-MAN187 | UTTRANCHAL CGHS PPG:ID | TG-MAN187A-1 | 19502425 | 400 | 120 | 246 | 0.97 | 117 | 42 | 173 | 53 | 219 | 22 | 91 | 112 | 2019-06-28 23:00 | 23.7 | 5 | 237 | Y | 109 | 140 | 51 | 89 |  |  | 3.2 | 96.8 | 440.01 | 267 | 719 | 533.3 | 278.59 | 445.3 | 445.3 | 185.3 |  | 6.3 | [10 empty] | 719 | 1 | 0.58 | 0.29
517 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN188 | 1S-DL-YP-ETC-DLNR-2503-MAN188 | UNA CGHS PPG:ID | TG-MAN188A-1 | 19502424 | 400 | 120 | 246 | 0.97 | 96 | 38 | 160 | 25 | 104 | 33 | 137 | 48 | 2019-06-29 23:00 | 17.4 | 2.2 | 160 | R | 112 | 100 | 88 | 24 |  |  | 7.9 | 92.1 | 660.29 | 714.59 | 709.08 | 713.59 | 58.3 | 4 | 4 | 5 | [12 empty] | 718.59 | 1.01 | 0.44 | 0.24
518 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN188 | 1S-DL-YP-ETC-DLNR-2503-MAN188 | UNA CGHS PPG:ID | TG-MAN188A-2 | 19502422 | 400 | 120 | 240 | 0.97 | 114 | 29 | 123 | 34 | 146 | 51 | 220 | 88 | 2019-06-12 | 50.2 | 1.9 | 220 | B | 83 | 88 | 129 | 46 |  | 0.1 | 18.2 | 81.7 | 691.08 | 597.38 | 401.16 | 540.59 | 27.52 | 121.22 | 121.22 | 178.01 | [12 empty] | 719 | 1 | 0.52 | 0.28
519 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN189 | 1S-DL-YP-ETC-DLNR-2503-MAN189 | DHARMA CGHS PPG:ID | TG-MAN189A-1 | 19502423 | 630 | 200 | 239 | 0.98 | 199 | 74 | 322 | 75 | 325 | 49 | 210 | 113 | 2019-06-12 | 38.2 | 9.2 | 347 | R | 116 | 110 | 74 | 42 |  |  |  | 100 | 283.59 | 329.3 | 617.59 | 407.29 | 435 | 389.29 | 389.29 | 311.3 | [12 empty] | 718.59 | 1.01 | 0.6 | 0.32
520 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN190 | 1S-DL-YP-ETC-DLNR-2503-MAN190 | NAVKALA CGHS PPG:ID | TG-MAN190A-1 | 19502034 | 630 | 200 | 239 | 0.97 | 152 | 47 | 202 | 59 | 252 | 46 | 194 | 54 | 2019-06-28 23:00 | 25.8 | 5.5 | 274 | Y | 95 | 108 | 97 | 13 |  |  | 0.1 | 99.9 | 696.29 | 617.05 | 699.52 | 681.59 | 22.3 | 101.54 | 101.54 | 37 | [12 empty] | 718.59 | 1.01 | 0.49 | 0.24
521 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN190 | 1S-DL-YP-ETC-DLNR-2503-MAN190 | NAVKALA CGHS PPG:ID | TG-MAN190A-2 | 19506132 | 630 | 200 | 246 | 0.97 | 146 | 26 | 108 | 91 | 392 | 29 | 120 | 278 | 2019-06-30 14:30 | 46 | 4.6 | 392 | Y | 102 | 121 | 76 | 45 | 99.9 | 0.1 |  |  | 681.58 | 617.03 | 718.28 | 706.28 | 37 | 101.25 | 101.25 | 12.3 |  | 0.3 | [10 empty] | 718.58 | 1.02 | 0.49 | 0.23
522 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN191 | 1S-DL-YP-ETC-DLNR-2503-MAN191 | DESH BANDHU CGHS,PPG:ID | TG-MAN191A-1 | 19505856 | 630 | 200 | 245 | 0.97 | 226 | 78 | 325 | 92 | 385 | 55 | 227 | 138 | 2019-06-26 23:00 | 71 | 10 | 411 | Y | 123 | 97 | 80 | 43 | 0.1 | 0.1 | 2.6 | 97.3 | 287.29 | 438.28 | 604.28 | 423.59 | 417.29 | 279.3 | 279.3 | 294.59 | 14 | 1 | [10 empty] | 718.58 | 1.02 | 0.53 | 0.36
523 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN192 | 1S-DL-YP-ETC-DLNR-2503-MAN192 | DHURVA CGHS PPG:ID | TG-MAN192A-1 | 19502366 | 630 | 200 | 239 | 0.97 | 169 | 51 | 213 | 60 | 250 | 58 | 240 | 33 | 2019-06-02 00:30 | 36.3 | 8.3 | 279 | Y | 93 | 109 | 97 | 16 |  |  |  | 100 | 635.05 | 513.28 | 603.05 | 595.05 | 83.54 | 205.31 | 205.31 | 123.54 | [12 empty] | 718.59 | 1.01 | 0.54 | 0.27
524 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN192 | 1S-DL-YP-ETC-DLNR-2503-MAN192 | DHURVA CGHS PPG:ID | TG-MAN192A-2 | 19502430 | 630 | 200 | 239 | 0.97 | 269 | 85 | 370 | 101 | 441 | 84 | 364 | 75 | 2019-06-11 23:30 | 74.1 | 9.7 | 441 | Y | 99 | 99 | 102 | 3 |  |  | 0.1 | 99.9 | 300.36 | 317.3 | 287 | 307 | 416.24 | 387.3 | 387.3 | 408 | 2 | 14 | 9.3 | 4 | [8 empty] | 719 | 1 | 0.53 | 0.43
525 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN193 | 1S-DL-YP-ETC-DLNR-2503-MAN193 | TECHNOLOGY CGHS, PPG:ID | TG-MAN193A-1 | 19500886 | 630 | 200 | 245.1006 | 0.98322 | 145.1111 | 57.1086 | 234.9084 | 34.5276 | 141.8903 | 53.4749 | 220.7972 | 86.8268 | 2019-06-09 | [15 empty] | 669 |  |  |  | 51 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.58846 | 0.23034
526 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN193 | 1S-DL-YP-ETC-DLNR-2503-MAN193 | TECHNOLOGY CGHS, PPG:ID | TG-MAN193A-2 | 19500979 | 630 | 200 | 244 | 0.98 | 158 | 60 | 249 | 44 | 181 | 55 | 228 | 61 | 2019-06-02 23:00 | 25.8 | 3.7 | 261 | Y | 100 | 101 | 98 | 3 |  | 0.2 | 15.6 | 84.2 | 658.31 | 657.25 | 658.25 | 671.25 | 60.54 | 62 | 62 | 48 | [12 empty] | 719.25 | 0.35 | 0.52 | 0.25
527 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN194 | 1S-DL-YP-ETC-DLNR-2503-MAN194 | ENGINEERS CGHS PPG S/S-1:ID | TG-MAN194A-1 | 19500948 | 630 | 200 | 246 | 0.98 | 176 | 71 | 309 | 54 | 235 | 50 | 217 | 84 | 2019-06-11 01:30 | 25.8 | 3.7 | 309 | R | 102 | 106 | 93 | 13 |  | 0.1 | 0.2 | 99.7 | 592.37 | 629.37 | 682.06 | 649.07 | 124.59 | 87.59 | 87.59 | 68.29 | [12 empty] | 717.36 | 2.24 | 0.5 | 0.28
528 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN194 | 1S-DL-YP-ETC-DLNR-2503-MAN194 | ENGINEERS CGHS PPG S/S-1:ID | TG-MAN194A-2 | 19500947 | 630 | 200 | 246 | 0.96 | 132 | 50 | 208 | 34 | 146 | 48 | 204 | 60 | 2019-06-11 23:00 | 29.4 | 6 | 236 | R | 110 | 83 | 108 | 27 | 83.2 | 16.8 |  |  | 688.4 | 718.36 | 708.06 | 716.36 | 29.56 |  |  | 2 | [12 empty] | 718.36 | 1.24 | 0.49 | 0.21
529 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN195 | 1S-DL-YP-ETC-DLNR-2503-MAN195 | ENGINEERS CGHS PPG S/S-2:ID | TG-MAN195A-1 | 19500949 | 630 | 200 | 246 | 0.97 | 115 | 42 | 174 | 29 | 121 | 45 | 186 | 60 | 2019-06-12 | 23.9 | 1.8 | 197 | B | 106 | 88 | 106 | 18 |  | 0.1 | 3.8 | 96.1 | 714.36 | 718.36 | 705.06 | 718.36 | 4 | [15 empty] | 718.36 | 1.24 | 0.53 | 0.18
530 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN195 | 1S-DL-YP-ETC-DLNR-2503-MAN195 | ENGINEERS CGHS PPG S/S-2:ID | TG-MAN195A-2 | 19500946 | 630 | 200 | 246 | 0.97 | 71 | 20 | 79 | 26 | 106 | 25 | 99 | 23 | 2019-06-02 23:30 | 17.5 | 0.9 | 116 | B | 84 | 104 | 113 | 29 |  | 0.1 | 0.2 | 99.7 | 718.37 | 718.37 | 718.37 | 718.37 | [16 empty] | 718.37 | 1.23 | 0.53 | 0.11
531 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN196 | 1S-DL-YP-ETC-DLNR-2503-MAN196 | SARANSH CGHS PPG S/S-1:ID | TG-MAN196A-1 | 19500868 | 400 | 120 | 239.684 | 0.98115 | 81.142 | 26.5032 | 110.7993 | 16.3424 | 68.4526 | 38.2964 | 160.8756 | 80.1339 | 2019-06-01 | [15 empty] | 718.5 |  |  |  | 1 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 719.5 |  | 0.46245 | 0.20285
532 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN196 | 1S-DL-YP-ETC-DLNR-2503-MAN196 | SARANSH CGHS PPG S/S-1:ID | TG-MAN196A-2 | 19500869 | 400 | 120 | 246.3713 | 0.94154 | 30.4594 | 10.448 | 41.7902 | 10.3711 | 41.4067 | 9.6403 | 38.3128 | 3.3024 | 2019-06-06 20:30 | [15 empty] | 720 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.3613 | 0.076148
533 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN197 | 1S-DL-YP-ETC-DLNR-2503-MAN197 | SARANSH CGHS PPG S/S-2:ID | TG-MAN197A-1 | 19500824 | 400 | 120 | 239.9154 | 0.99275 | 77.2251 | 33.948 | 154.555 | 34.0197 | 155.0439 | 9.2573 | 42.0138 | 112.7864 | 2019-06-11 | [15 empty] | 720 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.50284 | 0.19306
534 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN197 | 1S-DL-YP-ETC-DLNR-2503-MAN197 | SARANSH CGHS PPG S/S-2:ID | TG-MAN197A-2 | 19500870 | 400 | 120 | 240.2177 | 0.98874 | 108.6844 | 23.46 | 93.3211 | 37.9808 | 156.5252 | 47.2436 | 193.2332 | 87.5347 | 2019-06-16 01:30 | [15 empty] | 629 |  |  |  | 90 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 719 |  | 0.50214 | 0.27171
535 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN198 | 1S-DL-YP-ETC-DLNR-2503-MAN198 | ANKUR CGHS PPG S/S-1:ID | TG-MAN198A-1 | 19502429 | 630 | 200 | 242 | 0.97 | 212 | 60 | 259 | 73 | 314 | 79 | 338 | 71 | 2019-06-30 | 38.2 | 7.8 | 338 | B | 79 | 109 | 112 | 33 |  |  | 0.7 | 99.3 | 643.42 | 486.25 | 463.55 | 533.07 | 74.24 | 231.41 | 231.41 | 184.59 | [12 empty] | 718.06 | 1.54 | 0.48 | 0.34
536 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN198 | 1S-DL-YP-ETC-DLNR-2503-MAN198 | ANKUR CGHS PPG S/S-1:ID | TG-MAN198A-2 | 19500925 | 630 | 200 | 242 | 0.98 | 152 | 53 | 217 | 34 | 138 | 64 | 262 | 108 | 2019-06-03 | 26.7 | 3.2 | 297 | B | 94 | 57 | 149 | 92 |  |  | 0.1 | 99.9 | 702.42 | 718.06 | 495.11 | 699.36 | 15.24 |  |  | 18.3 | [12 empty] | 718.06 | 1.54 | 0.48 | 0.24
537 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN199 | 1S-DL-YP-ETC-DLNR-2503-MAN199 | ANKUR CGHS PPG S/S-2:ID | TG-MAN199A-1 | 19500900 | 400 | 120 | 242.1366 | 0.97464 | 56.7438 | 15.4806 | 66.9056 | 9.9971 | 43.2066 | 31.2661 | 137.4514 | 84.913 | 2019-06-11 01:00 | [15 empty] | 719.5 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 719.5 |  | 0.48863 | 0.14186
538 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN199 | 1S-DL-YP-ETC-DLNR-2503-MAN199 | ANKUR CGHS PPG S/S-2:ID | TG-MAN199A-2 | 19500898 | 400 | 120 | 235.2377 | 0.98522 | 189.8378 | 57.6523 | 239.8681 | 60.8034 | 251.5342 | 71.3822 | 295.8601 | 51.1663 | 2019-06-03 00:30 | [15 empty] | 164 |  |  |  | 497.5 |  |  |  | 58 |  |  |  | 0 |  |  |  | 0 | 719.5 |  | 0.5579 | 0.47459
539 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN200 | 1S-DL-YP-ETC-DLNR-2503-MAN200 | PARADISE CGHS PPG S/S-1:ID | TG-MAN200A-1 | 19505861 | 630 | 200 | 245 | 0.98 | 201 | 50 | 201 | 77 | 326 | 74 | 314 | 120 | 2019-06-02 23:00 | 58.4 | 4.8 | 366 | Y | 85 | 112 | 102 | 27 | 99.9 | 0.1 |  |  | 639.26 | 487.21 | 524.21 | 537.56 | 78.12 | 229.47 | 229.47 | 179.42 |  | 0.3 | [10 empty] | 717.38 | 2.22 | 0.51 | 0.32
540 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN201 | 1S-DL-YP-ETC-DLNR-2503-MAN201 | PARADISE CGHS PPG S/S-2:ID | TG-MAN201A-1 | 19500822 | 630 | 200 | 244.9554 | 0.97886 | 201.2838 | 49.1684 | 202.8231 | 78.0497 | 323.1871 | 74.0657 | 304.3713 | 112.1462 | 2019-06-01 | [15 empty] | 534.5 |  |  |  | 185 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 719.5 |  | 0.49831 | 0.3195
541 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN202 | 1S-DL-YP-ETC-DLNR-2503-MAN202 | PARIWAR CGHS PPG:ID | TG-MAN202A-1 | 19506485 | 630 | 200 | 244 | 0.98 | 264 | 121 | 617 | 96 | 442 | 48 | 197 | 366 | 2019-06-30 14:30 | 83.4 | 5 | 617 | R | 115 | 94 | 91 | 24 | 23.1 | 1.2 | 5.3 | 70.5 | 237.3 | 383.33 | 408.55 | 348.25 | 451.11 | 311.03 | 311.03 | 346.11 | 6.25 | 0.3 |  | 0.3 | [8 empty] | 695.06 | 24.54 | 0.5 | 0.42
542 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN204 | 1S-DL-YP-ETC-DLNR-2503-MAN204 | KONARK CGHS, PPG:ID | TG-MAN204A-1 | 19500371 | 630 | 200 | 239 | 0.98 | 72 | 42 | 184 | 13 | 56 | 17 | 73 | 120 | 2019-06-11 23:30 | 15.2 | 0.5 | 184 | R | 151 | 67 | 83 | 84 |  |  | 0.1 | 99.9 | 717.17 | 717.47 | 717.47 | 717.47 | 0.3 | [15 empty] | 717.47 | 2.13 | 0.52 | 0.11
543 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN204 | 1S-DL-YP-ETC-DLNR-2503-MAN204 | KONARK CGHS, PPG:ID | TG-MAN204A-2 | 19502036 | 630 | 200 | 240 | 0.97 | 87 | 24 | 103 | 29 | 121 | 34 | 141 | 33 | 2019-06-13 23:30 | 17 | 2.8 | 141 | B | 105 | 108 | 87 | 21 |  | 0.1 | 65.3 | 34.6 | 717.48 | 717.48 | 717.48 | 717.48 | [16 empty] | 717.48 | 2.12 | 0.52 | 0.14
544 | 2019-06-26 11:00 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN205 | 1S-DL-YP-ETC-DLNR-2503-MAN205 | SHUBHAM CGHS, PPG:ID | TG-MAN205A-1 | 19506933 | 630 | 200 | 247.6311 | 0.98613 | 151.8512 | 42.4952 | 176.5043 | 64.9569 | 270.6763 | 44.3991 | 185.1197 | 90.1736 | 2019-06-29 23:00 | [15 empty] | 96.5 |  |  |  | 12.5 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 109 |  | 0.57963 | 0.24103
545 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN205 | 1S-DL-YP-ETC-DLNR-2503-MAN205 | SHUBHAM CGHS, PPG:ID | TG-MAN205A-2 | 19500821 | 630 | 200 | 245.4699 | 0.97751 | 164.2538 | 63.9599 | 267.648 | 53.2906 | 222.7866 | 47.0034 | 196.3136 | 62.4579 | 2019-06-12 | [15 empty] | 593 |  |  |  | 127 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.54013 | 0.26072
546 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN206 | 1S-DL-YP-ETC-DLNR-2503-MAN206 | SUDH BHAWNA:ID | TG-MAN206A-1 | 19502393 | 630 | 200 | 240 | 0.95 | 65 | 22 | 87 | 22 | 89 | 22 | 91 | 3 | 2019-06-15 22:30 | 22.1 | 3.2 | 121 | R | 90 | 100 | 110 | 20 | 92.9 | 4.9 | 2.1 | 0.1 | 718.59 | 718.59 | 718.59 | 718.59 | [16 empty] | 718.59 | 1.01 | 0.57 | 0.1
547 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN206 | 1S-DL-YP-ETC-DLNR-2503-MAN206 | SUDH BHAWNA:ID | TG-MAN206A-2 | 19502394 | 630 | 200 | 245 | 0.98 | 214 | 90 | 381 | 64 | 268 | 59 | 250 | 123 | 2019-06-12 | 37.7 | 9.7 | 381 | R | 115 | 97 | 88 | 27 |  |  |  | 100 | 396.59 | 522.28 | 535.58 | 480.28 | 319.29 | 196.3 | 196.3 | 238.3 | 2.3 | [11 empty] | 718.58 | 1.02 | 0.52 | 0.34
548 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN207 | 1S-DL-YP-ETC-DLNR-2503-MAN207 | DVB COLONY, URJA VIHAR:K | TG-MAN207A-1 | 19505138 | 400 | 120 | 239 | 0.99 | 55 | 24 | 104 | 26 | 115 | 5 | 23 | 87 | 2019-06-10 01:00 | 7.2 | -0.1 | 123 | Y | 62 | 166 | 72 | 104 | 0.1 |  | 37.1 | 62.8 | 600.3 | 595 | 600.3 | 600.3 |  | 5.3 | 5.3 | [13 empty] | 600.3 | 23.3 | 0.43 | 0.14
549 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN207 | 1S-DL-YP-ETC-DLNR-2503-MAN207 | DVB COLONY, URJA VIHAR:K | TG-MAN207A-2 | 19506542 | 630 | 200 | 232.8028 | 0.97007 | 247.2505 | 78.5636 | 330.9195 | 86.744 | 366.5033 | 81.9429 | 343.8645 | 31.1953 | 2019-06-18 08:30 | [15 empty] | 704.5 |  |  |  | 14.5 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 719 |  | 0.30822 | 0.39246
550 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN212 | 1S-DL-YP-ETC-DLNR-2503-MAN212 | RAILWAY COLONY GALI NO. 2:PL | TG-MAN212A-1 | 19505555 | 990 | 320 | 235 | 0.98 | 1063 | 381 | 1715 | 374 | 1681 | 307 | 1386 | 313 | 2019-06-01 23:00 | 246.7 | 38.7 | 1716 | Y | 104 | 105 | 91 | 14 | 0.1 |  | 0.8 | 99.2 |  |  |  |  | 103.01 | 107.54 | 107.54 | 135.01 | 518.44 | 496.21 | 464.21 | 496.44 | 62.3 | 71 | 36.3 | 63.3 | 21.3 | 30.3 |  | 10.3 | 705.45 | 14.15 | 0.52 | 1.07
551 | 2019-06-17 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN212 | 1S-DL-YP-ETC-DLNR-2503-MAN212 | RAILWAY COLONY GALI NO. 2:PL | TG-MAN212A-2 | 19506923 | 630 | 200 | 237 | 0.98 | 499 | 173 | 760 | 183 | 814 | 143 | 637 | 156 | 2019-06-30 23:00 | 68.4 | 28 | 814 | Y | 103 | 107 | 90 | 17 | 0.2 |  | 63.1 | 36.8 |  |  |  |  | 101.04 | 93.34 | 93.34 | 116.04 | 212 | 215.3 | 149.3 | 198 | 1 | 5 | [6 empty] | 314.04 | 21.56 | 0.58 | 0.79
552 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN243 | 1S-DL-YP-ETC-DLNR-2503-MAN243 | 100KVA PMS NR P-4 RENNY WELL AKSHARDHAM | TG-MAN243A-1 | 19504575 | 400 | 120 | 244 | 0.99 | 101 | 36 | 145 | 32 | 129 | 33 | 134 | 14 | 2019-06-29 20:30 | 6.1 | 0.3 | 159 | Y | 105 | 89 | 106 | 17 |  |  | 5 | 95 | 600.23 | 646.27 | 611.34 | 632.34 | 117.33 | 71.29 | 71.29 | 85.22 | [12 empty] | 717.56 | 2.04 | 0.55 | 0.25
553 | 2019-06-24 16:30 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN244 | 1S-DL-YP-ETC-DLNR-2503-MAN244 | 100KVA PMS NR KAPOOR PETROL PUMP NARVANA | TG-MAN244A-1 | 19505157 | 400 | 120 | 241.3507 | 0.96061 | 105.9137 | 36.2908 | 147.3021 | 37.3248 | 150.5519 | 32.2981 | 130.5764 | 18.5652 | 2019-06-30 19:00 | [15 empty] | 49.5 |  |  |  | 102 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 151.5 |  | 0.62511 | 0.26478
554 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN247 | 1S-DL-YP-ETC-DLNR-2503-MAN247 | BUDHA MARG MANDAWALI | TG-MAN247A-1 | 19504474 | 990 | 320 | 235 | 0.97 | 951 | 348 | 1536 | 321 | 1422 | 282 | 1250 | 250 | 2019-06-30 23:30 | 162.7 | 30.9 | 1536 | R | 144 | 133 | 23 | 121 | 0.7 | 0.1 | 11.1 | 88.2 |  |  | 607.39 | 2.46 | 88.4 | 98.48 | 98.48 | 396.14 | 542.12 | 590.49 | 97 | 298.07 | 84.15 | 27.3 | 12 | 20 | 2 |  |  |  | 717.07 | 2.53 | 0.42 | 0.96
555 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN273 | 1S-DL-YP-ETC-DLNR-2503-MAN273 | Ew S/S D-Blk Ramleela Ground Pandav Ngr | TG-MAN273A-1 | 19504634 | 990 | 200 | 231 | 0.98 | 904 | 321 | 1476 | 262 | 1200 | 321 | 1461 | 269 | 2019-06-30 23:30 | 130.6 | 46 | 1509 | B | 105 | 88 | 107 | 19 |  | 0.3 | 21.7 | 78 |  |  |  |  | 145.58 | 257.47 | 257.47 | 162.28 | 500.45 | 460.3 | 515.15 | 516.37 | 71.34 |  | 89.34 | 39.12 |  |  | 0.3 |  | 718.17 | 1.43 | 0.57 | 0.91
556 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN273 | 1S-DL-YP-ETC-DLNR-2503-MAN273 | Ew S/S D-Blk Ramleela Ground Pandav Ngr | TG-MAN273A-2 | 19505682 | 630 | 200 | 241 | 0.97 | 407 | 148 | 639 | 139 | 599 | 121 | 519 | 106 | 2019-06-26 23:30 | 122.8 | 38.8 | 865 | Y | 104 | 106 | 89 | 17 | 0.1 | 0.1 | 23.6 | 76.2 |  |  | 0.3 |  | 186 | 160 | 160 | 214.3 | 532.27 | 557.27 | 361.32 | 503.57 |  | 1 | [6 empty] | 718.27 | 1.33 | 0.69 | 0.65
557 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN274 | 1S-DL-YP-ETC-DLNR-2503-MAN274 | Gnpn Complex, Rob-36 Pandav Nagar | TG-MAN274A-1 | 19504788 | 630 | 200 | 234 | 0.98 | 652 | 225 | 1017 | 211 | 947 | 217 | 973 | 61 | 2019-06-07 23:00 | 106.3 | 35.9 | 1051 | R | 102 | 100 | 98 | 4 |  |  | 4 | 96 |  |  |  |  | 25 | 16.3 | 16.3 | 30 | 557.54 | 592.41 | 544.41 | 569.49 | 123.43 | 105.26 | 106.43 | 114.48 | 11.47 | 3.47 | 7.3 | 3.47 | 718.24 | 1.36 | 0.59 | 1.04
558 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN275 | 1S-DL-YP-ETC-DLNR-2503-MAN275 | P.S MANDAWALI MANDAWALI | TG-MAN275A-1 | 19505572 | 630 | 200 | 241 | 0.98 | 109 | 56 | 247 | 22 | 93 | 31 | 132 | 139 | 2019-06-30 14:30 | 33.8 | 1.2 | 247 | R | 84 | 115 | 100 | 31 | 0.1 | 0.1 | 2.7 | 97.1 | 705.3 | 692.3 | 705.3 | 706 | 0.3 | 13.3 | 13.3 | [13 empty] | 706 | 14 | 0.6 | 0.17
559 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN296 | 1S-DL-YP-ETC-DLNR-2503-MAN296 | SOUTH GANESH NAGAR (NEAR RAILWAY LINE) | TG-MAN296A-1 | 19505316 | 630 | 200 | 236 | 0.97 | 628 | 211 | 935 | 205 | 915 | 211 | 936 | 21 | 2019-06-29 23:30 | 115.2 | 42.8 | 936 | B | 97 | 98 | 105 | 8 | 0.1 | 0.1 | 17.3 | 82.5 |  |  |  |  | 59.45 | 57.15 | 57.15 | 41.3 | 513.24 | 489.54 | 476.09 | 506.39 | 25.21 | 51.35 | 90.21 | 50.35 | 0.14 |  | 0.14 |  | 598.44 | 25.16 | 0.58 | 1
560 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR001 | 1S-DL-YP-ETC-DLNR-2502-PVR001 | G-II, PREET VIHAR:ID | TG-PVR001A-1 | 19503221 | 630 | 200 | 239 | 0.98 | 738 | 228 | 945 | 275 | 1145 | 235 | 975 | 187 | 2019-06-06 00:30 | 132.9 | 27.6 | 1145 | Y | 93 | 105 | 102 | 12 |  |  | 8.5 | 91.5 |  |  |  |  | 132.26 | 83.15 | 83.15 | 84.56 | 511.53 | 493.58 | 515.21 | 528.17 | 45.28 | 91.18 | 76.36 | 70.29 | 1.42 | 22.58 | 14.1 | 7.47 | 691.29 | 4.31 | 0.49 | 1.17
561 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR001 | 1S-DL-YP-ETC-DLNR-2502-PVR001 | G-II, PREET VIHAR:ID | TG-PVR001A-2 | 19503213 | 990 | 320 | 227 | 0.98 | 957 | 319 | 1423 | 308 | 1368 | 330 | 1474 | 92 | 2019-06-05 02:30 | 167.1 | 5.9 | 1474 | B | 102 | 95 | 102 | 7 |  |  | 7.6 | 92.4 | 16.46 | 77.27 | 17.3 | 24.3 | 527.1 | 486.51 | 486.51 | 535.13 | 144.47 | 124.25 | 142.34 | 129 | 0.3 | 0.3 |  | 0.3 |  |  | 0.3 |  | 689.13 | 6.47 | 0.34 | 0.97
562 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR002 | 1S-DL-YP-ETC-DLNR-2502-PVR002 | DDA BUILDING, LAXMI NAGAR:ID | TG-PVR002A-1 | 19506264 | 630 | 200 | 249 | 0.97 | 81 | 16 | 63 | 43 | 175 | 22 | 88 | 102 | 2019-06-06 11:30 | 27.8 | -0.2 | 203 | Y | 72 | 154 | 74 | 82 | 71.2 | 2.2 | 2.9 | 23.7 | 702.58 | 699.28 | 702.58 | 702.58 |  | 3.3 | 3.3 | [13 empty] | 702.58 | 17.02 | 0.27 | 0.13
563 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR002 | 1S-DL-YP-ETC-DLNR-2502-PVR002 | DDA BUILDING, LAXMI NAGAR:ID | TG-PVR002A-2 | 19504480 | 630 | 200 | 201 | 0.97 | 108 | 14 | 145 | 54 | 228 | 40 | 172 | 73 | 2019-06-26 16:00 | 28.5 | -1.4 | 243 | Y | 77 | 120 | 103 | 43 | 100 |  |  |  | 715.58 | 627.44 | 715.58 | 715.58 |  | 88.14 | 88.14 | [13 empty] | 715.58 | 4.02 | 0.39 | 0.17
564 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR004 | 1S-DL-YP-ETC-DLNR-2502-PVR004 | MADHUVAN:K | TG-PVR004A-1 | 19501091 | 990 | 320 | 231.3505 | 0.93094 | 473.0737 | 142.598 | 636.5413 | 144.4249 | 651.3841 | 186.0508 | 839.9966 | 196.4549 | 2019-06-30 23:30 | [15 empty] | 170 |  |  |  | 454 |  |  |  | 93 |  |  |  | 0 |  |  |  | 0 | 717 |  | 0.57846 | 0.47785
565 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR004 | 1S-DL-YP-ETC-DLNR-2502-PVR004 | MADHUVAN:K | TG-PVR004A-2 | 19506450 | 990 | 320 | 234 | 0.97 | 601 | 236 | 1083 | 169 | 759 | 197 | 886 | 283 | 2019-06-30 23:00 | 202.6 | 8 | 1083 | R | 106 | 87 | 107 | 20 | 0.4 | 0.1 | 29.1 | 70.4 | 1.3 | 17.3 | 3 | 4 | 421.3 | 566 | 566 | 468.3 | 283.18 | 122.48 | 291.18 | 233.48 | [8 empty] | 706.18 | 13.42 | 0.61 | 0.61
566 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR005 | 1S-DL-YP-ETC-DLNR-2502-PVR005 | GHAI PALACE:ID | TG-PVR005A-1 | 19506270 | 990 | 300 | 246 | 0.98 | 686 | 202 | 865 | 243 | 1047 | 240 | 1024 | 171 | 2019-06-10 22:30 | 197.4 | 41.1 | 1089 | Y | 91 | 107 | 101 | 16 | 0.2 | 0.1 | 3.3 | 96.3 |  |  |  |  | 291.01 | 121 | 121 | 176 | 414.36 | 584.37 | 535.07 | 529.37 | [8 empty] | 705.37 | 14.23 | 0.67 | 0.69
567 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR005 | 1S-DL-YP-ETC-DLNR-2502-PVR005 | GHAI PALACE:ID | TG-PVR005A-2 | 19501095 | 990 | 320 | 240.3214 | 0.97549 | 546.107 | 145.7206 | 619.9292 | 219.1316 | 978.1786 | 181.2549 | 804.9689 | 310.3094 | 2019-06-11 23:00 | [15 empty] | 0 |  |  |  | 402 |  |  |  | 293.5 |  |  |  | 0 |  |  |  | 0 | 695.5 |  | 0.68904 | 0.55162
568 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR006 | 1S-DL-YP-ETC-DLNR-2502-PVR006 | B BLOCK, PREET VIHAR:ID | TG-PVR006A-1 | 19501149 | 630 | 200 | 230 | 0.99 | 208 | 93 | 419 | 56 | 248 | 59 | 263 | 164 | 2019-06-03 00:30 | 29.9 | 3.2 | 446 | R | 132 | 88 | 80 | 52 |  |  | 62.5 | 37.5 | 77 | 498.3 | 577 | 365 | 627.48 | 221.18 | 221.18 | 354.48 | 15 | [11 empty] | 719.48 | 0.12 | 0.62 | 0.33
569 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR006 | 1S-DL-YP-ETC-DLNR-2502-PVR006 | B BLOCK, PREET VIHAR:ID | TG-PVR006A-2 | 19501150 | 630 | 200 | 232 | 0.97 | 487 | 172 | 769 | 118 | 519 | 197 | 882 | 322 | 2019-06-10 23:30 | 127 | 25.3 | 952 | B | 101 | 92 | 108 | 16 |  | 0.1 | 15.6 | 84.2 |  |  |  |  | 52.3 | 66.5 | 66.5 | 25.3 | 655.49 | 652.29 | 675.26 | 693.49 | 11 |  | 35.23 | [5 empty] | 719.19 | 0.41 | 0.72 | 0.77
570 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR007 | 1S-DL-YP-ETC-DLNR-2502-PVR007 | SWASTHY VIHAR:ID | TG-PVR007A-1 | 19501289 | 990 | 320 | 253 | 0.96 | 520 | 174 | 688 | 153 | 603 | 193 | 762 | 138 | 2019-06-11 23:30 | 159 | 20.6 | 796 | R | 101 | 88 | 111 | 23 |  |  | 1.8 | 98.2 | 37 | 49.3 | 3 | 11.3 | 482.15 | 610.25 | 610.25 | 571.15 | 174.57 | 34.17 | 208.54 | 111.27 | [8 empty] | 694.12 | 1.48 | 0.62 | 0.53
571 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR007 | 1S-DL-YP-ETC-DLNR-2502-PVR007 | SWASTHY VIHAR:ID | TG-PVR007A-2 | 19501273 | 630 | 200 | 248 | 0.98 | 420 | 130 | 510 | 141 | 569 | 149 | 603 | 82 | 2019-06-30 00:30 | 70.4 | 19.3 | 686 | Y | 92 | 108 | 100 | 16 | 45.3 | 6.8 | 40.2 | 7.7 | 2.3 | 1 | 2 |  | 391.3 | 236.3 | 236.3 | 325.3 | 300.48 | 457.18 | 347.25 | 369.18 | [8 empty] | 694.48 | 1.12 | 0.63 | 0.67
572 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR009 | 1S-DL-YP-ETC-DLNR-2502-PVR009 | EAST GURU ANGAD NAGAR:K | TG-PVR009A-1 | 19504643 | 630 | 200 | 244 | 0.97 | 669 | 211 | 892 | 193 | 833 | 265 | 1134 | 276 | 2019-06-30 23:30 | 127.9 | 24.4 | 1134 | B | 96 | 100 | 103 | 7 | 0.1 | 1.4 | 66.7 | 31.8 | 0.13 | 0.13 | 0.13 | 0.13 | 26 | 25.3 | 25.3 | 16 | 545.03 | 539.33 | 499.33 | 532.03 | 81.47 | 91.17 | 106 | 104 | 3.3 |  | 29.47 | 4.17 | 669.01 | 2.59 | 0.59 | 1.06
573 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR009 | 1S-DL-YP-ETC-DLNR-2502-PVR009 | EAST GURU ANGAD NAGAR:K | TG-PVR009A-2 | 19504514 | 990 | 320 | 245.2112 | 0.97575 | 1253.9548 | 325.802 | 1325.0987 | 572.0406 | 2396.0819 | 356.1122 | 1451.0909 | 1013.8755 | 2019-06-11 22:00 | [15 empty] | 0 |  |  |  | 23 |  |  |  | 449 |  |  |  | 107 |  |  |  | 43.5 | 622.5 |  | 0.5236 | 1.2666
574 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR009 | 1S-DL-YP-ETC-DLNR-2502-PVR009 | EAST GURU ANGAD NAGAR:K | TG-PVR009A-3 | 19504811 | 990 | 320 | 238 | 0.97 | 1096 | 325 | 1429 | 401 | 1769 | 370 | 1623 | 295 | 2019-06-03 | 196.5 | 81 | 1769 | Y | 90 | 104 | 105 | 15 |  |  | 0.8 | 99.2 |  |  |  |  | 61 | 22.3 | 22.3 | 17 | 617.59 | 536.51 | 580.26 | 587.26 | 39.06 | 129.05 | 119.43 | 110.39 |  | 29.39 | 12.26 | 3 | 718.05 | 1.55 | 0.57 | 1.11
575 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR010 | 1S-DL-YP-ETC-DLNR-2502-PVR010 | SHANKAR VIHAR:ID | TG-PVR010A-1 | 19503223 | 990 | 320 | 239 | 0.98 | 319 | 98 | 427 | 126 | 558 | 95 | 419 | 135 | 2019-06-10 23:30 | 62.6 | 11 | 585 | Y | 92 | 125 | 83 | 42 |  | 0.6 | 18.6 | 80.8 | 413.3 | 93 | 521.21 | 304.3 | 281.26 | 598.26 | 598.26 | 390.26 |  | 3.3 | [10 empty] | 694.56 | 1.04 | 0.65 | 0.32
576 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR010 | 1S-DL-YP-ETC-DLNR-2502-PVR010 | SHANKAR VIHAR:ID | TG-PVR010A-2 | 19503675 | 990 | 320 | 238 | 0.97 | 752 | 251 | 1049 | 224 | 932 | 278 | 1164 | 201 | 2019-06-12 | 151.6 | 36.8 | 1241 | R | 102 | 92 | 106 | 14 | 10 | 13.9 | 16.3 | 59.8 | 7.3 | 8 | 2.3 | 4.3 | 308.36 | 387.36 | 387.36 | 321.36 | 377.57 | 299.22 | 394.22 | 368.52 | 0.55 |  | 5 | [5 empty] | 694.58 | 1.02 | 0.56 | 0.76
577 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR012 | 1S-DL-YP-ETC-DLNR-2502-PVR012 | DEFENCE ENCLAVE:ID | TG-PVR012A-1 | 19506529 | 990 | 320 | 242 | 0.97 | 599 | 202 | 825 | 135 | 555 | 262 | 1096 | 468 | 2019-06-01 01:30 | 171.5 | 31.4 | 1096 | B | 98 | 92 | 110 | 18 | 0.1 | 0.1 | 1.9 | 97.9 | 13.3 | 1 |  |  | 443.17 | 550.17 | 550.17 | 461.21 | 246.55 | 152.25 | 342.12 | 242.21 | [8 empty] | 703.42 | 16.18 | 0.62 | 0.6
578 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR012 | 1S-DL-YP-ETC-DLNR-2502-PVR012 | DEFENCE ENCLAVE:ID | TG-PVR012A-2 | 19503201 | 990 | 320 | 247 | 0.97 | 161 | 50 | 203 | 61 | 246 | 51 | 206 | 41 | 2019-06-29 23:30 | 37.5 | 7.4 | 249 | Y | 101 | 114 | 85 | 29 |  |  | 0.7 | 99.3 | 718.44 | 718.44 | 718.44 | 718.44 | [16 empty] | 718.44 | 1.16 | 0.6 | 0.16
579 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR013 | 1S-DL-YP-ETC-DLNR-2502-PVR013 | NEW RAJDHANI ENCLAVE:ID | TG-PVR013A-1 | 19506383 | 630 | 200 | 246 | 0.97 | 437 | 181 | 770 | 130 | 552 | 127 | 537 | 226 | 2019-06-11 | 108.2 | 37.2 | 830 | R | 118 | 93 | 89 | 29 |  |  | 0.9 | 99.1 |  |  | 0.3 |  | 30.3 | 221.3 | 221.3 | 119 | 645.28 | 483.28 | 456.58 | 585.58 | 29 | [7 empty] | 704.58 | 15.02 | 0.69 | 0.69
580 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR013 | 1S-DL-YP-ETC-DLNR-2502-PVR013 | NEW RAJDHANI ENCLAVE:ID | TG-PVR013A-2 | 19505575 | 630 | 200 | 246 | 0.96 | 84 | 15 | 61 | 47 | 196 | 22 | 91 | 123 | 2019-06-14 14:30 | 28.4 | 6.2 | 196 | Y | 96 | 118 | 86 | 32 |  | 0.1 | 11.3 | 88.7 | 696.58 | 694.58 | 696.58 | 696.58 |  | 2 | 2 | [13 empty] | 696.58 | 23.02 | 0.65 | 0.13
581 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR013 | 1S-DL-YP-ETC-DLNR-2502-PVR013 | NEW RAJDHANI ENCLAVE:ID | TG-PVR013A-3 | 19505219 | 630 | 200 | 248 | 0.97 | 355 | 118 | 494 | 119 | 499 | 118 | 497 | 4 | 2019-06-11 23:00 | 81 | 21.4 | 624 | R | 109 | 91 | 100 | 18 |  | 0.2 | 2.5 | 97.3 | 1 | 15 | 4 | 1 | 324.29 | 504.29 | 504.29 | 416.59 | 379.15 | 185.15 | 257.14 | 286.45 | [8 empty] | 704.44 | 15.16 | 0.67 | 0.56
582 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR013 | 1S-DL-YP-ETC-DLNR-2502-PVR013 | NEW RAJDHANI ENCLAVE:ID | TG-PVR013A-4 | 19505149 | 630 | 200 | 239 | 0.96 | 271 | 43 | 176 | 147 | 621 | 80 | 334 | 391 | 2019-06-19 18:00 | 123 | 6 | 621 | Y | 110 | 95 | 95 | 15 | 0.1 | 0.1 | 0.2 | 99.6 | 461.3 | 475.3 | 485 | 476 | 210.57 | 216.25 | 216.25 | 227.25 | 32.58 | 13.3 | 5.3 | 2 | [8 empty] | 705.25 | 14.35 | 0.36 | 0.43
583 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR014 | 1S-DL-YP-ETC-DLNR-2502-PVR014 | L.S.C. NEW RAJDHANI:ID | TG-PVR014A-1 | 19501286 | 630 | 200 | 246 | 0.95 | 133 | 49 | 206 | 33 | 138 | 51 | 213 | 72 | 2019-06-12 15:30 | 35.4 | 1.8 | 231 | B | 115 | 67 | 118 | 51 |  |  | 18 | 82 | 712 | 719.58 | 664.28 | 717.28 | 7.58 |  |  | 2.3 | [12 empty] | 719.58 | 0.02 | 0.38 | 0.21
584 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR014 | 1S-DL-YP-ETC-DLNR-2502-PVR014 | L.S.C. NEW RAJDHANI:ID | TG-PVR014A-2 | 19501285 | 630 | 200 | 245 | 0.98 | 238 | 85 | 357 | 74 | 311 | 78 | 328 | 41 | 2019-06-11 14:00 | 30.8 | -26.2 | 377 | R | 116 | 90 | 94 | 26 |  | 0.1 | 2.5 | 97.4 | 489.3 | 509 | 516.3 | 501.3 | 226.28 | 210.58 | 210.58 | 218.28 | 4 | [11 empty] | 719.58 | 0.02 | 0.36 | 0.38
585 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR015 | 1S-DL-YP-ETC-DLNR-2502-PVR015 | G-I, PREET VIHAR:ID | TG-PVR015A-1 | 19501193 | 990 | 320 | 248 | 0.97 | 1017 | 343 | 1462 | 362 | 1548 | 312 | 1328 | 192 | 2019-06-10 13:00 | 249.5 | -68.4 | 1596 | Y | 106 | 101 | 93 | 13 |  |  | 0.6 | 99.4 |  | 13.3 | 14 | 3 | 46.3 | 67 | 67 | 88.3 | 454.1 | 422.45 | 378.45 | 424.45 | 207.34 | 178.01 | 170.29 | 195.29 | 11 | 37.58 | 2.3 | 7.3 | 719.14 | 0.46 | 0.62 | 1.03
586 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR015 | 1S-DL-YP-ETC-DLNR-2502-PVR015 | G-I, PREET VIHAR:ID | TG-PVR015A-2 | 19506821 | 990 | 320 | 249 | 0.97 | 884 | 301 | 1289 | 296 | 1277 | 287 | 1224 | 60 | 2019-06-01 15:30 | 245.8 | 59.8 | 1409 | Y | 108 | 100 | 92 | 16 | 0.4 | 0.1 | 2.8 | 96.7 |  |  |  |  | 22 | 49.3 | 49.3 | 34.3 | 567.47 | 598.46 | 613.46 | 619.46 | 112.29 | 54 | 10.3 | 48 |  |  |  |  | 702.16 | 17.44 | 0.68 | 0.89
587 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR016 | 1S-DL-YP-ETC-DLNR-2502-PVR016 | S/STN. NO. 1 PREET VIHAR:ID | TG-PVR016A-1 | 19506449 | 990 | 320 | 250 | 0.97 | 671 | 211 | 893 | 199 | 834 | 260 | 1103 | 245 | 2019-06-03 10:30 | 215.7 | 9 | 1103 | B | 98 | 98 | 104 | 6 | 0.3 | 0.1 | 4.7 | 94.8 | 442.38 | 441.08 | 425.38 | 433.38 | 183.14 | 161.54 | 161.54 | 156.02 | 72.53 | 95.43 | 149.41 | 109.05 | [8 empty] | 698.45 | 21.15 | 0.31 | 0.68
588 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR016 | 1S-DL-YP-ETC-DLNR-2502-PVR016 | S/STN. NO. 1 PREET VIHAR:ID | TG-PVR016A-2 | 19501147 | 990 | 320 | 234 | 0.99 | 160 | 30 | 130 | 52 | 221 | 78 | 334 | 177 | 2019-06-12 14:00 | 22.8 | -2.2 | 378 | B | 42 | 88 | 169 | 127 |  |  | 2.6 | 97.4 | 690.4 | 690.4 | 584.34 | 690.4 | [16 empty] | 690.4 | 5.2 | 0.36 | 0.16
589 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR017 | 1S-DL-YP-ETC-DLNR-2502-PVR017 | S/STN. NO. 3 PREET VIHAR:ID | TG-PVR017A-1 | 19501092 | 990 | 200 | 240 | 0.97 | 259 | 85 | 355 | 87 | 361 | 87 | 360 | 5 | 2019-06-12 16:00 | 55.7 | 4.6 | 420 | Y | 99 | 105 | 96 | 9 |  |  | 1.1 | 98.9 | 520.18 | 495.24 | 519.18 | 510.18 | 102.27 | 127.21 | 127.21 | 112.27 | [12 empty] | 622.45 | 1.15 | 0.45 | 0.26
590 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR018 | 1S-DL-YP-ETC-DLNR-2502-PVR018 | C-BLOCK, PREET VIHAR:ID | TG-PVR018A-1 | 19501148 | 630 | 200 | 242 | 0.97 | 618 | 194 | 838 | 236 | 1029 | 188 | 811 | 206 | 2019-06-02 14:00 | 145.8 | 44.2 | 1029 | Y | 102 | 96 | 103 | 7 |  |  | 2 | 98 |  |  |  |  | 3 | 14.3 | 14.3 | 4 | 657.47 | 658.17 | 652.17 | 671.17 | 33.3 | 21 | 37 | 19.3 | 0.3 | 1 |  |  | 694.47 | 1.13 | 0.64 | 0.98
591 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR018 | 1S-DL-YP-ETC-DLNR-2502-PVR018 | C-BLOCK, PREET VIHAR:ID | TG-PVR018A-2 | 19501056 | 630 | 200 | 237 | 0.99 | 483 | 159 | 702 | 147 | 646 | 178 | 791 | 127 | 2019-06-01 19:30 | 87.4 | -6 | 809 | B | 99 | 91 | 109 | 18 |  |  | 8.3 | 91.7 |  | 1.3 |  |  | 185.59 | 261.51 | 261.51 | 167.59 | 507.37 | 430.15 | 603.07 | 525.37 |  |  | 4.3 | [5 empty] | 693.36 | 2.24 | 0.63 | 0.77
592 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR018 | 1S-DL-YP-ETC-DLNR-2502-PVR018 | C-BLOCK, PREET VIHAR:ID | TG-PVR018A-3 | 19505781 | 630 | 200 | 239 | 0.97 | 333 | 125 | 542 | 114 | 495 | 95 | 407 | 119 | 2019-06-03 11:30 | 98.4 | -1.6 | 611 | R | 105 | 96 | 99 | 9 |  |  | 3.3 | 96.7 | 405.06 | 441.36 | 421.36 | 414.06 | 263.43 | 248.4 | 248.4 | 276.1 | 35.27 | 14 | 7 | 14 | [8 empty] | 704.16 | 15.44 | 0.33 | 0.53
593 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR019 | 1S-DL-YP-ETC-DLNR-2502-PVR019 | NIRMAN VIHAR (NEAR MKT.):ID | TG-PVR019A-1 | 19504881 | 990 | 320 | 240 | 0.98 | 802 | 225 | 970 | 272 | 1150 | 306 | 1342 | 322 | 2019-06-11 23:30 | 140.6 | 49.3 | 1369 | B | 97 | 98 | 105 | 8 | 100 | [7 empty] | 231.04 | 216.04 | 216.04 | 200.04 | 482.3 | 498.25 | 463 | 517.55 | 4.55 | 4 | 47 | 0.3 |  |  |  |  | 718.29 | 1.31 | 0.6 | 0.81
594 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR019 | 1S-DL-YP-ETC-DLNR-2502-PVR019 | NIRMAN VIHAR (NEAR MKT.):ID | TG-PVR019A-2 | 19501146 | 990 | 320 | 226 | 0.97 | 599 | 179 | 796 | 196 | 892 | 225 | 1015 | 190 | 2019-06-15 15:00 | 139.1 | 40.5 | 1015 | B | 89 | 104 | 107 | 18 | 69.9 | 27.2 | 2.9 |  | 5.3 |  |  |  | 420.43 | 261.29 | 261.29 | 272.43 | 292.31 | 457.15 | 508.44 | 446.01 | [8 empty] | 718.44 | 1.16 | 0.69 | 0.61
595 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR019 | 1S-DL-YP-ETC-DLNR-2502-PVR019 | NIRMAN VIHAR (NEAR MKT.):ID | TG-PVR019A-3 | 19505378 | 630 | 200 | 235 | 0.98 | 406 | 157 | 694 | 112 | 490 | 138 | 613 | 177 | 2019-06-11 23:00 | 111.4 | 26.2 | 752 | B | 105 | 91 | 104 | 14 | 0.2 | 0.1 | 0.8 | 98.8 |  | 0.3 |  |  | 164.3 | 292.24 | 292.24 | 184 | 551.55 | 423.31 | 560.55 | 532.25 |  |  | 0.3 | [5 empty] | 716.25 | 3.35 | 0.71 | 0.65
596 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR020 | 1S-DL-YP-ETC-DLNR-2502-PVR020 | NIRMAN VIHAR KIOSK:K | TG-PVR020A-1 | 19505705 | 990 | 320 | 235 | 0.98 | 685 | 216 | 907 | 227 | 950 | 242 | 1020 | 99 | 2019-06-11 22:30 | 194.6 | 49.6 | 1131 | Y | 98 | 98 | 104 | 6 | 0.3 | 0.1 | 7.7 | 91.9 |  |  |  |  | 292.23 | 268.53 | 268.53 | 241.23 | 413.12 | 436.42 | 500.35 | 464.12 | [8 empty] | 705.35 | 14.25 | 0.65 | 0.69
597 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR021 | 1S-DL-YP-ETC-DLNR-2502-PVR021 | BHARATI ARTIST COLONY:K | TG-PVR021A-1 | 19506726 | 990 | 320 | 239 | 0.98 | 1232 | 430 | 1911 | 426 | 1894 | 376 | 1671 | 232 | 2019-06-29 14:30 | 396.5 | 10.9 | 1981 | R | 109 | 99 | 92 | 17 | 0.1 | 0.1 | 1.4 | 98.3 |  |  | 3.3 |  | 196.55 | 271.43 | 271.43 | 264.13 | 215.18 | 182.34 | 196.34 | 184.36 | 114.22 | 121.47 | 134.17 | 125.28 | 164.52 | 115.23 | 67.23 | 117.1 | 691.27 | 28.33 | 0.51 | 1.24
598 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR023 | 1S-DL-YP-ETC-DLNR-2502-PVR023 | DISTRICT CENTER, L. NAGAR, NO3:ID | TG-PVR023A-1 | 19501287 | 630 | 200 | 239 | 0.9 | 150 | 48 | 196 | 58 | 239 | 44 | 180 | 53 | 2019-06-27 20:30 | 73.6 | 1.8 | 249 | Y | 108 | 121 | 70 | 51 |  |  |  | 100 | 704.03 | 669.44 | 713.17 | 699.33 | 14.14 | 48.33 | 48.33 | 18.44 | [12 empty] | 718.17 | 1.43 | 0.23 | 0.24
599 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR024 | 1S-DL-YP-ETC-DLNR-2502-PVR024 | MADHUBAN KIOSK:K | TG-PVR024A-1 | 19506559 | 630 | 200 | 229 | 0.99 | 305 | 85 | 394 | 121 | 558 | 99 | 453 | 144 | 2019-06-16 | 123.2 | -2.8 | 579 | Y | 87 | 116 | 97 | 29 | 6.6 | 0.4 | 3 | 90.1 | 82.3 | 2 | 62.3 | 17.3 | 602.41 | 524.46 | 524.46 | 615.46 | 10.23 | 168.48 | 91.48 | 62.18 | [8 empty] | 695.34 | 24.26 | 0.63 | 0.48
600 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR024 | 1S-DL-YP-ETC-DLNR-2502-PVR024 | MADHUBAN KIOSK:K | TG-PVR024A-2 | 19505003 | 630 | 200 | 230 | 0.98 | 122 | 39 | 176 | 39 | 181 | 44 | 199 | 21 | 2019-06-30 23:00 | 21.2 | 5.1 | 243 | B | 91 | 105 | 104 | 14 |  |  | 24.3 | 75.7 | 718.35 | 713.05 | 706.12 | 719.05 | 0.3 | 6 | 6 | [13 empty] | 719.05 | 0.55 | 0.64 | 0.19
601 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR025 | 1S-DL-YP-ETC-DLNR-2502-PVR025 | E-BLOCK, PREET VIHAR, KIOSK:K | TG-PVR025A-1 | 19504629 | 990 | 320 | 239 | 0.97 | 479 | 137 | 573 | 175 | 737 | 166 | 697 | 148 | 2019-06-12 | 103 | 16.2 | 773 | B | 87 | 109 | 103 | 22 |  |  | 22 | 78 | 174.14 | 16 | 64.3 | 42 | 507.4 | 589.54 | 589.54 | 588.24 | 13.3 | 89.3 | 110 | 65 | [8 empty] | 695.24 | 0.36 | 0.59 | 0.48
602 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR026 | 1S-DL-YP-ETC-DLNR-2502-PVR026 | B-BLOCK, PREET VIHAR, NEAR MKT.:ID | TG-PVR026A-1 | 19503229 | 630 | 200 | 243 | 0.97 | 523 | 180 | 774 | 191 | 823 | 152 | 646 | 158 | 2019-06-30 23:00 | 107.6 | 33.6 | 837 | Y | 114 | 107 | 79 | 35 | 3.3 | 6.7 | 56.6 | 33.4 |  |  | 3.3 |  | 49 | 96.58 | 96.58 | 128 | 636 | 603.02 | 316.53 | 588 | 34.23 | 19.23 |  | 3.23 |  |  |  |  | 719.23 | 0.37 | 0.61 | 0.83
603 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR053 | 1S-DL-YP-ETC-DLNR-2502-PVR053 | PLOT NO.5 ADITYA TOWER LNR:ID | TG-PVR053A-1 | 19501191 | 630 | 200 | 246 | 0.98 | 90 | 23 | 97 | 31 | 132 | 35 | 150 | 46 | 2019-06-11 14:00 | 12.4 | -5.1 | 156 | Y | 98 | 99 | 102 | 4 |  |  | 7.1 | 92.9 | 717.51 | 717.51 | 717.51 | 717.51 | [16 empty] | 717.51 | 2.09 | 0.41 | 0.14
604 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR053 | 1S-DL-YP-ETC-DLNR-2502-PVR053 | PLOT NO.5 ADITYA TOWER LNR:ID | TG-PVR053A-2 | 19501195 | 630 | 200 | 245 | 0.99 | 154 | 63 | 262 | 46 | 194 | 44 | 186 | 72 | 2019-06-06 15:00 | 13.8 | -6.9 | 273 | R | 117 | 82 | 101 | 35 |  |  | 17 | 83 | 516.55 | 698.19 | 682.51 | 605.25 | 200.54 | 19.3 | 19.3 | 112.24 | [12 empty] | 717.49 | 2.11 | 0.47 | 0.24
605 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR054 | 1S-DL-YP-ETC-DLNR-2502-PVR054 | D- BLOCK, PREET VIHAR:PL | TG-PVR054A-1 | 19501028 | 990 | 320 | 240 | 0.97 | 503 | 155 | 659 | 196 | 841 | 151 | 642 | 191 | 2019-06-30 23:30 | 97.9 | 25.8 | 841 | Y | 102 | 101 | 97 | 5 |  |  | 13.2 | 86.8 | 25.3 | 70 | 62.3 | 35 | 578.11 | 511.03 | 511.03 | 558.33 | 90.53 | 113.31 | 91.59 | 101.01 | [8 empty] | 694.34 | 1.26 | 0.59 | 0.51
606 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR064 | 1S-DL-YP-ETC-DLNR-2502-PVR064 | FIRE STN LAXMI NAGAR:ID | TG-PVR064A-1 | 19501284 | 400 | 120 | 243 | 0.96 | 25 | 11 | 42 | 13 | 51 | 2 | 8 | 39 | 2019-06-06 01:30 | 6.3 | -0.8 | 55 | Y | 108 | 178 | 14 | 164 | 47 | 5.2 | 16.1 | 31.8 | 695.36 | 695.36 | 695.36 | 695.36 | [16 empty] | 695.36 | 0.24 | 0.42 | 0.06
607 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR064 | 1S-DL-YP-ETC-DLNR-2502-PVR064 | FIRE STN LAXMI NAGAR:ID | TG-PVR064A-2 | 19501282 | 400 | 120 | 242 | 0.96 | 16 | 6 | 26 | 5 | 21 | 5 | 21 | 5 | 2019-06-03 | 2.8 | 0.3 | 30 | R | 126 | 90 | 84 | 42 |  |  | 9.3 | 90.7 | 718.52 | 718.52 | 718.52 | 718.52 | [16 empty] | 718.52 | 1.08 | 0.39 | 0.04
608 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR065 | 1S-DL-YP-ETC-DLNR-2502-PVR065 | ADITYA TOWER DIST. CENTER LNR:ID | TG-PVR065A-1 | 19505468 | 400 | 126 | 248 | 0.98 | 75 | 31 | 124 | 28 | 111 | 16 | 64 | 54 | 2019-06-11 15:30 | 28.5 | -0.4 | 141 | R | 115 | 112 | 73 | 42 |  |  | 7 | 93 | 642.3 | 686.28 | 692.28 | 692.28 | 49.58 | 6 | 6 | [13 empty] | 692.28 | 27.32 | 0.33 | 0.19
609 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR065 | 1S-DL-YP-ETC-DLNR-2502-PVR065 | ADITYA TOWER DIST. CENTER LNR:ID | TG-PVR065A-2 | 19505451 | 400 | 120 | 249 | 0.93 | 41 | 29 | 119 | 2 | 8 | 9 | 37 | 99 | 2019-06-10 14:00 | 12.5 | 0.1 | 119 | R | 209 | 15 | 76 | 194 |  | 0.1 | 1.7 | 98.2 | 704.57 | 706.27 | 706.27 | 706.27 | 1.3 | [15 empty] | 706.27 | 13.33 | 0.24 | 0.1
610 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR066 | 1S-DL-YP-ETC-DLNR-2502-PVR066 | ROOT TOWER LAXMI NAGAR | TG-PVR066A-1 | 19505355 | 630 | 200 | 249 | 0.97 | 158 | 48 | 190 | 55 | 217 | 55 | 221 | 29 | 2019-06-06 12:30 | 47.4 | -1.4 | 302 | R | 89 | 95 | 116 | 27 | 0.2 |  | 12.6 | 87.2 | 658.28 | 611.54 | 589.24 | 628.24 | 34 | 80.34 | 80.34 | 64.04 | [12 empty] | 692.28 | 27.32 | 0.34 | 0.25
611 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR066 | 1S-DL-YP-ETC-DLNR-2502-PVR066 | ROOT TOWER LAXMI NAGAR | TG-PVR066A-2 | 19503285 | 630 | 200 | 248 | 0.88 | 153 | 47 | 186 | 61 | 242 | 46 | 182 | 58 | 2019-06-11 15:00 | 32.7 | -35.4 | 257 | Y | 95 | 105 | 101 | 10 |  |  | 6.4 | 93.6 | 694.28 | 596 | 655 | 648.28 | 21.3 | 119.58 | 119.58 | 67.3 | [12 empty] | 715.58 | 4.02 | 0.38 | 0.24
612 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR066 | 1S-DL-YP-ETC-DLNR-2502-PVR066 | ROOT TOWER LAXMI NAGAR | TG-PVR066A-3 | 19503254 | 630 | 200 | 248 | 0.94 | 97 | 33 | 129 | 30 | 119 | 34 | 133 | 13 | 2019-06-11 10:30 | 21.2 | -12.4 | 157 | R | 141 | 84 | 75 | 66 |  | 0.1 | 14.9 | 85 | 715.59 | 715.59 | 715.59 | 715.59 | [16 empty] | 715.59 | 4.01 | 0.39 | 0.15
613 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR066 | 1S-DL-YP-ETC-DLNR-2502-PVR066 | ROOT TOWER LAXMI NAGAR | TG-PVR066A-4 | 19503273 | 630 | 200 | 248 | 0.95 | 145 | 39 | 157 | 72 | 289 | 34 | 135 | 144 | 2019-06-14 12:00 | 48.3 | 0.5 | 303 | Y | 80 | 155 | 65 | 90 |  |  | 10.2 | 89.8 | 715.29 | 503.21 | 715.59 | 681.31 | 0.3 | 212.38 | 212.38 | 34.28 | [12 empty] | 715.59 | 4.01 | 0.29 | 0.23
614 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR067 | 1S-DL-YP-ETC-DLNR-2502-PVR067 | SWASTHYA VIHAR KIOSK VIKAS MARG | TG-PVR067A-1 | 19502956 | 630 | 200 | 248 | 0.97 | 689 | 234 | 941 | 241 | 1003 | 213 | 880 | 107 | 2019-06-29 12:30 | 136.2 | 18.9 | 1032 | Y | 94 | 109 | 97 | 15 | 47.9 | 1.2 | 1.4 | 49.6 | 234.53 | 59 | 197.53 | 177.44 | 121.43 | 266.36 | 266.36 | 174.22 | 208 | 178.04 | 191 | 185.34 | 117.55 | 138.21 | 128.25 | 139.51 | 10.3 | 51 | 13.3 | 15.3 | 693.01 | 2.59 | 0.45 | 1.09
615 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR067 | 1S-DL-YP-ETC-DLNR-2502-PVR067 | SWASTHYA VIHAR KIOSK VIKAS MARG | TG-PVR067A-2 | 19504801 | 630 | 200 | 250 | 0.99 | 499 | 198 | 783 | 124 | 485 | 177 | 683 | 263 | 2019-06-12 17:00 | 94.3 | -12.4 | 819 | R | 113 | 85 | 102 | 28 | 0.1 | 25.6 | 73.7 | 0.6 | 17 | 168 | 113.21 | 64.3 | 360.06 | 281.3 | 281.3 | 325.36 | 266.49 | 269.1 | 311.04 | 328.34 | 74.45 |  | 22 | [5 empty] | 718.4 | 1.2 | 0.51 | 0.79
616 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR068 | 1S-DL-YP-ETC-DLNR-2502-PVR068 | CHITRA VIHAR:ID | TG-PVR068A-1 | 19506666 | 630 | 200 | 239 | 0.97 | 528 | 199 | 814 | 174 | 716 | 155 | 634 | 156 | 2019-06-30 01:00 | 118.4 | 23.4 | 814 | R | 111 | 101 | 88 | 23 | 0.1 |  | 29.7 | 70.2 |  |  | 2 |  | 57 | 134.55 | 134.55 | 145.3 | 641.59 | 568.04 | 431.04 | 558.59 | 6 | 2 |  | 0.3 |  |  |  |  | 704.59 | 15.01 | 0.6 | 0.84
617 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR068 | 1S-DL-YP-ETC-DLNR-2502-PVR068 | CHITRA VIHAR:ID | TG-PVR068A-2 | 19503203 | 630 | 200 | 249 | 0.97 | 567 | 238 | 1081 | 199 | 884 | 130 | 573 | 444 | 2019-06-02 22:30 | 106.7 | 24.8 | 1081 | R | 120 | 98 | 83 | 37 | 0.1 | 2.6 | 62 | 35.3 |  | 1 | 3 |  | 103.3 | 243 | 243 | 195 | 490.38 | 435.45 | 389.22 | 495.48 | 102.34 | 38.14 |  | 27.11 | 21.17 |  |  |  | 717.59 | 2.01 | 0.56 | 0.9
618 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR068 | 1S-DL-YP-ETC-DLNR-2502-PVR068 | CHITRA VIHAR:ID | TG-PVR068A-3 | 19505782 | 630 | 200 | 240 | 0.98 | 237 | 70 | 289 | 70 | 290 | 97 | 399 | 109 | 2019-06-11 23:30 | 59.4 | 10.6 | 435 | B | 112 | 65 | 123 | 58 | 0.1 |  | 1.6 | 98.3 | 174.18 | 464.3 | 134 | 326 | 527.32 | 240.08 | 240.08 | 378.38 | 2.48 |  | 12.14 | [9 empty] | 704.38 | 15.22 | 0.56 | 0.38
619 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR069 | 1S-DL-YP-ETC-DLNR-2502-PVR069 | DISTT.CENT.2 LNR | TG-PVR069A-1 | 19503211 | 400 | 120 | 248 | 0.96 | 25 | 5 | 18 | 4 | 15 | 17 | 69 | 52 | 2019-06-13 16:30 | 9.4 | 0.3 | 82 | B | 42 | 49 | 209 | 167 |  |  | 41.2 | 58.8 | 719.27 | 719.27 | 719.27 | 719.27 | [16 empty] | 719.27 | 0.33 | 0.62 | 0.06
620 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR073 | 1S-DL-YP-ETC-DLNR-2502-PVR073 | F-Blok Preet Vihar:Pl Preet Vihar | TG-PVR073A-1 | 19503374 | 630 | 200 | 247 | 0.98 | 367 | 127 | 518 | 106 | 431 | 134 | 546 | 104 | 2019-06-12 14:30 | 78.2 | 14.3 | 600 | B | 101 | 91 | 108 | 17 |  |  | 4.4 | 95.6 | 4 | 22.3 | 2 | 0.3 | 445.43 | 571.18 | 571.18 | 480.42 | 269.31 | 125.26 | 289.02 | 238.02 | [8 empty] | 719.14 | 0.46 | 0.63 | 0.58
621 | 2019-06-07 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR073 | 1S-DL-YP-ETC-DLNR-2502-PVR073 | F-Blok Preet Vihar:Pl Preet Vihar | TG-PVR073A-2 | 19506915 | 400 | 120 | 240 | 0.99 | 332 | 103 | 435 | 106 | 447 | 123 | 520 | 79 | 2019-06-13 22:30 | 62.8 | -2.9 | 533 | B | 96 | 102 | 102 | 6 | 0.2 | 0.1 | 20.7 | 79 | 2 | 3 | 8.3 |  | 244.45 | 219.45 | 219.45 | 227.45 | 311.21 | 338.51 | 385.21 | 331.51 | 3.3 |  | 3.3 | 2 |  |  |  |  | 561.36 | 14.24 | 0.56 | 0.83
622 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR074 | 1S-DL-YP-ETC-DLNR-2502-PVR074 | E BLOCK NIRMAN VIHAR , VIKAS MARG S/S | TG-PVR074A-1 | 19505028 | 990 | 320 | 241 | 0.88 | 503 | 202 | 865 | 151 | 647 | 151 | 646 | 219 | 2019-06-06 13:30 | 220.8 | 16.9 | 892 | R | 125 | 88 | 88 | 37 |  |  | 0.4 | 99.6 | 319.43 | 368.13 | 368.13 | 345.43 | 128.28 | 287.29 | 287.29 | 213.52 | 244.21 | 36.5 | 32.5 | 132.57 | [8 empty] | 692.32 | 3.28 | 0.47 | 0.51
623 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR078 | 1S-DL-YP-ETC-DLNR-2502-PVR078 | SAGAR PLAZA D.C. LNR | TG-PVR078A-1 | 19504512 | 400 | 120 | 245 | 0.81 | 78 | 19 | 82 | 29 | 124 | 29 | 124 | 42 | 2019-06-06 14:30 | 14.6 | -11.6 | 160 | Y | 103 | 119 | 77 | 42 |  |  |  | 100 | 718.47 | 676.17 | 719.17 | 719.47 | 1 | 43.3 | 43.3 | [13 empty] | 719.47 | 0.13 | 0.35 | 0.19
624 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR078 | 1S-DL-YP-ETC-DLNR-2502-PVR078 | SAGAR PLAZA D.C. LNR | TG-PVR078A-2 | 19504489 | 400 | 120 | 245 | 0.92 | 150 | 43 | 181 | 52 | 218 | 56 | 237 | 49 | 2019-06-10 12:00 | 62.4 | -0.3 | 237 | B | 96 | 100 | 104 | 8 |  |  | 0.3 | 99.7 | 502.18 | 499.48 | 491.48 | 496.18 | 193.28 | 194.28 | 194.28 | 199.28 |  | 1.3 | 1.3 | [9 empty] | 695.46 | 0.14 | 0.29 | 0.38
625 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR082 | 1S-DL-YP-ETC-DLNR-2502-PVR082 | E-BLK PREET VIHAR(NEAR E-95 PREET VIHAR) | TG-PVR082A-1 | 19503740 | 630 | 200 | 231 | 0.98 | 583 | 159 | 690 | 180 | 783 | 244 | 1070 | 343 | 2019-06-12 | 110.4 | 27.1 | 1070 | B | 94 | 87 | 119 | 32 |  | 0.6 | 19 | 80.4 |  | 3.3 |  |  | 182.55 | 265.05 | 265.05 | 128.25 | 502.29 | 420.19 | 533.01 | 537.06 | 10 | 6.3 | 127 | 29.53 |  |  | 11.23 |  | 695.24 | 0.36 | 0.57 | 0.93
626 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR085 | 1S-DL-YP-ETC-DLNR-2502-PVR085 | PARK END | TG-PVR085A-1 | 19505358 | 630 | 200 | 244 | 0.98 | 436 | 128 | 537 | 171 | 721 | 136 | 570 | 170 | 2019-06-06 16:00 | 114.2 | 29.2 | 813 | Y | 80 | 114 | 106 | 34 |  | 0.1 | 7.2 | 92.8 | 11.3 |  |  |  | 463 | 244 | 244 | 381.3 | 236.28 | 458.28 | 425.28 | 329.28 |  | 8.3 | [6 empty] | 710.58 | 9.02 | 0.62 | 0.69
627 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR088 | 1S-DL-YP-ETC-DLNR-2502-PVR088 | NEW RAJDHANI ENCLAVE S/S-2:OD | TG-PVR088A-1 | 19506416 | 630 | 200 | 239 | 0.98 | 260 | 69 | 296 | 96 | 415 | 96 | 414 | 118 | 2019-06-05 | 58.6 | 7.6 | 457 | B | 84 | 101 | 115 | 31 |  |  | 2.1 | 97.9 | 342.58 | 246.58 | 102 | 191.3 | 364 | 409.3 | 409.3 | 513.58 |  | 50.3 | 81 | 1.3 | [8 empty] | 706.58 | 13.02 | 0.6 | 0.41