## Loading Condition > 80%
MIS Report of Distribution Transformer - Jun19
Jun19 1230 LAXMI NAGAR (Loading Condition > 80% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN022 | 1S-DL-YP-ETC-DLNR-2503-MAN022 | JOSHI COLONY:ID | TG-MAN022A-2 | 19505405 | 990 | 320 | 241 | 0.97 | 900 | 316 | 1382 | 300 | 1324 | 285 | 1248 | 116 | 2019-06-29 23:00 | 249.9 | 68.8 | 1492 | Y | 110 | 99 | 92 | 18 | 0.1 | 0.1 | 16.9 | 82.9 |  |  |  |  | 16.42 | 138.08 | 138.08 | 64.42 | 618.42 | 521.46 | 556.12 | 607.42 | 59.3 | 35 | 4.3 | 22.3 |  |  |  |  | 694.54 | 25.06 | 0.61 | 0.91
2 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN049 | 1S-DL-YP-ETC-DLNR-2503-MAN049 | MADHU VIHAR S/STN-1:ID | TG-MAN049A-2 | 19501135 | 990 | 320 | 242 | 0.97 | 917 | 324 | 1306 | 299 | 1205 | 294 | 1185 | 113 | 2019-06-12 17:00 | 223 | 72.9 | 1344 | R | 98 | 107 | 95 | 12 |  |  | 1.5 | 98.5 |  |  |  |  | 29.3 | 2 | 2 | 15 | 601.23 | 617.01 | 629.17 | 628.24 | 87.01 | 98.53 | 59.07 | 74.3 |  |  |  |  | 717.54 | 2.06 | 0.67 | 0.93
3 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN049 | 1S-DL-YP-ETC-DLNR-2503-MAN049 | MADHU VIHAR S/STN-1:ID | TG-MAN049A-1 | 19506121 | 990 | 320 | 243 | 0.97 | 801 | 248 | 1042 | 267 | 1120 | 286 | 1209 | 145 | 2019-06-29 16:00 | 224 | 58.9 | 1325 | Y | 84 | 106 | 110 | 26 | 0.1 | 0.1 | 2 | 97.8 | 7.3 |  |  |  | 355.47 | 191 | 191 | 208 | 348.06 | 470.25 | 561.23 | 502.53 | 0.3 | 50.28 | 40 | 1 |  |  |  |  | 711.53 | 8.07 | 0.63 | 0.81
4 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN052 | 1S-DL-YP-ETC-DLNR-2503-MAN052 | HASANPUR VILLAGE:PL | TG-MAN052A-1 | 19504543 | 990 | 320 | 244 | 0.99 | 847 | 280 | 1155 | 266 | 1089 | 300 | 1234 | 126 | 2019-06-11 15:00 | 127.3 | 22.1 | 1265 | B | 103 | 94 | 103 | 9 |  |  | 0.6 | 99.4 |  |  |  |  | 221.59 | 361.57 | 361.57 | 265.29 | 473.28 | 356.3 | 441.58 | 439.28 | 24.3 | 1.3 | 48 | 15 |  |  |  |  | 719.57 | 0.03 | 0.57 | 0.86
5 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN053 | 1S-DL-YP-ETC-DLNR-2503-MAN053 | GAZIPUR VILLAGE NEAR TEMPEL:PL | TG-MAN053A-1 | 19506444 | 990 | 320 | 250 | 0.97 | 876 | 295 | 1224 | 298 | 1230 | 282 | 1168 | 59 | 2019-06-27 22:30 | 224.6 | 97.9 | 1319 | Y | 100 | 106 | 94 | 12 | 0.4 |  | 5.2 | 94.4 | [8 empty] | 390.17 | 340.17 | 411.17 | 394.17 | 31 | 81 | 9.3 | 27 |  |  |  |  | 712.11 | 7.49 | 0.76 | 0.88
6 | 2019-06-17 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN068 | 1S-DL-YP-ETC-DLNR-2503-MAN068 | S/STN.NO-13, PPG CGHS:ID | TG-MAN068A-1 | 19502466 | 400 | 120 | 236 | 0.97 | 312 | 92 | 408 | 128 | 568 | 91 | 403 | 162 | 2019-06-30 23:00 | 67.3 | 27.9 | 578 | Y | 88 | 120 | 93 | 32 |  |  |  | 100 |  |  |  |  | 46 | 7.3 | 7.3 | 15.3 | 290 | 262.3 | 306 | 320.3 |  | 66 | [6 empty] | 336 | 0 | 0.71 | 0.78
7 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN216 | 1S-DL-YP-ETC-DLNR-2503-MAN216 | DTC DEPOT GAZIPUR:ID | TG-MAN216A-1 | 19502566 | 100 | 40 | 245 | 0.96 | 85 | 27 | 109 | 22 | 90 | 36 | 151 | 54 | 2019-06-08 00:30 | 40.3 | -2.7 | 151 | B | 109 | 65 | 127 | 62 |  |  | 16 | 84 | 1 | 16 | 0.3 | 0.3 | 18.3 | 532.03 | 532.03 | 37.59 | 673.3 | 170.27 | 616.3 | 679.31 | 25.3 |  | 94.3 | 0.3 |  |  | 1 |  | 718.3 | 1.3 | 0.63 | 0.85
8 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN292 | 1S-DL-YP-ETC-DLNR-2503-MAN292 | GAZIPUR PARK NEAR ASHOK DAIRY STN:OD | TG-MAN292A-1 | 19506443 | 990 | 320 | 247 | 0.99 | 868 | 265 | 1058 | 276 | 1113 | 328 | 1327 | 247 | 2019-06-29 16:00 | 230.7 | -15 | 1438 | B | 95 | 90 | 115 | 25 |  | 0.2 | 21.8 | 77.9 | [5 empty] | 5.34 | 5.34 |  | 679.21 | 682.31 | 408.21 | 659.18 | 11.44 | 3 | 269.44 | 31.47 |  |  | 13 |  | 691.05 | 28.55 | 0.78 | 0.88
9 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR034 | 1S-DL-YP-ETC-DLNR-2502-PVR034 | S/STN. NO.8 F.I.E., PPG:ID | TG-PVR034A-1 | 19505921 | 630 | 200 | 248 | 0.99 | 577 | 191 | 806 | 190 | 798 | 195 | 820 | 19 | 2019-06-12 15:00 | 170 | -23.4 | 847 | Y | 102 | 96 | 102 | 6 |  | 0.1 | 3.4 | 96.5 | 41.57 | 67.27 | 26 | 40.57 | 334.3 | 328.56 | 328.56 | 336.56 | 266.55 | 270.29 | 299.59 | 282.59 | 61 | 37.3 | 42 | 43.3 |  |  |  |  | 704.22 | 15.38 | 0.48 | 0.92
10 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR040 | 1S-DL-YP-ETC-DLNR-2502-PVR040 | S/STN. NO.15 F.I.E., PPG:ID | TG-PVR040A-2 | 19504783 | 400 | 120 | 249 | 0.96 | 384 | 121 | 520 | 149 | 640 | 114 | 491 | 137 | 2019-06-06 11:30 | 93 | -64.9 | 661 | Y | 94 | 118 | 88 | 30 |  |  | 41.1 | 58.9 | 261.53 | 236.23 | 282.53 | 258.53 | 203.58 | 185.3 | 185.3 | 192.3 | 239.32 | 146.28 | 244.24 | 233 | 13.54 | 132.02 | 3.3 | 34.54 |  | 18.54 |  |  | 719.17 | 0.43 | 0.38 | 0.96
11 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR041 | 1S-DL-YP-ETC-DLNR-2502-PVR041 | S/STN. NO.16 F.I.E., PPG:ID | TG-PVR041A-2 | 19502874 | 630 | 200 | 248 | 0.97 | 573 | 195 | 801 | 180 | 738 | 198 | 818 | 74 | 2019-06-29 13:00 | 158.7 | -65.8 | 856 | B | 102 | 93 | 106 | 13 |  |  | 6.8 | 93.2 | 235.26 | 297.55 | 242.56 | 256.26 | 220.56 | 173.27 | 173.27 | 200.26 | 231.3 | 238.3 | 224.3 | 237 | 32 | 10 | 49 | 26 |  |  |  |  | 719.52 | 0.08 | 0.4 | 0.91
12 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR045 | 1S-DL-YP-ETC-DLNR-2502-PVR045 | S/STN. NO.20 F.I.E., PPG:ID | TG-PVR045A-3 | 19505035 | 630 | 200 | 248 | 0.97 | 589 | 199 | 827 | 216 | 903 | 174 | 724 | 156 | 2019-06-03 15:30 | 152.7 | -82.3 | 910 | Y | 103 | 99 | 97 | 6 |  |  | 0.5 | 99.5 | 39.3 | 71.3 | 50 | 51.3 | 367.23 | 373.51 | 373.51 | 382.53 | 245.07 | 198.09 | 266.07 | 228.37 | 67.3 | 72.3 | 15 | 56.3 |  | 3.3 |  |  | 719.3 | 0.3 | 0.47 | 0.94
13 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR045 | 1S-DL-YP-ETC-DLNR-2502-PVR045 | S/STN. NO.20 F.I.E., PPG:ID | TG-PVR045A-1 | 19505036 | 400 | 120 | 248 | 0.96 | 351 | 121 | 516 | 117 | 503 | 113 | 488 | 24 | 2019-06-13 12:30 | 117.6 | 0.8 | 530 | Y | 106 | 100 | 94 | 12 |  |  | 8.7 | 91.3 | 281.53 | 318.23 | 313.53 | 305.23 | 137.3 | 101.3 | 101.3 | 114.41 | 254.08 | 269.08 | 294.28 | 279.57 | 46 | 30.3 | 4 | 19.3 |  |  |  |  | 719.31 | 0.29 | 0.41 | 0.88
14 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR047 | 1S-DL-YP-ETC-DLNR-2502-PVR047 | S/STN. NO.22 F.I.E., PPG:ID | TG-PVR047A-2 | 19504981 | 630 | 200 | 248 | 0.94 | 643 | 193 | 799 | 228 | 956 | 222 | 925 | 144 | 2019-06-08 14:00 | 187.7 | -94.3 | 976 | B | 90 | 103 | 107 | 17 | 0.1 |  | 21.8 | 78.1 | 359.57 | 330.27 | 332.57 | 338.57 | 80.05 | 86.26 | 86.26 | 77.56 | 183.41 | 133.5 | 135.29 | 147.2 | 91.26 | 156.56 | 151.17 | 149.26 |  | 7.3 | 24 | 1.3 | 715.09 | 4.51 | 0.39 | 1.02
15 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR049 | 1S-DL-YP-ETC-DLNR-2502-PVR049 | S/STN. NO.24 F.I.E., PPG:ID | TG-PVR049A-2 | 19506489 | 630 | 200 | 243 | 0.98 | 576 | 190 | 808 | 174 | 745 | 212 | 911 | 145 | 2019-06-14 14:30 | 152.6 | -36.4 | 911 | B | 97 | 98 | 105 | 8 |  | 0.3 | 16.8 | 82.9 | 375.53 | 371.23 | 364.23 | 371.23 | 61.59 | 67.59 | 67.59 | 64.59 | 201.41 | 239.11 | 175.11 | 199.11 | 66.3 | 27.3 | 96 | 70.3 |  |  | 1 |  | 706.03 | 13.57 | 0.37 | 0.91
16 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR003 | 1S-DL-YP-ETC-DLNR-2501-LGR003 | LNR COMPLAINT CENTER:ID | TG-LGR003A-2 | 19505889 | 990 | 320 | 246 | 0.99 | 766 | 368 | 1603 | 260 | 1110 | 138 | 592 | 876 | 2019-06-02 21:00 | 120.3 | 11.2 | 1627 | R | 145 | 106 | 49 | 96 | 0.1 | 0.8 | 53.2 | 45.9 |  |  | 232.48 |  | 15 | 137.32 | 137.32 | 195.02 | 459.44 | 561.42 | 14.3 | 508.42 | 222.3 | 4.3 |  |  | 6.3 |  |  |  | 703.44 | 16.16 | 0.63 | 0.77
17 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR004 | 1S-DL-YP-ETC-DLNR-2501-LGR004 | KISHAN KUNJ:K | TG-LGR004A-1 | 19505542 | 990 | 200 | 245 | 0.98 | 1036 | 355 | 1502 | 336 | 1409 | 345 | 1445 | 82 | 2019-06-30 00:30 | 185.2 | 40.4 | 1582 | R | 105 | 94 | 101 | 11 | 4.7 | 23.4 | 32.8 | 39.1 |  |  |  |  | 84.44 | 180.25 | 180.25 | 114.14 | 535.05 | 493.55 | 523.56 | 533.05 | 72.03 | 22.06 | 56.26 | 47.56 | 4.42 | 0.08 | 1.49 | 1.19 | 696.34 | 23.26 | 0.52 | 1.05
18 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR007 | 1S-DL-YP-ETC-DLNR-2501-LGR007 | WALIA NURSHING HOME:PL | TG-LGR007A-2 | 19505459 | 630 | 200 | 238 | 0.98 | 631 | 208 | 906 | 207 | 912 | 215 | 940 | 32 | 2019-06-08 15:00 | 126.6 | 38.4 | 948 | Y | 101 | 97 | 102 | 5 | 0.1 | 0.1 | 11 | 88.9 |  |  |  |  | 28 | 75.3 | 75.3 | 18 | 555.04 | 548.04 | 624.31 | 590.04 | 120.43 | 80.43 | 68.3 | 96.27 | 1 | 0.3 | 0.16 | 0.16 | 704.47 | 15.13 | 0.62 | 1
19 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR008 | 1S-DL-YP-ETC-DLNR-2501-LGR008 | LALITA PARK:K | TG-LGR008A-1 | 19506683 | 990 | 320 | 239 | 0.98 | 825 | 272 | 1230 | 232 | 1033 | 320 | 1432 | 346 | 2019-06-28 23:30 | 186.2 | 41 | 1432 | B | 100 | 92 | 108 | 16 | 0.3 |  | 35.4 | 64.3 | 1.3 | 1 |  |  | 295.53 | 337.17 | 337.17 | 287.53 | 411.02 | 374.38 | 432.54 | 424.02 | 4.3 |  | 43.05 | 1 |  |  |  |  | 712.55 | 7.05 | 0.55 | 0.83
20 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR008 | 1S-DL-YP-ETC-DLNR-2501-LGR008 | LALITA PARK:K | TG-LGR008A-3 | 19506761 | 990 | 320 | 240 | 0.98 | 785 | 308 | 1371 | 191 | 842 | 286 | 1287 | 493 | 2019-06-28 23:30 | 175.7 | 41.6 | 1458 | R | 123 | 73 | 104 | 50 | 0.1 | 6 | 75.6 | 18.2 | 0.3 | 23.3 |  |  | 143.3 | 515.06 | 515.06 | 270.29 | 459.06 | 174.18 | 481.25 | 442.25 | 108.48 |  | 4.3 |  | 1 |  |  |  | 712.54 | 7.06 | 0.58 | 0.79
21 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR009 | 1S-DL-YP-ETC-DLNR-2501-LGR009 | RAMESH PARK AKHARA:PL | TG-LGR009A-1 | 19503006 | 990 | 320 | 240 | 0.97 | 855 | 273 | 1139 | 251 | 1040 | 332 | 1403 | 324 | 2019-06-01 04:30 | 167.8 | 58.9 | 1444 | B | 100 | 85 | 115 | 30 |  | 0.9 | 75 | 24.1 | 0.01 | 0.01 |  |  | 70 | 193.09 | 193.09 | 55.18 | 635.49 | 524.25 | 639.17 | 657.17 | 11.45 |  | 59.3 | 5 |  |  | 1 |  | 717.35 | 2.25 | 0.63 | 0.86
22 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR009 | 1S-DL-YP-ETC-DLNR-2501-LGR009 | RAMESH PARK AKHARA:PL | TG-LGR009A-2 | 19506036 | 990 | 320 | 241 | 0.98 | 917 | 363 | 1740 | 396 | 1763 | 158 | 673 | 1078 | 2019-06-01 19:00 | 302.4 | 25.6 | 1763 | Y | 89 | 123 | 88 | 35 | 0.5 | 0.1 | 11.5 | 88 | 48.35 | 6 | 30 | 10 | 397.32 | 154.57 | 154.57 | 359.27 | 269.32 | 484.22 | 253.3 | 344.42 |  | 70.2 | 1.3 | 1.54 | 0.24 | 0.24 |  |  | 716.03 | 3.57 | 0.47 | 0.93
23 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR011 | 1S-DL-YP-ETC-DLNR-2501-LGR011 | JAGAT RAM PARK:K | TG-LGR011A-1 | 19502822 | 990 | 320 | 244 | 0.97 | 934 | 359 | 1503 | 283 | 1197 | 292 | 1219 | 296 | 2019-06-30 00:30 | 192.1 | 53 | 1503 | R | 112 | 92 | 96 | 20 |  |  | 23.4 | 76.6 |  |  |  |  | 44 | 199.59 | 199.59 | 120 | 565.12 | 501.11 | 529.1 | 545.1 | 101.14 | 17.46 | 36.16 | 53.46 | 8.3 |  |  |  | 718.56 | 1.04 | 0.58 | 0.94
24 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR011 | 1S-DL-YP-ETC-DLNR-2501-LGR011 | JAGAT RAM PARK:K | TG-LGR011A-2 | 19502825 | 990 | 320 | 239 | 0.98 | 906 | 312 | 1349 | 302 | 1296 | 292 | 1269 | 70 | 2019-06-06 03:30 | 154.6 | 55.9 | 1439 | B | 100 | 95 | 104 | 9 |  | 6.6 | 81.8 | 11.6 |  |  |  |  | 112.57 | 196.56 | 196.56 | 138.26 | 590.55 | 497.27 | 531.28 | 547.27 | 14.26 | 23.55 | 58.24 | 32.25 |  |  | 0.3 |  | 718.18 | 1.42 | 0.57 | 0.91
25 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR012 | 1S-DL-YP-ETC-DLNR-2501-LGR012 | GURU RAM DASS NAGAR:PL | TG-LGR012A-1 | 19502826 | 990 | 320 | 244 | 0.97 | 891 | 298 | 1285 | 318 | 1368 | 276 | 1181 | 162 | 2019-06-30 23:30 | 159.7 | 47.1 | 1421 | Y | 98 | 110 | 92 | 18 | 0 |  | 0.1 | 99.8 | 0.07 |  | 0.07 |  | 184.5 | 101.2 | 101.2 | 163.27 | 515.35 | 521.01 | 469.17 | 525.05 | 17 | 93.11 | 8 | 29 |  | 2 |  |  | 717.32 | 2.28 | 0.57 | 0.9
26 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR012 | 1S-DL-YP-ETC-DLNR-2501-LGR012 | GURU RAM DASS NAGAR:PL | TG-LGR012A-3 | 19505569 | 990 | 320 | 245 | 0.97 | 1059 | 395 | 1655 | 367 | 1557 | 297 | 1238 | 378 | 2019-06-30 01:30 | 218.2 | 68.2 | 1655 | R | 108 | 103 | 89 | 19 | 0.3 | 0.6 | 28.8 | 70.3 |  |  |  |  | 63.53 | 66.23 | 66.23 | 77.23 | 508.59 | 542.05 | 568.26 | 552.35 | 120.41 | 98.35 | 11.42 | 82.05 | 21.28 | 7.58 |  | 2.58 | 715.01 | 4.59 | 0.54 | 1.07
27 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR014 | 1S-DL-YP-ETC-DLNR-2501-LGR014 | TIKONA PARK:ID | TG-LGR014A-1 | 19502942 | 990 | 320 | 241 | 0.98 | 1007 | 257 | 1050 | 366 | 1516 | 384 | 1597 | 511 | 2019-06-11 23:30 | 172.2 | 67.7 | 1622 | B | 87 | 108 | 105 | 21 |  | 0.5 | 16.7 | 82.8 |  |  |  |  | 59.57 | 10 | 10 | 12 | 634.47 | 540.48 | 529.28 | 607.15 | 20 | 141.26 | 130.49 | 94.59 |  | 22.3 | 25.3 | 0.3 | 714.44 | 5.16 | 0.62 | 1.02
28 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR014 | 1S-DL-YP-ETC-DLNR-2501-LGR014 | TIKONA PARK:ID | TG-LGR014A-2 | 19505669 | 990 | 200 | 244 | 0.98 | 865 | 241 | 1049 | 362 | 1591 | 262 | 1145 | 501 | 2019-06-30 23:30 | 202.4 | 39.2 | 1591 | Y | 92 | 109 | 98 | 17 | 0.2 | 0.1 | 4.7 | 95 | 1 |  |  |  | 257.3 | 156.04 | 156.04 | 185.53 | 445.24 | 511.5 | 511.2 | 513.01 | 0.3 | 31 | 1 | 6 | 0.3 | 6 | 0.3 |  | 704.54 | 15.06 | 0.54 | 0.87
29 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR014 | 1S-DL-YP-ETC-DLNR-2501-LGR014 | TIKONA PARK:ID | TG-LGR014A-4 | 19505750 | 630 | 200 | 244 | 0.97 | 505 | 232 | 949 | 134 | 545 | 139 | 561 | 396 | 2019-06-11 23:30 | 102.2 | 28.4 | 1106 | R | 130 | 88 | 82 | 48 | 0.1 | 0.5 | 48.4 | 51 |  | 7.56 | 22.23 |  | 134.19 | 426.11 | 426.11 | 341.37 | 476.41 | 270.23 | 221.24 | 362.23 | 83 |  |  | 0.3 | 10.3 |  |  |  | 704.3 | 15.3 | 0.54 | 0.8
30 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR018 | 1S-DL-YP-ETC-DLNR-2501-LGR018 | D BLOCK KHATTA VIKAS MARG:PL | TG-LGR018A-2 | 19504830 | 990 | 320 | 236 | 0.98 | 830 | 312 | 1363 | 283 | 1239 | 235 | 1038 | 284 | 2019-06-11 22:30 | 134.7 | 60.4 | 1480 | R | 114 | 97 | 90 | 24 |  |  | 47.1 | 52.9 |  |  |  |  | 1 | 10 | 10 | 6.3 | 524.1 | 686.37 | 697 | 706 | 193.5 | 22.53 |  | 7 | 0.3 |  |  |  | 719.3 | 0.3 | 0.75 | 0.84
31 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR019 | 1S-DL-YP-ETC-DLNR-2501-LGR019 | RAMESH PARK J & K BLOCK:PL | TG-LGR019A-1 | 19502336 | 1600 | 500 | 242 | 0.97 | 1286 | 421 | 1847 | 471 | 2103 | 393 | 1728 | 332 | 2019-06-01 | 203.6 | 88.6 | 2103 | Y | 95 | 114 | 91 | 23 |  | 0.9 | 93.3 | 5.8 |  |  | 1 |  | 269.27 | 83 | 83 | 202.57 | 450.09 | 604.17 | 391.09 | 516.09 |  | 32.19 |  | 0.3 |  |  |  |  | 719.36 | 0.24 | 0.6 | 0.8
32 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR020 | 1S-DL-YP-ETC-DLNR-2501-LGR020 | MASTER BLOCK SHAKARPUR:PL | TG-LGR020A-2 | 19505481 | 630 | 200 | 237 | 0.98 | 546 | 158 | 698 | 154 | 673 | 234 | 1044 | 359 | 2019-06-28 23:00 | 92.6 | 27 | 1099 | B | 94 | 94 | 113 | 19 | 0.3 | 1.1 | 27.4 | 71.2 |  | 3 |  |  | 212.52 | 249.22 | 249.22 | 169.52 | 376 | 332 | 416.52 | 405.3 |  | 4.3 | 53 | 13.3 |  |  | 9 |  | 696.11 | 23.49 | 0.57 | 0.87
33 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR022 | 1S-DL-YP-ETC-DLNR-2501-LGR022 | WB BLOCK SHAKARPUR:K | TG-LGR022A-2 | 19502950 | 990 | 320 | 241 | 0.97 | 984 | 348 | 1486 | 361 | 1563 | 274 | 1157 | 373 | 2019-06-30 23:30 | 160.4 | 57.4 | 1635 | Y | 96 | 112 | 92 | 20 |  | 2.4 | 57.5 | 40.1 |  |  |  |  | 154.27 | 40 | 40 | 95.27 | 475.47 | 528.14 | 543.17 | 530.17 | 85.3 | 124.3 | 31.3 | 92.3 | 2.3 | 25.3 |  |  | 718.14 | 1.46 | 0.57 | 0.99
34 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR022 | 1S-DL-YP-ETC-DLNR-2501-LGR022 | WB BLOCK SHAKARPUR:K | TG-LGR022A-4 | 19506276 | 630 | 200 | 242 | 0.98 | 639 | 187 | 800 | 213 | 908 | 240 | 1040 | 209 | 2019-06-03 00:30 | 142.8 | 10.6 | 1040 | B | 86 | 108 | 106 | 22 | 0.1 | 0.1 | 28.2 | 71.6 | 7 | 1.3 | 2.3 | 2.3 | 306.52 | 116.3 | 116.3 | 170 | 390.07 | 507.59 | 479.59 | 487.59 | 6.16 | 81.54 | 88.54 | 49.24 |  | 2.22 | 2.52 | 0.22 | 710.15 | 9.45 | 0.51 | 1.01
35 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR022 | 1S-DL-YP-ETC-DLNR-2501-LGR022 | WB BLOCK SHAKARPUR:K | TG-LGR022A-1 | 19506691 | 990 | 320 | 242 | 0.97 | 1031 | 336 | 1432 | 331 | 1384 | 363 | 1540 | 139 | 2019-06-30 23:00 | 207 | 60.8 | 1569 | R | 100 | 98 | 102 | 4 | 0.1 | 2.2 | 49.6 | 48.1 |  |  |  |  | 94 | 119.3 | 119.3 | 92.3 | 521.2 | 493.5 | 518.5 | 518.2 | 93 | 98 | 97 | 98.3 | 5 | 2 | 9.3 | 4 | 713.2 | 6.4 | 0.55 | 1.04
36 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR025 | 1S-DL-YP-ETC-DLNR-2501-LGR025 | DALL MILL SHAKARPUR:PM | TG-LGR025A-1 | 19502941 | 990 | 320 | 242 | 0.98 | 892 | 316 | 1331 | 264 | 1098 | 313 | 1310 | 223 | 2019-06-29 23:30 | 141.3 | 53 | 1417 | R | 115 | 82 | 103 | 33 |  |  | 55 | 45 |  |  |  |  | 6.3 | 226.27 | 226.27 | 41 | 587.45 | 491.48 | 609.15 | 641.45 | 125 | 1 | 73 | 36.3 |  |  |  |  | 719.15 | 0.45 | 0.63 | 0.9
37 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR026 | 1S-DL-YP-ETC-DLNR-2501-LGR026 | POLICE BOOTH S. PUR, V. MARG:PL | TG-LGR026A-1 | 19506000 | 990 | 320 | 238 | 0.98 | 843 | 263 | 1204 | 209 | 939 | 371 | 1723 | 691 | 2019-06-10 23:30 | 191.4 | 27.2 | 1742 | B | 108 | 79 | 113 | 34 | 0.7 | 12.1 | 75.2 | 11.9 |  | 4 | 0.3 | 1.3 | 10.3 | 158.3 | 158.3 | 17 | 640.54 | 548.49 | 579.54 | 677.19 | 59.55 |  | 116.55 | 15.3 |  |  | 4 |  | 711.19 | 8.41 | 0.7 | 0.85
38 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR027 | 1S-DL-YP-ETC-DLNR-2501-LGR027 | U BLOCK SHAKARPUR, V. MARG:PL | TG-LGR027A-2 | 19504762 | 990 | 320 | 243 | 0.98 | 840 | 310 | 1318 | 257 | 1111 | 273 | 1159 | 187 | 2019-06-29 16:00 | 170.8 | 43.4 | 1387 | R | 102 | 91 | 108 | 17 |  | 2.9 | 91.1 | 6.1 |  | 0.3 |  |  | 296.23 | 322.23 | 322.23 | 215.23 | 321.29 | 395.45 | 599.08 | 485.29 | 100.46 |  | 13.3 | 17.46 |  |  |  |  | 718.38 | 1.22 | 0.59 | 0.85
39 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR030 | 1S-DL-YP-ETC-DLNR-2501-LGR030 | BODH VIHAR LAXMI NAGAR:K | TG-LGR030A-1 | 19503402 | 990 | 320 | 238 | 0.98 | 815 | 229 | 1030 | 308 | 1413 | 278 | 1260 | 333 | 2019-06-01 | 159 | 45.6 | 1424 | Y | 88 | 115 | 98 | 27 |  | 0.5 | 34.6 | 64.9 | 3.3 |  |  |  | 318.51 | 102.3 | 102.3 | 202.24 | 396.03 | 532.37 | 496.32 | 511.32 |  | 83.17 | 2.28 | 4.28 |  |  |  |  | 718.24 | 1.36 | 0.6 | 0.82
40 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR030 | 1S-DL-YP-ETC-DLNR-2501-LGR030 | BODH VIHAR LAXMI NAGAR:K | TG-LGR030A-2 | 19504644 | 630 | 200 | 244 | 0.97 | 580 | 189 | 766 | 215 | 884 | 175 | 719 | 148 | 2019-06-05 03:30 | 122.8 | 32.2 | 973 | Y | 95 | 110 | 95 | 15 |  | 0.6 | 51.8 | 47.6 |  |  |  |  | 177.57 | 101.3 | 101.3 | 136.3 | 514.52 | 510.37 | 544.25 | 540.53 | 25.35 | 103.47 | 9.3 | 41.01 |  | 2.3 |  |  | 718.24 | 1.36 | 0.58 | 0.92
41 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR031 | 1S-DL-YP-ETC-DLNR-2501-LGR031 | MANGAL BAZAR LAXMI NAGAR:PL | TG-LGR031A-3 | 19506025 | 990 | 320 | 249 | 0.97 | 830 | 319 | 1367 | 256 | 1094 | 255 | 1098 | 271 | 2019-06-10 23:30 | 191 | 57.6 | 1537 | R | 110 | 95 | 95 | 15 | 0.3 |  | 3.6 | 96.1 |  |  |  |  | 115.21 | 236.09 | 236.09 | 186.39 | 554.55 | 480.37 | 469.37 | 525.07 | 46.3 | 0.3 | 3.3 | 5.3 | 0.3 |  |  |  | 717.16 | 2.44 | 0.59 | 0.84
42 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR032 | 1S-DL-YP-ETC-DLNR-2501-LGR032 | KULDEEP NURSING HOME LNG:K | TG-LGR032A-1 | 19502461 | 990 | 320 | 244 | 0.97 | 902 | 287 | 1171 | 298 | 1227 | 318 | 1304 | 116 | 2019-06-11 21:30 | 171.5 | 56.7 | 1344 | B | 93 | 102 | 105 | 12 |  | 0.3 | 22.1 | 77.7 |  |  |  |  | 110.23 | 91.01 | 91.01 | 91.01 | 592.55 | 564.47 | 554.23 | 576.47 | 10 | 57.3 | 82.43 | 45.3 |  |  |  |  | 713.18 | 6.42 | 0.62 | 0.91
43 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR032 | 1S-DL-YP-ETC-DLNR-2501-LGR032 | KULDEEP NURSING HOME LNG:K | TG-LGR032A-2 | 19502463 | 990 | 320 | 245 | 0.98 | 917 | 310 | 1253 | 284 | 1148 | 323 | 1315 | 146 | 2019-06-12 00:30 | 153.1 | 36.8 | 1355 | R | 102 | 97 | 101 | 5 |  | 0.1 | 14.6 | 85.3 |  |  |  |  | 169.55 | 205 | 205 | 191.25 | 491.18 | 498.3 | 447.35 | 484.05 | 58 | 15.43 | 60.43 | 43.43 |  |  |  |  | 719.13 | 0.47 | 0.55 | 0.93
44 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR034 | 1S-DL-YP-ETC-DLNR-2501-LGR034 | MOHAN PARK LAXMI NAGAR:K | TG-LGR034A-1 | 19502470 | 990 | 320 | 239 | 0.98 | 910 | 305 | 1298 | 293 | 1254 | 312 | 1330 | 66 | 2019-06-11 19:30 | 155.3 | 53 | 1413 | B | 97 | 95 | 108 | 13 |  |  | 17.8 | 82.2 |  |  |  |  | 11 | 19.3 | 19.3 | 7.3 | 660.42 | 667.42 | 600.17 | 659.58 | 46 | 30.3 | 111.55 | 50.14 |  |  |  |  | 717.42 | 2.18 | 0.68 | 0.92
45 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR035 | 1S-DL-YP-ETC-DLNR-2501-LGR035 | N.GANESH NAGAR SHAKARPUR:PL | TG-LGR035A-1 | 19502820 | 630 | 200 | 229 | 0.98 | 563 | 151 | 668 | 205 | 922 | 208 | 917 | 251 | 2019-06-30 | 84.2 | 23.5 | 1027 | B | 81 | 109 | 110 | 29 |  | 1.8 | 62 | 36.2 | 5.59 |  | 3 | 1 | 340.36 | 94 | 94 | 151.21 | 372 | 551.35 | 512.35 | 530.44 |  | 73 | 95.3 | 35.3 |  |  | 6.3 |  | 718.35 | 1.25 | 0.59 | 0.89
46 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR036 | 1S-DL-YP-ETC-DLNR-2501-LGR036 | SHIROMANI SCHOOL, SHAKARPUR:PL | TG-LGR036A-1 | 19506252 | 990 | 320 | 240 | 0.95 | 1033 | 357 | 1551 | 242 | 1048 | 433 | 1908 | 748 | 2019-06-30 23:30 | 327 | 83.8 | 1908 | B | 101 | 84 | 115 | 31 | 0.1 | 0.1 | 25.5 | 74.3 | 5.09 | 5.3 |  |  | 179.45 | 276.5 | 276.5 | 128.2 | 407.09 | 410.42 | 524.24 | 496.43 | 92.59 | 2.3 | 119.59 | 69.59 | 10.3 |  | 22 | 0.3 | 695.32 | 24.28 | 0.52 | 1.04
47 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR041 | 1S-DL-YP-ETC-DLNR-2501-LGR041 | KUNDAN NAGAR, LAXMI NAGAR:K | TG-LGR041A-1 | 19505457 | 990 | 320 | 236 | 0.98 | 1052 | 348 | 1512 | 313 | 1354 | 391 | 1710 | 308 | 2019-06-11 01:00 | 202.6 | 64.6 | 1729 | R | 101 | 87 | 112 | 25 | 0.2 |  | 14 | 85.7 |  |  |  |  | 35.3 | 100.03 | 100.03 | 37.3 | 513.24 | 515.07 | 479.54 | 519.54 | 76.31 | 11.15 | 106.46 | 68.31 | 1 |  | 21.45 | 0.3 | 626.25 | 45.35 | 0.55 | 1.06
48 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR042 | 1S-DL-YP-ETC-DLNR-2501-LGR042 | V. SAVARKAR BLOCK, SHAKARPUR:PL | TG-LGR042A-1 | 19506382 | 990 | 320 | 244 | 0.98 | 975 | 304 | 1266 | 339 | 1415 | 332 | 1401 | 143 | 2019-06-10 15:00 | 267.5 | 14.1 | 2020 | Y | 98 | 115 | 86 | 29 | 0.4 |  | 15.9 | 83.7 | 372.52 | 357.52 | 413.52 | 374.52 | 103.57 | 104.57 | 104.57 | 103.27 | 169.47 | 113.53 | 211.29 | 186.04 | 62.4 | 124.33 | 0.3 | 45.22 | 0.29 | 8.3 | 0.3 |  | 709.45 | 10.15 | 0.34 | 0.98
49 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR049 | 1S-DL-YP-ETC-DLNR-2501-LGR049 | R BLOCK SHAKARPUR:PL | TG-LGR049A-2 | 19504448 | 630 | 200 | 231 | 0.98 | 544 | 205 | 896 | 205 | 891 | 134 | 578 | 315 | 2019-06-29 23:30 | 91.5 | 33.6 | 928 | B | 102 | 105 | 93 | 12 |  | 0.3 | 30.9 | 68.7 |  |  |  |  | 16.3 | 4.3 | 4.3 | 15 | 659.5 | 657.24 | 520.2 | 697.5 | 43.24 | 57.5 | 44.54 | 6.54 |  |  |  |  | 719.44 | 0.16 | 0.69 | 0.86
50 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR052 | 1S-DL-YP-ETC-DLNR-2501-LGR052 | RAMESH PARK, G NO.12, LN:PL | TG-LGR052A-1 | 19504589 | 990 | 320 | 235 | 0.98 | 903 | 283 | 1203 | 368 | 1576 | 253 | 1085 | 444 | 2019-06-30 00:30 | 159 | 64 | 1576 | Y | 103 | 108 | 89 | 19 |  |  | 1.2 | 98.8 |  |  |  |  | 22.3 | 15.3 | 15.3 | 28.3 | 642.2 | 580.33 | 622.06 | 642.03 | 52.13 | 118 | 2.3 | 48.3 | 2 | 5 |  |  | 719.03 | 0.57 | 0.65 | 0.91
51 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR054 | 1S-DL-YP-ETC-DLNR-2501-LGR054 | KISHAN KUNJ ENTN.:PL | TG-LGR054A-2 | 19506147 | 630 | 200 | 240 | 0.97 | 579 | 164 | 710 | 208 | 987 | 208 | 949 | 260 | 2019-06-11 01:00 | 127 | 34.2 | 995 | B | 99 | 81 | 120 | 39 | 0.3 | 0.1 | 11.6 | 88 |  | 5.3 |  |  | 179.23 | 328.52 | 328.52 | 131.53 | 504.52 | 384.53 | 557.15 | 565.52 | 35.3 | 0.3 | 123.3 | 22 |  |  | 10 |  | 719.45 | 0.15 | 0.57 | 0.92
52 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR084 | 1S-DL-YP-ETC-DLNR-2501-LGR084 | WEST GURU ANGAD NAGER GALI NO-2 | TG-LGR084A-1 | 19502464 | 990 | 320 | 246 | 0.97 | 904 | 329 | 1359 | 268 | 1114 | 307 | 1271 | 215 | 2019-06-12 | 151.6 | 58.1 | 1420 | R | 114 | 91 | 94 | 23 |  |  | 9.6 | 90.4 |  |  |  |  | 46 | 231.3 | 231.3 | 158 | 573.04 | 485.04 | 449.04 | 531.34 | 99 | 2.3 | 20.3 | 29.3 | 1 |  |  |  | 719.04 | 0.56 | 0.57 | 0.91
53 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR090 | 1S-DL-YP-ETC-DLNR-2501-LGR090 | SCHOOL BLOCK,PARK WALA S/S NEAR MANDIR | TG-LGR090A-2 | 19503652 | 630 | 200 | 245 | 0.97 | 617 | 188 | 769 | 186 | 755 | 244 | 996 | 234 | 2019-06-03 | 118.2 | 46 | 996 | B | 89 | 103 | 108 | 19 |  | 2.8 | 35.9 | 61.3 | 0.3 | 0.3 | 0.3 | 0.3 | 59 | 9.3 | 9.3 | 12 | 638.13 | 596.43 | 548.52 | 635.13 | 21.21 | 112.21 | 140.51 | 71.21 |  |  | 23.21 |  | 719.04 | 0.56 | 0.65 | 0.98
54 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR090 | 1S-DL-YP-ETC-DLNR-2501-LGR090 | SCHOOL BLOCK,PARK WALA S/S NEAR MANDIR | TG-LGR090A-1 | 19504463 | 990 | 320 | 247 | 0.98 | 968 | 321 | 1329 | 295 | 1221 | 353 | 1462 | 209 | 2019-06-10 13:00 | 163.4 | 50 | 1510 | B | 103 | 96 | 100 | 7 |  |  | 22.5 | 77.5 |  |  |  |  | 63 | 152.27 | 152.27 | 112.55 | 547.36 | 497.09 | 467.14 | 501.11 | 108 | 69.3 | 112 | 105 | 0.3 |  | 6 |  | 719.06 | 0.54 | 0.57 | 0.98
55 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR093 | 1S-DL-YP-ETC-DLNR-2501-LGR093 | SURANA DHARAMSHALA S/S | TG-LGR093A-2 | 19506459 | 990 | 320 | 238 | 0.98 | 828 | 249 | 1062 | 271 | 1161 | 308 | 1347 | 251 | 2019-06-30 23:30 | 175 | 33 | 1441 | Y | 97 | 105 | 98 | 8 | 0.1 | 4.1 | 59.3 | 36.5 | 0.3 |  | 1 | 0.3 | 113.3 | 122.3 | 122.3 | 108.3 | 600.14 | 540.14 | 556.14 | 603.44 |  | 51.3 | 7 | 1.3 |  |  |  |  | 714.14 | 5.46 | 0.6 | 0.84
56 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR097 | 1S-DL-YP-ETC-DLNR-2501-LGR097 | A BLK P,D.VIHAR PARK NR. O/H WATER TANK | TG-LGR097A-1 | 19505222 | 630 | 200 | 246 | 0.98 | 550 | 205 | 833 | 135 | 544 | 211 | 857 | 302 | 2019-06-11 23:30 | 186.6 | 31 | 1240 | B | 108 | 82 | 109 | 27 | 0.3 | 0.1 | 23.7 | 75.8 |  |  |  |  | 18.32 | 127.53 | 127.53 | 30.32 | 567.58 | 565.44 | 537 | 636.27 | 107.37 | 0.3 | 125.57 | 27.08 |  |  | 3.08 |  | 694.07 | 25.53 | 0.68 | 0.87
57 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR101 | 1S-DL-YP-ETC-DLNR-2501-LGR101 | VEER SAVARKAR BLOCK VIKAS MARG | TG-LGR101A-1 | 19504960 | 990 | 320 | 225 | 0.98 | 907 | 235 | 1071 | 328 | 1506 | 344 | 1597 | 487 | 2019-06-27 14:00 | 131 | 9.6 | 1597 | B | 88 | 101 | 112 | 24 |  | 0.3 | 36.5 | 63.2 | 358.3 | 369.3 | 361.3 | 362 | 137.3 | 103.3 | 103.3 | 116.3 | 220.24 | 159.11 | 132.2 | 207.35 |  | 84.13 | 114.34 | 30.19 |  |  | 1 |  | 716.24 | 3.36 | 0.37 | 0.92
58 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR103 | 1S-DL-YP-ETC-DLNR-2501-LGR103 | NEW WB BLOCK (NEAR AGGARWAL SWEETS) | TG-LGR103A-1 | 19505891 | 990 | 320 | 243 | 0.98 | 910 | 281 | 1163 | 314 | 1318 | 314 | 1307 | 150 | 2019-06-30 | 190.4 | 75.5 | 1472 | Y | 94 | 108 | 98 | 14 | 0.1 |  | 37.2 | 62.6 |  |  |  |  | 19.3 | 6 | 6 | 11 | 695.08 | 582.42 | 661.5 | 660.42 | 5 | 127.56 | 46.18 | 47.56 |  | 3 |  |  | 719.38 | 0.22 | 0.69 | 0.92
59 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR108 | 1S-DL-YP-ETC-DLNR-2501-LGR108 | COMMUNITY CENTER SHAKARPUR | TG-LGR108A-1 | 19505626 | 630 | 200 | 246 | 0.97 | 533 | 185 | 781 | 190 | 801 | 158 | 659 | 133 | 2019-06-30 23:30 | 139.2 | 28.2 | 982 | Y | 94 | 109 | 96 | 15 | 0.1 | 0.1 | 8 | 91.8 |  |  |  |  | 203 | 78 | 78 | 146.3 | 508.35 | 587.22 | 494.06 | 558.35 | 1.3 | 47.13 | 3.59 | 8 |  | 0.3 |  |  | 713.05 | 6.55 | 0.6 | 0.85
60 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | PVR008 | 1S-DL-YP-ETC-DLNR-2502-PVR008 | DDA FLAT NIRMAN VIHAR:ID | TG-PVR008A-2 | 19504486 | 990 | 320 | 234 | 0.98 | 857 | 282 | 1257 | 270 | 1195 | 305 | 1356 | 141 | 2019-06-11 23:30 | 136.9 | 39 | 1384 | B | 106 | 91 | 103 | 15 |  |  | 7.9 | 92.1 |  |  |  |  | 65 | 199 | 199 | 110 | 606.23 | 517.53 | 550.23 | 587.53 | 48.3 | 3 | 53 | 22 |  |  |  |  | 719.53 | 0.07 | 0.61 | 0.87
61 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN006 | 1S-DL-YP-ETC-DLNR-2503-MAN006 | PANDAV NAGAR D PARK:K | TG-MAN006A-2 | 19501944 | 990 | 320 | 242 | 0.97 | 965 | 324 | 1357 | 345 | 1439 | 296 | 1224 | 188 | 2019-06-05 00:30 | 211.2 | 78 | 1537 | Y | 96 | 107 | 97 | 11 |  | 0.1 | 38 | 61.9 |  |  |  |  | 55 | 21.3 | 21.3 | 31 | 587.58 | 572.43 | 631.13 | 607.43 | 73.38 | 118.56 | 52.23 | 77.53 |  | 3.27 |  |  | 716.36 | 3.24 | 0.63 | 0.97
62 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN006 | 1S-DL-YP-ETC-DLNR-2503-MAN006 | PANDAV NAGAR D PARK:K | TG-MAN006A-3 | 19505981 | 990 | 320 | 238 | 0.98 | 917 | 297 | 1366 | 349 | 1604 | 271 | 1250 | 312 | 2019-06-07 23:30 | 186.9 | 59.5 | 1604 | Y | 96 | 110 | 94 | 16 | 0.2 |  | 23.6 | 76.1 |  |  |  |  | 109.3 | 48 | 48 | 76 | 577.52 | 564.24 | 570.59 | 590.52 | 29.09 | 97.25 | 22.32 | 49.39 |  | 6.42 |  |  | 716.31 | 3.29 | 0.6 | 0.93
63 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN007 | 1S-DL-YP-ETC-DLNR-2503-MAN007 | PANDAV NAGAR S BLOCK:ID | TG-MAN007A-1 | 19501803 | 990 | 320 | 235 | 0.97 | 874 | 274 | 1152 | 287 | 1212 | 314 | 1319 | 146 | 2019-06-06 03:00 | 192.1 | 56.7 | 1505 | B | 95 | 92 | 112 | 20 |  |  | 10.2 | 89.8 |  |  |  |  | 207.23 | 249.53 | 249.53 | 154.57 | 502.21 | 457.21 | 566.33 | 536.17 | 7.55 | 10.25 | 90.09 | 26.25 |  |  |  |  | 717.39 | 2.21 | 0.59 | 0.88
64 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN021 | 1S-DL-YP-ETC-DLNR-2503-MAN021 | MANDAWALI SUBJI MANDI:PL | TG-MAN021A-1 | 19504821 | 990 | 320 | 243 | 0.97 | 939 | 324 | 1402 | 301 | 1309 | 315 | 1369 | 81 | 2019-06-30 23:00 | 159.7 | 68.4 | 1487 | R | 107 | 96 | 98 | 11 |  |  | 1.2 | 98.8 |  |  | 0.3 |  | 14 | 83.5 | 83.5 | 38 | 620.51 | 603.01 | 616.3 | 633.51 | 81.3 | 32.3 | 39.3 | 47.3 | 3 |  |  |  | 719.21 | 0.39 | 0.61 | 0.95
65 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN021 | 1S-DL-YP-ETC-DLNR-2503-MAN021 | MANDAWALI TRY POLE:PM | TG-MAN021A-2 | 19504828 | 990 | 320 | 244 | 0.97 | 1069 | 345 | 1485 | 370 | 1589 | 354 | 1523 | 91 | 2019-06-29 23:00 | 208.3 | 62.6 | 1617 | Y | 98 | 102 | 100 | 4 |  |  | 1.4 | 98.6 |  |  |  |  | 9 | 3.3 | 3.3 | 4 | 590.21 | 553.53 | 565.53 | 570.53 | 114.3 | 148.28 | 145.28 | 139.28 | 4.3 | 12.3 | 4 | 4 | 718.21 | 1.39 | 0.63 | 1.08
66 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN023 | 1S-DL-YP-ETC-DLNR-2503-MAN023 | UTTARY SCHOOL BLOCK:K | TG-MAN023A-3 | 19504321 | 630 | 200 | 236 | 0.97 | 609 | 222 | 965 | 215 | 937 | 171 | 742 | 210 | 2019-06-30 23:00 | 123.3 | 29.4 | 974 | R | 107 | 101 | 92 | 15 | 0.2 | 0.1 | 2.1 | 97.6 |  | 0.3 | 0.3 | 0.3 | 16.3 | 12.3 | 12.3 | 15 | 397.17 | 468.47 | 494.17 | 462.47 | 120.5 | 67.23 | 18.53 | 72.23 | 16.03 | 1.3 |  |  | 716.58 | 3.02 | 0.63 | 0.97
67 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN024 | 1S-DL-YP-ETC-DLNR-2503-MAN024 | CHANDERVIHAR SS-1:ID | TG-MAN024A-2 | 19500076 | 990 | 320 | 243 | 0.97 | 1018 | 354 | 1525 | 325 | 1403 | 339 | 1461 | 105 | 2019-06-29 23:00 | 211.2 | 77.3 | 1538 | R | 99 | 100 | 101 | 2 | 0.1 | 0.1 | 2.6 | 97.2 |  |  |  |  | 94.3 | 101.29 | 101.29 | 80.3 | 543.56 | 522.27 | 590.26 | 556.26 | 77.3 | 93.3 | 72 | 81 | 4 | 2.3 | 0.3 | 2 | 719.56 | 0.04 | 0.56 | 1.03
68 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN026 | 1S-DL-YP-ETC-DLNR-2503-MAN026 | WESTVINOD NAGAR NEAR MANGLAM:PL | TG-MAN026A-1 | 19506612 | 990 | 320 | 238 | 0.97 | 943 | 293 | 1232 | 330 | 1392 | 319 | 1345 | 142 | 2019-06-02 23:30 | 256.3 | 50.2 | 1456 | Y | 94 | 108 | 99 | 14 | 0.1 | 0.1 | 0.7 | 99.2 | 3.3 |  |  |  | 337.57 | 226.55 | 226.55 | 282.54 | 343.03 | 418.39 | 371.55 | 386.36 | 18 | 54.26 | 30.3 | 33 |  | 2.3 | 0.3 |  | 702.3 | 17.3 | 0.5 | 0.95
69 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN030 | 1S-DL-YP-ETC-DLNR-2503-MAN030 | E BLOCK WESTVINOD NAGAR:ID | TG-MAN030A-2 | 19505463 | 990 | 320 | 241 | 0.97 | 927 | 272 | 1197 | 353 | 1559 | 301 | 1321 | 319 | 2019-06-26 23:00 | 347.5 | 81 | 1587 | Y | 92 | 111 | 97 | 19 | 0.1 | 0.1 | 0.1 | 99.7 |  |  |  |  | 98.44 | 20.14 | 20.14 | 37.44 | 604.01 | 563.24 | 643.01 | 628.01 | 14.26 | 128.37 | 26.56 | 51.26 |  | 4.56 |  |  | 717.11 | 2.49 | 0.63 | 0.94
70 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN034 | 1S-DL-YP-ETC-DLNR-2503-MAN034 | C BLOCK WESTVINOD NAGAR:PL | TG-MAN034A-1 | 19505260 | 990 | 320 | 244 | 0.96 | 1068 | 368 | 1536 | 326 | 1358 | 374 | 1573 | 200 | 2019-06-26 23:30 | 273.3 | 54.7 | 1650 | B | 100 | 94 | 106 | 12 | 0.1 | 0.1 | 2.3 | 97.5 |  |  |  |  | 79 | 95 | 95 | 55 | 504.42 | 542.12 | 542.11 | 539.12 | 113.3 | 68.21 | 116.01 | 107 | 8.21 |  | 18.51 | 4.21 | 705.33 | 14.27 | 0.56 | 1.08
71 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN034 | 1S-DL-YP-ETC-DLNR-2503-MAN034 | C BLOCK WESTVINOD NAGAR:PL | TG-MAN034A-2 | 19506137 | 630 | 200 | 257 | 0.96 | 669 | 150 | 595 | 245 | 980 | 275 | 1121 | 472 | 2019-06-26 23:00 | 209.6 | 32.6 | 1134 | B | 100 | 88 | 112 | 24 | 0.1 | 1 | 0.8 | 98.1 | 2.3 | 9.3 | 2.3 | 2.3 | 275.26 | 342.11 | 342.11 | 290.11 | 248.44 | 174.59 | 246.18 | 229.03 | 0.3 |  | 30 | 4.56 |  | 0.3 | 6.56 | 0.3 | 527.1 | 0.5 | 0.39 | 1.06
72 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN039 | 1S-DL-YP-ETC-DLNR-2503-MAN039 | ALLAH COLONY MANDAWALI:PL | TG-MAN039A-1 | 19506415 | 630 | 200 | 244 | 0.96 | 616 | 194 | 840 | 212 | 923 | 210 | 913 | 78 | 2019-06-29 23:30 | 185.2 | 47.2 | 923 | Y | 99 | 103 | 97 | 6 | 0.1 | 0.4 | 5.9 | 93.6 |  |  |  |  | 53 | 47.3 | 47.3 | 54.3 | 619.06 | 601.36 | 558.36 | 613.06 | 24 | 46 | 23.3 | 28.3 |  | 1 | 0.3 |  | 696.06 | 23.54 | 0.57 | 0.98
73 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN059 | 1S-DL-YP-ETC-DLNR-2503-MAN059 | S/STN.NO-2, PPG CGHS:ID | TG-MAN059A-1 | 19501860 | 630 | 200 | 233 | 0.98 | 635 | 225 | 1040 | 202 | 918 | 208 | 947 | 110 | 2019-06-30 23:00 | 112.2 | 41.9 | 1059 | R | 100 | 95 | 105 | 10 |  | 2 | 26.3 | 71.7 |  |  |  |  | 12.3 | 31.3 | 31.3 | 8 | 609.25 | 603.26 | 594.25 | 623.49 | 91.31 | 81.19 | 120.2 | 84.37 | 3.19 | 0.3 |  | 0.19 | 716.45 | 3.15 | 0.63 | 1.01
74 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN247 | 1S-DL-YP-ETC-DLNR-2503-MAN247 | BUDHA MARG MANDAWALI | TG-MAN247A-1 | 19504474 | 990 | 320 | 235 | 0.97 | 951 | 348 | 1536 | 321 | 1422 | 282 | 1250 | 250 | 2019-06-30 23:30 | 162.7 | 30.9 | 1536 | R | 144 | 133 | 23 | 121 | 0.7 | 0.1 | 11.1 | 88.2 |  |  | 607.39 | 2.46 | 88.4 | 98.48 | 98.48 | 396.14 | 542.12 | 590.49 | 97 | 298.07 | 84.15 | 27.3 | 12 | 20 | 2 |  |  |  | 717.07 | 2.53 | 0.42 | 0.96
75 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN273 | 1S-DL-YP-ETC-DLNR-2503-MAN273 | Ew S/S D-Blk Ramleela Ground Pandav Ngr | TG-MAN273A-1 | 19504634 | 990 | 200 | 231 | 0.98 | 904 | 321 | 1476 | 262 | 1200 | 321 | 1461 | 269 | 2019-06-30 23:30 | 130.6 | 46 | 1509 | B | 105 | 88 | 107 | 19 |  | 0.3 | 21.7 | 78 |  |  |  |  | 145.58 | 257.47 | 257.47 | 162.28 | 500.45 | 460.3 | 515.15 | 516.37 | 71.34 |  | 89.34 | 39.12 |  |  | 0.3 |  | 718.17 | 1.43 | 0.57 | 0.91
76 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN274 | 1S-DL-YP-ETC-DLNR-2503-MAN274 | Gnpn Complex, Rob-36 Pandav Nagar | TG-MAN274A-1 | 19504788 | 630 | 200 | 234 | 0.98 | 652 | 225 | 1017 | 211 | 947 | 217 | 973 | 61 | 2019-06-07 23:00 | 106.3 | 35.9 | 1051 | R | 102 | 100 | 98 | 4 |  |  | 4 | 96 |  |  |  |  | 25 | 16.3 | 16.3 | 30 | 557.54 | 592.41 | 544.41 | 569.49 | 123.43 | 105.26 | 106.43 | 114.48 | 11.47 | 3.47 | 7.3 | 3.47 | 718.24 | 1.36 | 0.59 | 1.04
77 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN296 | 1S-DL-YP-ETC-DLNR-2503-MAN296 | SOUTH GANESH NAGAR (NEAR RAILWAY LINE) | TG-MAN296A-1 | 19505316 | 630 | 200 | 236 | 0.97 | 628 | 211 | 935 | 205 | 915 | 211 | 936 | 21 | 2019-06-29 23:30 | 115.2 | 42.8 | 936 | B | 97 | 98 | 105 | 8 | 0.1 | 0.1 | 17.3 | 82.5 |  |  |  |  | 59.45 | 57.15 | 57.15 | 41.3 | 513.24 | 489.54 | 476.09 | 506.39 | 25.21 | 51.35 | 90.21 | 50.35 | 0.14 |  | 0.14 |  | 598.44 | 25.16 | 0.58 | 1
78 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR001 | 1S-DL-YP-ETC-DLNR-2502-PVR001 | G-II, PREET VIHAR:ID | TG-PVR001A-1 | 19503221 | 630 | 200 | 239 | 0.98 | 738 | 228 | 945 | 275 | 1145 | 235 | 975 | 187 | 2019-06-06 00:30 | 132.9 | 27.6 | 1145 | Y | 93 | 105 | 102 | 12 |  |  | 8.5 | 91.5 |  |  |  |  | 132.26 | 83.15 | 83.15 | 84.56 | 511.53 | 493.58 | 515.21 | 528.17 | 45.28 | 91.18 | 76.36 | 70.29 | 1.42 | 22.58 | 14.1 | 7.47 | 691.29 | 4.31 | 0.49 | 1.17
79 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR006 | 1S-DL-YP-ETC-DLNR-2502-PVR006 | B BLOCK, PREET VIHAR:ID | TG-PVR006A-2 | 19501150 | 630 | 200 | 232 | 0.97 | 487 | 172 | 769 | 118 | 519 | 197 | 882 | 322 | 2019-06-10 23:30 | 127 | 25.3 | 952 | B | 101 | 92 | 108 | 16 |  | 0.1 | 15.6 | 84.2 |  |  |  |  | 52.3 | 66.5 | 66.5 | 25.3 | 655.49 | 652.29 | 675.26 | 693.49 | 11 |  | 35.23 | [5 empty] | 719.19 | 0.41 | 0.72 | 0.77
80 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR009 | 1S-DL-YP-ETC-DLNR-2502-PVR009 | EAST GURU ANGAD NAGAR:K | TG-PVR009A-3 | 19504811 | 990 | 320 | 238 | 0.97 | 1096 | 325 | 1429 | 401 | 1769 | 370 | 1623 | 295 | 2019-06-03 | 196.5 | 81 | 1769 | Y | 90 | 104 | 105 | 15 |  |  | 0.8 | 99.2 |  |  |  |  | 61 | 22.3 | 22.3 | 17 | 617.59 | 536.51 | 580.26 | 587.26 | 39.06 | 129.05 | 119.43 | 110.39 |  | 29.39 | 12.26 | 3 | 718.05 | 1.55 | 0.57 | 1.11
81 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR015 | 1S-DL-YP-ETC-DLNR-2502-PVR015 | G-I, PREET VIHAR:ID | TG-PVR015A-2 | 19506821 | 990 | 320 | 249 | 0.97 | 884 | 301 | 1289 | 296 | 1277 | 287 | 1224 | 60 | 2019-06-01 15:30 | 245.8 | 59.8 | 1409 | Y | 108 | 100 | 92 | 16 | 0.4 | 0.1 | 2.8 | 96.7 |  |  |  |  | 22 | 49.3 | 49.3 | 34.3 | 567.47 | 598.46 | 613.46 | 619.46 | 112.29 | 54 | 10.3 | 48 |  |  |  |  | 702.16 | 17.44 | 0.68 | 0.89
82 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR018 | 1S-DL-YP-ETC-DLNR-2502-PVR018 | C-BLOCK, PREET VIHAR:ID | TG-PVR018A-1 | 19501148 | 630 | 200 | 242 | 0.97 | 618 | 194 | 838 | 236 | 1029 | 188 | 811 | 206 | 2019-06-02 14:00 | 145.8 | 44.2 | 1029 | Y | 102 | 96 | 103 | 7 |  |  | 2 | 98 |  |  |  |  | 3 | 14.3 | 14.3 | 4 | 657.47 | 658.17 | 652.17 | 671.17 | 33.3 | 21 | 37 | 19.3 | 0.3 | 1 |  |  | 694.47 | 1.13 | 0.64 | 0.98
83 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR019 | 1S-DL-YP-ETC-DLNR-2502-PVR019 | NIRMAN VIHAR (NEAR MKT.):ID | TG-PVR019A-1 | 19504881 | 990 | 320 | 240 | 0.98 | 802 | 225 | 970 | 272 | 1150 | 306 | 1342 | 322 | 2019-06-11 23:30 | 140.6 | 49.3 | 1369 | B | 97 | 98 | 105 | 8 | 100 | [7 empty] | 231.04 | 216.04 | 216.04 | 200.04 | 482.3 | 498.25 | 463 | 517.55 | 4.55 | 4 | 47 | 0.3 |  |  |  |  | 718.29 | 1.31 | 0.6 | 0.81
84 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR026 | 1S-DL-YP-ETC-DLNR-2502-PVR026 | B-BLOCK, PREET VIHAR, NEAR MKT.:ID | TG-PVR026A-1 | 19503229 | 630 | 200 | 243 | 0.97 | 523 | 180 | 774 | 191 | 823 | 152 | 646 | 158 | 2019-06-30 23:00 | 107.6 | 33.6 | 837 | Y | 114 | 107 | 79 | 35 | 3.3 | 6.7 | 56.6 | 33.4 |  |  | 3.3 |  | 49 | 96.58 | 96.58 | 128 | 636 | 603.02 | 316.53 | 588 | 34.23 | 19.23 |  | 3.23 |  |  |  |  | 719.23 | 0.37 | 0.61 | 0.83
85 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR067 | 1S-DL-YP-ETC-DLNR-2502-PVR067 | SWASTHYA VIHAR KIOSK VIKAS MARG | TG-PVR067A-2 | 19504801 | 630 | 200 | 250 | 0.99 | 499 | 198 | 783 | 124 | 485 | 177 | 683 | 263 | 2019-06-12 17:00 | 94.3 | -12.4 | 819 | R | 113 | 85 | 102 | 28 | 0.1 | 25.6 | 73.7 | 0.6 | 17 | 168 | 113.21 | 64.3 | 360.06 | 281.3 | 281.3 | 325.36 | 266.49 | 269.1 | 311.04 | 328.34 | 74.45 |  | 22 | [5 empty] | 718.4 | 1.2 | 0.51 | 0.79
86 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR068 | 1S-DL-YP-ETC-DLNR-2502-PVR068 | CHITRA VIHAR:ID | TG-PVR068A-2 | 19503203 | 630 | 200 | 249 | 0.97 | 567 | 238 | 1081 | 199 | 884 | 130 | 573 | 444 | 2019-06-02 22:30 | 106.7 | 24.8 | 1081 | R | 120 | 98 | 83 | 37 | 0.1 | 2.6 | 62 | 35.3 |  | 1 | 3 |  | 103.3 | 243 | 243 | 195 | 490.38 | 435.45 | 389.22 | 495.48 | 102.34 | 38.14 |  | 27.11 | 21.17 |  |  |  | 717.59 | 2.01 | 0.56 | 0.9
87 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR082 | 1S-DL-YP-ETC-DLNR-2502-PVR082 | E-BLK PREET VIHAR(NEAR E-95 PREET VIHAR) | TG-PVR082A-1 | 19503740 | 630 | 200 | 231 | 0.98 | 583 | 159 | 690 | 180 | 783 | 244 | 1070 | 343 | 2019-06-12 | 110.4 | 27.1 | 1070 | B | 94 | 87 | 119 | 32 |  | 0.6 | 19 | 80.4 |  | 3.3 |  |  | 182.55 | 265.05 | 265.05 | 128.25 | 502.29 | 420.19 | 533.01 | 537.06 | 10 | 6.3 | 127 | 29.53 |  |  | 11.23 |  | 695.24 | 0.36 | 0.57 | 0.93

## Loading Condition > 100%
MIS Report of Distribution Transformer - Jun19
Jun19 1230 LAXMI NAGAR (Loading Condition > 100% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN054 | 1S-DL-YP-ETC-DLNR-2503-MAN054 | GAZIPUR VILLAGE NEAR SCHOOL:PL | TG-MAN054A-1 | 19502869 | 990 | 320 | 249 | 0.97 | 991 | 371 | 1488 | 285 | 1232 | 336 | 1415 | 228 | 2019-06-13 15:00 | 295.9 | 70.7 | 1524 | R | 107 | 94 | 99 | 13 | 17.3 | 25.1 | 42.1 | 15.5 | [8 empty] | 289.27 | 598.36 | 446.1 | 430.51 | 393.27 | 117.18 | 268.14 | 284.33 | 33 |  | 1.3 | 0.3 | 715.54 | 4.06 | 0.77 | 1
2 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN066 | 1S-DL-YP-ETC-DLNR-2503-MAN066 | S/STN.NO-9, PPG CGHS:ID | TG-MAN066A-2 | 19506561 | 630 | 200 | 244 | 0.96 | 791 | 245 | 1039 | 259 | 1103 | 288 | 1219 | 158 | 2019-06-30 23:30 | 220.6 | 51.8 | 1219 | B | 93 | 103 | 103 | 10 | 0.1 | 0.2 | 5.8 | 93.8 |  |  |  |  | 20 | 2 | 2 | 6.3 | 520 | 480.29 | 467 | 502 | 147.26 | 170.57 | 147.56 | 149.56 | 26.3 | 60.3 | 91.3 | 55.3 | 713.56 | 6.04 | 0.57 | 1.26
3 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN252 | 1S-DL-YP-ETC-DLNR-2503-MAN252 | S/STN NO-10, CGHS, PPG | TG-MAN252A-2 | 19504305 | 630 | 200 | 236 | 0.97 | 714 | 210 | 953 | 276 | 1274 | 227 | 1037 | 289 | 2019-06-30 23:30 | 155.5 | 81.4 | 1274 | Y | 98 | 108 | 94 | 14 |  |  | 8.1 | 91.9 | [8 empty] | 468.21 | 353.2 | 513.51 | 442.21 | 231 | 257.31 | 201 | 255 | 20 | 108.3 | 4.3 | 22 | 719.21 | 0.39 | 0.68 | 1.13
4 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR047 | 1S-DL-YP-ETC-DLNR-2502-PVR047 | S/STN. NO.22 F.I.E., PPG:ID | TG-PVR047A-1 | 19506769 | 630 | 200 | 248 | 0.98 | 782 | 271 | 1097 | 257 | 1032 | 254 | 1028 | 67 | 2019-06-06 17:00 | 182.8 | -80.2 | 1119 | R | 104 | 98 | 98 | 6 |  |  | 15.4 | 84.6 | 107.3 | 237.57 | 220.27 | 194.27 | 285.22 | 157.25 | 157.25 | 202.55 | 88.33 | 90.33 | 85.33 | 86.33 | 101.3 | 120 | 113.3 | 108.3 | 122.15 | 99.15 | 104.15 | 112.45 | 705.1 | 14.5 | 0.41 | 1.24
5 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR002 | 1S-DL-YP-ETC-DLNR-2501-LGR002 | PNB BANK ENCLAVE:ID | TG-LGR002A-3 | 19504436 | 990 | 320 | 240 | 0.98 | 1045 | 391 | 1644 | 320 | 1326 | 334 | 1396 | 289 | 2019-06-12 00:30 | 214.9 | 29.4 | 1694 | R | 104 | 105 | 91 | 14 |  | 1.2 | 72.2 | 26.6 |  | 0.12 | 0.42 | 0.12 | 55.12 | 30.3 | 30.3 | 52.3 | 489.42 | 514.12 | 493.22 | 515.12 | 121 | 112 | 75.54 | 109.3 | 23.24 | 32.24 | 3 | 11.54 | 689.18 | 6.42 | 0.58 | 1.06
6 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR003 | 1S-DL-YP-ETC-DLNR-2501-LGR003 | LNR COMPLAINT CENTER:ID | TG-LGR003A-1 | 19502778 | 630 | 200 | 245 | 0.98 | 523 | 239 | 988 | 145 | 586 | 139 | 569 | 410 | 2019-06-30 20:00 | 91.1 | 29.4 | 1020 | R | 125 | 96 | 79 | 46 |  | 0.3 | 52.3 | 47.4 |  |  | 2.3 |  | 37.25 | 104.24 | 104.24 | 106.24 | 451.5 | 614.27 | 461.06 | 607.57 | 199.06 | 0.3 |  | 5 | 31 |  |  |  | 719.21 | 0.39 | 0.67 | 0.83
7 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR004 | 1S-DL-YP-ETC-DLNR-2501-LGR004 | KISHAN KUNJ:K | TG-LGR004A-2 | 19505955 | 990 | 320 | 244 | 0.98 | 1288 | 470 | 2013 | 417 | 1756 | 401 | 1689 | 296 | 2019-06-30 00:30 | 252.5 | 52.2 | 2026 | R | 113 | 92 | 95 | 21 | 0.6 | 1.7 | 41.2 | 56.5 |  |  |  |  | 25.53 | 113.25 | 113.25 | 54.53 | 460.58 | 466.52 | 521.24 | 491.54 | 116.06 | 105.41 | 106.12 | 120.4 | 94.56 | 11.55 | 6.54 | 30.26 | 697.53 | 22.07 | 0.49 | 1.3
8 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR004 | 1S-DL-YP-ETC-DLNR-2501-LGR004 | KISHAN KUNJ:K | TG-LGR004A-3 | 19506173 | 990 | 320 | 244 | 0.97 | 1313 | 476 | 2043 | 448 | 1904 | 389 | 1642 | 353 | 2019-06-30 00:30 | 270.4 | 14.1 | 2043 | R | 108 | 101 | 91 | 17 | 0.3 | 1.2 | 18.7 | 79.8 | 0.01 | 0.01 | 0.01 | 0.01 | 9 | 19.3 | 19.3 | 14.3 | 429.54 | 452.03 | 507.3 | 464.24 | 137.06 | 140.54 | 137.19 | 141.33 | 121.34 | 85.07 | 23.15 | 77.07 | 697.35 | 22.25 | 0.54 | 1.33
9 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR014 | 1S-DL-YP-ETC-DLNR-2501-LGR014 | TIKONA PARK:ID | TG-LGR014A-3 | 19505467 | 630 | 200 | 249 | 0.98 | 727 | 295 | 1191 | 198 | 794 | 234 | 935 | 349 | 2019-06-11 23:30 | 134.2 | 30 | 1206 | R | 119 | 83 | 98 | 36 | 0.2 | 0.1 | 36.5 | 63.2 |  |  |  |  | 0.3 | 113.05 | 113.05 | 18.3 | 390.27 | 525.36 | 516.26 | 546.47 | 208.44 | 65.3 | 108.24 | 103.24 | 104.3 |  | 39 | 35.3 | 704.11 | 15.49 | 0.58 | 1.15
10 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR021 | 1S-DL-YP-ETC-DLNR-2501-LGR021 | G-BLOCK SHAKARPUR:K | TG-LGR021A-2 | 19502945 | 990 | 320 | 240 | 0.98 | 1186 | 406 | 1720 | 384 | 1638 | 396 | 1690 | 72 | 2019-06-30 01:00 | 202.4 | 54.5 | 1931 | B | 92 | 95 | 113 | 21 |  | 1.3 | 45.9 | 52.8 |  |  |  |  | 121.3 | 100.46 | 100.46 | 75.16 | 512.02 | 511.33 | 471.55 | 501.33 | 70.48 | 96.01 | 90.08 | 120.43 | 8.51 | 4.51 | 99.52 | 15.39 | 713.11 | 6.49 | 0.51 | 1.2
11 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR021 | 1S-DL-YP-ETC-DLNR-2501-LGR021 | G-BLOCK SHAKARPUR:K | TG-LGR021A-1 | 19504461 | 990 | 320 | 240 | 0.98 | 1055 | 367 | 1564 | 359 | 1533 | 330 | 1417 | 134 | 2019-06-12 | 175.9 | 61.1 | 1617 | Y | 105 | 100 | 95 | 10 |  |  | 23 | 77 |  |  |  |  | 31.11 | 57.16 | 57.16 | 48.1 | 501.22 | 494.5 | 503.4 | 507.26 | 125 | 107.54 | 102.53 | 116.45 | 29.18 | 26.51 | 0.3 | 14.3 | 686.51 | 33.09 | 0.58 | 1.07
12 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR024 | 1S-DL-YP-ETC-DLNR-2501-LGR024 | SHAKARPUR SANJAY PARK | TG-LGR024A-2 | 19502827 | 990 | 320 | 232 | 0.98 | 1061 | 345 | 1568 | 374 | 1705 | 342 | 1563 | 139 | 2019-06-11 23:30 | 187.7 | 32.4 | 1841 | R | 114 | 91 | 95 | 23 |  |  | 25.4 | 74.6 |  | 1 | 0.3 | 0.3 | 8 | 94.18 | 94.18 | 43.23 | 507.33 | 542.15 | 521.42 | 551.57 | 147.3 | 70.15 | 94.43 | 106.43 | 53.15 | 8.3 | 7.45 | 13.45 | 716.18 | 3.42 | 0.58 | 1.07
13 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR024 | 1S-DL-YP-ETC-DLNR-2501-LGR024 | SHAKARPUR SANJAY PARK | TG-LGR024A-1 | 19505154 | 990 | 320 | 242 | 0.98 | 1211 | 417 | 1835 | 489 | 2257 | 305 | 1329 | 804 | 2019-06-02 00:30 | 209.3 | 61.4 | 2257 | Y | 98 | 104 | 98 | 6 | 0.2 | 0.1 | 28.6 | 71.1 |  |  |  |  | 25 | 17.3 | 17.3 | 14.3 | 514.12 | 476.06 | 526.42 | 511.58 | 141.3 | 137.06 | 153 | 144.14 | 25.45 | 75.45 | 14.45 | 35.45 | 706.27 | 13.33 | 0.56 | 1.22
14 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR031 | 1S-DL-YP-ETC-DLNR-2501-LGR031 | MANGAL BAZAR LAXMI NAGAR:PL | TG-LGR031A-1 | 19504511 | 990 | 320 | 244 | 0.98 | 1213 | 387 | 1620 | 461 | 1944 | 364 | 1536 | 373 | 2019-06-12 00:30 | 228.2 | 63.3 | 1944 | Y | 99 | 111 | 91 | 20 |  |  | 3.3 | 96.7 |  |  |  |  | 8.5 | 0.3 | 0.3 | 6 | 528.49 | 419.4 | 557.08 | 516.25 | 155.15 | 207.28 | 108 | 166.18 | 21.49 | 87.05 | 7.3 | 26 | 714.43 | 5.17 | 0.57 | 1.22
15 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR040 | 1S-DL-YP-ETC-DLNR-2501-LGR040 | J EXTN. LAXMI NAGAR:PM | TG-LGR040A-1 | 19503409 | 990 | 320 | 229 | 0.98 | 1156 | 351 | 1489 | 365 | 1626 | 440 | 1926 | 387 | 2019-06-30 01:30 | 214.9 | 67 | 2005 | B | 90 | 95 | 115 | 25 | 74.4 | 10 | 7 | 8.7 |  |  |  |  | 20.23 | 70.16 | 70.16 | 31.23 | 601.11 | 518.37 | 453.3 | 527.06 | 85.33 | 114.14 | 181.38 | 143.48 | 1.29 | 5.29 | 62.58 | 6.19 | 708.36 | 11.24 | 0.56 | 1.17
16 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR051 | 1S-DL-YP-ETC-DLNR-2501-LGR051 | H BLOCK LAXMI NAGAR:PL | TG-LGR051A-2 | 19504765 | 630 | 200 | 242 | 0.99 | 696 | 206 | 893 | 280 | 1226 | 210 | 904 | 327 | 2019-06-26 14:30 | 75.4 | -6.9 | 1230 | Y | 90 | 113 | 96 | 23 |  |  | 16.9 | 83.1 |  |  |  |  | 87.28 | 33 | 33 | 45.58 | 502.13 | 386.23 | 481.46 | 475.55 | 127.45 | 156.24 | 154.27 | 162.03 | 1 | 142.39 | 9.15 | 34.3 | 718.26 | 1.34 | 0.59 | 1.1
17 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR080 | 1S-DL-YP-ETC-DLNR-2501-LGR080 | GALI MASJID ANAR WALI | TG-LGR080A-1 | 19506548 | 990 | 320 | 239 | 0.97 | 1118 | 370 | 1595 | 396 | 1704 | 352 | 1499 | 178 | 2019-06-30 01:00 | 339.5 | 70.1 | 1911 | Y | 102 | 104 | 94 | 10 | 0.2 | 0.1 | 60.2 | 39.5 |  |  | 33.3 |  | 5.3 | 1.3 | 1.3 | 29.3 | 444.27 | 436.27 | 463.27 | 437.27 | 176.1 | 187.32 | 173.1 | 174.32 | 73.38 | 74.16 | 29.38 | 58.16 | 699.45 | 20.15 | 0.64 | 1.13
18 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR082 | 1S-DL-YP-ETC-DLNR-2501-LGR082 | E BLOCK ,VIKAS MARG | TG-LGR082A-1 | 19506667 | 990 | 320 | 238 | 0.98 | 1152 | 389 | 1684 | 407 | 1762 | 356 | 1539 | 196 | 2019-06-08 16:00 | 279.4 | 65 | 2038 | R | 99 | 107 | 94 | 13 | 0.2 |  | 0.3 | 99.5 |  |  |  |  | 60.3 | 25.3 | 25.3 | 51.3 | 443.3 | 450.58 | 387.11 | 447.18 | 136.46 | 115.1 | 136.36 | 127.28 | 62.43 | 111.51 | 51.42 | 77.13 | 703.29 | 16.31 | 0.58 | 1.16
19 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR083 | 1S-DL-YP-ETC-DLNR-2501-LGR083 | EK MINAR MASID | TG-LGR083A-1 | 19506852 | 990 | 320 | 247 | 0.97 | 1349 | 452 | 1858 | 431 | 1757 | 467 | 1921 | 144 | 2019-06-08 | 315.2 | 91.2 | 1921 | B | 102 | 101 | 97 | 5 | 0.1 | 0.1 | 25.1 | 74.6 | [8 empty] | 383.23 | 402 | 445.53 | 415.23 | 193.47 | 177.1 | 140.17 | 170.17 | 130.4 | 128.4 | 116.4 | 122.1 | 707.5 | 12.1 | 0.58 | 1.36
20 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN003 | 1S-DL-YP-ETC-DLNR-2503-MAN003 | SOUTH GANESH NAGAR:PM | TG-MAN003A-1 | 19505687 | 400 | 120 | 234 | 0.98 | 588 | 183 | 823 | 190 | 864 | 216 | 982 | 143 | 2019-06-30 | 126.6 | 34 | 982 | B | 94 | 103 | 103 | 9 | 0.1 | 0.1 | 29.1 | 70.6 | [8 empty] | 417.59 | 336.3 | 361.29 | 373.59 | 180.57 | 200.59 | 143.57 | 175.27 | 107.56 | 169.23 | 199.56 | 157.26 | 706.52 | 13.08 | 0.56 | 1.47
21 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN004 | 1S-DL-YP-ETC-DLNR-2503-MAN004 | SOUTH GANESH NAGAR EXTN.:ID | TG-MAN004A-2 | 19506133 | 630 | 200 | 229 | 0.98 | 711 | 231 | 1065 | 223 | 1024 | 258 | 1201 | 160 | 2019-06-30 | 141.6 | 41.6 | 1299 | B | 100 | 93 | 107 | 14 | 0.2 | 0.1 | 5.4 | 94.3 |  |  |  |  | 60.3 | 98 | 98 | 46.3 | 518.56 | 529.26 | 519.56 | 538.56 | 114.26 | 77.56 | 110.3 | 112 | 13 | 1.3 | 49.56 | 9.26 | 706.52 | 13.08 | 0.54 | 1.13
22 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN006 | 1S-DL-YP-ETC-DLNR-2503-MAN006 | PANDAV NAGAR D PARK:K | TG-MAN006A-1 | 19505744 | 990 | 320 | 239 | 0.98 | 1034 | 340 | 1441 | 383 | 1639 | 312 | 1335 | 267 | 2019-06-05 01:00 | 239 | 64.3 | 1869 | Y | 101 | 110 | 89 | 21 | 0.3 | 0.4 | 52.2 | 47.1 |  |  |  |  | 63.28 | 50.3 | 50.3 | 75.28 | 534.52 | 490.2 | 525.54 | 517.22 | 103.4 | 106 | 43.01 | 115.1 | 15.21 | 70.31 |  | 9.21 | 717.21 | 2.39 | 0.57 | 1.04
23 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN009 | 1S-DL-YP-ETC-DLNR-2503-MAN009 | J PARK PANDAV NAGAR:K | TG-MAN009A-1 | 19502964 | 990 | 320 | 239 | 0.98 | 1094 | 368 | 1588 | 397 | 1713 | 330 | 1407 | 266 | 2019-06-29 23:00 | 172.2 | 63.3 | 1810 | Y | 99 | 109 | 92 | 17 |  |  | 49.8 | 50.2 |  |  |  |  | 91.28 | 48.3 | 48.3 | 80.28 | 481.37 | 465.08 | 462.08 | 478.07 | 109.49 | 122.57 | 101.49 | 120.49 | 19.52 | 66.11 | 4.22 | 23.22 | 702.46 | 17.14 | 0.55 | 1.11
24 | 2019-06-10 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN010 | 1S-DL-YP-ETC-DLNR-2503-MAN010 | GANESH NAGAR COM. E BLCK.:PL | TG-MAN010A-1 | 19506916 | 990 | 320 | 238 | 0.98 | 1131 | 341 | 1514 | 427 | 1915 | 362 | 1608 | 364 | 2019-06-30 | 298.6 | 81.9 | 1915 | Y | 93 | 105 | 101 | 12 | 0.1 | 0.2 | 8.2 | 91.5 |  |  |  |  | 36.27 | 6.27 | 6.27 | 14.27 | 381.07 | 371.02 | 367.31 | 376.34 | 77.26 | 81.35 | 91.33 | 88.03 | 5.59 | 41.55 | 25.25 | 21.55 | 500.59 | 3.01 | 0.56 | 1.14
25 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN013 | 1S-DL-YP-ETC-DLNR-2503-MAN013 | MANDAWALI A BLOCK SHIV MANDIR MARG:PL | TG-MAN013A-2 | 19502779 | 990 | 320 | 238 | 0.97 | 1242 | 438 | 1889 | 398 | 1731 | 405 | 1772 | 142 | 2019-06-29 23:30 | 222.3 | 64 | 1976 | B | 105 | 93 | 102 | 12 | 1 | 4.5 | 90.4 | 4.2 |  |  |  |  | 5.3 | 15.3 | 15.3 | 10.3 | 346.37 | 416.35 | 369.05 | 379.35 | 125 | 110.55 | 100.3 | 107.32 | 100.34 | 34.41 | 95.36 | 80.04 | 715.5 | 4.1 | 0.58 | 1.25
26 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN013 | 1S-DL-YP-ETC-DLNR-2503-MAN013 | MANDAWALI A BLOCK SHIV MANDIR MARG:PL | TG-MAN013A-1 | 19506457 | 990 | 320 | 248 | 0.97 | 1135 | 413 | 1753 | 358 | 1510 | 364 | 1524 | 236 | 2019-06-30 23:30 | 219.2 | 81.9 | 1753 | R | 98 | 100 | 102 | 4 | 0.1 |  | 4 | 95.9 |  |  |  |  | 25 | 9.3 | 9.3 | 12 | 516.34 | 523.34 | 508.04 | 519.34 | 130.52 | 130.22 | 138.18 | 137.52 | 19.3 | 28.3 | 31.04 | 22.3 | 691.56 | 28.04 | 0.57 | 1.15
27 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN016 | 1S-DL-YP-ETC-DLNR-2503-MAN016 | MANDAWALI PRIMARY SCHOOL:PL | TG-MAN016A-1 | 19506407 | 990 | 320 | 243 | 0.97 | 1132 | 393 | 1678 | 339 | 1439 | 400 | 1714 | 259 | 2019-06-29 23:30 | 279.4 | 88.3 | 1889 | R | 109 | 89 | 102 | 20 | 0.1 | 0.1 | 10.6 | 89.1 |  |  |  |  | 1 | 47.36 | 47.36 | 6.53 | 472.35 | 553.34 | 512.29 | 530.12 | 158.05 | 113.25 | 164.05 | 146.35 | 86.25 | 3.3 | 34.55 | 34.25 | 718.05 | 1.55 | 0.6 | 1.14
28 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN016 | 1S-DL-YP-ETC-DLNR-2503-MAN016 | MANDAWALI PRIMARY SCHOOL:PL | TG-MAN016A-3 | 19506597 | 630 | 200 | 237 | 0.98 | 670 | 209 | 913 | 201 | 881 | 260 | 1143 | 247 | 2019-06-11 | 189.2 | 46.2 | 1143 | B | 93 | 91 | 116 | 25 | 0.1 | 0.1 | 6.8 | 92.9 |  |  |  |  | 70 | 43 | 43 | 16.3 | 545.2 | 605.2 | 476.3 | 559.2 | 89.3 | 58 | 155.5 | 128 | 1.3 |  | 74 | 2.3 | 706.2 | 13.4 | 0.6 | 1.06
29 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN019 | 1S-DL-YP-ETC-DLNR-2503-MAN019 | MANDAWALI UNCHEPAR;PL | TG-MAN019A-1 | 19501990 | 990 | 320 | 241 | 0.97 | 1093 | 353 | 1547 | 387 | 1699 | 353 | 1528 | 162 | 2019-06-29 23:30 | 193.6 | 69.2 | 1813 | Y | 97 | 109 | 95 | 14 |  | 0.1 | 9.2 | 90.7 |  |  |  |  | 97.56 | 37 | 37 | 88.26 | 537.23 | 515.56 | 459.23 | 511.53 | 81.57 | 133.23 | 104.58 | 106.37 | 2 | 32.57 | 5.29 | 12.2 | 719.16 | 0.44 | 0.54 | 1.1
30 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN023 | 1S-DL-YP-ETC-DLNR-2503-MAN023 | UTTARY SCHOOL BLOCK:K | TG-MAN023A-1 | 19502766 | 990 | 320 | 244 | 0.97 | 1159 | 407 | 1693 | 384 | 1608 | 368 | 1538 | 134 | 2019-06-30 23:30 | 237 | 98.6 | 1727 | R | 103 | 100 | 97 | 6 |  |  | 1.3 | 98.7 |  |  |  |  | 6.3 | 12 | 12 | 8 | 487.14 | 498.14 | 531.44 | 505.44 | 137.27 | 158.57 | 149.23 | 146.57 | 87.01 | 49.01 | 31.35 | 57.31 | 718.12 | 1.48 | 0.6 | 1.17
31 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN023 | 1S-DL-YP-ETC-DLNR-2503-MAN023 | UTTARY SCHOOL BLOCK:K | TG-MAN023A-2 | 19502768 | 630 | 200 | 242 | 0.99 | 720 | 283 | 1170 | 218 | 911 | 220 | 911 | 259 | 2019-06-29 23:00 | 40.5 | -89.7 | 1206 | R | 111 | 95 | 95 | 16 |  |  | 18.2 | 81.8 |  |  |  |  | 17 | 34 | 34 | 21.3 | 480 | 561.12 | 557.12 | 534.15 | 121.27 | 116.33 | 121.14 | 134.11 | 99.18 | 6 | 6.19 | 27.49 | 717.45 | 2.15 | 0.57 | 1.14
32 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN025 | 1S-DL-YP-ETC-DLNR-2503-MAN025 | CHANDERVIHAR SS-II:ID | TG-MAN025A-1 | 19500845 | 630 | 200 | 242 | 0.97 | 751 | 254 | 1085 | 250 | 1063 | 247 | 1057 | 25 | 2019-06-15 23:00 | 167.9 | 9.2 | 1138 | R | 100 | 96 | 104 | 8 |  |  | 33.7 | 66.3 | 0.3 | 0.3 | 0.3 | 0.3 | 11 | 13 | 13 | 6.3 | 527.28 | 556.28 | 491.28 | 528.28 | 139 | 123.27 | 174.27 | 146.57 | 41.57 | 26.3 | 50.3 | 37.3 | 719.55 | 0.05 | 0.57 | 1.19
33 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN025 | 1S-DL-YP-ETC-DLNR-2503-MAN025 | CHANDERVIHAR SS-II:ID | TG-MAN025A-2 | 19504725 | 630 | 200 | 237 | 0.98 | 675 | 245 | 1072 | 231 | 1004 | 199 | 861 | 186 | 2019-06-29 23:00 | 118.7 | 8.3 | 1097 | R | 110 | 99 | 91 | 19 |  |  | 24 | 76 | 0.3 | 0.3 | 1 | 0.3 | 36.3 | 97 | 97 | 68 | 533.59 | 513.59 | 572.59 | 547.59 | 114 | 95 | 49 | 95 | 34.3 | 13 |  | 8 | 719.29 | 0.31 | 0.56 | 1.07
34 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN026 | 1S-DL-YP-ETC-DLNR-2503-MAN026 | WESTVINOD NAGAR NEAR MANGLAM:PL | TG-MAN026A-3 | 19505743 | 990 | 320 | 244 | 0.97 | 1060 | 331 | 1380 | 333 | 1382 | 396 | 1650 | 269 | 2019-06-26 23:00 | 329.3 | 28.2 | 1905 | B | 92 | 97 | 111 | 19 | 0.1 |  | 2.6 | 97.2 | 0.3 | 0.3 | 0.3 | 0.3 | 166.55 | 105.4 | 105.4 | 112.37 | 481.44 | 539.59 | 460.02 | 488.1 | 50.44 | 52.13 | 97.02 | 92.36 | 1.29 | 3 | 66.13 | 7.29 | 701.22 | 18.38 | 0.53 | 1.07
35 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN027 | 1S-DL-YP-ETC-DLNR-2503-MAN027 | WESTVINOD NAGAR D BLOCK:ID | TG-MAN027A-2 | 19505858 | 990 | 320 | 243 | 0.97 | 1271 | 421 | 1841 | 446 | 1954 | 404 | 1758 | 170 | 2019-06-30 23:30 | 429.8 | 95.7 | 1954 | Y | 98 | 107 | 95 | 12 | 0.1 | 0.1 | 4.8 | 95 |  |  |  |  | 10 | 5 | 5 | 8.3 | 475.49 | 387.49 | 492.19 | 462.19 | 149.46 | 185.3 | 153.16 | 156.16 | 70.15 | 127.31 | 47.15 | 78.45 | 705.5 | 14.1 | 0.57 | 1.28
36 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN029 | 1S-DL-YP-ETC-DLNR-2503-MAN029 | A BLOCK WEST VINOD NAGAR | TG-MAN029A-2 | 19501888 | 990 | 320 | 249 | 0.97 | 1185 | 360 | 1530 | 401 | 1700 | 424 | 1813 | 246 | 2019-06-30 23:30 | 221.5 | 88.3 | 1897 | B | 89 | 105 | 106 | 17 |  |  | 4.4 | 95.6 |  |  |  |  | 34.3 | 7 | 7 | 12 | 566.22 | 481.03 | 471.33 | 507.33 | 113.42 | 137.49 | 155.3 | 147.19 | 4 | 92.42 | 82.31 | 51.42 | 718.34 | 1.26 | 0.58 | 1.2
37 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN029 | 1S-DL-YP-ETC-DLNR-2503-MAN029 | A BLOCK WESTVINOD NAGAR | TG-MAN029A-1 | 19504659 | 990 | 320 | 243 | 0.97 | 1213 | 384 | 1682 | 446 | 1966 | 383 | 1685 | 282 | 2019-06-30 23:30 | 212 | 78.8 | 1966 | Y | 96 | 105 | 99 | 9 |  |  | 0.8 | 99.2 |  |  |  |  | 43 | 25 | 25 | 27 | 538.58 | 492.57 | 535.28 | 528.58 | 117 | 135.31 | 127 | 128.3 | 19 | 64.3 | 26.3 | 33.3 | 717.58 | 2.02 | 0.54 | 1.22
38 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN031 | 1S-DL-YP-ETC-DLNR-2503-MAN031 | MOHAN BABA MANDIR MANDAWALI:PL | TG-MAN031A-1 | 19506135 | 990 | 320 | 243 | 0.98 | 1290 | 448 | 1956 | 447 | 1951 | 395 | 1723 | 231 | 2019-06-30 23:30 | 336.3 | 71.7 | 2118 | Y | 103 | 106 | 91 | 15 | 0.1 |  | 0.3 | 99.6 | [8 empty] | 254.31 | 235.18 | 380.36 | 276.48 | 230.52 | 212.05 | 241.06 | 239.35 | 215.3 | 253.3 | 79.11 | 184.3 | 700.53 | 19.07 | 0.66 | 1.3
39 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN032 | 1S-DL-YP-ETC-DLNR-2503-MAN032 | SONIYA VIHAR MANDAWALI:PL | TG-MAN032A-1 | 19505665 | 400 | 120 | 233 | 0.98 | 430 | 151 | 683 | 136 | 612 | 143 | 641 | 62 | 2019-06-11 23:00 | 96 | 27.8 | 772 | R | 106 | 100 | 94 | 12 | 0.1 | 0.6 | 12.9 | 86.4 | [5 empty] | 1 | 1 |  | 424.28 | 470.42 | 503.28 | 472.58 | 221.3 | 212.46 | 197.3 | 218 | 59.3 | 21 | 4 | 14.3 | 705.28 | 14.32 | 0.69 | 1.07
40 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN033 | 1S-DL-YP-ETC-DLNR-2503-MAN033 | B BLOCK MANDAWALI:ID | TG-MAN033A-1 | 19506545 | 990 | 320 | 240 | 0.97 | 1105 | 394 | 1767 | 366 | 1644 | 344 | 1544 | 194 | 2019-06-30 23:30 | 318.1 | 83.2 | 1777 | R | 105 | 103 | 92 | 13 | 0.1 | 0.4 | 29.1 | 70.4 |  |  |  |  | 15 | 31.3 | 31.3 | 32 | 512.38 | 495.13 | 559.13 | 526.13 | 144.05 | 153.3 | 73.25 | 132 | 31.55 | 23.25 | 2 | 13.25 | 703.38 | 16.22 | 0.57 | 1.12
41 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN037 | 1S-DL-YP-ETC-DLNR-2503-MAN037 | SHANKAR MARG MANDAWALI:PL | TG-MAN037A-1 | 19506836 | 990 | 320 | 244 | 0.97 | 1290 | 420 | 1822 | 386 | 1678 | 484 | 2131 | 400 | 2019-06-30 23:30 | 354.9 | 95.4 | 2131 | B | 102 | 95 | 103 | 8 | 0.1 | 0.1 | 2.8 | 97 |  |  |  |  | 11 | 24 | 24 | 15 | 450 | 485 | 455.3 | 466 | 130 | 125.05 | 115.3 | 120.35 | 113.31 | 70.26 | 121.01 | 102.56 | 704.31 | 15.29 | 0.56 | 1.3
42 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN038 | 1S-DL-YP-ETC-DLNR-2503-MAN038 | KRISHNA PURI MANDAWALI:PL | TG-MAN038A-1 | 19504301 | 630 | 200 | 233 | 0.97 | 589 | 208 | 954 | 192 | 865 | 189 | 855 | 94 | 2019-06-30 23:30 | 92.9 | 46.5 | 1097 | B | 107 | 84 | 109 | 25 | 0.5 | 21.1 | 74.9 | 3.5 |  |  |  |  | 40 | 183.33 | 183.33 | 53.48 | 554.33 | 527.3 | 526.09 | 599.15 | 122.3 | 7.3 | 89 | 65.3 | 1.3 |  | 39.3 |  | 718.33 | 1.27 | 0.61 | 0.93
43 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN212 | 1S-DL-YP-ETC-DLNR-2503-MAN212 | RAILWAY COLONY GALI NO. 2:PL | TG-MAN212A-1 | 19505555 | 990 | 320 | 235 | 0.98 | 1063 | 381 | 1715 | 374 | 1681 | 307 | 1386 | 313 | 2019-06-01 23:00 | 246.7 | 38.7 | 1716 | Y | 104 | 105 | 91 | 14 | 0.1 |  | 0.8 | 99.2 |  |  |  |  | 103.01 | 107.54 | 107.54 | 135.01 | 518.44 | 496.21 | 464.21 | 496.44 | 62.3 | 71 | 36.3 | 63.3 | 21.3 | 30.3 |  | 10.3 | 705.45 | 14.15 | 0.52 | 1.07
44 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR009 | 1S-DL-YP-ETC-DLNR-2502-PVR009 | EAST GURU ANGAD NAGAR:K | TG-PVR009A-1 | 19504643 | 630 | 200 | 244 | 0.97 | 669 | 211 | 892 | 193 | 833 | 265 | 1134 | 276 | 2019-06-30 23:30 | 127.9 | 24.4 | 1134 | B | 96 | 100 | 103 | 7 | 0.1 | 1.4 | 66.7 | 31.8 | 0.13 | 0.13 | 0.13 | 0.13 | 26 | 25.3 | 25.3 | 16 | 545.03 | 539.33 | 499.33 | 532.03 | 81.47 | 91.17 | 106 | 104 | 3.3 |  | 29.47 | 4.17 | 669.01 | 2.59 | 0.59 | 1.06
45 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR015 | 1S-DL-YP-ETC-DLNR-2502-PVR015 | G-I, PREET VIHAR:ID | TG-PVR015A-1 | 19501193 | 990 | 320 | 248 | 0.97 | 1017 | 343 | 1462 | 362 | 1548 | 312 | 1328 | 192 | 2019-06-10 13:00 | 249.5 | -68.4 | 1596 | Y | 106 | 101 | 93 | 13 |  |  | 0.6 | 99.4 |  | 13.3 | 14 | 3 | 46.3 | 67 | 67 | 88.3 | 454.1 | 422.45 | 378.45 | 424.45 | 207.34 | 178.01 | 170.29 | 195.29 | 11 | 37.58 | 2.3 | 7.3 | 719.14 | 0.46 | 0.62 | 1.03
46 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR021 | 1S-DL-YP-ETC-DLNR-2502-PVR021 | BHARATI ARTIST COLONY:K | TG-PVR021A-1 | 19506726 | 990 | 320 | 239 | 0.98 | 1232 | 430 | 1911 | 426 | 1894 | 376 | 1671 | 232 | 2019-06-29 14:30 | 396.5 | 10.9 | 1981 | R | 109 | 99 | 92 | 17 | 0.1 | 0.1 | 1.4 | 98.3 |  |  | 3.3 |  | 196.55 | 271.43 | 271.43 | 264.13 | 215.18 | 182.34 | 196.34 | 184.36 | 114.22 | 121.47 | 134.17 | 125.28 | 164.52 | 115.23 | 67.23 | 117.1 | 691.27 | 28.33 | 0.51 | 1.24
47 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR067 | 1S-DL-YP-ETC-DLNR-2502-PVR067 | SWASTHYA VIHAR KIOSK VIKAS MARG | TG-PVR067A-1 | 19502956 | 630 | 200 | 248 | 0.97 | 689 | 234 | 941 | 241 | 1003 | 213 | 880 | 107 | 2019-06-29 12:30 | 136.2 | 18.9 | 1032 | Y | 94 | 109 | 97 | 15 | 47.9 | 1.2 | 1.4 | 49.6 | 234.53 | 59 | 197.53 | 177.44 | 121.43 | 266.36 | 266.36 | 174.22 | 208 | 178.04 | 191 | 185.34 | 117.55 | 138.21 | 128.25 | 139.51 | 10.3 | 51 | 13.3 | 15.3 | 693.01 | 2.59 | 0.45 | 1.09