## Underload DTs
MIS Report of Distribution Transformer - Jun19
Jun19 1230 LAXMI NAGAR (Underload DTs)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | LGR073 | 1S-DL-YP-ETC-DLNR-2501-LGR073 | RISHABH IPEX MALL:ID | TG-LGR073A-1 | 19506541 | 400 | 120 | 240 | 0.97 | 88 | 15 | 67 | 31 | 133 | 42 | 181 | 100 | 2019-06-10 13:30 | 27.1 | 1.4 | 183 | B | 59 | 85 | 157 | 98 |  | 0.1 | 5.5 | 94.3 | 696.26 | 659.26 | 521.26 | 683.56 |  | 37 | 37 | 12.3 | [12 empty] | 696.26 | 23.34 | 0.33 | 0.22
2 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN028 | 1S-DL-YP-ETC-DLNR-2503-MAN028 | SFS GAZIPUR:ID | TG-MAN028A-1 | 19505327 | 990 | 320 | 253 | 0.98 | 138 | 45 | 181 | 34 | 137 | 60 | 244 | 93 | 2019-06-11 00:30 | 24.3 | 5.1 | 254 | B | 106 | 67 | 128 | 61 | 0.1 |  | 11 | 88.9 | 714.3 | 714.3 | 714.3 | 714.3 | [16 empty] | 714.3 | 5.3 | 0.52 | 0.14
3 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN028 | 1S-DL-YP-ETC-DLNR-2503-MAN028 | SFS GAZIPUR:ID | TG-MAN028A-2 | 19506204 | 630 | 200 | 253 | 0.96 | 139 | 48 | 196 | 29 | 120 | 62 | 250 | 113 | 2019-06-12 | 45.8 | 5.8 | 279 | B | 103 | 58 | 139 | 81 | 0.1 | 0.2 | 9 | 90.7 | 680.3 | 714.3 | 493.3 | 706 | 34 |  |  | 8.3 | [12 empty] | 714.3 | 5.3 | 0.55 | 0.22
4 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN046 | 1S-DL-YP-ETC-DLNR-2503-MAN046 | TAJMAN SINGH:ID | TG-MAN046A-1 | 19500432 | 630 | 200 | 245 | 0.98 | 125 | 39 | 167 | 51 | 216 | 35 | 149 | 60 | 2019-06-02 22:30 | 28.5 | 5.1 | 217 | Y | 103 | 109 | 88 | 21 |  |  | 16.3 | 83.7 | 720 | 709.3 | 720 | 720 |  | 10.3 | 10.3 | [13 empty] | 720 | 0 | 0.52 | 0.2
5 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN046 | 1S-DL-YP-ETC-DLNR-2503-MAN046 | TAJMAN SINGH:ID | TG-MAN046A-2 | 19500435 | 630 | 200 | 248 | 0.97 | 116 | 45 | 184 | 23 | 94 | 48 | 196 | 96 | 2019-06-01 | 23.5 | 2.8 | 213 | B | 114 | 64 | 123 | 59 | 32.3 | 11.4 | 40.5 | 15.8 | 708.3 | 720 | 698 | 720 | 11.3 | [15 empty] | 720 | 0 | 0.53 | 0.18
6 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN057 | 1S-DL-YP-ETC-DLNR-2503-MAN057 | S/STN.NO-2, GAZIPUR:ID | TG-MAN057A-1 | 19506839 | 400 | 120 | 257 | 0.86 | 37 | 12 | 43 | 0 | 0 | 26 | 98 | 85 | 2019-06-20 19:00 | 32.8 | 0.1 | 98 | B | 149 | 0 | 151 | 151 | 0.1 | 0.6 | 59.2 | 40.1 | 706.05 | 706.05 | 706.05 | 706.05 | [16 empty] | 706.05 | 13.55 | 0.3 | 0.09
7 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN065 | 1S-DL-YP-ETC-DLNR-2503-MAN065 | S/STN.NO-8, PPG CGHS:ID | TG-MAN065A-1 | 19506154 | 400 | 120 | 246 | 0.98 | 49 | 18 | 73 | 24 | 93 | 7 | 30 | 56 | 2019-06-12 12:30 | 12 | 1.3 | 101 | R | 122 | 100 | 78 | 44 |  | 0.1 | 19.5 | 80.4 | 705.03 | 705.03 | 705.03 | 705.03 | [16 empty] | 705.03 | 14.57 | 0.66 | 0.12
8 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN070 | 1S-DL-YP-ETC-DLNR-2503-MAN070 | S/STN.NO-15, PPG CGHS:ID | TG-MAN070A-1 | 19501207 | 400 | 120 | 240 | 0.91 | 94 | 24 | 99 | 42 | 175 | 28 | 118 | 68 | 2019-06-03 13:00 | 36.7 | -0.3 | 176 | Y | 88 | 125 | 87 | 38 |  |  | 12.5 | 87.5 | 694.58 | 606.28 | 708.28 | 676.58 | 25 | 113.3 | 113.3 | 43 | [12 empty] | 719.58 | 0.02 | 0.36 | 0.24
9 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN072 | 1S-DL-YP-ETC-DLNR-2503-MAN072 | S/STN.NO-19, PPG CGHS:ID | TG-MAN072A-1 | 19500775 | 400 | 120 | 238 | 0.88 | 19 | 9 | 40 | 5 | 22 | 4 | 18 | 20 | 2019-06-10 19:30 | 8.6 | -1.7 | 40 | R | 133 | 75 | 91 | 58 |  |  | 0.2 | 99.8 | 647.31 | 647.31 | 647.31 | 647.31 | [16 empty] | 647.31 | 0.29 | 0.51 | 0.05
10 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN073 | 1S-DL-YP-ETC-DLNR-2503-MAN073 | MAY FAIR CGHS, PPG.:ID | TG-MAN073A-1 | 19505986 | 400 | 120 | 246 | 0.98 | 97 | 19 | 83 | 36 | 156 | 41 | 177 | 86 | 2019-06-05 23:30 | 27 | 2.6 | 186 | Y | 55 | 122 | 123 | 68 | 0.2 |  | 0.3 | 99.4 | 714.58 | 552.28 | 566.28 | 664.58 |  | 162.3 | 162.3 | 50 | [12 empty] | 714.58 | 5.02 | 0.51 | 0.24
11 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN078 | 1S-DL-YP-ETC-DLNR-2503-MAN078 | NEELKANTH CGHS, PPG:ID | TG-MAN078A-2 | 19502541 | 630 | 200 | 246 | 0.98 | 134 | 57 | 231 | 24 | 101 | 52 | 221 | 125 | 2019-06-09 23:30 | 26.2 | 3.7 | 276 | R | 139 | 68 | 93 | 71 | 100 |  |  |  | 552 | 719.59 | 699.29 | 713.59 | 167.59 |  |  | 6 | [12 empty] | 719.59 | 0.01 | 0.52 | 0.21
12 | 2019-06-08 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN078 | 1S-DL-YP-ETC-DLNR-2503-MAN078 | NEELKANTH CGHS, PPG:ID | TG-MAN078A-1 | 19506184 | 630 | 200 | 247 | 0.98 | 111 | 25 | 104 | 52 | 221 | 34 | 143 | 103 | 2019-06-27 | 19 | 1.6 | 241 | Y | 65 | 136 | 99 | 71 | 0.1 |  | 14 | 85.9 | 551.58 | 508 | 551.58 | 551.58 |  | 43.58 | 43.58 | [13 empty] | 551.58 | 0.02 | 0.5 | 0.18
13 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN079 | 1S-DL-YP-ETC-DLNR-2503-MAN079 | ANAMIKA CGHS,PPG:ID | TG-MAN079A-1 | 19501142 | 400 | 120 | 246 | 0.98 | 41 | 9 | 37 | 22 | 90 | 11 | 43 | 50 | 2019-06-12 | 8 | 0.6 | 90 | Y | 86 | 131 | 83 | 48 |  |  | 4.9 | 95.1 | 719.58 | 719.58 | 719.58 | 719.58 | [16 empty] | 719.58 | 0.02 | 0.47 | 0.1
14 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN079 | 1S-DL-YP-ETC-DLNR-2503-MAN079 | ANAMIKA CGHS,PPG:ID | TG-MAN079A-2 | 19505402 | 400 | 120 | 241 | 0.98 | 81 | 25 | 110 | 10 | 44 | 45 | 195 | 131 | 2019-06-29 23:00 | 16 | 1.3 | 195 | B | 91 | 52 | 157 | 105 | 0.1 | 3.6 | 79.8 | 16.5 | 707.28 | 707.28 | 534 | 706.58 |  |  |  | 0.3 | [12 empty] | 707.28 | 12.32 | 0.5 | 0.2
15 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN080 | 1S-DL-YP-ETC-DLNR-2503-MAN080 | FRIENDS CGHS, PPG:ID | TG-MAN080A-1 | 19506122 | 630 | 200 | 240 | 0.98 | 148 | 37 | 154 | 61 | 253 | 51 | 212 | 87 | 2019-06-16 00:30 | 30.2 | 4.2 | 265 | B | 88 | 105 | 108 | 20 | 0.1 |  | 1.6 | 98.3 | 717.28 | 678 | 617 | 693.28 | 2.3 | 41.58 | 41.58 | 26.3 | [12 empty] | 719.58 | 0.02 | 0.52 | 0.23
16 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN080 | 1S-DL-YP-ETC-DLNR-2503-MAN080 | FRIENDS CGHS, PPG:ID | TG-MAN080A-2 | 19506484 | 630 | 200 | 240 | 0.97 | 142 | 71 | 309 | 32 | 139 | 39 | 172 | 156 | 2019-06-10 23:00 | 30.8 | 6.2 | 309 | R | 136 | 75 | 89 | 61 |  |  | 8.2 | 91.8 | 479.58 | 719.58 | 698.28 | 699.28 | 240 |  |  | 20.3 | [12 empty] | 719.58 | 0.02 | 0.58 | 0.23
17 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN081 | 1S-DL-YP-ETC-DLNR-2503-MAN081 | VIDYUT CGHS,PPG :ID | TG-MAN081A-1 | 19501153 | 400 | 120 | 230 | 0.98 | 75 | 17 | 74 | 44 | 193 | 14 | 63 | 125 | 2019-06-09 23:30 | 13.5 | 0.8 | 210 | Y | 72 | 175 | 53 | 122 | 57.7 | 13.8 | 17.9 | 10.6 | 719.58 | 476.3 | 719.58 | 719.58 |  | 243.28 | 243.28 | [13 empty] | 719.58 | 0.02 | 0.54 | 0.19
18 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN081 | 1S-DL-YP-ETC-DLNR-2503-MAN081 | VIDYUT CGHS,PPG :ID | TG-MAN081A-2 | 19501188 | 400 | 120 | 239 | 0.98 | 60 | 17 | 74 | 30 | 132 | 13 | 57 | 69 | 2019-06-05 | 11.6 | 0.3 | 134 | Y | 70 | 149 | 81 | 79 | 49.4 | 44.7 | 4.4 | 1.4 | 719.58 | 711.28 | 719.58 | 719.58 |  | 8.3 | 8.3 | [13 empty] | 719.58 | 0.02 | 0.45 | 0.15
19 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN084 | 1S-DL-YP-ETC-DLNR-2503-MAN084 | RAMA KRISHNA CGHS, PPG, S/STN-2:ID | TG-MAN084A-2 | 19501877 | 630 | 200 | 246 | 0.97 | 139 | 35 | 147 | 40 | 167 | 64 | 269 | 114 | 2019-06-10 23:30 | 32.7 | 5.1 | 278 | B | 82 | 84 | 134 | 52 | 0.2 | 10.6 | 88 | 1.1 | 719.17 | 718.17 | 597.47 | 708.47 |  | 1 | 1 | 10.3 | [12 empty] | 719.17 | 0.43 | 0.51 | 0.22
20 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN085 | 1S-DL-YP-ETC-DLNR-2503-MAN085 | SAHYADRI CGHS, PPG:ID | TG-MAN085A-1 | 19501452 | 400 | 120 | 245 | 0.97 | 64 | 12 | 53 | 27 | 116 | 24 | 101 | 57 | 2019-06-30 23:00 | 9.9 | 0.8 | 124 | Y | 76 | 122 | 102 | 46 |  |  | 2.8 | 97.2 | 719.57 | 717.57 | 719.57 | 719.57 |  | 2 | 2 | [13 empty] | 719.57 | 0.03 | 0.39 | 0.16
21 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN085 | 1S-DL-YP-ETC-DLNR-2503-MAN085 | SAHYADRI CGHS, PPG:ID | TG-MAN085A-2 | 19501455 | 400 | 120 | 245 | 0.96 | 69 | 28 | 120 | 22 | 90 | 18 | 78 | 38 | 2019-06-09 22:30 | 18.8 | 1.4 | 130 | R | 98 | 107 | 95 | 12 |  |  | 10.3 | 89.7 | 718.27 | 718.57 | 719.57 | 719.57 | 1.3 | 1 | 1 | [13 empty] | 719.57 | 0.03 | 0.51 | 0.17
22 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN086 | 1S-DL-YP-ETC-DLNR-2503-MAN086 | PHARMA CGHS, PPG S/STN-1:ID | TG-MAN086A-1 | 19501294 | 400 | 120 | 239 | 0.98 | 80 | 37 | 158 | 21 | 90 | 22 | 92 | 67 | 2019-06-29 | 17.9 | 0.6 | 159 | R | 141 | 78 | 81 | 63 |  |  | 2.9 | 97.1 | 583.26 | 719.56 | 719.56 | 719.56 | 136.3 | [15 empty] | 719.56 | 0.04 | 0.55 | 0.2
23 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN088 | 1S-DL-YP-ETC-DLNR-2503-MAN088 | PHARMA CGHS, PPG S/STN-3:ID | TG-MAN088A-2 | 19501209 | 400 | 120 | 239 | 0.98 | 94 | 35 | 147 | 41 | 173 | 19 | 80 | 84 | 2019-06-01 | 16.8 | 2.5 | 191 | Y | 110 | 128 | 62 | 66 |  |  | 11.5 | 88.5 | 614.29 | 549.59 | 719.56 | 679.26 | 105.27 | 169.57 | 169.57 | 40.3 | [12 empty] | 719.56 | 0.04 | 0.52 | 0.24
24 | 2019-06-19 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN089 | 1S-DL-YP-ETC-DLNR-2503-MAN089 | RAJDHANI NI-KUNJ CGHS PPG:ID | TG-MAN089A-2 | 19506924 | 400 | 120 | 246 | 0.99 | 38 | 16 | 66 | 10 | 42 | 13 | 55 | 21 | 2019-06-30 23:30 | 10.9 | 0.1 | 71 | Y | 86 | 69 | 145 | 76 |  |  | 0.4 | 99.6 | 264 | 264 | 264 | 264 | [16 empty] | 264 | 24 | 0.59 | 0.1
25 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN091 | 1S-DL-YP-ETC-DLNR-2503-MAN091 | NARWANA CGHS,PPG S/STN-1:ID | TG-MAN091A-1 | 19501225 | 630 | 200 | 244 | 0.97 | 142 | 37 | 154 | 47 | 196 | 57 | 236 | 71 | 2019-06-01 00:30 | 32.7 | 3.2 | 261 | B | 86 | 98 | 116 | 30 |  |  | 2.1 | 97.9 | 719.26 | 703.26 | 583.29 | 692.26 | 0.3 | 16.3 | 16.3 | 27.3 | [12 empty] | 719.56 | 0.04 | 0.55 | 0.22
26 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN092 | 1S-DL-YP-ETC-DLNR-2503-MAN092 | NARWANA CGHS,PPG S/STN-2:ID | TG-MAN092A-1 | 19501222 | 630 | 200 | 240 | 0.97 | 133 | 50 | 205 | 52 | 219 | 32 | 137 | 75 | 2019-06-11 23:30 | 30.8 | 6 | 242 | Y | 117 | 102 | 81 | 36 | 97.8 | 2.2 |  |  | 648.56 | 681.26 | 719.56 | 711.56 | 71 | 38.3 | 38.3 | 8 | [12 empty] | 719.56 | 0.04 | 0.58 | 0.21
27 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN095 | 1S-DL-YP-ETC-DLNR-2503-MAN095 | NATRAJ CGHS, PPG:ID | TG-MAN095A-2 | 19501172 | 400 | 120 | 239 | 0.97 | 98 | 29 | 122 | 29 | 123 | 40 | 169 | 46 | 2019-06-01 00:30 | 26.8 | 4.1 | 208 | B | 88 | 81 | 131 | 50 |  |  | 39.2 | 60.8 | 699.26 | 694.26 | 471.29 | 659.26 | 20.3 | 25.3 | 25.3 | 60.3 | [12 empty] | 719.56 | 0.04 | 0.57 | 0.24
28 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN095 | 1S-DL-YP-ETC-DLNR-2503-MAN095 | NATRAJ CGHS, PPG:ID | TG-MAN095A-1 | 19505401 | 400 | 120 | 246 | 0.97 | 75 | 24 | 101 | 29 | 123 | 21 | 88 | 30 | 2019-06-05 00:30 | 17.2 | 1.6 | 127 | R | 126 | 87 | 87 | 39 | 0.1 |  | 1.4 | 98.5 | 708.56 | 710.26 | 713.56 | 713.56 | 5 | 3.3 | 3.3 | [13 empty] | 713.56 | 6.04 | 0.48 | 0.19
29 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN096 | 1S-DL-YP-ETC-DLNR-2503-MAN096 | SAH-VIKAS CGHS, PPG:ID | TG-MAN096A-1 | 19501221 | 630 | 200 | 239 | 0.97 | 118 | 41 | 174 | 39 | 167 | 38 | 165 | 8 | 2019-06-30 00:30 | 24.4 | 2.3 | 177 | B | 104 | 102 | 94 | 10 |  |  | 1.3 | 98.7 | 719.56 | 719.56 | 719.26 | 719.56 | [16 empty] | 719.56 | 0.04 | 0.51 | 0.19
30 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN096 | 1S-DL-YP-ETC-DLNR-2503-MAN096 | SAH-VIKAS CGHS, PPG:ID | TG-MAN096A-2 | 19503809 | 630 | 200 | 239 | 0.98 | 101 | 51 | 203 | 17 | 70 | 34 | 140 | 115 | 2019-06-09 01:00 | 19.3 | 2.3 | 246 | R | 153 | 51 | 96 | 102 | 51.7 | 48.3 |  |  | 631.26 | 719.56 | 719.56 | 719.56 | 88.3 | [15 empty] | 719.56 | 0.04 | 0.5 | 0.16
31 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN097 | 1S-DL-YP-ETC-DLNR-2503-MAN097 | KAMAYANI KUNJ CGHS,PPG:ID | TG-MAN097A-1 | 19505412 | 400 | 120 | 241 | 0.98 | 93 | 21 | 90 | 34 | 144 | 38 | 159 | 63 | 2019-06-02 | 18.1 | 2.3 | 180 | B | 82 | 105 | 113 | 31 |  | 0.2 | 62.7 | 37.1 | 715.58 | 650.28 | 604 | 690.28 | 4 | 69.3 | 69.3 | 29.3 | [12 empty] | 719.58 | 0.02 | 0.53 | 0.23
32 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN098 | 1S-DL-YP-ETC-DLNR-2503-MAN098 | PLATO SCHOOL:PM | TG-MAN098A-1 | 19502763 | 100 | 40 | 246 | 0.96 | 32 | 8 | 31 | 4 | 17 | 20 | 80 | 57 | 2019-06-28 12:30 | 6 | -0.1 | 80 | B | 117 | 70 | 113 | 47 |  |  | 4.1 | 95.9 | 712.58 | 719.58 | 704.28 | 709.58 | 7 |  |  | 10 |  |  | 2.3 | [9 empty] | 719.58 | 0.02 | 0.1 | 0.32
33 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN100 | 1S-DL-YP-ETC-DLNR-2503-MAN100 | POOJA CGHS, PPG:ID | TG-MAN100A-2 | 19501113 | 630 | 200 | 245 | 0.98 | 121 | 29 | 120 | 35 | 144 | 56 | 230 | 100 | 2019-06-02 23:30 | 23.9 | 0.5 | 257 | B | 74 | 81 | 145 | 71 | 1.2 | 3.3 | 7.2 | 88.3 | 719.56 | 719.56 | 582.29 | 719.56 | [16 empty] | 719.56 | 0.04 | 0.5 | 0.19
34 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN100 | 1S-DL-YP-ETC-DLNR-2503-MAN100 | POOJA CGHS, PPG:ID | TG-MAN100A-1 | 19501293 | 630 | 200 | 240 | 0.95 | 77 | 23 | 97 | 26 | 111 | 28 | 119 | 19 | 2019-06-30 20:00 | 25.8 | 5.1 | 157 | B | 81 | 103 | 116 | 35 |  |  | 5.3 | 94.7 | 719.53 | 719.53 | 719.53 | 719.53 | [16 empty] | 719.53 | 0.07 | 0.57 | 0.12
35 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN101 | 1S-DL-YP-ETC-DLNR-2503-MAN101 | MITHILA CGHS, PPG:ID | TG-MAN101A-1 | 19506885 | 630 | 200 | 246 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [7 empty] | 5 | 95 | 711.56 | 711.56 | 711.56 | 711.56 | [16 empty] | 711.56 | 8.04 |  | 0
36 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN103 | 1S-DL-YP-ETC-DLNR-2503-MAN103 | SHRI GANESH CGHS, PPG:ID | TG-MAN103A-2 | 19501063 | 630 | 200 | 239 | 0.98 | 121 | 61 | 258 | 43 | 182 | 17 | 73 | 161 | 2019-06-12 00:30 | 23.5 | 3.2 | 269 | R | 143 | 94 | 63 | 80 |  |  | 0.1 | 99.9 | 592.35 | 716.33 | 718.33 | 718.33 | 125.58 | 2 | 2 | [13 empty] | 718.33 | 1.27 | 0.52 | 0.19
37 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN108 | 1S-DL-YP-ETC-DLNR-2503-MAN108 | TAKSHSHILA CGHS, PPG S/STN-2:ID | TG-MAN108A-2 | 19501132 | 400 | 120 | 237 | 0.98 | 89 | 47 | 194 | 28 | 116 | 14 | 58 | 118 | 2019-06-03 | 13 | 2.5 | 220 | R | 140 | 100 | 60 | 80 |  |  | 2.4 | 97.6 | 533.11 | 709.01 | 719.31 | 711.31 | 186.2 | 10.3 | 10.3 | 8 | [12 empty] | 719.31 | 0.29 | 0.49 | 0.22
38 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN109 | 1S-DL-YP-ETC-DLNR-2503-MAN109 | JAI LAXMI CGHS, PPG AVAS:ID | TG-MAN109A-2 | 19506199 | 630 | 200 | 237 | 0.98 | 148 | 53 | 227 | 56 | 241 | 39 | 166 | 70 | 2019-06-12 00:30 | 27.4 | 3 | 260 | Y | 106 | 108 | 87 | 21 | 0.1 |  | 0.1 | 99.8 | 622.35 | 588.35 | 695 | 657.05 | 73.25 | 107.25 | 107.25 | 38.55 | [12 empty] | 696 | 24 | 0.51 | 0.23
39 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN120 | 1S-DL-YP-ETC-DLNR-2503-MAN120 | KALLOL CGHS, PPG:ID | TG-MAN120A-2 | 19501171 | 630 | 200 | 246 | 0.98 | 111 | 25 | 106 | 30 | 126 | 57 | 240 | 126 | 2019-06-30 23:30 | 15.2 | 2.3 | 240 | B | 72 | 89 | 140 | 68 |  |  | 10.6 | 89.4 | 719.58 | 719.58 | 686.28 | 719.58 | [16 empty] | 719.58 | 0.02 | 0.46 | 0.18
40 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN120 | 1S-DL-YP-ETC-DLNR-2503-MAN120 | KALLOL CGHS, PPG:ID | TG-MAN120A-1 | 19501241 | 630 | 200 | 245 | 0.97 | 90 | 20 | 83 | 46 | 188 | 24 | 101 | 98 | 2019-06-03 00:30 | 17.9 | 2.8 | 201 | Y | 80 | 138 | 81 | 58 |  |  | 16.7 | 83.3 | 719.58 | 706.58 | 719.58 | 719.58 |  | 13 | 13 | [13 empty] | 719.58 | 0.02 | 0.52 | 0.14
41 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN121 | 1S-DL-YP-ETC-DLNR-2503-MAN121 | ARUNA CGHS, PPG:ID | TG-MAN121A-1 | 19501242 | 400 | 120 | 246 | 0.97 | 79 | 24 | 102 | 32 | 140 | 23 | 101 | 38 | 2019-06-30 23:00 | 17.1 | 2.2 | 151 | Y | 74 | 143 | 82 | 69 |  |  | 1.9 | 98.1 | 719.05 | 604.05 | 719.05 | 719.05 |  | 115 | 115 | [13 empty] | 719.05 | 0.55 | 0.5 | 0.2
42 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN121 | 1S-DL-YP-ETC-DLNR-2503-MAN121 | ARUNA CGHS, PPG:ID | TG-MAN121A-2 | 19506196 | 400 | 120 | 246 | 0.97 | 85 | 32 | 128 | 34 | 139 | 19 | 80 | 55 | 2019-06-26 23:30 | 22 | 2.2 | 184 | Y | 104 | 130 | 67 | 63 | 0.1 |  | 0.7 | 99.2 | 663.06 | 598.06 | 696 | 693 | 32.54 | 97.54 | 97.54 | 3 | [12 empty] | 696 | 24 | 0.49 | 0.21
43 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN122 | 1S-DL-YP-ETC-DLNR-2503-MAN122 | KAILASH APARTMENT, PPG:ID | TG-MAN122A-2 | 19505398 | 630 | 200 | 247 | 0.98 | 149 | 49 | 200 | 68 | 276 | 32 | 130 | 126 | 2019-06-01 22:00 | 31.2 | 3.2 | 331 | Y | 110 | 128 | 62 | 66 | 0.1 |  | 0.3 | 99.7 | 661.06 | 541.04 | 719.05 | 681.06 | 57.59 | 178.01 | 178.01 | 37.59 | [12 empty] | 719.05 | 0.55 | 0.51 | 0.24
44 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN122 | 1S-DL-YP-ETC-DLNR-2503-MAN122 | KAILASH APARTMENT, PPG:ID | TG-MAN122A-1 | 19505417 | 630 | 200 | 247 | 0.98 | 114 | 31 | 132 | 15 | 64 | 68 | 287 | 198 | 2019-06-09 23:30 | 28.8 | -9.6 | 295 | B | 87 | 38 | 175 | 137 | 0.1 |  | 0.2 | 99.7 | 719.01 | 719.01 | 555.31 | 719.01 | [16 empty] | 719.01 | 0.59 | 0.43 | 0.18
45 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN123 | 1S-DL-YP-ETC-DLNR-2503-MAN123 | SITA RAM CGHS,PPG,S/S-1:ID | TG-MAN123A-1 | 19501870 | 400 | 120 | 236 | 0.98 | 93 | 20 | 82 | 45 | 188 | 28 | 118 | 93 | 2019-06-11 23:00 | 15.7 | 1.4 | 212 | Y | 76 | 133 | 91 | 57 |  |  | 2.6 | 97.4 | 719.16 | 504 | 692.16 | 686.28 |  | 215.16 | 215.16 | 32.48 | [12 empty] | 719.16 | 0.44 | 0.54 | 0.23
46 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN124 | 1S-DL-YP-ETC-DLNR-2503-MAN124 | SITA RAM CGHS,PPG,S/S-2:ID | TG-MAN124A-2 | 19506620 | 630 | 200 | 234 | 0.99 | 124 | 24 | 114 | 31 | 138 | 70 | 318 | 193 | 2019-06-10 23:30 | 20.2 | 0.8 | 318 | B | 63 | 84 | 152 | 89 | 50.9 | 22.9 | 17.7 | 8.4 | 692.1 | 692.1 | 547.14 | 692.1 | [16 empty] | 692.1 | 27.5 | 0.48 | 0.2
47 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN127 | 1S-DL-YP-ETC-DLNR-2503-MAN127 | ASHIRWAD ENCLAVE, PPG:ID | TG-MAN127A-1 | 19505571 | 630 | 200 | 239 | 0.98 | 79 | 21 | 90 | 26 | 112 | 31 | 133 | 37 | 2019-06-12 00:30 | 16.4 | 0.4 | 143 | Y | 89 | 95 | 116 | 27 | 0.2 | 0.1 | 2.4 | 97.3 | 714.28 | 714.28 | 714.28 | 714.28 | [16 empty] | 714.28 | 5.32 | 0.53 | 0.13
48 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN128 | 1S-DL-YP-ETC-DLNR-2503-MAN128 | VARDAN CGHS, PPG:ID | TG-MAN128A-2 | 19501190 | 630 | 200 | 253 | 0.97 | 154 | 47 | 182 | 48 | 188 | 59 | 235 | 50 | 2019-06-11 00:30 | 33.1 | 6.4 | 237 | B | 101 | 77 | 122 | 45 |  |  | 5.8 | 94.2 | 682.26 | 716.56 | 613.59 | 696.56 | 37.3 | 3 | 3 | 23 | [12 empty] | 719.56 | 0.04 | 0.51 | 0.24
49 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN129 | 1S-DL-YP-ETC-DLNR-2503-MAN129 | DELHI RAJDHANI CGHS, PPG:ID | TG-MAN129A-1 | 19501334 | 630 | 200 | 246 | 0.98 | 137 | 47 | 191 | 48 | 194 | 42 | 168 | 25 | 2019-06-11 01:30 | 23.5 | 4.1 | 212 | Y | 101 | 108 | 91 | 17 |  |  | 11.9 | 88.1 | 696.42 | 693.42 | 710.12 | 713.12 | 23 | 26 | 26 | 6.3 | [12 empty] | 719.42 | 0.18 | 0.5 | 0.22
50 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN129 | 1S-DL-YP-ETC-DLNR-2503-MAN129 | DELHI RAJDHANI CGHS, PPG:ID | TG-MAN129A-2 | 19501333 | 630 | 200 | 247 | 0.96 | 113 | 48 | 194 | 28 | 114 | 37 | 151 | 69 | 2019-06-11 23:30 | 26.7 | 5.5 | 194 | R | 113 | 75 | 113 | 38 |  |  | 1.9 | 98.1 | 713.26 | 719.56 | 717.56 | 719.56 | 6.3 | [15 empty] | 719.56 | 0.04 | 0.53 | 0.18
51 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN131 | 1S-DL-YP-ETC-DLNR-2503-MAN131 | MAYUR DHWAJ CGHS,PPG,S/S-1:ID | TG-MAN131A-2 | 19501174 | 630 | 200 | 240 | 0.98 | 153 | 25 | 109 | 54 | 233 | 74 | 327 | 189 | 2019-06-10 23:30 | 29.4 | 3.2 | 331 | B | 49 | 101 | 150 | 101 |  |  | 5.3 | 94.7 | 719.58 | 664.28 | 453.3 | 674.28 |  | 55.3 | 55.3 | 45.3 | [12 empty] | 719.58 | 0.02 | 0.51 | 0.24
52 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN131 | 1S-DL-YP-ETC-DLNR-2503-MAN131 | MAYUR DHWAJ CGHS,PPG,S/S-1:ID | TG-MAN131A-1 | 19501186 | 630 | 200 | 245 | 0.98 | 144 | 27 | 113 | 67 | 284 | 50 | 213 | 148 | 2019-06-10 23:30 | 20.2 | 2.8 | 290 | Y | 56 | 152 | 92 | 96 |  |  | 0.6 | 99.4 | 719.58 | 538.58 | 710.28 | 715.58 |  | 181 | 181 | 4 | [12 empty] | 719.58 | 0.02 | 0.47 | 0.23
53 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN132 | 1S-DL-YP-ETC-DLNR-2503-MAN132 | MAYUR DHWAJ CGHS,PPG,S/S-2:ID | TG-MAN132A-2 | 19501235 | 630 | 200 | 240 | 0.98 | 126 | 26 | 108 | 47 | 200 | 54 | 230 | 110 | 2019-06-02 00:30 | 22.1 | 2.3 | 238 | Y | 50 | 121 | 129 | 79 |  |  | 1.5 | 98.5 | 719.58 | 677.28 | 636.28 | 718.58 |  | 42.3 | 42.3 | 1 | [12 empty] | 719.58 | 0.02 | 0.5 | 0.2
54 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN132 | 1S-DL-YP-ETC-DLNR-2503-MAN132 | MAYUR DHWAJ CGHS,PPG,S/S-2:ID | TG-MAN132A-1 | 19505300 | 630 | 200 | 241 | 0.98 | 132 | 46 | 199 | 57 | 248 | 29 | 128 | 104 | 2019-06-05 23:30 | 23.8 | 3 | 248 | Y | 116 | 112 | 72 | 44 | 0.1 |  | 10.7 | 89.2 | 643.28 | 650.58 | 719.58 | 711.58 | 76.3 | 69 | 69 | 8 | [12 empty] | 719.58 | 0.02 | 0.53 | 0.21
55 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN133 | 1S-DL-YP-ETC-DLNR-2503-MAN133 | MAYUR DHWAJ CGHS,PPG,S/S-3:ID | TG-MAN133A-1 | 19501231 | 400 | 120 | 246 | 0.98 | 89 | 35 | 148 | 18 | 75 | 37 | 153 | 76 | 2019-06-01 23:30 | 14.6 | 0.8 | 169 | R | 122 | 65 | 114 | 57 |  |  | 12.1 | 87.9 | 603.58 | 719.58 | 678.58 | 713.58 | 116 |  |  | 6 | [12 empty] | 719.58 | 0.02 | 0.46 | 0.22
56 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN135 | 1S-DL-YP-ETC-DLNR-2503-MAN135 | PRINCE CGHS,PPG S/S-2:ID | TG-MAN135A-1 | 19501966 | 630 | 200 | 241 | 0.99 | 157 | 53 | 221 | 46 | 192 | 58 | 242 | 43 | 2019-06-11 23:30 | 34.5 | -1.8 | 278 | B | 98 | 89 | 113 | 24 |  |  |  | 100 | 669.26 | 685.56 | 596.56 | 660.26 | 50.3 | 34 | 34 | 59.3 | [12 empty] | 719.56 | 0.04 | 0.56 | 0.25
57 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN135 | 1S-DL-YP-ETC-DLNR-2503-MAN135 | PRINCE CGHS,PPG S/S-2:ID | TG-MAN135A-2 | 19502564 | 630 | 200 | 241 | 0.97 | 134 | 44 | 187 | 45 | 190 | 45 | 191 | 4 | 2019-06-11 22:30 | 23 | 2.3 | 229 | B | 93 | 91 | 115 | 24 |  |  | 19 | 81 | 715.56 | 715.26 | 684.56 | 717.26 | 4 | 4.3 | 4.3 | 2.3 | [12 empty] | 719.56 | 0.04 | 0.48 | 0.21
58 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN136 | 1S-DL-YP-ETC-DLNR-2503-MAN136 | SUKH-SAGAR CGHS,PPG:ID | TG-MAN136A-1 | 19501332 | 630 | 200 | 246 | 0.98 | 93 | 38 | 164 | 22 | 95 | 34 | 146 | 63 | 2019-06-10 23:30 | 25.8 | 0.9 | 180 | R | 127 | 75 | 98 | 52 |  |  | 0.3 | 99.7 | 719 | 719.3 | 719.3 | 719.3 | 0.3 | [15 empty] | 719.3 | 0.3 | 0.49 | 0.15
59 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN137 | 1S-DL-YP-ETC-DLNR-2503-MAN137 | SHIKA APARTMENT,PPG:ID | TG-MAN137A-1 | 19501321 | 400 | 120 | 246 | 0.96 | 73 | 32 | 131 | 12 | 46 | 29 | 119 | 79 | 2019-06-15 23:30 | 22.6 | 0.6 | 145 | R | 137 | 54 | 109 | 83 |  |  | 0.1 | 99.9 | 641.13 | 719.3 | 717 | 719.3 | 78.17 | [15 empty] | 719.3 | 0.3 | 0.53 | 0.18
60 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN137 | 1S-DL-YP-ETC-DLNR-2503-MAN137 | SHIKA APARTMENT,PPG:ID | TG-MAN137A-2 | 19501325 | 400 | 120 | 240 | 0.97 | 62 | 22 | 92 | 23 | 94 | 18 | 73 | 21 | 2019-06-14 | 14.1 | 1.1 | 118 | R | 97 | 102 | 100 | 5 | 3.3 | 17.7 | 12.4 | 66.5 | 719 | 719 | 719.3 | 719.3 | 0.3 | 0.3 | 0.3 | [13 empty] | 719.3 | 0.3 | 0.47 | 0.16
61 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN138 | 1S-DL-YP-ETC-DLNR-2503-MAN138 | HANUMAN MANGLA CGHS,PPG:ID | TG-MAN138A-2 | 19501316 | 400 | 120 | 240 | 0.98 | 80 | 21 | 92 | 24 | 103 | 35 | 150 | 54 | 2019-06-11 23:00 | 14.1 | 2.5 | 150 | B | 105 | 98 | 97 | 8 |  |  | 0.3 | 99.7 | 719.29 | 709.59 | 705.59 | 718.59 |  | 9.3 | 9.3 | 0.3 | [12 empty] | 719.29 | 0.31 | 0.51 | 0.2
62 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN138 | 1S-DL-YP-ETC-DLNR-2503-MAN138 | HANUMAN MANGLA CGHS,PPG:ID | TG-MAN138A-1 | 19501320 | 400 | 120 | 247 | 0.97 | 95 | 37 | 159 | 28 | 122 | 30 | 131 | 33 | 2019-06-10 23:00 | 22.4 | 3 | 159 | R | 117 | 104 | 79 | 38 |  |  | 0.1 | 99.9 | 611 | 688.32 | 706.3 | 696 | 108.3 | 30.58 | 30.58 | 23.3 | [12 empty] | 719.3 | 0.3 | 0.5 | 0.24
63 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN139 | 1S-DL-YP-ETC-DLNR-2503-MAN139 | UNESCO CGHS, S/S-1,PPG:ID | TG-MAN139A-2 | 19501065 | 630 | 200 | 239 | 0.98 | 162 | 54 | 232 | 57 | 246 | 52 | 223 | 20 | 2019-06-02 | 25.3 | 2.3 | 338 | Y | 88 | 120 | 92 | 32 |  |  | 0.1 | 99.9 | 692.28 | 560 | 694.28 | 656.58 | 27.3 | 159.58 | 159.58 | 63 | [12 empty] | 719.58 | 0.02 | 0.51 | 0.26
64 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN140 | 1S-DL-YP-ETC-DLNR-2503-MAN140 | UNESCO CGHS,S/S-2,PPG:ID | TG-MAN140A-2 | 19501987 | 630 | 200 | 246 | 0.97 | 150 | 79 | 334 | 34 | 143 | 37 | 153 | 186 | 2019-06-10 22:00 | 29 | 3.2 | 334 | R | 136 | 84 | 80 | 56 | 87.8 | 12.2 |  |  | 460.3 | 717.58 | 697.58 | 677.58 | 259.28 | 2 | 2 | 42 | [12 empty] | 719.58 | 0.02 | 0.56 | 0.24
65 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN140 | 1S-DL-YP-ETC-DLNR-2503-MAN140 | UNESCO CGHS,S/S-2,PPG:ID | TG-MAN140A-1 | 19505975 | 630 | 200 | 246 | 0.98 | 106 | 53 | 230 | 0 | 0 | 53 | 217 | 224 | 2019-06-30 23:30 | 18.8 | 3 | 253 | B | 138 | 0 | 162 | 162 | 100 |  |  |  | 675.58 | 719.58 | 552.58 | 719.58 | 44 | [15 empty] | 719.58 | 0.02 | 0.59 | 0.17
66 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN141 | 1S-DL-YP-ETC-DLNR-2503-MAN141 | AMAR PALI CGHS,S/S-1,PPG:ID | TG-MAN141A-2 | 19506201 | 630 | 200 | 231 | 0.97 | 155 | 56 | 227 | 38 | 152 | 62 | 252 | 90 | 2019-06-03 01:00 | 31.6 | 6.4 | 283 | B | 107 | 74 | 119 | 45 | 37.2 |  | 55.2 | 7.5 | 407.3 | 461.28 | 342 | 425.3 | 55.58 | 2 | 2 | 37.58 | [12 empty] | 714.58 | 5.02 | 0.52 | 0.25
67 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN142 | 1S-DL-YP-ETC-DLNR-2503-MAN142 | AMAR PALI CGHS,S/S-2,PPG:ID | TG-MAN142A-1 | 19506203 | 630 | 200 | 240 | 0.96 | 105 | 30 | 133 | 24 | 105 | 51 | 222 | 106 | 2019-06-30 23:30 | 26 | 3.8 | 222 | B | 102 | 68 | 130 | 62 |  |  | 3.6 | 96.4 | 714.58 | 714.58 | 704.28 | 714.58 | [16 empty] | 714.58 | 5.02 | 0.5 | 0.17
68 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN143 | 1S-DL-YP-ETC-DLNR-2503-MAN143 | NAVNEETI CGHS, PPG:ID | TG-MAN143A-1 | 19505341 | 630 | 200 | 248 | 0.97 | 151 | 72 | 297 | 39 | 159 | 40 | 165 | 135 | 2019-06-11 22:30 | 30.6 | 4.8 | 298 | R | 111 | 101 | 87 | 24 | 0.1 |  | 4.8 | 95.1 | 628.56 | 670.56 | 694.56 | 689.56 | 72.3 | 30.3 | 30.3 | 11.3 | [12 empty] | 701.26 | 18.34 | 0.47 | 0.24
69 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN144 | 1S-DL-YP-ETC-DLNR-2503-MAN144 | KAKATYA, CGHS, PPG:ID | TG-MAN144A-1 | 19501228 | 630 | 200 | 246 | 0.95 | 141 | 43 | 183 | 58 | 248 | 40 | 168 | 74 | 2019-06-30 23:30 | 31.3 | 4.1 | 265 | Y | 94 | 129 | 77 | 52 |  |  | 1.4 | 98.6 | 715.28 | 615.3 | 719.58 | 715.28 | 4.3 | 104.28 | 104.28 | 4.3 | [12 empty] | 719.58 | 0.02 | 0.47 | 0.22
70 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN144 | 1S-DL-YP-ETC-DLNR-2503-MAN144 | KAKATYA, CGHS, PPG:ID | TG-MAN144A-2 | 19501066 | 630 | 200 | 246 | 0.97 | 113 | 46 | 192 | 31 | 127 | 35 | 146 | 58 | 2019-06-11 23:30 | 21.2 | 4.1 | 208 | B | 108 | 83 | 108 | 25 |  |  | 0.6 | 99.4 | 713.28 | 719.58 | 715.58 | 719.58 | 6.3 | [15 empty] | 719.58 | 0.02 | 0.51 | 0.18
71 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN146 | 1S-DL-YP-ETC-DLNR-2503-MAN146 | AAKRITI CGHS,PPG:ID | TG-MAN146A-2 | 19505919 | 630 | 200 | 240 | 0.98 | 116 | 27 | 119 | 50 | 218 | 38 | 167 | 86 | 2019-06-30 23:30 | 19.6 | -23.4 | 242 | Y | 38 | 221 | 41 | 183 | 3.5 | 0.1 | 3.2 | 93.2 | 719.5 | 675.2 | 719.5 | 719.5 |  | 44.3 | 44.3 | [13 empty] | 719.5 | 0.1 | 0.3 | 0.18
72 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN146 | 1S-DL-YP-ETC-DLNR-2503-MAN146 | AAKRITI CGHS,PPG:ID | TG-MAN146A-1 | 19505979 | 630 | 200 | 240 | 0.97 | 114 | 30 | 127 | 38 | 161 | 46 | 197 | 60 | 2019-06-02 23:30 | 28.4 | 5.4 | 208 | B | 78 | 108 | 114 | 36 |  |  | 1.7 | 98.3 | 719.52 | 716.52 | 699.52 | 719.52 |  | 3 | 3 | [13 empty] | 719.52 | 0.08 | 0.53 | 0.18
73 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN147 | 1S-DL-YP-ETC-DLNR-2503-MAN147 | NEW SURYA KIRAN CGHS,PPG:ID | TG-MAN147A-1 | 19505366 | 630 | 200 | 241 | 0.98 | 147 | 40 | 173 | 45 | 195 | 63 | 275 | 93 | 2019-06-04 23:00 | 25.6 | 5 | 285 | B | 91 | 86 | 123 | 37 |  | 0.1 | 11.3 | 88.6 | 692.33 | 698.33 | 537.05 | 655.33 | 21 | 15 | 15 | 58 | [12 empty] | 713.33 | 6.27 | 0.55 | 0.23
74 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN148 | 1S-DL-YP-ETC-DLNR-2503-MAN148 | DOOR SANCHAR CGHS,PPG:ID | TG-MAN148A-2 | 19505425 | 630 | 200 | 240 | 0.97 | 125 | 32 | 135 | 45 | 187 | 48 | 199 | 59 | 2019-06-11 23:30 | 30.6 | 4.6 | 239 | Y | 74 | 113 | 114 | 40 | 0.1 | 0.1 | 4.8 | 95.1 | 718.46 | 679.17 | 706.16 | 718.46 |  | 39.29 | 39.29 | [13 empty] | 718.46 | 1.14 | 0.52 | 0.2
75 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN148 | 1S-DL-YP-ETC-DLNR-2503-MAN148 | DOOR SANCHAR CGHS,PPG:ID | TG-MAN148A-1 | 19506200 | 630 | 200 | 241 | 0.98 | 149 | 67 | 278 | 48 | 200 | 34 | 143 | 118 | 2019-06-11 23:30 | 25.2 | 5.2 | 314 | R | 133 | 97 | 70 | 63 | 0.1 |  | 6.7 | 93.3 | 524.49 | 703.46 | 718.16 | 677.16 | 193.57 | 15 | 15 | 41.3 | [12 empty] | 718.46 | 1.14 | 0.52 | 0.24
76 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN149 | 1S-DL-YP-ETC-DLNR-2503-MAN149 | SIDH CGHS, PPG:ID | TG-MAN149A-1 | 19505413 | 630 | 200 | 240 | 0.98 | 212 | 73 | 305 | 61 | 256 | 78 | 326 | 63 | 2019-06-01 01:00 | 31.6 | 2.6 | 386 | B | 100 | 87 | 113 | 26 | 0.1 | 0.1 | 1.9 | 97.9 | 684.48 | 673.18 | 641.48 | 670.48 | 34 | 45.3 | 45.3 | 48 |  |  | 0.3 | [9 empty] | 718.48 | 1.12 | 0.34 | 0.34
77 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN149 | 1S-DL-YP-ETC-DLNR-2503-MAN149 | SIDH CGHS, PPG:ID | TG-MAN149A-2 | 19506202 | 630 | 200 | 246 | 0.98 | 107 | 37 | 156 | 43 | 181 | 27 | 114 | 59 | 2019-06-29 23:00 | 25.6 | -0.8 | 189 | Y | 97 | 114 | 89 | 25 | 0.1 |  | 32.1 | 67.8 | 694.48 | 691.48 | 695.18 | 695.18 | 0.3 | 3.3 | 3.3 | [13 empty] | 695.18 | 24.42 | 0.48 | 0.17
78 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN150 | 1S-DL-YP-ETC-DLNR-2503-MAN150 | ARYANAGAR CGHS,S/S-1.PPG:ID | TG-MAN150A-1 | 19503045 | 630 | 200 | 238 | 0.98 | 150 | 58 | 248 | 43 | 187 | 49 | 209 | 54 | 2019-06-11 23:30 | 20.7 | 3.7 | 264 | R | 117 | 84 | 99 | 33 |  |  | 0.1 | 99.9 | 600 | 716 | 684 | 692 | 119.3 | 3.3 | 3.3 | 27.3 | [12 empty] | 719.3 | 0.3 | 0.51 | 0.24
79 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN150 | 1S-DL-YP-ETC-DLNR-2503-MAN150 | ARYANAGAR CGHS,S/S-1.PPG:ID | TG-MAN150A-2 | 19504181 | 630 | 200 | 238 | 0.98 | 144 | 50 | 206 | 53 | 221 | 41 | 170 | 46 | 2019-06-11 22:30 | 27.1 | 3.7 | 257 | Y | 91 | 114 | 94 | 23 |  |  | 2.4 | 97.6 | 699.58 | 605.22 | 715.22 | 694.52 | 19.24 | 114 | 114 | 24.3 | [12 empty] | 719.22 | 0.38 | 0.5 | 0.23
80 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN151 | 1S-DL-YP-ETC-DLNR-2503-MAN151 | ARYANAGAR CGHS,S/S-2,PPG:ID | TG-MAN151A-2 | 19501994 | 630 | 200 | 237 | 0.97 | 158 | 48 | 213 | 80 | 356 | 30 | 132 | 196 | 2019-06-29 23:30 | 46.5 | 5.5 | 356 | Y | 94 | 140 | 67 | 73 |  | 0.1 | 36.1 | 63.8 | 682.01 | 337.38 | 719.31 | 649.31 | 37.3 | 381.53 | 381.53 | 70 | [12 empty] | 719.31 | 0.29 | 0.59 | 0.25
81 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN151 | 1S-DL-YP-ETC-DLNR-2503-MAN151 | ARYANAGAR CGHS,S/S-2,PPG:ID | TG-MAN151A-1 | 19502528 | 630 | 200 | 237 | 0.98 | 98 | 30 | 128 | 51 | 216 | 17 | 72 | 126 | 2019-06-02 23:00 | 19.3 | 2.3 | 240 | Y | 82 | 150 | 69 | 81 | 0.1 | 3.9 | 55.5 | 40.6 | 719.3 | 683 | 719.3 | 719.3 |  | 36.3 | 36.3 | [13 empty] | 719.3 | 0.3 | 0.53 | 0.16
82 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN152 | 1S-DL-YP-ETC-DLNR-2503-MAN152 | ARYANAGAR CGHS,S/S-3,PPG:ID | TG-MAN152A-1 | 19501992 | 630 | 200 | 237 | 0.99 | 151 | 47 | 199 | 65 | 271 | 39 | 166 | 93 | 2019-06-01 23:00 | 16.1 | 0.9 | 283 | Y | 92 | 133 | 75 | 58 |  |  | 0.3 | 99.7 | 704.31 | 558 | 718.01 | 698.31 | 15 | 161.31 | 161.31 | 21 | [12 empty] | 719.31 | 0.29 | 0.49 | 0.24
83 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN154 | 1S-DL-YP-ETC-DLNR-2503-MAN154 | VIDHI CGHS, PPG:ID | TG-MAN154A-2 | 19504827 | 400 | 120 | 239 | 0.97 | 95 | 34 | 140 | 36 | 150 | 25 | 103 | 43 | 2019-06-15 23:30 | 21.5 | 2.5 | 200 | Y | 88 | 141 | 71 | 70 |  |  | 12.2 | 87.8 | 699.56 | 438.59 | 717.26 | 663.26 | 20 | 280.57 | 280.57 | 56.3 | [12 empty] | 719.56 | 0.04 | 0.55 | 0.24
84 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN155 | 1S-DL-YP-ETC-DLNR-2503-MAN155 | KURMANCHAL CGHS, PPG:ID | TG-MAN155A-1 | 19505414 | 400 | 120 | 240 | 0.98 | 102 | 33 | 144 | 35 | 150 | 35 | 151 | 7 | 2019-06-30 23:30 | 24.1 | 1.4 | 175 | B | 115 | 75 | 110 | 40 | 0.1 |  | 5.7 | 94.2 | 631.41 | 667.41 | 657.41 | 678.11 | 87 | 51 | 51 | 40.3 | [12 empty] | 718.41 | 1.19 | 0.44 | 0.26
85 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN157 | 1S-DL-YP-ETC-DLNR-2503-MAN157 | SAGAR CGHS, PPG:ID | TG-MAN157A-2 | 19506849 | 400 | 120 | 240 | 0.97 | 63 | 2 | 10 | 32 | 136 | 29 | 123 | 120 | 2019-06-30 | 13.9 | 1.4 | 152 | Y | 7 | 138 | 155 | 148 |  |  | 4.9 | 95.1 | 696.26 | 674.56 | 679.26 | 696.26 |  | 21.3 | 21.3 | [13 empty] | 696.26 | 23.34 | 0.47 | 0.16
86 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN158 | 1S-DL-YP-ETC-DLNR-2503-MAN158 | KAYMES VRINDAVAN,CGHS PPJ:ID | TG-MAN158A-1 | 19501245 | 400 | 120 | 240 | 0.97 | 40 | 16 | 70 | 18 | 79 | 7 | 31 | 44 | 2019-06-02 22:00 | 8.3 | 0.3 | 79 | Y | 101 | 122 | 76 | 46 |  |  | 1.1 | 98.9 | 719.56 | 719.56 | 719.56 | 719.56 | [16 empty] | 719.56 | 0.04 | 0.49 | 0.1
87 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN158 | 1S-DL-YP-ETC-DLNR-2503-MAN158 | KAYMES VRINDAVAN,CGHS PPJ:ID | TG-MAN158A-2 | 19506661 | 400 | 120 | 240 | 0.99 | 82 | 33 | 136 | 34 | 140 | 15 | 61 | 77 | 2019-06-12 | 11.8 | 0.7 | 164 | Y | 129 | 115 | 55 | 74 | 0.1 | 0.2 | 15.3 | 84.4 | 657.56 | 629.56 | 696.26 | 695.26 | 38.3 | 66.3 | 66.3 | 1 | [12 empty] | 696.26 | 23.34 | 0.5 | 0.2
88 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN159 | 1S-DL-YP-ETC-DLNR-2503-MAN159 | NDMC (VIDYUT NIKUNJ),CGHS PPG:ID | TG-MAN159A-1 | 19503056 | 400 | 120 | 245 | 0.97 | 80 | 46 | 190 | 19 | 78 | 14 | 58 | 122 | 2019-06-02 23:30 | 17.7 | 2.2 | 212 | R | 154 | 74 | 71 | 83 |  | 0.1 | 24.8 | 75.1 | 499 | 719.57 | 719.57 | 719.57 | 220.57 | [15 empty] | 719.57 | 0.03 | 0.55 | 0.2
89 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN159 | 1S-DL-YP-ETC-DLNR-2503-MAN159 | NDMC (VIDYUT NIKUNJ),CGHS PPG:ID | TG-MAN159A-2 | 19504178 | 400 | 120 | 245 | 0.98 | 89 | 29 | 115 | 33 | 133 | 27 | 107 | 23 | 2019-06-13 23:00 | 21 | 1.7 | 151 | Y | 94 | 110 | 97 | 16 |  |  | 0.7 | 99.3 | 679.26 | 647.56 | 683.26 | 685.26 | 16.3 | 48 | 48 | 10.3 | [12 empty] | 695.56 | 0.04 | 0.5 | 0.22
90 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN160 | 1S-DL-YP-ETC-DLNR-2503-MAN160 | VIJAY LAXMI CGHS, PPG:ID | TG-MAN160A-1 | 19501922 | 400 | 120 | 246 | 0.97 | 67 | 20 | 83 | 33 | 136 | 14 | 57 | 70 | 2019-06-30 | 13.8 | 1.4 | 138 | Y | 91 | 129 | 81 | 48 |  |  | 0.2 | 99.8 | 719.04 | 707.04 | 719.04 | 719.04 |  | 12 | 12 | [13 empty] | 719.04 | 0.56 | 0.48 | 0.17
91 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN160 | 1S-DL-YP-ETC-DLNR-2503-MAN160 | VIJAY LAXMI CGHS, PPG:ID | TG-MAN160A-2 | 19501986 | 400 | 120 | 246 | 0.98 | 89 | 36 | 152 | 24 | 102 | 29 | 119 | 44 | 2019-06-11 23:30 | 17.4 | 2.2 | 168 | R | 118 | 87 | 95 | 31 |  |  | 0.8 | 99.2 | 627.35 | 718.35 | 711.35 | 708.35 | 91.3 | 0.3 | 0.3 | 10.3 | [12 empty] | 719.05 | 0.55 | 0.48 | 0.22
92 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN161 | 1S-DL-YP-ETC-DLNR-2503-MAN161 | JAI APARTMENT, JAI SANTOSHI PPG:ID | TG-MAN161A-1 | 19502529 | 630 | 200 | 237 | 0.98 | 157 | 65 | 266 | 31 | 129 | 61 | 249 | 129 | 2019-06-03 | 26.7 | 3.7 | 293 | R | 119 | 62 | 119 | 57 |  |  |  | 100 | 534.32 | 719.3 | 565.3 | 656.02 | 184.58 |  |  | 63.28 | [12 empty] | 719.3 | 0.3 | 0.53 | 0.25
93 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN161 | 1S-DL-YP-ETC-DLNR-2503-MAN161 | JAI APARTMENT, JAI SANTOSHI PPG:ID | TG-MAN161A-2 | 19504324 | 630 | 200 | 237 | 0.98 | 145 | 37 | 164 | 44 | 193 | 63 | 279 | 103 | 2019-06-30 | 26.7 | 2.3 | 284 | B | 87 | 82 | 131 | 49 |  |  | 0.4 | 99.6 | 712.01 | 709.31 | 552.3 | 687.01 | 7.3 | 10 | 10 | 32.3 | [12 empty] | 719.31 | 0.29 | 0.51 | 0.23
94 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN162 | 1S-DL-YP-ETC-DLNR-2503-MAN162 | HIMVARSHA CGHS, PPG:ID | TG-MAN162A-1 | 19501891 | 630 | 200 | 246 | 0.97 | 146 | 53 | 212 | 50 | 205 | 43 | 178 | 31 | 2019-06-13 23:00 | 32.7 | 5.1 | 247 | R | 116 | 90 | 94 | 26 | 99.3 | 0.7 |  |  | 595.58 | 700.58 | 703.28 | 686.58 | 124 | 19 | 19 | 33 | [12 empty] | 719.58 | 0.02 | 0.54 | 0.23
95 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN162 | 1S-DL-YP-ETC-DLNR-2503-MAN162 | HIMVARSHA CGHS, PPG:ID | TG-MAN162A-2 | 19506486 | 630 | 200 | 245 | 0.97 | 149 | 55 | 232 | 50 | 213 | 44 | 184 | 42 | 2019-06-30 00:30 | 27.2 | 5.6 | 287 | R | 116 | 78 | 106 | 38 | 0.1 | 2.1 | 36.9 | 60.9 | 609.3 | 715.28 | 640 | 680.58 | 110.28 | 4.3 | 4.3 | 39 | [12 empty] | 719.58 | 0.02 | 0.51 | 0.24
96 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN163 | 1S-DL-YP-ETC-DLNR-2503-MAN163 | SHIVALIK CGHS, PPG:ID | TG-MAN163A-2 | 19502549 | 630 | 200 | 246 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [8 empty] | 100 | 719.58 | 719.58 | 719.58 | 719.58 | [16 empty] | 719.58 | 0.02 |  | 0
97 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN165 | 1S-DL-YP-ETC-DLNR-2503-MAN165 | MOON LIGHT CGHS, PPG:ID | TG-MAN165A-1 | 19501970 | 630 | 200 | 239 | 0.97 | 106 | 37 | 159 | 39 | 165 | 30 | 127 | 36 | 2019-06-11 00:30 | 24.4 | 5.1 | 184 | R | 118 | 102 | 80 | 38 | 0.2 | 16.7 | 55.3 | 27.8 | 718.28 | 719.58 | 719.58 | 719.58 | 1.3 | [15 empty] | 719.58 | 0.02 | 0.55 | 0.17
98 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN165 | 1S-DL-YP-ETC-DLNR-2503-MAN165 | MOON LIGHT CGHS, PPG:ID | TG-MAN165A-2 | 19506888 | 630 | 200 | 241 | 0.98 | 79 | 4 | 18 | 38 | 162 | 37 | 159 | 143 | 2019-06-01 23:30 | 21.2 | 2 | 206 | B | 11 | 137 | 152 | 141 | 0.1 |  | 3.3 | 96.6 | 710.28 | 710.28 | 705.58 | 710.28 | [16 empty] | 710.28 | 9.32 | 0.49 | 0.13
99 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN167 | 1S-DL-YP-ETC-DLNR-2503-MAN167 | AZAD APARTMENT, PPG:ID | TG-MAN167A-2 | 19502514 | 630 | 200 | 246 | 0.95 | 97 | 26 | 106 | 37 | 154 | 34 | 138 | 43 | 2019-06-12 00:30 | 34 | 1.8 | 215 | Y | 82 | 156 | 62 | 94 |  |  | 1.4 | 98.6 | 717.13 | 703.13 | 717.13 | 717.13 |  | 14 | 14 | [13 empty] | 717.13 | 2.47 | 0.4 | 0.15
100 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN167 | 1S-DL-YP-ETC-DLNR-2503-MAN167 | AZAD APARTMENT, PPG:ID | TG-MAN167A-1 | 19506727 | 630 | 200 | 246 | 0.98 | 177 | 78 | 309 | 49 | 196 | 50 | 210 | 106 | 2019-06-29 04:00 | 80.2 | 0.8 | 309 | R | 99 | 133 | 68 | 65 | 100 |  |  |  | 691.01 | 642.59 | 716.29 | 715.29 | 26.58 | 75 | 75 | 2.3 | [12 empty] | 717.59 | 2.01 | 0.36 | 0.28
101 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN203 | 1S-DL-YP-ETC-DLNR-2503-MAN203 | SHIVANI CGHS, PPG:ID | TG-MAN203A-2 | 19501879 | 400 | 120 | 239 | 0.98 | 66 | 16 | 71 | 32 | 141 | 17 | 74 | 69 | 2019-06-01 23:00 | 11 | 0.3 | 150 | Y | 72 | 148 | 80 | 76 |  |  | 16.1 | 83.9 | 719.3 | 706.3 | 719.3 | 719.3 |  | 13 | 13 | [13 empty] | 719.3 | 0.3 | 0.48 | 0.16
102 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN203 | 1S-DL-YP-ETC-DLNR-2503-MAN203 | SHIVANI CGHS, PPG:ID | TG-MAN203A-1 | 19505990 | 400 | 120 | 253 | 0.97 | 70 | 17 | 69 | 23 | 95 | 30 | 122 | 46 | 2019-06-05 00:30 | 17.8 | 2.2 | 128 | B | 73 | 99 | 127 | 54 | 0.1 | 0.2 | 42.3 | 57.3 | 715 | 715 | 699 | 715 | [16 empty] | 715 | 5 | 0.49 | 0.17
103 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN210 | 1S-DL-YP-ETC-DLNR-2503-MAN210 | MILAN VIH SS I:ID | TG-MAN209A-2 | 19506900 | 630 | 200 | 246 | 0.97 | 149 | 40 | 164 | 49 | 203 | 61 | 252 | 77 | 2019-06-28 23:30 | 27 | -31.2 | 278 | B | 85 | 96 | 119 | 34 | 0.1 |  | 3 | 96.8 | 707.29 | 702.59 | 667.59 | 697.29 | 0.3 | 5 | 5 | 10.3 | [12 empty] | 707.59 | 12.01 | 0.2 | 0.24
104 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN211 | 1S-DL-YP-ETC-DLNR-2503-MAN211 | SUDARSHAN,PPG.:ID | TG-MAN211A-1 | 19501346 | 630 | 200 | 246 | 0.97 | 120 | 43 | 173 | 37 | 148 | 40 | 160 | 22 | 2019-06-10 23:30 | 27.6 | 2.3 | 202 | R | 119 | 92 | 89 | 30 |  |  | 3.1 | 96.9 | 689.56 | 719.56 | 718.56 | 719.56 | 30 | [15 empty] | 719.56 | 0.04 | 0.51 | 0.19
105 | 2019-06-16 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN211 | 1S-DL-YP-ETC-DLNR-2503-MAN211 | SUDARSHAN,PPG.:ID | TG-MAN211A-2 | 19501291 | 630 | 200 | 247 | 0.98 | 173 | 89 | 363 | 38 | 154 | 46 | 188 | 195 | 2019-06-30 23:30 | 26.2 | 2.3 | 363 | R | 148 | 64 | 88 | 84 |  |  | 0.4 | 99.6 | 227.3 | 359.57 | 345.57 | 328.57 | 131.27 |  |  | 31 | 1 | [11 empty] | 359.57 | 0.03 | 0.45 | 0.27
106 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN237 | 1S-DL-YP-ETC-DLNR-2503-MAN237 | KANCHAN CHANGA APPT:ID | TG-MAN237A-1 | 19502565 | 400 | 120 | 239 | 0.98 | 105 | 49 | 214 | 18 | 78 | 39 | 171 | 121 | 2019-06-30 23:30 | 19.9 | 1.4 | 240 | B | 105 | 64 | 132 | 68 | 2.6 | 8.3 | 58.8 | 30.2 | 631.3 | 719.58 | 519 | 651 | 88.28 |  |  | 68.58 |  |  | 1 | [9 empty] | 719.58 | 0.02 | 0.47 | 0.26
107 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN237 | 1S-DL-YP-ETC-DLNR-2503-MAN237 | KANCHAN CHANGA APPT:ID | TG-MAN237A-2 | 19502952 | 400 | 120 | 240 | 0.96 | 73 | 20 | 87 | 24 | 107 | 29 | 127 | 35 | 2019-06-08 23:00 | 22.4 | 1.9 | 129 | B | 80 | 99 | 121 | 41 |  |  | 0.1 | 99.9 | 719.58 | 719.58 | 716.58 | 719.58 | [16 empty] | 719.58 | 0.02 | 0.5 | 0.18
108 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN238 | 1S-DL-YP-ETC-DLNR-2503-MAN238 | CNG PETROL PUMP:PM | TG-MAN238A-1 | 19505950 | 630 | 200 | 255 | 0.98 | 454 | 152 | 622 | 193 | 778 | 109 | 440 | 293 | 2019-06-12 10:30 | 89 | -3.4 | 778 | Y | 126 | 76 | 98 | 50 |  |  | 4.3 | 95.7 | 712.26 | 713.26 | 713.26 | 713.26 | 1 |  |  |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 | [6 empty] | 713.56 | 6.04 | 0.05 | 0.72
109 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN240 | 1S-DL-YP-ETC-DLNR-2503-MAN240 | MILAN VIHAR SUB STN 3:ID | TG-MAN240A-1 | 19502513 | 630 | 200 | 240 | 0.98 | 154 | 73 | 302 | 41 | 172 | 40 | 172 | 130 | 2019-06-12 00:30 | 28.1 | 2.8 | 313 | R | 122 | 89 | 89 | 33 | 10.5 | 89.4 | 0.1 |  | 591.02 | 715.3 | 716 | 689 | 128.28 | 4 | 4 | 30.3 | [12 empty] | 719.3 | 0.3 | 0.49 | 0.24
110 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN240 | 1S-DL-YP-ETC-DLNR-2503-MAN240 | MILAN VIHAR SUB STN 3:ID | TG-MAN240A-2 | 19502515 | 630 | 200 | 246 | 0.97 | 122 | 27 | 111 | 54 | 224 | 41 | 171 | 98 | 2019-06-02 23:30 | 26.7 | 4.1 | 232 | Y | 81 | 131 | 88 | 50 |  | 0.2 | 11.6 | 88.2 | 719.3 | 629.32 | 719 | 719.3 |  | 89.58 | 89.58 | [13 empty] | 719.3 | 0.3 | 0.56 | 0.19
111 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN241 | 1S-DL-YP-ETC-DLNR-2503-MAN241 | MILAN VIHAR SUB STN 4:ID | TG-MAN241A-1 | 19502567 | 630 | 200 | 240 | 0.99 | 143 | 56 | 243 | 39 | 169 | 47 | 206 | 64 | 2019-06-30 23:30 | 17.5 | 1.8 | 251 | R | 96 | 103 | 101 | 7 |  |  | 4.8 | 95.2 | 672 | 708.3 | 711 | 710 | 47.3 | 11 | 11 | 9.3 | [12 empty] | 719.3 | 0.3 | 0.5 | 0.23
112 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN246 | 1S-DL-YP-ETC-DLNR-2503-MAN246 | STORM W/PUMP STN. NR. MAYFAIR IP EXT.:ID | TG-MAN246A-1 | 19506123 | 400 | 120 | 242 | 0.94 | 138 | 46 | 188 | 45 | 181 | 47 | 190 | 8 | 2019-06-23 18:00 | 117.4 | -21.2 | 221 | R | 104 | 88 | 109 | 21 | 45.5 | 6 | 30.3 | 18.3 | 646.58 | 664.58 | 637.58 | 657.28 | 57 | 39 | 39 | 46.3 | [12 empty] | 708.58 | 11.02 | 0.2 | 0.34
113 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN250 | 1S-DL-YP-ETC-DLNR-2503-MAN250 | INSTITUTIONAL AREA S/STN NO-1 | TG-MAN250A-1 | 19504473 | 630 | 200 | 248 | 0.99 | 81 | 28 | 117 | 27 | 111 | 25 | 102 | 13 | 2019-06-09 16:00 | 17 | -2.8 | 117 | R | 116 | 110 | 74 | 42 |  |  | 1.4 | 98.6 | 719.56 | 719.56 | 719.56 | 719.56 | [16 empty] | 719.56 | 0.04 | 0.32 | 0.13
114 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN251 | 1S-DL-YP-ETC-DLNR-2503-MAN251 | INSTITUTIONAL AREA S/STN NO-3 | TG-MAN251A-1 | 19504487 | 630 | 200 | 247 | 0.95 | 244 | 73 | 295 | 79 | 319 | 93 | 377 | 73 | 2019-06-28 09:30 | 52 | -22.1 | 395 | B | 89 | 86 | 126 | 40 |  |  | 19.9 | 80.1 | 676.57 | 682.27 | 639.57 | 669.27 | 42.3 | 37.3 | 37.3 | 50.3 | 0.3 |  | 12 | [9 empty] | 719.57 | 0.03 | 0.23 | 0.39
115 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN252 | 1S-DL-YP-ETC-DLNR-2503-MAN252 | S/STN NO-10, CGHS, PPG | TG-MAN252A-1 | 19504304 | 630 | 200 | 241 | 0.98 | 113 | 45 | 191 | 39 | 167 | 29 | 120 | 62 | 2019-06-10 14:30 | 31.3 | -7.8 | 208 | R | 95 | 112 | 93 | 19 |  | 27.7 | 72.2 | 0.1 | 700.2 | 711.2 | 719.2 | 719.2 | 19 | 8 | 8 | [13 empty] | 719.2 | 0.4 | 0.56 | 0.18
116 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN278 | 1S-DL-YP-ETC-DLNR-2503-MAN278 | New Gazi Pur Vag Mkt.S/Stn | TG-MAN278A-2 | 19506322 | 630 | 200 | 250 | 0.99 | 65 | 31 | 123 | 15 | 60 | 19 | 76 | 57 | 2019-06-24 12:00 | 16 | 1.6 | 125 | B | 94 | 89 | 117 | 28 |  | 0.1 | 9.7 | 90.1 | 713.51 | 713.51 | 713.51 | 713.51 | [16 empty] | 713.51 | 6.09 | 0.66 | 0.1
117 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | MAN298 | 1S-DL-YP-ETC-DLNR-2503-MAN298 | DCP OFFICE MANDAWALI | TG-MAN298A-1 | 19506362 | 400 | 120 | 248 | 0.97 | 69 | 30 | 120 | 20 | 82 | 20 | 79 | 40 | 2019-06-10 | 16.6 | 0.6 | 140 | R | 122 | 93 | 85 | 37 |  | 0.1 | 16.7 | 83.1 | 650.37 | 713.37 | 713.37 | 713.37 | 63 | [15 empty] | 713.37 | 6.23 | 0.54 | 0.17
118 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR030 | 1S-DL-YP-ETC-DLNR-2502-PVR030 | S/STN. NO.5 F.I.E., PPG:ID | TG-PVR030A-1 | 19500815 | 630 | 200 | 250 | 0.72 | 134 | 50 | 203 | 59 | 242 | 26 | 108 | 119 | 2019-06-27 11:30 | 34.5 | -46.9 | 250 | Y | 111 | 111 | 78 | 33 |  | 0.1 | 12.8 | 87.2 | 677.21 | 585.51 | 719.51 | 705.21 | 42.3 | 134 | 134 | 14.3 | [12 empty] | 719.51 | 0.09 | 0.43 | 0.21
119 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR036 | 1S-DL-YP-ETC-DLNR-2502-PVR036 | S/STN. NO.11 F.I.E., PPG:ID | TG-PVR036A-1 | 19503810 | 630 | 200 | 244 | 0.96 | 117 | 41 | 172 | 31 | 131 | 45 | 190 | 53 | 2019-06-03 15:00 | 30.8 | -4.1 | 194 | B | 102 | 83 | 115 | 32 |  |  | 0.1 | 99.9 | 719.22 | 719.52 | 712.52 | 719.52 | 0.3 | [15 empty] | 719.52 | 0.08 | 0.27 | 0.19
120 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR037 | 1S-DL-YP-ETC-DLNR-2502-PVR037 | S/STN. NO.12 F.I.E., PPG:ID | TG-PVR037A-1 | 19506518 | 630 | 200 | 250 | 0.9 | 137 | 49 | 200 | 55 | 222 | 33 | 133 | 80 | 2019-06-28 16:00 | 55 | -43.2 | 302 | R | 120 | 115 | 65 | 55 |  | 0.2 | 7.5 | 92.3 | 680.52 | 552.52 | 712.52 | 703.22 | 32 | 160 | 160 | 9.3 | [12 empty] | 712.52 | 7.08 | 0.4 | 0.22
121 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR062 | 1S-DL-YP-ETC-DLNR-2502-PVR062 | DSIDC S/STN-1 PPG COMPLEX:ID | TG-PVR062A-1 | 19502569 | 630 | 200 | 250 | 0.95 | 151 | 51 | 209 | 45 | 181 | 55 | 224 | 38 | 2019-06-07 17:00 | 33.6 | -18.4 | 245 | B | 104 | 86 | 111 | 25 |  |  | 41.2 | 58.8 | 618.52 | 713.52 | 582.52 | 649.52 | 101 | 6 | 6 | 70 | [12 empty] | 719.52 | 0.08 | 0.36 | 0.24
122 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR087 | 1S-DL-YP-ETC-DLNR-2502-PVR087 | ISBT Anand Vihar Outside | TG-PVR087A-1 | 19504989 | 400 | 120 | 250 | 0.86 | 45 | 21 | 79 | 12 | 46 | 12 | 48 | 32 | 2019-06-06 18:00 | 31.5 | -0.3 | 81 | R | 126 | 83 | 91 | 43 |  |  | 0.4 | 99.6 | 719.52 | 719.52 | 719.52 | 719.52 | [16 empty] | 719.52 | 0.08 | 0.36 | 0.11
123 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR017 | 1S-DL-YP-ETC-DLNR-2501-LGR017 | POLICE QTR SHAKARPUR:ID | TG-LGR017A-1 | 19505830 | 990 | 320 | 242 | 0.98 | 224 | 90 | 381 | 75 | 315 | 60 | 256 | 108 | 2019-06-30 | 61.8 | 13.4 | 618 | R | 117 | 93 | 90 | 27 | 0.3 | 0.1 | 40.8 | 58.7 | 575.23 | 708.53 | 711.23 | 686.23 | 139.3 | 6 | 6 | 28.3 | [12 empty] | 714.53 | 5.07 | 0.57 | 0.23
124 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR095 | 1S-DL-YP-ETC-DLNR-2501-LGR095 | DMRC STAFF QUARTERS | TG-LGR095A-1 | 19504745 | 990 | 320 | 244 | 0.99 | 79 | 34 | 136 | 19 | 77 | 26 | 104 | 51 | 2019-06-12 01:30 | 9.6 | -0.7 | 141 | R | 137 | 74 | 89 | 63 |  |  | 8.5 | 91.5 | 716.31 | 716.31 | 716.31 | 716.31 | [16 empty] | 716.31 | 3.29 | 0.49 | 0.08
125 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | LAXMI NAGAR | 1230 | LGR095 | 1S-DL-YP-ETC-DLNR-2501-LGR095 | DMRC STAFF QUARTERS | TG-LGR095A-2 | 19504750 | 630 | 200 | 243 | 0.88 | 61 | 21 | 87 | 19 | 78 | 21 | 86 | 9 | 2019-06-30 17:30 | 34.5 | 1.4 | 92 | B | 107 | 94 | 99 | 13 |  |  | 8.1 | 91.9 | 719.24 | 719.24 | 719.24 | 719.24 | [16 empty] | 719.24 | 0.36 | 0.57 | 0.1
126 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN005 | 1S-DL-YP-ETC-DLNR-2503-MAN005 | MOTHER DAIRY STAFF QUARTOR:ID | TG-MAN005A-1 | 19504306 | 630 | 200 | 231 | 0.97 | 77 | 20 | 93 | 28 | 129 | 29 | 130 | 37 | 2019-06-07 23:00 | 13.8 | 3.2 | 139 | Y | 79 | 114 | 107 | 35 |  |  | 0.3 | 99.7 | 718.59 | 718.59 | 718.59 | 718.59 | [16 empty] | 718.59 | 1.01 | 0.52 | 0.12
127 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN035 | 1S-DL-YP-ETC-DLNR-2503-MAN035 | LSC-II, MANDAWALI:ID | TG-MAN035A-2 | 19505525 | 630 | 200 | 241 | 0.96 | 97 | 32 | 130 | 36 | 144 | 29 | 119 | 22 | 2019-06-27 12:30 | 52.8 | 0.6 | 172 | B | 90 | 107 | 103 | 17 | 0.1 |  | 0.2 | 99.7 | 719.05 | 719.05 | 719.05 | 719.05 | [16 empty] | 719.05 | 0.55 | 0.43 | 0.15
128 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN035 | 1S-DL-YP-ETC-DLNR-2503-MAN035 | LSC-II, MANDAWALI:ID | TG-MAN035A-1 | 19501890 | 630 | 200 | 240 | 0.98 | 97 | 40 | 167 | 28 | 118 | 29 | 122 | 47 | 2019-06-09 13:30 | 22.1 | 4.6 | 183 | R | 134 | 84 | 82 | 52 |  |  |  | 100 | 717.05 | 719.05 | 719.05 | 719.05 | 2 | [15 empty] | 719.05 | 0.55 | 0.51 | 0.15
129 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN036 | 1S-DL-YP-ETC-DLNR-2503-MAN036 | SWAMINARAIN TEMPLE YAMUNA PUSTA | TG-MAN036A-1 | 19505948 | 400 | 120 | 245 | 0.88 | 40 | 12 | 46 | 14 | 54 | 14 | 57 | 9 | 2019-06-06 06:30 | 21.8 | -36.7 | 71 | B | 102 | 91 | 107 | 16 |  |  | 4.2 | 95.8 | 717.55 | 717.55 | 717.55 | 717.55 | [16 empty] | 717.55 | 2.05 | 0.58 | 0.1
130 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN050 | 1S-DL-YP-ETC-DLNR-2503-MAN050 | NOIDA MORE FLYOVER:PM | TG-MAN050A-1 | 19506321 | 400 | 120 | 245 | 0.99 | 69 | 26 | 103 | 22 | 88 | 21 | 83 | 18 | 2019-06-21 18:30 | 9.4 | -5.4 | 103 | R | 103 | 95 | 102 | 8 |  |  | 0.6 | 99.4 | 647.12 | 647.12 | 647.12 | 647.12 | [16 empty] | 647.12 | 48.48 | 0.33 | 0.17
131 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN060 | 1S-DL-YP-ETC-DLNR-2503-MAN060 | S/STN.NO-3, PPG CGHS:ID | TG-MAN060A-2 | 19506318 | 400 | 120 | 238 | 0.98 | 79 | 20 | 92 | 38 | 172 | 21 | 95 | 79 | 2019-06-10 23:00 | 16 | 2.5 | 172 | Y | 84 | 130 | 86 | 46 | 0.1 |  | 1 | 98.9 | 718.52 | 629.58 | 716.52 | 718.52 |  | 88.54 | 88.54 | [13 empty] | 718.52 | 1.08 | 0.52 | 0.2
132 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN060 | 1S-DL-YP-ETC-DLNR-2503-MAN060 | S/STN.NO-3, PPG CGHS:ID | TG-MAN060A-1 | 19506319 | 400 | 120 | 237 | 0.98 | 87 | 51 | 229 | 22 | 100 | 14 | 62 | 152 | 2019-06-30 14:30 | 26.3 | 1.9 | 229 | R | 107 | 94 | 100 | 13 | 0.1 | 0.3 | 13.9 | 85.7 | 678.52 | 688.52 | 681.16 | 694.52 | 16.3 | 6.3 | 6.3 | 0.3 | [12 empty] | 695.22 | 24.38 | 0.55 | 0.22
133 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN061 | 1S-DL-YP-ETC-DLNR-2503-MAN061 | S/STN.NO-4, PPG CGHS:ID | TG-MAN061A-1 | 19506534 | 400 | 120 | 243 | 0.97 | 304 | 65 | 275 | 97 | 415 | 142 | 600 | 283 | 2019-06-26 12:00 | 67.4 | 0.7 | 600 | B | 128 | 68 | 104 | 60 |  |  | 0.9 | 99.1 | 576.47 | 688.37 | 621.47 | 650.37 | 115.5 | 6 | 6 | 44 | 2.3 | 0.3 |  | 0.3 | [6 empty] | 0.3 |  | 695.07 | 24.53 | 0.13 | 0.76
134 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN062 | 1S-DL-YP-ETC-DLNR-2503-MAN062 | S/STN.NO-5, PPG CGHS:ID | TG-MAN062A-1 | 19504610 | 400 | 120 | 246 | 0.97 | 64 | 35 | 141 | 21 | 85 | 7 | 28 | 98 | 2019-06-10 11:00 | 16.8 | -1.7 | 147 | R | 155 | 100 | 45 | 110 |  |  |  | 100 | 616.01 | 719.31 | 719.31 | 719.31 | 103.3 | [15 empty] | 719.31 | 0.29 | 0.3 | 0.16
135 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN110 | 1S-DL-YP-ETC-DLNR-2503-MAN110 | BATLA CGHS,PPG,S/STN-1:ID | TG-MAN110A-1 | 19500971 | 400 | 120 | 243 | 0.98 | 68 | 44 | 189 | 24 | 106 | 0 | 0 | 164 | 2019-06-11 00:30 | 13.2 | 1.9 | 199 | R | 201 | 99 | 0 | 201 |  |  | 0.1 | 99.9 | 486.3 | 719.3 | 719.3 | 719.3 | 233 | [15 empty] | 719.3 | 0.3 | 0.51 | 0.17
136 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN112 | 1S-DL-YP-ETC-DLNR-2503-MAN112 | KARISHMA APTT. PPG S/S-1:ID | TG-MAN112A-2 | 19500973 | 630 | 200 | 237 | 0.97 | 103 | 34 | 142 | 45 | 184 | 24 | 98 | 75 | 2019-06-02 23:30 | 20.7 | 2.3 | 221 | Y | 97 | 120 | 83 | 37 |  |  | 0.1 | 99.9 | 719.31 | 707.01 | 719.31 | 719.31 |  | 12.3 | 12.3 | [13 empty] | 719.31 | 0.29 | 0.55 | 0.16
137 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN113 | 1S-DL-YP-ETC-DLNR-2503-MAN113 | KARISHMA APTT. PPG S/S-2:ID | TG-MAN113A-1 | 19500988 | 630 | 200 | 243 | 0.97 | 129 | 44 | 185 | 43 | 179 | 42 | 175 | 8 | 2019-06-12 | 25.3 | 4.1 | 204 | Y | 93 | 107 | 100 | 14 |  |  | 0.1 | 99.9 | 717.01 | 705.01 | 716.01 | 719.01 | 2.3 | 14.3 | 14.3 | 0.3 | [12 empty] | 719.31 | 0.29 | 0.46 | 0.2
138 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN113 | 1S-DL-YP-ETC-DLNR-2503-MAN113 | KARISHMA APTT. PPG S/S-2:ID | TG-MAN113A-2 | 19504822 | 630 | 200 | 243 | 0.97 | 165 | 66 | 292 | 42 | 185 | 56 | 248 | 94 | 2019-06-11 | 35 | 5.1 | 307 | R | 133 | 75 | 92 | 58 |  |  | 19.1 | 80.9 | 515.3 | 713.01 | 686.04 | 648.04 | 204.01 | 6.3 | 6.3 | 71.27 | [12 empty] | 719.31 | 0.29 | 0.47 | 0.26
139 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN114 | 1S-DL-YP-ETC-DLNR-2503-MAN114 | KRIPAL CGHS, PPG:ID | TG-MAN114A-1 | 19500977 | 630 | 200 | 242 | 0.97 | 138 | 59 | 254 | 27 | 114 | 53 | 229 | 129 | 2019-06-30 | 28.1 | 5.1 | 255 | B | 119 | 63 | 119 | 56 |  |  | 0.2 | 99.8 | 639.3 | 719.3 | 651.3 | 707.3 | 80 |  |  | 12 | [12 empty] | 719.3 | 0.3 | 0.51 | 0.22
140 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN116 | 1S-DL-YP-ETC-DLNR-2503-MAN116 | ORIENTAL CGHS, PPG:ID | TG-MAN116A-2 | 19500984 | 400 | 120 | 246 | 0.97 | 17 | 0 | 0 | 17 | 69 | 0 | 0 | 69 | 2019-06-06 06:30 | 6.3 | 0.3 | 74 | Y | 0 | 300 | 0 | 300 |  |  | 0.2 | 99.8 | 719.04 | 719.04 | 719.04 | 719.04 | [16 empty] | 719.04 | 0.56 | 0.49 | 0.04
141 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN117 | 1S-DL-YP-ETC-DLNR-2503-MAN117 | AJANTA CGHS, PPG:ID | TG-MAN117A-2 | 19500987 | 630 | 200 | 246 | 0.97 | 135 | 54 | 223 | 48 | 199 | 32 | 133 | 81 | 2019-06-13 23:30 | 27.1 | 2.8 | 223 | R | 120 | 112 | 69 | 51 |  |  | 0.5 | 99.5 | 666.06 | 666.06 | 719.06 | 712.36 | 53 | 53 | 53 | 6.3 | [12 empty] | 719.06 | 0.54 | 0.49 | 0.21
142 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN117 | 1S-DL-YP-ETC-DLNR-2503-MAN117 | AJANTA CGHS, PPG:ID | TG-MAN117A-1 | 19500995 | 630 | 200 | 246 | 0.98 | 129 | 59 | 237 | 47 | 189 | 23 | 92 | 127 | 2019-06-03 | 20.7 | 2.8 | 249 | R | 134 | 107 | 59 | 75 |  |  | 0.3 | 99.7 | 637.27 | 698.57 | 718.57 | 717.27 | 81.3 | 20 | 20 | 1.3 | [12 empty] | 718.57 | 1.03 | 0.42 | 0.2
143 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN118 | 1S-DL-YP-ETC-DLNR-2503-MAN118 | VANDANA CGHS, PPG:ID | TI-MAN118A-2 | 19506910 | 400 | 120 | 241 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [7 empty] | 0.4 | 99.6 | 707.04 | 707.04 | 707.04 | 707.04 | [16 empty] | 707.04 | 12.56 |  | 0
144 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN119 | 1S-DL-YP-ETC-DLNR-2503-MAN119 | MIRTRADEEP CGHS, PPG:ID | TG-MAN119A-1 | 19504367 | 630 | 200 | 237 | 0.98 | 148 | 52 | 216 | 36 | 151 | 60 | 248 | 86 | 2019-06-11 23:00 | 23.5 | 2.3 | 286 | B | 103 | 80 | 117 | 37 |  |  | 0.1 | 99.9 | 694.01 | 719.01 | 622.01 | 694.01 | 25.3 | 0.3 | 0.3 | 25.3 | [12 empty] | 719.31 | 0.29 | 0.5 | 0.23
145 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN125 | 1S-DL-YP-ETC-DLNR-2503-MAN125 | SAVARKAR CGHS, PPG:ID | TG-MAN125A-2 | 19500975 | 630 | 200 | 246 | 0.98 | 93 | 31 | 126 | 27 | 109 | 35 | 145 | 31 | 2019-06-26 23:30 | 16.1 | 1.4 | 188 | B | 94 | 81 | 126 | 45 |  |  | 0.3 | 99.7 | 719.05 | 719.05 | 712.05 | 719.05 | [16 empty] | 719.05 | 0.55 | 0.51 | 0.15
146 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN153 | 1S-DL-YP-ETC-DLNR-2503-MAN153 | BROTHERS CGHS, PPG:ID | TG-MAN153A-1 | 19506889 | 400 | 120 | 246 | 0.97 | 96 | 22 | 90 | 25 | 103 | 49 | 204 | 108 | 2019-06-02 22:30 | 35.2 | 3.5 | 204 | B | 87 | 88 | 125 | 38 | 0.1 |  | 0.3 | 99.6 | 688.05 | 649.35 | 500.4 | 647.35 | 17 | 55.3 | 55.3 | 57.3 | [12 empty] | 705.05 | 14.55 | 0.58 | 0.24
147 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN168 | 1S-DL-YP-ETC-DLNR-2503-MAN168 | PANCH MAHAL,PPG CGHS:ID | TG-MAN168A-2 | 19506138 | 400 | 120 | 240 | 0.98 | 102 | 29 | 125 | 46 | 194 | 27 | 114 | 75 | 2019-06-02 23:00 | 21.2 | 2.2 | 211 | Y | 81 | 138 | 81 | 57 | 0.1 |  | 0.1 | 99.9 | 678.36 | 463.06 | 691.06 | 636.12 | 16.3 | 232 | 232 | 58.54 | [12 empty] | 695.06 | 24.54 | 0.46 | 0.26
148 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN168 | 1S-DL-YP-ETC-DLNR-2503-MAN168 | PANCH MAHAL,PPG CGHS:ID | TG-MAN168A-1 | 19500993 | 400 | 120 | 240 | 0.99 | 81 | 17 | 78 | 32 | 144 | 32 | 144 | 66 | 2019-06-30 23:30 | 9.4 | 0.6 | 150 | Y | 80 | 107 | 113 | 33 |  |  | 1.5 | 98.5 | 718.36 | 698.06 | 682.06 | 717.36 |  | 20.3 | 20.3 | 1 | [12 empty] | 718.36 | 1.24 | 0.46 | 0.2
149 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN169 | 1S-DL-YP-ETC-DLNR-2503-MAN169 | SARASWATI KUNJ CGHS S/S-1:ID | TG-MAN169A-2 | 19506456 | 630 | 200 | 244 | 0.96 | 120 | 38 | 147 | 33 | 137 | 48 | 197 | 56 | 2019-06-02 23:30 | 39 | 5.2 | 197 | B | 98 | 98 | 104 | 6 | 100 |  |  |  | 719.3 | 719.3 | 718.3 | 719.3 | [16 empty] | 719.3 | 0.3 | 0.46 | 0.19
150 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN169 | 1S-DL-YP-ETC-DLNR-2503-MAN169 | SARASWATI KUNJ CGHS S/S-1:ID | TG-MAN169A-1 | 19500950 | 630 | 200 | 243 | 0.98 | 136 | 51 | 206 | 35 | 141 | 50 | 203 | 63 | 2019-06-03 | 23 | 3.7 | 244 | R | 114 | 94 | 92 | 22 |  |  | 2.6 | 97.4 | 617 | 708.3 | 707.3 | 702.3 | 102.3 | 11 | 11 | 17 | [12 empty] | 719.3 | 0.3 | 0.53 | 0.22
151 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN171 | 1S-DL-YP-ETC-DLNR-2503-MAN171 | AKASH BHARTI CGHS PPG:ID | TG-MAN171A-2 | 19500951 | 630 | 200 | 240 | 0.98 | 153 | 46 | 204 | 54 | 238 | 52 | 228 | 31 | 2019-06-30 23:00 | 28.5 | 5.1 | 243 | Y | 102 | 102 | 96 | 6 |  |  | 8.2 | 91.8 | 682.22 | 650.22 | 649.42 | 673.52 | 36 | 68 | 68 | 44.3 | [12 empty] | 718.22 | 1.38 | 0.51 | 0.24
152 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN172 | 1S-DL-YP-ETC-DLNR-2503-MAN172 | PRESS APPARTMENT CGHS PPG:ID | TG-MAN172A-1 | 19500955 | 630 | 200 | 247 | 0.98 | 46 | 26 | 104 | 0 | 0 | 19 | 76 | 93 | 2019-06-03 06:00 | 11 | 0.9 | 112 | R | 165 | 0 | 135 | 165 |  |  | 2.3 | 97.7 | 718.21 | 718.21 | 718.21 | 718.21 | [16 empty] | 718.21 | 1.39 | 0.55 | 0.07
153 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN172 | 1S-DL-YP-ETC-DLNR-2503-MAN172 | PRESS APPARTMENT CGHS PPG:ID | TG-MAN172A-2 | 19500952 | 630 | 200 | 247 | 0.98 | 98 | 32 | 140 | 30 | 132 | 35 | 148 | 14 | 2019-06-02 22:30 | 18.9 | 2.3 | 168 | B | 89 | 94 | 117 | 28 |  |  | 29.6 | 70.4 | 718.21 | 718.21 | 718.21 | 718.21 | [16 empty] | 718.21 | 1.39 | 0.52 | 0.15
154 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN173 | 1S-DL-YP-ETC-DLNR-2503-MAN173 | RETREET CGHS PPG S/S-1:ID | TG-MAN173A-1 | 19502053 | 630 | 200 | 246 | 0.97 | 70 | 16 | 67 | 23 | 96 | 31 | 127 | 52 | 2019-06-09 23:00 | 13.3 | 1.8 | 137 | B | 61 | 104 | 135 | 74 |  | 0.1 | 58.1 | 41.7 | 718.21 | 718.21 | 718.21 | 718.21 | [16 empty] | 718.21 | 1.39 | 0.47 | 0.11
155 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN173 | 1S-DL-YP-ETC-DLNR-2503-MAN173 | RETREET CGHS PPG S/S-1:ID | TG-MAN173A-2 | 19505533 | 630 | 200 | 241 | 0.98 | 139 | 67 | 296 | 20 | 83 | 52 | 225 | 188 | 2019-06-30 14:30 | 45 | 2.4 | 296 | R | 89 | 112 | 98 | 23 | 0.1 | 0.1 | 5.5 | 94.3 | 717.51 | 713.51 | 717.51 | 717.51 | 0.3 | 4.3 | 4.3 | 0.3 | [12 empty] | 718.21 | 1.39 | 0.43 | 0.22
156 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN174 | 1S-DL-YP-ETC-DLNR-2503-MAN174 | RETREET CGHS PPG S/S-2:ID | TG-MAN174A-2 | 19502055 | 630 | 200 | 241 | 0.97 | 101 | 9 | 39 | 40 | 165 | 52 | 219 | 160 | 2019-06-16 00:30 | 17.9 | 2.3 | 219 | B | 49 | 120 | 130 | 81 |  |  | 4.1 | 95.9 | 718.22 | 718.22 | 707.22 | 718.22 | [16 empty] | 718.22 | 1.38 | 0.47 | 0.16
157 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN174 | 1S-DL-YP-ETC-DLNR-2503-MAN174 | RETREET CGHS PPG S/S-2:ID | TG-MAN174A-1 | 19502056 | 630 | 200 | 241 | 0.94 | 135 | 47 | 203 | 31 | 133 | 57 | 248 | 101 | 2019-06-30 23:30 | 45.1 | 10.6 | 271 | B | 92 | 85 | 124 | 39 |  |  | 0.1 | 99.9 | 717.21 | 716.21 | 571.51 | 714.51 | 1 | 2 | 2 | 3.3 | [12 empty] | 718.21 | 1.39 | 0.6 | 0.21
158 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN175 | 1S-DL-YP-ETC-DLNR-2503-MAN175 | TARANG CGHS PPG S/S-1:ID | TG-MAN175A-2 | 19502057 | 630 | 200 | 237 | 0.96 | 148 | 56 | 245 | 42 | 183 | 50 | 222 | 54 | 2019-06-12 23:30 | 29.9 | 4.6 | 245 | R | 96 | 95 | 109 | 14 |  |  | 1 | 99 | 697.07 | 687.07 | 668.42 | 693.07 | 21.3 | 31.3 | 31.3 | 25.3 | [12 empty] | 718.37 | 1.23 | 0.47 | 0.23
159 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN175 | 1S-DL-YP-ETC-DLNR-2503-MAN175 | TARANG CGHS PPG S/S-1:ID | TG-MAN175A-1 | 19502059 | 630 | 200 | 237 | 0.98 | 139 | 66 | 296 | 45 | 200 | 29 | 128 | 146 | 2019-06-10 22:30 | 25.8 | 1.8 | 309 | R | 129 | 97 | 74 | 55 |  |  | 0.2 | 99.8 | 584.27 | 693.38 | 718.38 | 704.08 | 134.11 | 25 | 25 | 14.3 | [12 empty] | 718.38 | 1.22 | 0.52 | 0.22
160 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN176 | 1S-DL-YP-ETC-DLNR-2503-MAN176 | TARANG CGHS PPG S/S-2:ID | TG-MAN176A-1 | 19502058 | 400 | 120 | 242 | 0.98 | 99 | 25 | 103 | 18 | 77 | 56 | 234 | 146 | 2019-06-15 01:00 | 17.1 | 2.2 | 234 | B | 81 | 71 | 149 | 78 |  |  | 1.1 | 98.9 | 688.08 | 718.38 | 403.37 | 663.08 | 30.3 |  |  | 55.3 |  |  | 0.3 | [9 empty] | 718.38 | 1.22 | 0.54 | 0.25
161 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN176 | 1S-DL-YP-ETC-DLNR-2503-MAN176 | TARANG CGHS PPG S/S-2:ID | TG-MAN176A-2 | 19505527 | 400 | 120 | 243 | 0.98 | 79 | 35 | 145 | 25 | 104 | 20 | 82 | 55 | 2019-06-09 22:00 | 19.7 | 1.6 | 153 | R | 110 | 99 | 91 | 19 | 0.1 |  | 0.7 | 99.2 | 675.08 | 717.08 | 718.38 | 718.38 | 43.3 | 1.3 | 1.3 | [13 empty] | 718.38 | 1.22 | 0.51 | 0.2
162 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN177 | 1S-DL-YP-ETC-DLNR-2503-MAN177 | PRIYADARSHANI CGHS PPG:ID | TG-MAN177A-2 | 19505857 | 400 | 120 | 237 | 0.98 | 102 | 51 | 227 | 24 | 104 | 27 | 121 | 115 | 2019-06-30 | 15.8 | 1.7 | 231 | R | 152 | 55 | 93 | 97 |  | 0.2 | 67.6 | 32.2 | 373.37 | 718.08 | 663.08 | 667.38 | 345.01 | 0.3 | 0.3 | 51 | [12 empty] | 718.38 | 1.22 | 0.52 | 0.26
163 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN177 | 1S-DL-YP-ETC-DLNR-2503-MAN177 | PRIYADARSHANI CGHS PPG:ID | TG-MAN177A-1 | 19500915 | 400 | 120 | 236 | 0.96 | 64 | 23 | 99 | 31 | 136 | 11 | 46 | 79 | 2019-06-03 22:30 | 21.3 | 1.7 | 158 | Y | 99 | 135 | 66 | 69 |  | 0.1 | 67.8 | 32.1 | 718.38 | 674.08 | 718.38 | 718.38 |  | 44.3 | 44.3 | [13 empty] | 718.38 | 1.22 | 0.57 | 0.16
164 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN179 | 1S-DL-YP-ETC-DLNR-2503-MAN179 | EKTA GARDEN CGHS PPG S/S-2:ID | TG-MAN179A-1 | 19500921 | 630 | 200 | 242 | 0.91 | 136 | 47 | 199 | 46 | 191 | 43 | 180 | 17 | 2019-06-30 19:30 | 67.6 | 15.2 | 212 | Y | 98 | 103 | 98 | 5 |  |  | 0.1 | 99.9 | 702.38 | 690.08 | 700.08 | 715.08 | 16 | 28.3 | 28.3 | 3.3 | [12 empty] | 718.38 | 1.22 | 0.67 | 0.22
165 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN180 | 1S-DL-YP-ETC-DLNR-2503-MAN180 | NAVKUNJ CGHS PPG S/S-1:ID | TG-MAN180A-2 | 19505855 | 630 | 200 | 242 | 0.93 | 121 | 29 | 121 | 55 | 228 | 37 | 154 | 95 | 2019-06-30 16:30 | 66.6 | 6.6 | 228 | Y | 80 | 127 | 93 | 47 |  | 0.1 | 0.2 | 99.7 | 718.38 | 682.19 | 718.38 | 718.38 |  | 36.19 | 36.19 | [13 empty] | 718.38 | 1.22 | 0.62 | 0.19
166 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN182 | 1S-DL-YP-ETC-DLNR-2503-MAN182 | LINK HOUSE CGHS PPG:ID | TG-MAN182A-2 | 19500913 | 630 | 200 | 242 | 0.97 | 73 | 31 | 131 | 21 | 92 | 20 | 87 | 42 | 2019-06-14 23:30 | 13.8 | 0.5 | 131 | R | 118 | 99 | 83 | 35 |  |  |  | 100 | 718.37 | 718.37 | 718.37 | 718.37 | [16 empty] | 718.37 | 1.23 | 0.53 | 0.12
167 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN183 | 1S-DL-YP-ETC-DLNR-2503-MAN183 | ADITI CGHS PPG:ID | TG-MAN183A-2 | 19502039 | 400 | 120 | 238 | 0.96 | 64 | 23 | 101 | 23 | 101 | 18 | 82 | 19 | 2019-06-02 21:00 | 3.3 | -20.4 | 136 | R | 132 | 93 | 75 | 57 |  |  | 1.7 | 98.3 | 713.11 | 716.41 | 716.41 | 716.41 | 3.3 | [15 empty] | 716.41 | 3.19 | 0.49 | 0.16
168 | 2019-06-17 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN183 | 1S-DL-YP-ETC-DLNR-2503-MAN183 | ADITI CGHS PPG:ID | TG-MAN183A-1 | 19506927 | 400 | 120 | 239 | 0.99 | 11 | 2 | 10 | 1 | 3 | 8 | 35 | 30 | 2019-06-25 11:00 | -0.1 | -11.4 | 35 | B | 134 | 24 | 142 | 118 |  |  |  | 100 | 321.53 | 321.53 | 321.53 | 321.53 | [16 empty] | 321.53 | 14.07 | 0.42 | 0.03
169 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN185 | 1S-DL-YP-ETC-DLNR-2503-MAN185 | DEEPA CGHS PPG:ID | TG-MAN185A-2 | 19502427 | 630 | 200 | 240 | 0.97 | 121 | 33 | 139 | 45 | 187 | 42 | 176 | 43 | 2019-06-08 23:00 | 22.5 | 4.1 | 197 | B | 88 | 103 | 109 | 21 |  |  |  | 100 | 695.28 | 690.58 | 688.58 | 695.28 |  | 4.3 | 4.3 | [13 empty] | 718.34 | 1.26 | 0.51 | 0.19
170 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN185 | 1S-DL-YP-ETC-DLNR-2503-MAN185 | DEEPA CGHS PPG:ID | TG-MAN185A-1 | 19502428 | 630 | 200 | 240 | 0.97 | 111 | 37 | 155 | 34 | 140 | 40 | 167 | 24 | 2019-06-02 23:30 | 23 | 5.1 | 185 | B | 88 | 90 | 122 | 34 |  |  | 0.1 | 99.9 | 718.59 | 718.59 | 717.59 | 718.59 | [16 empty] | 718.59 | 1.01 | 0.52 | 0.18
171 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN188 | 1S-DL-YP-ETC-DLNR-2503-MAN188 | UNA CGHS PPG:ID | TG-MAN188A-1 | 19502424 | 400 | 120 | 246 | 0.97 | 96 | 38 | 160 | 25 | 104 | 33 | 137 | 48 | 2019-06-29 23:00 | 17.4 | 2.2 | 160 | R | 112 | 100 | 88 | 24 |  |  | 7.9 | 92.1 | 660.29 | 714.59 | 709.08 | 713.59 | 58.3 | 4 | 4 | 5 | [12 empty] | 718.59 | 1.01 | 0.44 | 0.24
172 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN190 | 1S-DL-YP-ETC-DLNR-2503-MAN190 | NAVKALA CGHS PPG:ID | TG-MAN190A-1 | 19502034 | 630 | 200 | 239 | 0.97 | 152 | 47 | 202 | 59 | 252 | 46 | 194 | 54 | 2019-06-28 23:00 | 25.8 | 5.5 | 274 | Y | 95 | 108 | 97 | 13 |  |  | 0.1 | 99.9 | 696.29 | 617.05 | 699.52 | 681.59 | 22.3 | 101.54 | 101.54 | 37 | [12 empty] | 718.59 | 1.01 | 0.49 | 0.24
173 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN190 | 1S-DL-YP-ETC-DLNR-2503-MAN190 | NAVKALA CGHS PPG:ID | TG-MAN190A-2 | 19506132 | 630 | 200 | 246 | 0.97 | 146 | 26 | 108 | 91 | 392 | 29 | 120 | 278 | 2019-06-30 14:30 | 46 | 4.6 | 392 | Y | 102 | 121 | 76 | 45 | 99.9 | 0.1 |  |  | 681.58 | 617.03 | 718.28 | 706.28 | 37 | 101.25 | 101.25 | 12.3 |  | 0.3 | [10 empty] | 718.58 | 1.02 | 0.49 | 0.23
174 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN193 | 1S-DL-YP-ETC-DLNR-2503-MAN193 | TECHNOLOGY CGHS, PPG:ID | TG-MAN193A-2 | 19500979 | 630 | 200 | 244 | 0.98 | 158 | 60 | 249 | 44 | 181 | 55 | 228 | 61 | 2019-06-02 23:00 | 25.8 | 3.7 | 261 | Y | 100 | 101 | 98 | 3 |  | 0.2 | 15.6 | 84.2 | 658.31 | 657.25 | 658.25 | 671.25 | 60.54 | 62 | 62 | 48 | [12 empty] | 719.25 | 0.35 | 0.52 | 0.25
175 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN194 | 1S-DL-YP-ETC-DLNR-2503-MAN194 | ENGINEERS CGHS PPG S/S-1:ID | TG-MAN194A-2 | 19500947 | 630 | 200 | 246 | 0.96 | 132 | 50 | 208 | 34 | 146 | 48 | 204 | 60 | 2019-06-11 23:00 | 29.4 | 6 | 236 | R | 110 | 83 | 108 | 27 | 83.2 | 16.8 |  |  | 688.4 | 718.36 | 708.06 | 716.36 | 29.56 |  |  | 2 | [12 empty] | 718.36 | 1.24 | 0.49 | 0.21
176 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN194 | 1S-DL-YP-ETC-DLNR-2503-MAN194 | ENGINEERS CGHS PPG S/S-1:ID | TG-MAN194A-1 | 19500948 | 630 | 200 | 246 | 0.98 | 176 | 71 | 309 | 54 | 235 | 50 | 217 | 84 | 2019-06-11 01:30 | 25.8 | 3.7 | 309 | R | 102 | 106 | 93 | 13 |  | 0.1 | 0.2 | 99.7 | 592.37 | 629.37 | 682.06 | 649.07 | 124.59 | 87.59 | 87.59 | 68.29 | [12 empty] | 717.36 | 2.24 | 0.5 | 0.28
177 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN195 | 1S-DL-YP-ETC-DLNR-2503-MAN195 | ENGINEERS CGHS PPG S/S-2:ID | TG-MAN195A-2 | 19500946 | 630 | 200 | 246 | 0.97 | 71 | 20 | 79 | 26 | 106 | 25 | 99 | 23 | 2019-06-02 23:30 | 17.5 | 0.9 | 116 | B | 84 | 104 | 113 | 29 |  | 0.1 | 0.2 | 99.7 | 718.37 | 718.37 | 718.37 | 718.37 | [16 empty] | 718.37 | 1.23 | 0.53 | 0.11
178 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN195 | 1S-DL-YP-ETC-DLNR-2503-MAN195 | ENGINEERS CGHS PPG S/S-2:ID | TG-MAN195A-1 | 19500949 | 630 | 200 | 246 | 0.97 | 115 | 42 | 174 | 29 | 121 | 45 | 186 | 60 | 2019-06-12 | 23.9 | 1.8 | 197 | B | 106 | 88 | 106 | 18 |  | 0.1 | 3.8 | 96.1 | 714.36 | 718.36 | 705.06 | 718.36 | 4 | [15 empty] | 718.36 | 1.24 | 0.53 | 0.18
179 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN198 | 1S-DL-YP-ETC-DLNR-2503-MAN198 | ANKUR CGHS PPG S/S-1:ID | TG-MAN198A-2 | 19500925 | 630 | 200 | 242 | 0.98 | 152 | 53 | 217 | 34 | 138 | 64 | 262 | 108 | 2019-06-03 | 26.7 | 3.2 | 297 | B | 94 | 57 | 149 | 92 |  |  | 0.1 | 99.9 | 702.42 | 718.06 | 495.11 | 699.36 | 15.24 |  |  | 18.3 | [12 empty] | 718.06 | 1.54 | 0.48 | 0.24
180 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN204 | 1S-DL-YP-ETC-DLNR-2503-MAN204 | KONARK CGHS, PPG:ID | TG-MAN204A-1 | 19500371 | 630 | 200 | 239 | 0.98 | 72 | 42 | 184 | 13 | 56 | 17 | 73 | 120 | 2019-06-11 23:30 | 15.2 | 0.5 | 184 | R | 151 | 67 | 83 | 84 |  |  | 0.1 | 99.9 | 717.17 | 717.47 | 717.47 | 717.47 | 0.3 | [15 empty] | 717.47 | 2.13 | 0.52 | 0.11
181 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN204 | 1S-DL-YP-ETC-DLNR-2503-MAN204 | KONARK CGHS, PPG:ID | TG-MAN204A-2 | 19502036 | 630 | 200 | 240 | 0.97 | 87 | 24 | 103 | 29 | 121 | 34 | 141 | 33 | 2019-06-13 23:30 | 17 | 2.8 | 141 | B | 105 | 108 | 87 | 21 |  | 0.1 | 65.3 | 34.6 | 717.48 | 717.48 | 717.48 | 717.48 | [16 empty] | 717.48 | 2.12 | 0.52 | 0.14
182 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN206 | 1S-DL-YP-ETC-DLNR-2503-MAN206 | SUDH BHAWNA:ID | TG-MAN206A-1 | 19502393 | 630 | 200 | 240 | 0.95 | 65 | 22 | 87 | 22 | 89 | 22 | 91 | 3 | 2019-06-15 22:30 | 22.1 | 3.2 | 121 | R | 90 | 100 | 110 | 20 | 92.9 | 4.9 | 2.1 | 0.1 | 718.59 | 718.59 | 718.59 | 718.59 | [16 empty] | 718.59 | 1.01 | 0.57 | 0.1
183 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN207 | 1S-DL-YP-ETC-DLNR-2503-MAN207 | DVB COLONY, URJA VIHAR:K | TG-MAN207A-1 | 19505138 | 400 | 120 | 239 | 0.99 | 55 | 24 | 104 | 26 | 115 | 5 | 23 | 87 | 2019-06-10 01:00 | 7.2 | -0.1 | 123 | Y | 62 | 166 | 72 | 104 | 0.1 |  | 37.1 | 62.8 | 600.3 | 595 | 600.3 | 600.3 |  | 5.3 | 5.3 | [13 empty] | 600.3 | 23.3 | 0.43 | 0.14
184 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | MANDAWALI | 1230 | MAN275 | 1S-DL-YP-ETC-DLNR-2503-MAN275 | P.S MANDAWALI MANDAWALI | TG-MAN275A-1 | 19505572 | 630 | 200 | 241 | 0.98 | 109 | 56 | 247 | 22 | 93 | 31 | 132 | 139 | 2019-06-30 14:30 | 33.8 | 1.2 | 247 | R | 84 | 115 | 100 | 31 | 0.1 | 0.1 | 2.7 | 97.1 | 705.3 | 692.3 | 705.3 | 706 | 0.3 | 13.3 | 13.3 | [13 empty] | 706 | 14 | 0.6 | 0.17
185 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR002 | 1S-DL-YP-ETC-DLNR-2502-PVR002 | DDA BUILDING, LAXMI NAGAR:ID | TG-PVR002A-2 | 19504480 | 630 | 200 | 201 | 0.97 | 108 | 14 | 145 | 54 | 228 | 40 | 172 | 73 | 2019-06-26 16:00 | 28.5 | -1.4 | 243 | Y | 77 | 120 | 103 | 43 | 100 |  |  |  | 715.58 | 627.44 | 715.58 | 715.58 |  | 88.14 | 88.14 | [13 empty] | 715.58 | 4.02 | 0.39 | 0.17
186 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR002 | 1S-DL-YP-ETC-DLNR-2502-PVR002 | DDA BUILDING, LAXMI NAGAR:ID | TG-PVR002A-1 | 19506264 | 630 | 200 | 249 | 0.97 | 81 | 16 | 63 | 43 | 175 | 22 | 88 | 102 | 2019-06-06 11:30 | 27.8 | -0.2 | 203 | Y | 72 | 154 | 74 | 82 | 71.2 | 2.2 | 2.9 | 23.7 | 702.58 | 699.28 | 702.58 | 702.58 |  | 3.3 | 3.3 | [13 empty] | 702.58 | 17.02 | 0.27 | 0.13
187 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR012 | 1S-DL-YP-ETC-DLNR-2502-PVR012 | DEFENCE ENCLAVE:ID | TG-PVR012A-2 | 19503201 | 990 | 320 | 247 | 0.97 | 161 | 50 | 203 | 61 | 246 | 51 | 206 | 41 | 2019-06-29 23:30 | 37.5 | 7.4 | 249 | Y | 101 | 114 | 85 | 29 |  |  | 0.7 | 99.3 | 718.44 | 718.44 | 718.44 | 718.44 | [16 empty] | 718.44 | 1.16 | 0.6 | 0.16
188 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR013 | 1S-DL-YP-ETC-DLNR-2502-PVR013 | NEW RAJDHANI ENCLAVE:ID | TG-PVR013A-2 | 19505575 | 630 | 200 | 246 | 0.96 | 84 | 15 | 61 | 47 | 196 | 22 | 91 | 123 | 2019-06-14 14:30 | 28.4 | 6.2 | 196 | Y | 96 | 118 | 86 | 32 |  | 0.1 | 11.3 | 88.7 | 696.58 | 694.58 | 696.58 | 696.58 |  | 2 | 2 | [13 empty] | 696.58 | 23.02 | 0.65 | 0.13
189 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR014 | 1S-DL-YP-ETC-DLNR-2502-PVR014 | L.S.C. NEW RAJDHANI:ID | TG-PVR014A-1 | 19501286 | 630 | 200 | 246 | 0.95 | 133 | 49 | 206 | 33 | 138 | 51 | 213 | 72 | 2019-06-12 15:30 | 35.4 | 1.8 | 231 | B | 115 | 67 | 118 | 51 |  |  | 18 | 82 | 712 | 719.58 | 664.28 | 717.28 | 7.58 |  |  | 2.3 | [12 empty] | 719.58 | 0.02 | 0.38 | 0.21
190 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR016 | 1S-DL-YP-ETC-DLNR-2502-PVR016 | S/STN. NO. 1 PREET VIHAR:ID | TG-PVR016A-2 | 19501147 | 990 | 320 | 234 | 0.99 | 160 | 30 | 130 | 52 | 221 | 78 | 334 | 177 | 2019-06-12 14:00 | 22.8 | -2.2 | 378 | B | 42 | 88 | 169 | 127 |  |  | 2.6 | 97.4 | 690.4 | 690.4 | 584.34 | 690.4 | [16 empty] | 690.4 | 5.2 | 0.36 | 0.16
191 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR023 | 1S-DL-YP-ETC-DLNR-2502-PVR023 | DISTRICT CENTER, L. NAGAR, NO3:ID | TG-PVR023A-1 | 19501287 | 630 | 200 | 239 | 0.9 | 150 | 48 | 196 | 58 | 239 | 44 | 180 | 53 | 2019-06-27 20:30 | 73.6 | 1.8 | 249 | Y | 108 | 121 | 70 | 51 |  |  |  | 100 | 704.03 | 669.44 | 713.17 | 699.33 | 14.14 | 48.33 | 48.33 | 18.44 | [12 empty] | 718.17 | 1.43 | 0.23 | 0.24
192 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR024 | 1S-DL-YP-ETC-DLNR-2502-PVR024 | MADHUBAN KIOSK:K | TG-PVR024A-2 | 19505003 | 630 | 200 | 230 | 0.98 | 122 | 39 | 176 | 39 | 181 | 44 | 199 | 21 | 2019-06-30 23:00 | 21.2 | 5.1 | 243 | B | 91 | 105 | 104 | 14 |  |  | 24.3 | 75.7 | 718.35 | 713.05 | 706.12 | 719.05 | 0.3 | 6 | 6 | [13 empty] | 719.05 | 0.55 | 0.64 | 0.19
193 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR053 | 1S-DL-YP-ETC-DLNR-2502-PVR053 | PLOT NO.5 ADITYA TOWER LNR:ID | TG-PVR053A-1 | 19501191 | 630 | 200 | 246 | 0.98 | 90 | 23 | 97 | 31 | 132 | 35 | 150 | 46 | 2019-06-11 14:00 | 12.4 | -5.1 | 156 | Y | 98 | 99 | 102 | 4 |  |  | 7.1 | 92.9 | 717.51 | 717.51 | 717.51 | 717.51 | [16 empty] | 717.51 | 2.09 | 0.41 | 0.14
194 | 2019-06-02 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR064 | 1S-DL-YP-ETC-DLNR-2502-PVR064 | FIRE STN LAXMI NAGAR:ID | TG-PVR064A-1 | 19501284 | 400 | 120 | 243 | 0.96 | 25 | 11 | 42 | 13 | 51 | 2 | 8 | 39 | 2019-06-06 01:30 | 6.3 | -0.8 | 55 | Y | 108 | 178 | 14 | 164 | 47 | 5.2 | 16.1 | 31.8 | 695.36 | 695.36 | 695.36 | 695.36 | [16 empty] | 695.36 | 0.24 | 0.42 | 0.06
195 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR064 | 1S-DL-YP-ETC-DLNR-2502-PVR064 | FIRE STN LAXMI NAGAR:ID | TG-PVR064A-2 | 19501282 | 400 | 120 | 242 | 0.96 | 16 | 6 | 26 | 5 | 21 | 5 | 21 | 5 | 2019-06-03 | 2.8 | 0.3 | 30 | R | 126 | 90 | 84 | 42 |  |  | 9.3 | 90.7 | 718.52 | 718.52 | 718.52 | 718.52 | [16 empty] | 718.52 | 1.08 | 0.39 | 0.04
196 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR065 | 1S-DL-YP-ETC-DLNR-2502-PVR065 | ADITYA TOWER DIST. CENTER LNR:ID | TG-PVR065A-1 | 19505468 | 400 | 126 | 248 | 0.98 | 75 | 31 | 124 | 28 | 111 | 16 | 64 | 54 | 2019-06-11 15:30 | 28.5 | -0.4 | 141 | R | 115 | 112 | 73 | 42 |  |  | 7 | 93 | 642.3 | 686.28 | 692.28 | 692.28 | 49.58 | 6 | 6 | [13 empty] | 692.28 | 27.32 | 0.33 | 0.19
197 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR065 | 1S-DL-YP-ETC-DLNR-2502-PVR065 | ADITYA TOWER DIST. CENTER LNR:ID | TG-PVR065A-2 | 19505451 | 400 | 120 | 249 | 0.93 | 41 | 29 | 119 | 2 | 8 | 9 | 37 | 99 | 2019-06-10 14:00 | 12.5 | 0.1 | 119 | R | 209 | 15 | 76 | 194 |  | 0.1 | 1.7 | 98.2 | 704.57 | 706.27 | 706.27 | 706.27 | 1.3 | [15 empty] | 706.27 | 13.33 | 0.24 | 0.1
198 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR066 | 1S-DL-YP-ETC-DLNR-2502-PVR066 | ROOT TOWER LAXMI NAGAR | TG-PVR066A-3 | 19503254 | 630 | 200 | 248 | 0.94 | 97 | 33 | 129 | 30 | 119 | 34 | 133 | 13 | 2019-06-11 10:30 | 21.2 | -12.4 | 157 | R | 141 | 84 | 75 | 66 |  | 0.1 | 14.9 | 85 | 715.59 | 715.59 | 715.59 | 715.59 | [16 empty] | 715.59 | 4.01 | 0.39 | 0.15
199 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR066 | 1S-DL-YP-ETC-DLNR-2502-PVR066 | ROOT TOWER LAXMI NAGAR | TG-PVR066A-4 | 19503273 | 630 | 200 | 248 | 0.95 | 145 | 39 | 157 | 72 | 289 | 34 | 135 | 144 | 2019-06-14 12:00 | 48.3 | 0.5 | 303 | Y | 80 | 155 | 65 | 90 |  |  | 10.2 | 89.8 | 715.29 | 503.21 | 715.59 | 681.31 | 0.3 | 212.38 | 212.38 | 34.28 | [12 empty] | 715.59 | 4.01 | 0.29 | 0.23
200 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR066 | 1S-DL-YP-ETC-DLNR-2502-PVR066 | ROOT TOWER LAXMI NAGAR | TG-PVR066A-2 | 19503285 | 630 | 200 | 248 | 0.88 | 153 | 47 | 186 | 61 | 242 | 46 | 182 | 58 | 2019-06-11 15:00 | 32.7 | -35.4 | 257 | Y | 95 | 105 | 101 | 10 |  |  | 6.4 | 93.6 | 694.28 | 596 | 655 | 648.28 | 21.3 | 119.58 | 119.58 | 67.3 | [12 empty] | 715.58 | 4.02 | 0.38 | 0.24
201 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR066 | 1S-DL-YP-ETC-DLNR-2502-PVR066 | ROOT TOWER LAXMI NAGAR | TG-PVR066A-1 | 19505355 | 630 | 200 | 249 | 0.97 | 158 | 48 | 190 | 55 | 217 | 55 | 221 | 29 | 2019-06-06 12:30 | 47.4 | -1.4 | 302 | R | 89 | 95 | 116 | 27 | 0.2 |  | 12.6 | 87.2 | 658.28 | 611.54 | 589.24 | 628.24 | 34 | 80.34 | 80.34 | 64.04 | [12 empty] | 692.28 | 27.32 | 0.34 | 0.25
202 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR069 | 1S-DL-YP-ETC-DLNR-2502-PVR069 | DISTT.CENT.2 LNR | TG-PVR069A-1 | 19503211 | 400 | 120 | 248 | 0.96 | 25 | 5 | 18 | 4 | 15 | 17 | 69 | 52 | 2019-06-13 16:30 | 9.4 | 0.3 | 82 | B | 42 | 49 | 209 | 167 |  |  | 41.2 | 58.8 | 719.27 | 719.27 | 719.27 | 719.27 | [16 empty] | 719.27 | 0.33 | 0.62 | 0.06
203 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR078 | 1S-DL-YP-ETC-DLNR-2502-PVR078 | SAGAR PLAZA D.C. LNR | TG-PVR078A-1 | 19504512 | 400 | 120 | 245 | 0.81 | 78 | 19 | 82 | 29 | 124 | 29 | 124 | 42 | 2019-06-06 14:30 | 14.6 | -11.6 | 160 | Y | 103 | 119 | 77 | 42 |  |  |  | 100 | 718.47 | 676.17 | 719.17 | 719.47 | 1 | 43.3 | 43.3 | [13 empty] | 719.47 | 0.13 | 0.35 | 0.19