## Complete Report
MIS Report of Distribution Transformer - Jun19
Jun19 1230 LAXMI NAGAR (Complete Report)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | LGR075 | 1S-DL-YP-ETC-DLNR-2501-LGR075 | DP ANAND VIHAR:PM | TG-LGR075A-1 | 19505783 | 100 | 40 | 249 | 0.74 | 78 | 16 | 67 | 15 | 61 | 47 | 193 | 130 | 2019-06-21 23:00 | 63.3 | 0 | 193 | B | 107 | 100 | 93 | 14 |  | 0.2 | 41 | 58.8 | 410.25 | 410.25 | 409.55 | 410.25 |  | 52.3 | 52.3 | 19 | 298.27 | 244.27 | 107.3 | 279.27 |  | 1.3 | 0.3 |  |  |  | 0.3 |  | 708.52 | 11.08 | 0.26 | 0.78
2 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR030 | 1S-DL-YP-ETC-DLNR-2502-PVR030 | S/STN. NO.5 F.I.E., PPG:ID | TG-PVR030A-1 | 19500815 | 630 | 200 | 250 | 0.72 | 134 | 50 | 203 | 59 | 242 | 26 | 108 | 119 | 2019-06-27 11:30 | 34.5 | -46.9 | 250 | Y | 111 | 111 | 78 | 33 |  | 0.1 | 12.8 | 87.2 | 677.21 | 585.51 | 719.51 | 705.21 | 42.3 | 134 | 134 | 14.3 | [12 empty] | 719.51 | 0.09 | 0.43 | 0.21
3 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | ANAND VIHAR ISBT | 1230 | PVR037 | 1S-DL-YP-ETC-DLNR-2502-PVR037 | S/STN. NO.12 F.I.E., PPG:ID | TG-PVR037A-2 | 19505476 | 990 | 320 | 251 | 0.78 | 427 | 158 | 630 | 135 | 538 | 135 | 536 | 93 | 2019-06-27 12:00 | 67.5 | -116.2 | 649 | R | 107 | 98 | 95 | 12 | 0.1 | 0.1 | 6.9 | 92.9 | 466.22 | 482.22 | 477.52 | 475.52 | 159 | 218.59 | 218.59 | 218.59 | 87.29 | 11.3 | 5 | 18 | [8 empty] | 712.51 | 7.09 | 0.43 | 0.43
4 | 2019-06-01 | 2019-06-30 23:30 | LAXMI NAGAR | PREET VIHAR | 1230 | PVR078 | 1S-DL-YP-ETC-DLNR-2502-PVR078 | SAGAR PLAZA D.C. LNR | TG-PVR078A-1 | 19504512 | 400 | 120 | 245 | 0.81 | 78 | 19 | 82 | 29 | 124 | 29 | 124 | 42 | 2019-06-06 14:30 | 14.6 | -11.6 | 160 | Y | 103 | 119 | 77 | 42 |  |  |  | 100 | 718.47 | 676.17 | 719.17 | 719.47 | 1 | 43.3 | 43.3 | [13 empty] | 719.47 | 0.13 | 0.35 | 0.19