## Loading Condition > 80%
MIS Report of Distribution Transformer - Jun19
Jun19 1240 MAYUR VIHAR PH- I & II (Loading Condition > 80% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | S/STN 8 POCKET C | 1240 | MV2002 | 1S-DL-YP-ETC-DMVR-2302-MV2002 | 15 BLCIK KALYAN PURI:K | TG-MV2002A-2 | 19505816 | 630 | 200 | 246 | 0.97 | 558 | 171 | 705 | 137 | 559 | 250 | 1031 | 419 | 2019-06-30 23:00 | 206.8 | 40.4 | 1031 | B | 103 | 91 | 107 | 16 | 0.2 | 0.2 | 11.4 | 88.2 | 0.58 | 1 |  |  | 141.41 | 237.09 | 237.09 | 151.39 | 553.04 | 473.11 | 534.49 | 559.04 | 21.07 | 6 | 49.28 | 6.37 | 0.3 |  | 8.54 |  | 717.2 | 2.4 | 0.59 | 0.89
2 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | S/STN 8 POCKET C | 1240 | MV2004 | 1S-DL-YP-ETC-DMVR-2302-MV2004 | 13 & 18 BLK,KALYANPURI | TG-MV2004A-1 | 19505817 | 990 | 320 | 231 | 0.97 | 956 | 334 | 1439 | 291 | 1254 | 331 | 1424 | 178 | 2019-06-09 06:00 | 311.4 | 84.8 | 1517 | B | 102 | 94 | 104 | 10 | 0.1 |  | 1.2 | 98.7 |  |  |  |  | 2 | 3 | 3 | 1.3 | 566.43 | 666.27 | 514.13 | 573.43 | 136.08 | 36.1 | 189.08 | 130.24 | 0.46 |  | 0.46 |  | 705.37 | 14.23 | 0.7 | 0.97
3 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | S/STN 8 POCKET C | 1240 | MV2007 | 1S-DL-YP-ETC-DMVR-2302-MV2007 | KHP VILLAGE MAIN ROAD:PL | TG-MV2007A-1 | 19506237 | 630 | 200 | 238 | 0.98 | 555 | 152 | 661 | 191 | 818 | 212 | 917 | 224 | 2019-06-11 23:30 | 146.6 | 35.4 | 1059 | B | 92 | 94 | 114 | 22 | 0.1 | 0.2 | 45.2 | 54.5 |  |  |  |  | 22 | 38 | 38 | 6 | 670.5 | 603.5 | 506.42 | 645.55 | 2 | 53 | 186.38 | 42.55 |  |  | 1.3 |  | 694.5 | 25.1 | 0.72 | 0.88
4 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | S/STN 8 POCKET C | 1240 | MV2009 | 1S-DL-YP-ETC-DMVR-2302-MV2009 | A BLOCK V. NAGAR:PL | TG-MV2009A-1 | 19502531 | 990 | 200 | 225 | 0.98 | 934 | 347 | 1658 | 287 | 1363 | 301 | 1433 | 266 | 2019-06-30 23:00 | 165.6 | 48.8 | 1718 | R | 115 | 90 | 95 | 25 |  |  | 0.6 | 99.4 |  |  | 0.3 |  | 118 | 281.26 | 281.26 | 210 | 445.4 | 402.45 | 425.55 | 433.06 | 117.41 | 10.3 | 22.2 | 51.35 | 13.2 |  |  |  | 718.03 | 1.57 | 0.55 | 0.94
5 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | S/STN 8 POCKET C | 1240 | MV2026 | 1S-DL-YP-ETC-DMVR-2302-MV2026 | S/S NO.2 PKT E MVR-II:ID | TG-MV2026A-1 | 19502122 | 400 | 120 | 241 | 0.98 | 323 | 144 | 672 | 90 | 412 | 90 | 414 | 259 | 2019-06-26 23:30 | 50.8 | 7.2 | 672 | R | 118 | 97 | 86 | 32 |  |  | 7.4 | 92.6 | 11 | 32.3 | 94 | 29.3 | 277.58 | 371.29 | 371.29 | 346.28 | 399.43 | 315.1 | 261.11 | 342.41 | 29.36 |  |  | 0.3 | 0.52 |  |  |  | 719.09 | 0.51 | 0.5 | 0.81
6 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | S/STN 8 POCKET C | 1240 | MV2034 | 1S-DL-YP-ETC-DMVR-2302-MV2034 | D BLOCK GAZIPUR:ID | TG-MV2034A-2 | 19506238 | 400 | 120 | 245 | 0.99 | 332 | 137 | 556 | 90 | 365 | 105 | 425 | 169 | 2019-06-25 17:30 | 67.6 | 8.5 | 695 | R | 115 | 90 | 96 | 25 |  | 0.1 | 20.8 | 79.1 |  |  |  |  | 68.3 | 113.3 | 113.3 | 67.3 | 514.5 | 581.14 | 581.14 | 627.44 | 110.24 | 1 | 14.3 | 1 | 2.3 | 0.3 |  |  | 696.14 | 23.46 | 0.68 | 0.83
7 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | S/STN 8 POCKET C | 1240 | MV2036 | 1S-DL-YP-ETC-DMVR-2302-MV2036 | DDA JANTA FLAT GAZIPUR:ID | TG-MV2036A-2 | 19502496 | 990 | 320 | 243 | 0.97 | 906 | 244 | 1036 | 330 | 1392 | 332 | 1411 | 366 | 2019-06-30 | 169.3 | 70.7 | 1462 | B | 82 | 108 | 110 | 28 |  |  | 3.5 | 96.5 |  |  |  |  | 243.01 | 24.47 | 24.47 | 73.17 | 476.3 | 568.14 | 531.44 | 586.44 |  | 126 | 144.3 | 59.3 |  | 0.3 | 1.3 |  | 719.31 | 0.29 | 0.62 | 0.91
8 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | S/STN 8 POCKET C | 1240 | MV2037 | 1S-DL-YP-ETC-DMVR-2302-MV2037 | S/S NO. 1 PKT A MVR-II:ID | TG-MV2037A-1 | 19502073 | 630 | 200 | 244 | 0.97 | 606 | 211 | 886 | 202 | 842 | 193 | 807 | 69 | 2019-06-11 23:30 | 110.9 | 33.6 | 908 | R | 103 | 98 | 100 | 5 | 0.1 | 0.3 | 56.3 | 43.3 |  |  |  |  | 148.32 | 192.52 | 192.52 | 156.32 | 509.35 | 473.15 | 561.15 | 514.35 | 58.47 | 52.17 | 32.47 | 47.17 | 1.3 |  |  |  | 718.24 | 1.36 | 0.56 | 0.96
9 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | S/STN 8 POCKET C | 1240 | MV2041 | 1S-DL-YP-ETC-DMVR-2302-MV2041 | S/S NO. 1 KHR COLONY:ID | TG-MV2041A-1 | 19502491 | 990 | 320 | 244 | 0.95 | 786 | 263 | 1082 | 212 | 868 | 310 | 1269 | 347 | 2019-06-26 22:30 | 196.5 | 85.4 | 1278 | B | 99 | 86 | 115 | 29 |  |  | 0.5 | 99.5 |  |  |  |  | 88.46 | 213.14 | 213.14 | 70.46 | 628.24 | 503.56 | 640.04 | 646.24 |  |  | 52.2 | [5 empty] | 717.1 | 2.5 | 0.65 | 0.79
10 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | S/STN 8 POCKET C | 1240 | MV2041 | 1S-DL-YP-ETC-DMVR-2302-MV2041 | S/S NO. 1 KHR COLONY:ID | TG-MV2041A-2 | 19504469 | 400 | 120 | 248 | 0.95 | 343 | 84 | 332 | 166 | 659 | 93 | 389 | 302 | 2019-06-11 03:00 | 85.6 | 17.1 | 683 | Y | 93 | 111 | 96 | 18 | 33.7 | 7.4 | 5.7 | 53.2 | 4.3 | 9 | 2 | 4.3 | 284.09 | 304.43 | 304.43 | 284.55 | 345.32 | 239.14 | 306.46 | 338.46 |  | 67.44 |  | 6 |  | 13.3 |  |  | 717.14 | 2.46 | 0.51 | 0.86
11 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | S/STN 8 POCKET C | 1240 | MV2045 | 1S-DL-YP-ETC-DMVR-2302-MV2045 | S/S 8 BLK KHP COLONY:PL | TG-MV2045A-1 | 19505911 | 630 | 200 | 237 | 0.96 | 619 | 226 | 988 | 218 | 950 | 175 | 761 | 211 | 2019-06-10 10:30 | 240.4 | 35 | 1257 | R | 117 | 90 | 93 | 27 |  | 0.1 | 1.7 | 98.2 |  | 137.06 | 2 |  | 3.36 | 3.3 | 3.3 | 41.36 | 487.42 | 433.35 | 677.22 | 563.05 | 212.1 | 144 | 18.43 | 114 | 15.13 | 0.3 |  |  | 718.41 | 1.19 | 0.64 | 0.98
12 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | S/STN 8 POCKET C | 1240 | MV2046 | 1S-DL-YP-ETC-DMVR-2302-MV2046 | S/S 10 BLK KHP COLONY (OLD):PL | TG-MV2046A-1 | 19502572 | 990 | 320 | 245 | 0.96 | 876 | 253 | 1031 | 303 | 1253 | 319 | 1324 | 264 | 2019-06-30 23:30 | 261.3 | 94.2 | 1324 | B | 92 | 105 | 104 | 13 |  | 0.6 | 82 | 17.4 |  |  |  |  | 60 | 36 | 36 | 37.3 | 658.1 | 590.36 | 617.07 | 656.36 |  | 91.34 | 66.34 | 24.04 |  |  |  |  | 718.1 | 1.5 | 0.66 | 0.88
13 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | S/STN 8 POCKET C | 1240 | MV2062 | 1S-DL-YP-ETC-DMVR-2302-MV2062 | D BLK EAST VINOD NAGAR | TG-MV2062A-1 | 19505701 | 630 | 200 | 242 | 0.98 | 620 | 248 | 1094 | 186 | 813 | 186 | 817 | 279 | 2019-06-30 23:30 | 120.2 | 23 | 1105 | R | 99 | 95 | 106 | 11 | 0.1 | 0.4 | 16.7 | 82.8 | 41.3 | 43 | 38 | 35 | 310 | 349 | 349 | 340 | 334.01 | 316.01 | 279.47 | 309.31 | 31 | 11 | 56.44 | 35 | 3 | 0.3 | 6.3 |  | 719.31 | 0.29 | 0.45 | 0.98
14 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1008 | 1S-DL-YP-ETC-DMVR-2301-MV1008 | ACHARYA NIKETAN:ID | TG-MV1008A-2 | 19504284 | 990 | 320 | 235 | 0.98 | 855 | 297 | 1268 | 308 | 1321 | 249 | 1063 | 237 | 2019-06-13 17:30 | 159.7 | 49.3 | 1439 | Y | 98 | 108 | 94 | 14 |  |  | 2 | 98 |  |  |  |  | 19 | 16.3 | 16.3 | 15.3 | 643.57 | 550.27 | 700.57 | 667.57 | 55 | 150.3 | 0.3 | 34.3 |  | 0.3 |  |  | 717.57 | 2.03 | 0.72 | 0.86
15 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1018 | 1S-DL-YP-ETC-DMVR-2301-MV1018 | S/S-2 PKT-I MVR PH-I:ID | TG-MV1018A-1 | 19502099 | 630 | 200 | 247 | 0.97 | 540 | 158 | 669 | 218 | 923 | 164 | 685 | 247 | 2019-06-30 23:30 | 153.2 | 28.5 | 949 | Y | 86 | 124 | 89 | 38 |  | 0.1 | 55.5 | 44.4 | 3.3 |  | 1 |  | 236.21 | 73.27 | 73.27 | 169.51 | 479.45 | 484.09 | 503.15 | 540.15 |  | 149.3 | 1.3 | 9.3 |  | 12.3 |  |  | 719.36 | 0.24 | 0.62 | 0.86
16 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1021 | 1S-DL-YP-ETC-DMVR-2301-MV1021 | S/S-4 PKT-1 MVR PH-I:ID | TG-MV1021A-1 | 19503445 | 630 | 200 | 241 | 0.98 | 437 | 130 | 548 | 125 | 529 | 182 | 770 | 232 | 2019-06-04 23:00 | 74.1 | 17.9 | 886 | B | 87 | 85 | 128 | 43 |  |  | 1.8 | 98.2 | 152.29 | 112.59 | 21 | 59 | 387.3 | 483 | 483 | 422.59 | 179.12 | 123.12 | 348.2 | 237.12 |  |  | 42.22 | [5 empty] | 719.11 | 0.49 | 0.51 | 0.69
17 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1023 | 1S-DL-YP-ETC-DMVR-2301-MV1023 | S/S-B PKT-2 MVR PH-I:ID | TG-MV1023A-1 | 19502096 | 630 | 200 | 236 | 0.98 | 536 | 206 | 911 | 141 | 628 | 188 | 821 | 250 | 2019-06-10 23:30 | 86.9 | 19.8 | 911 | R | 111 | 89 | 101 | 22 |  | 0.1 | 28.3 | 71.6 | 6.3 | 26 | 14.3 | 12.3 | 214.51 | 343.17 | 343.17 | 271.5 | 445.03 | 350.07 | 418.04 | 430.34 | 53 |  | 13.3 | 4.3 |  |  |  |  | 719.24 | 0.36 | 0.54 | 0.85
18 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1028 | 1S-DL-YP-ETC-DMVR-2301-MV1028 | S/S-2 PKT IV MVR PH-1:ID | TG-MV1028A-2 | 19502067 | 630 | 200 | 234 | 0.98 | 569 | 182 | 772 | 206 | 877 | 182 | 776 | 103 | 2019-06-02 23:30 | 81.4 | 6.4 | 1171 | Y | 121 | 138 | 41 | 97 |  |  | 2.9 | 97.1 | 8 | 11.3 | 476.57 | 84.1 | 296.15 | 229.15 | 229.15 | 341.05 | 383.17 | 366.41 | 141 | 273.42 | 30.25 | 97.36 | 7.3 | 19 |  | 12.55 |  |  | 717.57 | 2.03 | 0.43 | 0.9
19 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1056 | 1S-DL-YP-ETC-DMVR-2301-MV1056 | CHILLA VILLAGE DL/M SCHOOL WALA:PL | TG-MV1056A-1 | 19502535 | 400 | 120 | 249 | 0.96 | 300 | 76 | 307 | 91 | 372 | 132 | 535 | 203 | 2019-06-30 23:30 | 110.7 | 9.4 | 549 | B | 80 | 85 | 135 | 55 |  |  | 13 | 87 | 26.3 | 15 |  |  | 373.23 | 347.4 | 347.4 | 269.55 | 245.15 | 282.28 | 462.56 | 375.13 |  |  | 121.09 |  |  |  | 1 |  | 645.08 | 2.52 | 0.6 | 0.75
20 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1058 | 1S-DL-YP-ETC-DMVR-2301-MV1058 | CHILLA VILLAGE (OLD):PL | TG-MV1058A-1 | 19505242 | 990 | 320 | 243 | 0.98 | 869 | 324 | 1356 | 220 | 915 | 326 | 1395 | 461 | 2019-06-29 00:30 | 226.2 | 45.8 | 1494 | R | 112 | 92 | 96 | 20 | 0.1 | 0.2 | 35.9 | 63.7 |  |  |  |  | 17 | 84.47 | 84.47 | 42.47 | 609.5 | 623.38 | 636.41 | 665.08 | 81.05 |  | 1 | 0.3 | 0.3 |  |  |  | 708.25 | 11.35 | 0.63 | 0.88
21 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1074 | 1S-DL-YP-ETC-DMVR-2301-MV1074 | ADRESH MOHALLA:PL | TG-MV1074A-1 | 19502118 | 990 | 200 | 246 | 0.98 | 827 | 332 | 1370 | 279 | 1136 | 216 | 886 | 419 | 2019-06-02 | 152.7 | 43.7 | 1370 | R | 118 | 109 | 73 | 45 |  |  | 10.8 | 89.2 |  |  | 2.3 |  | 27.31 | 34 | 34 | 90.01 | 598.25 | 659.27 | 261.55 | 620.4 | 88.03 | 20.48 |  | 3.34 | 0.16 |  |  |  | 714.15 | 5.45 | 0.63 | 0.83
22 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1074 | 1S-DL-YP-ETC-DMVR-2301-MV1074 | ADRESH MOHALLA:PL | TG-MV1074A-2 | 19504290 | 630 | 200 | 229 | 0.98 | 602 | 184 | 823 | 184 | 827 | 234 | 1061 | 237 | 2019-06-30 00:30 | 96.6 | 33.1 | 1061 | B | 90 | 102 | 108 | 18 |  |  | 11.3 | 88.7 |  |  |  |  | 108 | 98.33 | 98.33 | 35.3 | 597.2 | 517.49 | 621.38 | 636.59 | 10.19 | 94.06 | 83.01 | 43.1 |  | 5.11 | 5 |  | 715.39 | 4.21 | 0.61 | 0.96
23 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1077 | 1S-DL-YP-ETC-DMVR-2301-MV1077 | PATPAR GANJ VILLAGE:ID | TG-MV1077A-1 | 19504556 | 990 | 320 | 234 | 0.98 | 974 | 361 | 1576 | 308 | 1334 | 305 | 1330 | 244 | 2019-06-30 | 206.8 | 19.9 | 1632 | R | 109 | 99 | 92 | 17 |  | 0.1 | 11.5 | 88.4 | 0.11 | 0.11 | 0.11 | 0.11 |  | 0.3 | 0.3 |  | 412.35 | 581.17 | 607.16 | 548.47 | 285.54 | 131.53 | 101.48 | 165.47 | 16.05 | 0.54 |  |  | 714.45 | 5.15 | 0.72 | 0.98
24 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1106 | 1S-DL-YP-ETC-DMVR-2301-MV1106 | S/S-4 PKT-5 PH-1:ID | TG-MV1106A-1 | 19502538 | 400 | 120 | 242 | 0.98 | 385 | 156 | 678 | 124 | 535 | 105 | 446 | 203 | 2019-06-26 22:30 | 58.8 | 0.8 | 678 | R | 103 | 100 | 97 | 6 | 0.1 | 10.9 | 58.5 | 30.5 | 56.24 | 8 | 8 | 2.3 | 81.39 | 131.4 | 131.4 | 133.4 | 239.3 | 281.53 | 275.49 | 279.23 | 51.3 | 15.59 | 14.3 | 22.26 | 8.56 | 0.27 |  |  | 715.44 | 4.16 | 0.52 | 0.96
25 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1107 | 1S-DL-YP-ETC-DMVR-2301-MV1107 | NEW S/S SHASHIGARDEN:PLM | TG-MV1107A-3 | 19505731 | 630 | 200 | 238 | 0.98 | 569 | 186 | 776 | 177 | 748 | 206 | 868 | 108 | 2019-06-26 23:30 | 166.8 | 42 | 921 | B | 94 | 95 | 111 | 17 | 0.1 | 0.2 | 6.8 | 92.9 |  |  |  |  | 34.3 | 34.3 | 34.3 | 16 | 658.45 | 662.27 | 585.57 | 657.57 | 12.55 | 9.13 | 115.48 | 32.13 |  |  | 0.25 |  | 706.1 | 13.5 | 0.67 | 0.9
26 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1117 | 1S-DL-YP-ETC-DMVR-2301-MV1117 | STN-4 CHILLA VIL NR DDA FLAT | TG-MV1117A-1 | 19505536 | 630 | 200 | 236 | 0.98 | 531 | 175 | 761 | 153 | 649 | 204 | 883 | 202 | 2019-06-10 02:00 | 157.4 | 27.4 | 905 | B | 101 | 90 | 109 | 19 | 0.3 | 3 | 82.6 | 14.2 |  |  |  |  | 2 | 31.3 | 31.3 | 4 | 704.26 | 676.56 | 631.56 | 700.56 | 2.3 | 0.3 | 74.3 | 4 |  |  | 0.3 |  | 708.56 | 11.04 | 0.74 | 0.84
27 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | TRILOKPURI | 1240 | TKP003 | 1S-DL-YP-ETC-DMVR-2304-TKP003 | 7 BLOCK TKP:K | TG-TKP003A-1 | 19505097 | 990 | 320 | 239 | 0.97 | 873 | 304 | 1292 | 262 | 1116 | 306 | 1311 | 186 | 2019-06-26 23:00 | 278.1 | 69.4 | 1399 | R | 105 | 91 | 104 | 14 | 0.1 |  | 3.4 | 96.4 |  |  |  |  | 93 | 162.49 | 162.49 | 102 | 526.21 | 549.49 | 594.4 | 589.4 | 98.12 | 4.55 | 60.53 | 25.53 |  |  |  |  | 717.33 | 2.27 | 0.63 | 0.88
28 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | TRILOKPURI | 1240 | TKP005 | 1S-DL-YP-ETC-DMVR-2304-TKP005 | 10 BLOCK TKP:PL | TG-TKP005A-1 | 19505993 | 400 | 120 | 245 | 0.96 | 360 | 141 | 591 | 111 | 463 | 108 | 446 | 138 | 2019-06-22 20:00 | 129.8 | 31.3 | 669 | R | 109 | 78 | 112 | 34 | 0.1 | 0.1 | 20.9 | 78.9 |  |  |  |  | 24.5 | 235.24 | 235.24 | 37.36 | 613.09 | 470.31 | 546.09 | 665.25 | 62.13 | 0.3 | 126 | 3.24 | 6.13 |  | 6 |  | 706.25 | 13.35 | 0.64 | 0.9
29 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | TRILOKPURI | 1240 | TKP006 | 1S-DL-YP-ETC-DMVR-2304-TKP006 | 18 BLOCK TKP:PL:ID | TG-TKP006A-1 | 19505763 | 630 | 200 | 237 | 0.97 | 567 | 182 | 818 | 186 | 827 | 198 | 898 | 77 | 2019-06-30 23:30 | 183.6 | 55 | 928 | Y | 99 | 99 | 101 | 2 |  | 0.6 | 44.3 | 55 |  |  |  |  | 9 | 10.3 | 10.3 | 7 | 647.52 | 616.52 | 606.52 | 626.22 | 51 | 80.3 | 93.3 | 74.3 |  |  |  |  | 707.52 | 12.08 | 0.69 | 0.9
30 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | TRILOKPURI | 1240 | TKP007 | 1S-DL-YP-ETC-DMVR-2304-TKP007 | 13 BLOCK TKP:ID | TG-TKP007A-1 | 19500453 | 630 | 200 | 237 | 0.97 | 647 | 221 | 960 | 194 | 839 | 233 | 1018 | 158 | 2019-06-30 01:00 | 121.9 | 34.5 | 1018 | B | 101 | 90 | 109 | 19 |  | 0.1 | 30.3 | 69.6 | 0.3 | 0.3 | 0.3 | 0.3 | 33 | 89.3 | 89.3 | 41 | 645.55 | 624.24 | 569.25 | 635.55 | 38.54 | 4.55 | 119.29 | 40.54 | 1 |  | 3.55 | 1 | 719.19 | 0.41 | 0.58 | 1.03
31 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | TRILOKPURI | 1240 | TKP007 | 1S-DL-YP-ETC-DMVR-2304-TKP007 | 13 BLOCK TKP:ID | TG-TKP007A-2 | 19506208 | 990 | 320 | 239 | 0.97 | 916 | 395 | 1711 | 258 | 1122 | 263 | 1125 | 587 | 2019-06-30 01:00 | 251.5 | 67.5 | 1711 | R | 119 | 90 | 91 | 29 | 0.1 | 0.5 | 36.7 | 62.7 | 1.3 | 1.3 | 1.3 | 1.3 | 8 | 151.3 | 151.3 | 67 | 574.59 | 558.49 | 572.49 | 638.27 | 124.28 |  |  | 4.52 | 2.52 |  |  |  | 711.49 | 8.11 | 0.6 | 0.93
32 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | TRILOKPURI | 1240 | TKP008 | 1S-DL-YP-ETC-DMVR-2304-TKP008 | 23 BLOCK TKP:PL | TG-TKP008A-1 | 19504151 | 990 | 320 | 238 | 0.97 | 944 | 326 | 1360 | 310 | 1301 | 308 | 1280 | 72 | 2019-06-26 23:00 | 221.5 | 79.5 | 1612 | B | 100 | 103 | 98 | 5 |  | 0.1 | 12.2 | 87.7 |  |  |  |  | 46.51 | 36 | 36 | 51.29 | 610.17 | 584.37 | 566.46 | 595.38 | 60.35 | 96.36 | 61.2 | 70.36 |  | 0.3 | 3.16 |  | 717.43 | 2.17 | 0.62 | 0.95
33 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | TRILOKPURI | 1240 | TKP008 | 1S-DL-YP-ETC-DMVR-2304-TKP008 | 23 BLOCK TKP:PL | TG-TKP008A-2 | 19504155 | 630 | 200 | 244 | 0.97 | 709 | 246 | 1012 | 206 | 850 | 257 | 1069 | 197 | 2019-06-12 06:00 | 184.5 | 28.5 | 1069 | B | 109 | 92 | 99 | 17 |  | 1 | 19.3 | 79.7 |  |  |  |  | 3.3 | 21.29 | 21.29 | 7 | 499.13 | 662.31 | 596.08 | 602.16 | 189.15 | 29.46 | 111 | 106.52 | 24.51 | 3.03 | 0.41 | 0.41 | 716.49 | 3.11 | 0.59 | 1.12
34 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | TRILOKPURI | 1240 | TKP013 | 1S-DL-YP-ETC-DMVR-2304-TKP013 | 134 WORK CENTER:ID | TG-TKP013A-1 | 19505258 | 630 | 200 | 241 | 0.96 | 535 | 217 | 899 | 144 | 590 | 174 | 725 | 268 | 2019-06-26 00:30 | 179.2 | 52 | 911 | Y | 81 | 111 | 107 | 30 |  | 0.4 | 28.3 | 71.3 | 1.3 | 1.3 | 1.3 | 1.3 | 267.23 | 16 | 16 | 85.08 | 438.48 | 685.11 | 561.38 | 619.03 |  | 5 | 58 | 2.3 | 0.3 | 0.3 | 0.3 |  | 708.11 | 11.49 | 0.62 | 0.85
35 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | TRILOKPURI | 1240 | TKP020 | 1S-DL-YP-ETC-DMVR-2304-TKP020 | KOTLA VILLAGE:PL | TG-TKP020A-2 | 19505256 | 630 | 200 | 235 | 0.97 | 651 | 191 | 819 | 244 | 1050 | 215 | 918 | 201 | 2019-06-12 00:30 | 189.2 | 54.6 | 1050 | Y | 99 | 106 | 95 | 11 | 0.1 | 1.4 | 36.6 | 62 | [8 empty] | 565.4 | 507.12 | 583.42 | 564.12 | 137.16 | 187 | 117.48 | 138.48 | 0.3 | 9.14 | 0.56 | 0.26 | 703.26 | 16.34 | 0.68 | 1.03
36 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | TRILOKPURI | 1240 | TKP025 | 1S-DL-YP-ETC-DMVR-2304-TKP025 | 15 BLOCK TKP:PL | TG-TKP025A-1 | 19502486 | 630 | 200 | 238 | 0.96 | 562 | 208 | 882 | 165 | 701 | 189 | 799 | 157 | 2019-06-26 23:30 | 130.6 | 48.3 | 882 | R | 113 | 91 | 96 | 22 |  |  | 5.5 | 94.5 |  |  |  |  | 10 | 140.56 | 140.56 | 59.3 | 616.44 | 573.41 | 547.43 | 629.14 | 91.53 | 4 | 44.54 | 29.53 |  |  |  |  | 718.37 | 1.23 | 0.65 | 0.89
37 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | TRILOKPURI | 1240 | TKP032 | 1S-DL-YP-ETC-DMVR-2304-TKP032 | NEW 28 BLOCK TRILOKPURI | TG-TKP032A-1 | 19506216 | 630 | 200 | 247 | 0.96 | 647 | 203 | 828 | 220 | 891 | 224 | 927 | 86 | 2019-06-27 06:00 | 238.6 | 52.4 | 975 | B | 95 | 106 | 99 | 11 | 0.1 | 0.2 | 8.4 | 91.3 |  |  |  |  | 73.56 | 25 | 25 | 35 | 596.19 | 558.23 | 636.23 | 611.45 | 39 | 119.52 | 38.22 | 61.3 |  | 6 | 1.3 | 1 | 709.15 | 10.45 | 0.59 | 1.03

## Loading Condition > 100%
MIS Report of Distribution Transformer - Jun19
Jun19 1240 MAYUR VIHAR PH- I & II (Loading Condition > 100% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | S/STN 8 POCKET C | 1240 | MV2010 | 1S-DL-YP-ETC-DMVR-2302-MV2010 | E BLOCK V. NAGAR:PL | TG-MV2010A-1 | 19503465 | 630 | 200 | 240 | 0.97 | 656 | 181 | 777 | 205 | 889 | 271 | 1187 | 367 | 2019-06-30 02:00 | 111.8 | 34 | 1193 | B | 89 | 96 | 115 | 26 |  |  | 18.2 | 81.8 | 0.3 |  |  |  | 259.3 | 205.51 | 205.51 | 189 | 441.27 | 451.02 | 461.53 | 450.53 | 17 | 60.34 | 102.11 | 77.04 |  | 1 | 48.23 | 1.3 | 718.27 | 1.33 | 0.52 | 1.04
2 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | S/STN 8 POCKET C | 1240 | MV2010 | 1S-DL-YP-ETC-DMVR-2302-MV2010 | E BLOCK V. NAGAR:PL | TG-MV2010A-2 | 19502553 | 990 | 320 | 233 | 0.98 | 1099 | 336 | 1513 | 406 | 1836 | 357 | 1596 | 290 | 2019-06-30 23:00 | 185.5 | 21.3 | 2349 | Y | 115 | 130 | 55 | 75 |  | 0.1 | 11.8 | 88.2 |  |  | 404.16 |  | 88.3 | 46 | 46 | 176.42 | 487.1 | 445.49 | 190.44 | 468.51 | 106.04 | 125.21 | 29.11 | 57.41 | 35.3 | 100.04 | 5 | 14 | 717.14 | 2.46 | 0.49 | 1.11
3 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | S/STN 8 POCKET C | 1240 | MV2043 | 1S-DL-YP-ETC-DMVR-2302-MV2043 | S/S -10 BLK KHP. COROM:PL | TG-MV2043A-2 | 19505915 | 630 | 200 | 244 | 0.96 | 691 | 221 | 940 | 248 | 1055 | 222 | 933 | 118 | 2019-06-29 23:30 | 265 | 64.6 | 1189 | B | 92 | 99 | 109 | 17 | 0.1 | 0.6 | 40.7 | 58.6 |  |  |  |  | 5 | 4 | 4 | 0.3 | 553.19 | 480.14 | 358.58 | 466.19 | 154.55 | 157.27 | 206.17 | 224.37 | 4.53 | 76.26 | 147.52 | 26.41 | 718.07 | 1.53 | 0.68 | 1.1
4 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | S/STN 8 POCKET C | 1240 | MV2047 | 1S-DL-YP-ETC-DMVR-2302-MV2047 | S/S 2 BLK KHP COLONY:ID | TG-MV2047A-1 | 19506725 | 630 | 200 | 249 | 0.96 | 750 | 230 | 942 | 258 | 1066 | 262 | 1089 | 137 | 2019-06-06 | 238.4 | 65.6 | 1089 | Y | 83 | 108 | 109 | 26 | 0.2 | 2.3 | 94.8 | 2.7 |  |  |  |  | 72 | 6.3 | 6.3 | 7 | 607.52 | 443.52 | 470.22 | 526.22 | 14.38 | 192 | 205.48 | 158.18 | 0.3 | 52.38 | 17.5 | 3.2 | 695 | 25 | 0.57 | 1.19
5 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1008 | 1S-DL-YP-ETC-DMVR-2301-MV1008 | ACHARYA NIKETAN:ID | TG-MV1008A-3 | 19505647 | 630 | 200 | 241 | 0.98 | 627 | 127 | 540 | 348 | 1581 | 152 | 681 | 977 | 2019-06-30 14:30 | 180.6 | 36.4 | 1581 | Y | 80 | 122 | 98 | 42 | 0.4 | 0.1 | 21 | 78.5 |  |  |  |  | 50.29 |  |  | 3.3 | 656.13 | 354.32 | 664.5 | 629.42 |  | 252.1 | 39.52 | 73.3 |  | 100 |  |  | 706.42 | 13.18 | 0.67 | 1
6 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1009 | 1S-DL-YP-ETC-DMVR-2301-MV1009 | SHASHI GARDEN PLM:PL | TG-MV1009A-1 | 19502111 | 990 | 320 | 245 | 0.97 | 1297 | 363 | 1522 | 473 | 2002 | 460 | 1939 | 452 | 2019-06-30 01:00 | 203.9 | 85.4 | 2126 | B | 91 | 105 | 104 | 14 |  |  | 1.2 | 98.8 |  |  |  |  | 17.3 |  |  | 6 | 524.16 | 457.13 | 444.43 | 481.43 | 139.58 | 147.01 | 128.03 | 133.01 | 37.03 | 114.33 | 136.01 | 98.03 | 718.47 | 1.13 | 0.57 | 1.31
7 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1024 | 1S-DL-YP-ETC-DMVR-2301-MV1024 | PARTAP NAGAR PLM:PL | TG-MV1024A-1 | 19500719 | 990 | 320 | 245 | 0.98 | 1051 | 438 | 1804 | 302 | 1229 | 311 | 1268 | 557 | 2019-06-06 17:30 | 215.6 | 16.2 | 1992 | R | 134 | 75 | 91 | 59 |  | 0.5 | 58.9 | 40.6 | 0 | 0 | 0 | 0 |  | 185.15 | 185.15 | 18.3 | 299.15 | 503.24 | 573.02 | 575.21 | 240.03 | 1.35 | 47.57 | 95.18 | 150.56 |  |  | 1.05 | 713.09 | 6.51 | 0.6 | 1.06
8 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1092 | 1S-DL-YP-ETC-DMVR-2301-MV1092 | S.S 1 CGHS MVR PH 1:ID | TG-MV1092A-1 | 19502958 | 990 | 320 | 244 | 0.97 | 1000 | 398 | 1667 | 287 | 1192 | 315 | 1315 | 427 | 2019-06-11 23:30 | 179.6 | 48.6 | 1673 | R | 115 | 87 | 99 | 28 |  |  | 15.3 | 84.7 |  |  | 0.3 |  | 23 | 146.59 | 146.59 | 58.59 | 530.38 | 556.45 | 522.44 | 563.39 | 116.36 | 13.58 | 101.3 | 93.34 | 47.28 |  | 1.28 | 1.3 | 717.42 | 2.18 | 0.57 | 1.01
9 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1092 | 1S-DL-YP-ETC-DMVR-2301-MV1092 | S.S 1 CGHS MVR PH 1:ID | TG-MV1092A-3 | 19506267 | 630 | 200 | 236 | 0.98 | 741 | 319 | 1549 | 213 | 1000 | 209 | 995 | 551 | 2019-06-26 23:00 | 178 | 37.2 | 1554 | R | 123 | 91 | 86 | 37 | 0.4 | 1.2 | 20.5 | 77.9 |  |  | 1.3 |  | 19.3 | 157 | 157 | 84 | 456.23 | 482.29 | 462.29 | 497.53 | 117 | 65.36 | 44.05 | 113.42 | 112.41 | 0.29 |  | 9.59 | 705.34 | 14.26 | 0.5 | 1.18
10 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1107 | 1S-DL-YP-ETC-DMVR-2301-MV1107 | NEW S/S SHASHIGARDEN:PLM | TG-MV1107A-2 | 19502512 | 630 | 200 | 240 | 0.97 | 685 | 213 | 881 | 265 | 1101 | 207 | 856 | 233 | 2019-06-26 23:30 | 163.3 | 69.9 | 1145 | Y | 86 | 122 | 91 | 36 |  | 0.1 | 52.1 | 47.8 |  |  |  |  | 4 |  |  |  | 538.49 | 88.3 | 495.49 | 405.46 | 171.38 | 342.16 | 218.38 | 280.03 | 1 | 284.41 |  | 29.38 | 715.27 | 4.33 | 0.73 | 1.09
11 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | TRILOKPURI | 1240 | TKP016 | 1S-DL-YP-ETC-DMVR-2304-TKP016 | 31 BLOCK TKP:K | TG-TKP016A-1 | 19504812 | 630 | 200 | 232 | 0.97 | 784 | 229 | 1007 | 287 | 1293 | 269 | 1214 | 255 | 2019-06-30 23:00 | 171.6 | 68.5 | 1306 | Y | 87 | 113 | 100 | 26 |  | 26.7 | 72.2 | 1.1 |  |  |  |  | 2 |  |  |  | 469.54 | 188.58 | 354.28 | 332.27 | 202.48 | 272.26 | 200.56 | 230.27 | 44.14 | 257.32 | 163.32 | 156.02 | 718.56 | 1.04 | 0.67 | 1.24
12 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | TRILOKPURI | 1240 | TKP023 | 1S-DL-YP-ETC-DMVR-2304-TKP023 | 17 BLOCK TKP:PL | TG-TKP023A-1 | 19502505 | 990 | 320 | 230 | 0.97 | 1079 | 343 | 1449 | 333 | 1410 | 402 | 1694 | 266 | 2019-06-03 02:00 | 222.3 | 62.6 | 1799 | R | 112 | 91 | 97 | 21 |  |  | 66.6 | 33.4 |  |  |  |  | 1 | 24.44 | 24.44 | 13.44 | 476.14 | 605.58 | 539.58 | 543.58 | 146.22 | 82.21 | 132.19 | 141.1 | 89.45 | 0.18 | 12.2 | 14.29 | 713.21 | 6.39 | 0.62 | 1.09
13 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | TRILOKPURI | 1240 | TKP023 | 1S-DL-YP-ETC-DMVR-2304-TKP023 | 17 BLOCK TKP:PL | TG-TKP023A-2 | 19505648 | 630 | 200 | 229 | 0.97 | 722 | 274 | 1235 | 261 | 1183 | 187 | 840 | 372 | 2019-06-03 | 228.4 | 33.8 | 1354 | B | 101 | 93 | 106 | 13 | 1 | 1.6 | 32.9 | 64.4 |  |  |  |  | 58.23 | 113.24 | 113.24 | 66.4 | 547.15 | 547.27 | 509.28 | 541.58 | 102.19 | 48 | 93.51 | 95.04 | 4.54 | 4 | 42.34 | 9.09 | 712.51 | 7.09 | 0.52 | 1.15
14 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | TRILOKPURI | 1240 | TKP024 | 1S-DL-YP-ETC-DMVR-2304-TKP024 | 2 BLOCK TKP:PL | TG-TKP024A-1 | 19505548 | 630 | 200 | 221 | 0.97 | 764 | 245 | 1182 | 239 | 1145 | 281 | 1361 | 200 | 2019-06-09 | 301.8 | 37 | 1361 | B | 97 | 94 | 109 | 15 |  |  | 9.6 | 90.4 |  |  |  |  | 171.04 | 176 | 176 | 156.34 | 484.26 | 500.3 | 463.26 | 481.56 | 57.19 | 37.56 | 58.3 | 71.5 | 1.54 | 0.17 | 58.13 | 4.23 | 714.43 | 5.17 | 0.45 | 1.21
15 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | TRILOKPURI | 1240 | TKP027 | 1S-DL-YP-ETC-DMVR-2304-TKP027 | 11&12 BLOCK TRILOK TRILOK PURI | TG-TKP027A-1 | 19505745 | 630 | 200 | 239 | 0.96 | 597 | 175 | 750 | 219 | 935 | 203 | 871 | 163 | 2019-06-22 20:00 | 218.2 | 30.6 | 1056 | B | 91 | 94 | 115 | 24 | 0.1 | 0.4 | 30.4 | 69 | 0.01 | 3.01 |  | 0.01 | 102.23 | 122.27 | 122.27 | 50.42 | 601.57 | 523.58 | 514.23 | 632.26 | 1 | 52.43 | 126.42 | 22.12 |  | 3.12 | 33 |  | 705.21 | 14.39 | 0.61 | 0.95
16 | 2019-06-10 | 2019-06-30 23:30 | MAYUR VIHAR I & II | TRILOKPURI | 1240 | TKP030 | 1S-DL-YP-ETC-DMVR-2304-TKP030 | KOTLA VILLAGE NEW | TG-TKP030A-1 | 19504357 | 630 | 200 | 237 | 0.97 | 675 | 226 | 962 | 223 | 946 | 226 | 965 | 17 | 2019-06-13 23:30 | 148.6 | 25.8 | 1106 | Y | 99 | 106 | 95 | 11 | 0 |  | 6.8 | 93.2 |  | 0.02 |  | 0.02 | 1.02 |  |  |  | 303.58 | 280.11 | 299.38 | 312.38 | 125.51 | 140.38 | 88.11 | 106.11 | 9.3 | 19.3 | 35 | 21.3 | 486.16 | 17.44 | 0.67 | 1.07