## Complete Report
MIS Report of Distribution Transformer - Jun19
Jun19 1240 MAYUR VIHAR PH- I & II (Complete Report)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1027 | 1S-DL-YP-ETC-DMVR-2301-MV1027 | DDA PUMP HOUSE PKT-IV MVR PH-1:PM | TG-MV1027A-1 | 19502574 | 400 | 120 | 237 | 0.61 | 61 | 20 | 82 | 22 | 90 | 19 | 79 | 10 | 2019-06-29 19:30 | 56.3 | -42.2 | 90 | Y | 99 | 103 | 99 | 4 |  | 0.1 | 0.7 | 99.2 | 717.55 | 717.55 | 717.55 | 717.55 | [16 empty] | 717.55 | 2.05 | 0.21 | 0.15
2 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1088 | 1S-DL-YP-ETC-DMVR-2301-MV1088 | D.P. NO 1 NOIDA RD:PL | TG-MV1088A-1 | 19505815 | 100 | 40 | 246 | 0.78 | 60 | 14 | 57 | 31 | 128 | 14 | 58 | 70 | 2019-06-26 19:30 | 55.2 | -0.1 | 131 | Y | 67 | 169 | 64 | 105 |  | 1.7 | 46.1 | 52.2 | 467.45 | 402.15 | 415.15 | 402.15 | 232.49 |  |  | 275.19 | 4.28 | 286.49 | 8.3 | 27.28 |  | 15.58 | [6 empty] | 705.02 | 14.58 | 0.29 | 0.6
3 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1090 | 1S-DL-YP-ETC-DMVR-2301-MV1090 | D.P. NO 3 NOIDA RD:PM | TG-MV1090A-1 | 19504654 | 400 | 120 | 245 | 0.76 | 129 | 42 | 168 | 56 | 228 | 32 | 127 | 88 | 2019-06-06 19:00 | 106.3 | 0.3 | 228 | Y | 88 | 142 | 70 | 72 |  | 4.7 | 74.2 | 21.2 | 513.45 | 421.45 | 706.45 | 426.15 | 206 | 296.3 | 296.3 | 293.3 |  | 1.3 | [10 empty] | 719.45 | 0.15 | 0.32 | 0.32
4 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | SADAR APPARTMENTS | 1240 | MV1091 | 1S-DL-YP-ETC-DMVR-2301-MV1091 | D.P. NO 4 NOIDA RD:PL | TG-MV1091A-1 | 19505529 | 100 | 40 | 245 | 0.8 | 78 | 20 | 81 | 31 | 127 | 27 | 111 | 41 | 2019-06-06 19:30 | 69 | -1.2 | 129 | Y | 85 | 118 | 97 | 33 | 5.3 | 8.3 | 41.7 | 44.7 | 397.18 | 410.15 | 409.15 | 410.15 | 267.27 |  |  |  | 46.3 | 287 | 294.3 | 301 |  | 14 | 6.3 | [5 empty] | 711.15 | 8.45 | 0.31 | 0.78
5 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR I & II | TRILOKPURI | 1240 | TKP006 | 1S-DL-YP-ETC-DMVR-2304-TKP006 | 18 BLOCK TKP:PL:ID | TG-TKP006A-2 | 19506209 | 100 | 40 | 239 | 0.73 | 126 | 47 | 207 | 0 | 0 | 79 | 362 | 315 | 2019-06-09 19:30 | 68.2 | 14.2 | 362 | B | 133 | 0 | 167 | 167 | 12.3 | 27.6 | 19.3 | 40.8 | 390.22 | 707.52 | 392.52 | 390.22 | 15 |  |  | 300 | 302 |  | 297 | 17 |  |  | 10 |  | 0.3 |  | 0.3 | 0.3 | 707.52 | 12.08 | 0.12 | 1.26