## Complete Report
MIS Report of Distribution Transformer - Jun19
Jun19 1241 MAYUR VIHAR III (Complete Report)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE001 | 1S-DL-YP-ETC-DVSE-2351-VSE001 | S/STN 1 A1 PKT MVR-III:ID | TG-VSE001A-1 | 19502409 | 630 | 200 | 242 | 0.97 | 391 | 127 | 548 | 138 | 592 | 127 | 546 | 46 | 2019-06-30 23:30 | 30.4 | -63.5 | 592 | Y | 104 | 103 | 94 | 10 |  |  | 12.1 | 87.9 | 17.59 | 22.3 | 24.59 | 19.3 | 540.59 | 564.42 | 564.42 | 587.42 | 155.05 | 126.51 | 81.52 | 106.51 | [8 empty] | 714.03 | 5.57 | 0.53 | 0.62
2 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE001 | 1S-DL-YP-ETC-DVSE-2351-VSE001 | S/STN 1 A1 PKT MVR-III:ID | TG-VSE001A-2 | 19506139 | 630 | 200 | 248 | 0.96 | 198 | 69 | 287 | 42 | 173 | 87 | 359 | 163 | 2019-06-30 | 43.4 | 12.4 | 359 | B | 106 | 59 | 134 | 75 | 0.3 | 8.3 | 46.3 | 45.1 | 481.29 | 687.05 | 341.15 | 522.41 | 209.06 | 3.3 | 3.3 | 167.54 |  |  | 0.3 | [9 empty] | 690.35 | 29.25 | 0.5 | 0.31
3 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE002 | 1S-DL-YP-ETC-DVSE-2351-VSE002 | S/STN 3 A1 PKT MVR-III:ID | TG-VSE002A-1 | 19505965 | 630 | 200 | 249 | 0.97 | 315 | 111 | 461 | 114 | 473 | 89 | 368 | 100 | 2019-06-29 23:30 | 55.8 | 16.2 | 523 | R | 117 | 99 | 83 | 34 | 0.1 | 0.5 | 15.5 | 83.9 | 148.3 | 248.33 | 390.03 | 250 | 436.58 | 430.1 | 430.1 | 427.15 | 133.45 | 40.3 | 5.3 | 41.58 | [8 empty] | 719.13 | 0.47 | 0.5 | 0.5
4 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE002 | 1S-DL-YP-ETC-DVSE-2351-VSE002 | S/STN 3 A1 PKT MVR-III:ID | TG-VSE002A-2 | 19505590 | 630 | 200 | 249 | 0.97 | 147 | 52 | 219 | 45 | 189 | 49 | 206 | 26 | 2019-06-11 | 36.4 | 5.4 | 252 | B | 116 | 86 | 98 | 30 | 0.1 | 0.3 | 22.8 | 76.9 | 642.58 | 706.57 | 684.43 | 689.13 | 76.14 | 12.15 | 12.15 | 29.59 | [12 empty] | 719.12 | 0.48 | 0.49 | 0.23
5 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE003 | 1S-DL-YP-ETC-DVSE-2351-VSE003 | S/STN 4 A2 PKT MVR-III:ID | TG-VSE003A-1 | 19502403 | 630 | 200 | 241 | 0.98 | 402 | 84 | 340 | 160 | 664 | 158 | 655 | 319 | 2019-06-14 | 74.1 | 23.9 | 730 | B | 73 | 104 | 123 | 50 |  | 3.3 | 11.7 | 85 | 73.3 | 12.05 |  | 5 | 633.03 | 451.3 | 451.3 | 475.55 | 12 | 254.58 | 429.33 | 237.38 |  |  | 0.3 | [5 empty] | 718.33 | 1.27 | 0.57 | 0.64
6 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE003 | 1S-DL-YP-ETC-DVSE-2351-VSE003 | S/STN 4 A2 PKT MVR-III:ID | TG-VSE003A-2 | 19504338 | 400 | 120 | 248 | 0.96 | 180 | 57 | 236 | 55 | 223 | 68 | 281 | 52 | 2019-06-30 20:30 | 69.6 | 3.6 | 281 | B | 102 | 77 | 121 | 44 |  | 0.4 | 16.5 | 83.1 | 409.3 | 577.29 | 298.07 | 475.25 | 262.29 | 137 | 137 | 198.34 | 46.3 | 4 | 75.3 | 44.3 | [8 empty] | 718.29 | 1.31 | 0.44 | 0.45
7 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE004 | 1S-DL-YP-ETC-DVSE-2351-VSE004 | S/STN 5 A2 PKT MVR-III:ID | TG-VSE004A-1 | 19506007 | 400 | 120 | 246 | 0.97 | 227 | 86 | 372 | 72 | 314 | 68 | 295 | 70 | 2019-06-03 01:00 | 35 | 10.3 | 372 | R | 112 | 98 | 90 | 22 |  | 0.4 | 66.1 | 33.5 | 145.28 | 281.48 | 330.17 | 258.08 | 456.19 | 347.59 | 347.59 | 384.09 | 115.34 | 87.34 | 33.04 | 75.04 | [8 empty] | 717.21 | 2.39 | 0.45 | 0.57
8 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE004 | 1S-DL-YP-ETC-DVSE-2351-VSE004 | S/STN 5 A2 PKT MVR-III:ID | TG-VSE004A-2 | 19503533 | 400 | 120 | 238 | 0.97 | 440 | 172 | 781 | 165 | 744 | 103 | 455 | 309 | 2019-06-03 01:00 | 64.9 | 19.9 | 781 | R | 112 | 107 | 81 | 31 | 0.5 | 34.2 | 65.1 | 0.2 | 9.59 | 11.59 | 19.25 | 10.59 | 221.29 | 253.49 | 253.49 | 268.58 | 357.2 | 339.3 | 306.35 | 366.51 | 91.3 | 95.3 | 1 | 68.55 | 37.05 | 16.35 |  | 1.4 | 717.23 | 2.37 | 0.45 | 1.1
9 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE005 | 1S-DL-YP-ETC-DVSE-2351-VSE005 | S/STN 6 A3 PKT MVR - III:ID | TG-VSE005A-1 | 19502414 | 630 | 200 | 243 | 0.97 | 380 | 134 | 587 | 104 | 451 | 143 | 618 | 154 | 2019-06-30 23:30 | 67.6 | 18.4 | 625 | B | 100 | 83 | 117 | 34 |  |  | 78.1 | 21.9 | 137.29 | 272.3 | 40.3 | 133.59 | 422 | 367.29 | 367.29 | 421.3 | 160.3 | 80 | 234 | 164.3 | [8 empty] | 719.59 | 0.01 | 0.51 | 0.6
10 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE006 | 1S-DL-YP-ETC-DVSE-2351-VSE006 | S/STN 7 A3 PKT MVR - III:ID | TG-VSE006A-1 | 19505077 | 990 | 320 | 237 | 0.97 | 762 | 241 | 1067 | 211 | 937 | 311 | 1389 | 402 | 2019-06-03 01:00 | 98.6 | 33.9 | 1389 | B | 96 | 84 | 120 | 36 |  |  | 0.3 | 99.7 | 147.57 | 253.37 | 66.08 | 153.42 | 381.05 | 315.43 | 315.43 | 353.58 | 186.56 | 146.38 | 262.03 | 208.18 |  |  | 14.38 | [5 empty] | 715.58 | 4.02 | 0.43 | 0.77
11 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE006 | 1S-DL-YP-ETC-DVSE-2351-VSE006 | S/STN 7 A3 PKT MVR - III:ID | TG-VSE006A-2 | 19503534 | 400 | 120 | 243 | 0.97 | 180 | 50 | 214 | 58 | 249 | 72 | 313 | 87 | 2019-06-03 01:00 | 32.3 | 7.7 | 315 | B | 81 | 100 | 119 | 38 |  |  | 1 | 99 | 510.29 | 407.59 | 283.29 | 411.29 | 208.08 | 279.52 | 279.52 | 293.3 |  | 30.46 | 75.08 | 13.38 | [8 empty] | 718.37 | 1.23 | 0.46 | 0.45
12 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE007 | 1S-DL-YP-ETC-DVSE-2351-VSE007 | S/STN 8 A2 PKT MVR - III:ID | TG-VSE007A-1 | 19502374 | 630 | 200 | 240 | 0.98 | 180 | 45 | 190 | 41 | 176 | 95 | 406 | 224 | 2019-06-01 22:00 | 28.1 | 7.4 | 412 | B | 79 | 79 | 142 | 63 |  |  | 2.6 | 97.4 | 699.46 | 716.46 | 326.16 | 607.46 | 20 | 3 | 3 | 112 |  |  | 13 | [9 empty] | 719.46 | 0.14 | 0.54 | 0.29
13 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE007 | 1S-DL-YP-ETC-DVSE-2351-VSE007 | S/STN 8 A2 PKT MVR - III:ID | TG-VSE007A-2 | 19502410 | 630 | 200 | 240 | 0.97 | 224 | 83 | 354 | 66 | 280 | 75 | 322 | 64 | 2019-06-30 23:00 | 35 | 12.4 | 368 | B | 120 | 74 | 107 | 46 |  |  | 74.3 | 25.7 | 430.15 | 640.45 | 505.15 | 546.15 | 289 | 79 | 79 | 173.3 | 0.3 |  | 1 | [9 empty] | 719.45 | 0.15 | 0.46 | 0.36
14 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE008 | 1S-DL-YP-ETC-DVSE-2351-VSE008 | S/STN 9 A2 PKT MVR - III:ID | TG-VSE008A-1 | 19505180 | 990 | 320 | 241 | 0.97 | 347 | 77 | 339 | 159 | 703 | 111 | 487 | 317 | 2019-06-03 01:30 | 64 | 16.6 | 756 | Y | 78 | 124 | 98 | 46 |  | 0.1 | 7.4 | 92.6 | 640.14 | 390.44 | 519.14 | 505.44 | 54.34 | 298 | 298 | 189.04 |  | 6.04 | [10 empty] | 694.48 | 25.12 | 0.48 | 0.35
15 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE008 | 1S-DL-YP-ETC-DVSE-2351-VSE008 | S/STN 9 A2 PKT MVR - III:ID | TG-VSE008A-2 | 19502404 | 630 | 200 | 244 | 0.97 | 550 | 175 | 728 | 215 | 908 | 160 | 666 | 218 | 2019-06-29 23:30 | 107.6 | 28.5 | 908 | Y | 95 | 114 | 91 | 23 |  |  | 20.7 | 79.3 | 44.3 | 7.3 | 25.58 | 18 | 398.15 | 327.45 | 327.45 | 393.45 | 271.58 | 335.28 | 262.34 | 301.58 | 3.36 | 46.36 |  | 4.36 |  | 1 |  |  | 718.19 | 1.41 | 0.47 | 0.87
16 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE009 | 1S-DL-YP-ETC-DVSE-2351-VSE009 | S/STN 12 A3 PKT MVR-III:ID | TG-VSE009A-1 | 19506286 | 400 | 120 | 237 | 0.98 | 223 | 70 | 315 | 117 | 552 | 37 | 162 | 340 | 2019-06-30 23:00 | 86.9 | 7.2 | 552 | Y | 126 | 115 | 59 | 67 | 0.2 | 0.1 | 26.2 | 73.5 | 232.59 | 267 | 566.29 | 374 | 316.3 | 341.29 | 341.29 | 282.59 | 147 | 87.3 |  | 39.3 |  | 0.3 | [6 empty] | 696.29 | 23.31 | 0.4 | 0.56
17 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE010 | 1S-DL-YP-ETC-DVSE-2351-VSE010 | S/STN B1 DDA JANTA FLATE:ID | TG-VSE010A-1 | 19502734 | 630 | 200 | 239 | 0.96 | 404 | 153 | 663 | 140 | 601 | 110 | 471 | 169 | 2019-06-30 23:00 | 86.5 | 35.4 | 672 | R | 105 | 105 | 91 | 14 |  |  | 25.7 | 74.3 | 1 | 1.3 | 16 | 1 | 436.33 | 420.34 | 420.34 | 472.03 | 281.3 | 296.59 | 184 | 246 | [8 empty] | 719.03 | 0.57 | 0.58 | 0.64
18 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE010 | 1S-DL-YP-ETC-DVSE-2351-VSE010 | S/STN B1 DDA JANTA FLATE:ID | TG-VSE010A-2 | 19502735 | 630 | 200 | 239 | 0.98 | 351 | 127 | 537 | 127 | 543 | 97 | 414 | 126 | 2019-06-29 23:30 | 61.6 | 21.2 | 554 | Y | 107 | 109 | 85 | 24 |  |  | 50.6 | 49.4 | 1 | 3 | 76.5 | 7.3 | 473.34 | 470.04 | 470.04 | 522.04 | 244.17 | 245.47 | 63.47 | 189.17 | [8 empty] | 718.51 | 1.09 | 0.62 | 0.56
19 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE011 | 1S-DL-YP-ETC-DVSE-2351-VSE011 | S/STN B5 DDA JANTA FLATE:ID | TG-VSE011A-1 | 19506212 | 400 | 120 | 251 | 0.95 | 369 | 109 | 442 | 142 | 578 | 119 | 486 | 120 | 2019-06-30 23:00 | 98.2 | 29.4 | 601 | Y | 84 | 115 | 101 | 31 |  | 0.2 | 9.4 | 90.4 | 5 | 1.3 |  |  | 395.46 | 217.46 | 217.46 | 294.16 | 295 | 357 | 376 | 369.3 | 0.3 | 105 | 37.3 | 32.3 |  | 15 |  |  | 696.16 | 23.44 | 0.52 | 0.92
20 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE012 | 1S-DL-YP-ETC-DVSE-2351-VSE012 | S/STN 3 B-7 DDA JANTA FLAT:ID | TG-VSE012A-1 | 19502420 | 400 | 120 | 246 | 0.96 | 477 | 197 | 833 | 104 | 433 | 176 | 751 | 366 | 2019-06-30 22:30 | 86.9 | 36.4 | 833 | R | 110 | 75 | 115 | 40 |  | 8.3 | 79.8 | 11.9 |  |  |  |  | 105.16 | 340.59 | 340.59 | 135.15 | 415.43 | 378.3 | 463.43 | 450.14 | 111.3 |  | 105.3 | 111 | 87 |  | 90 | 23 | 719.29 | 0.31 | 0.49 | 1.19
21 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE012 | 1S-DL-YP-ETC-DVSE-2351-VSE012 | S/STN 3 B-7 DDA JANTA FLAT:ID | TG-VSE012A-2 | 19503538 | 400 | 120 | 250 | 0.95 | 283 | 98 | 411 | 80 | 334 | 105 | 444 | 97 | 2019-06-30 23:30 | 74.5 | 18.5 | 465 | B | 104 | 88 | 108 | 20 |  | 0.1 | 15.7 | 84.2 | 70.21 | 122.18 | 44.28 | 65.23 | 367.39 | 401.12 | 401.12 | 407.37 | 281.3 | 196 | 270.3 | 246.3 |  |  | 2 | [5 empty] | 719.3 | 0.3 | 0.51 | 0.71
22 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE013 | 1S-DL-YP-ETC-DVSE-2351-VSE013 | S/STN 4 B-8 DDA JANTA FLAT:ID | TG-VSE013A-1 | 19502375 | 400 | 120 | 246 | 0.95 | 109 | 48 | 200 | 45 | 186 | 16 | 67 | 126 | 2019-06-30 23:30 | 37.3 | 9.1 | 200 | R | 126 | 124 | 50 | 76 |  | 0.1 | 5.3 | 94.6 | 433.2 | 427.51 | 716.5 | 582.5 | 285 | 290.29 | 290.29 | 135.3 | [12 empty] | 718.2 | 1.4 | 0.57 | 0.27
23 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE013 | 1S-DL-YP-ETC-DVSE-2351-VSE013 | S/STN 4 B-8 DDA JANTA FLAT:ID | TG-VSE013A-2 | 19503774 | 400 | 120 | 239 | 0.97 | 257 | 123 | 532 | 61 | 265 | 73 | 312 | 247 | 2019-06-28 23:30 | 50.8 | 18.8 | 546 | R | 137 | 76 | 87 | 61 |  | 0.1 | 15.4 | 84.6 | 3 | 164.15 | 54.3 | 33 | 199.15 | 512.59 | 512.59 | 402.45 | 480.59 | 42.3 | 151.59 | 283.59 | 36.3 | [7 empty] | 719.44 | 0.16 | 0.57 | 0.64
24 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE014 | 1S-DL-YP-ETC-DVSE-2351-VSE014 | S/STN C-1 PKT DDA JANTA FLAT:ID | TG-VSE014A-1 | 19506899 | 630 | 200 | 245 | 0.97 | 527 | 211 | 873 | 143 | 593 | 173 | 718 | 243 | 2019-06-02 | 137.8 | 25 | 897 | R | 105 | 93 | 101 | 12 | 0.1 | 0.2 | 10.8 | 88.8 |  |  | 0.3 |  | 162.16 | 223.31 | 223.31 | 136.45 | 486.03 | 478.33 | 616.01 | 567.25 | 57.51 | 4.3 | 7.24 | 2.24 | 0.24 |  |  |  | 706.34 | 13.26 | 0.61 | 0.84
25 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE015 | 1S-DL-YP-ETC-DVSE-2351-VSE015 | S/STN C-2 PKT DDA JANTA FLAT:ID | TG-VSE015A-1 | 19502405 | 630 | 200 | 243 | 0.97 | 661 | 226 | 949 | 242 | 1025 | 193 | 819 | 181 | 2019-06-30 23:00 | 132.9 | 46.9 | 1025 | Y | 104 | 104 | 92 | 12 |  |  | 31.4 | 68.6 |  |  |  |  | 24.25 | 27.25 | 27.25 | 33.25 | 550.28 | 537.58 | 577.1 | 556.58 | 130.3 | 124.3 | 68.41 | 123 | 13.41 | 29.11 |  | 5.41 | 719.04 | 0.56 | 0.6 | 1.05
26 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE016 | 1S-DL-YP-ETC-DVSE-2351-VSE016 | S/STN D-1 PKT DDA JANTA FLAT:ID | TG-VSE016A-1 | 19502731 | 400 | 120 | 241 | 0.97 | 221 | 65 | 282 | 71 | 305 | 85 | 365 | 75 | 2019-06-29 23:00 | 44.2 | 15.2 | 378 | B | 89 | 91 | 121 | 32 |  | 0.2 | 8.8 | 91 | 81 | 39 | 5.3 | 18.3 | 569.17 | 627.47 | 627.47 | 555.47 | 67.3 | 51 | 300.36 | 143.3 | [8 empty] | 717.47 | 2.13 | 0.59 | 0.55
27 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE016 | 1S-DL-YP-ETC-DVSE-2351-VSE016 | S/STN D-1 PKT DDA JANTA FLAT:ID | TG-VSE016A-2 | 19502733 | 400 | 120 | 246 | 0.96 | 207 | 72 | 302 | 57 | 238 | 78 | 330 | 82 | 2019-06-30 23:00 | 46.4 | 17.4 | 356 | B | 101 | 90 | 109 | 19 |  | 1.2 | 41.3 | 57.5 | 42.3 | 196.09 | 25 | 48.3 | 562.36 | 428.27 | 428.27 | 548.06 | 112.3 | 93 | 159 | 121 | [8 empty] | 717.36 | 2.24 | 0.58 | 0.52
28 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE017 | 1S-DL-YP-ETC-DVSE-2351-VSE017 | S/STN D-2 PKT DDA JANTA FLAT:ID | TG-VSE017A-1 | 19502832 | 400 | 120 | 241 | 0.97 | 213 | 72 | 312 | 65 | 280 | 76 | 330 | 44 | 2019-06-30 23:30 | 46.4 | -5 | 330 | B | 97 | 99 | 104 | 7 | 76.9 | 3.6 | 4.2 | 15.2 | 155.07 | 117.36 | 139 | 132.37 | 360.3 | 408.31 | 408.31 | 386.3 | 32.3 | 22 | 43.3 | 29 | [8 empty] | 548.07 | 27.53 | 0.49 | 0.53
29 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE017 | 1S-DL-YP-ETC-DVSE-2351-VSE017 | S/STN D-2 PKT DDA JANTA FLAT:ID | TG-VSE017A-2 | 19502839 | 400 | 120 | 241 | 0.96 | 221 | 88 | 382 | 69 | 297 | 63 | 271 | 100 | 2019-06-30 23:00 | 43.1 | 15.7 | 382 | R | 113 | 93 | 93 | 20 | 0.1 | 0.5 | 8.2 | 91.3 | 37.26 | 171.52 | 55.3 | 62.56 | 471.33 | 425.07 | 425.07 | 523.33 | 208.3 | 120.3 | 33 | 131 | [8 empty] | 717.29 | 2.31 | 0.55 | 0.55
30 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE018 | 1S-DL-YP-ETC-DVSE-2351-VSE018 | S/STN 1 SFS FLATE MVR -III:ID | TG-VSE018A-1 | 19504937 | 630 | 200 | 243 | 0.97 | 127 | 30 | 129 | 42 | 182 | 55 | 234 | 91 | 2019-06-02 23:00 | 28.5 | 2.3 | 234 | B | 76 | 105 | 120 | 44 |  | 0.8 | 40.1 | 59.1 | 719.49 | 696.19 | 665.49 | 719.19 |  | 23.3 | 23.3 | 0.3 | [12 empty] | 719.49 | 0.11 | 0.48 | 0.2
31 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE018 | 1S-DL-YP-ETC-DVSE-2351-VSE018 | S/STN 1 SFS FLATE MVR -III:ID | TG-VSE018A-2 | 19505823 | 630 | 200 | 244 | 0.98 | 143 | 65 | 276 | 28 | 117 | 51 | 216 | 139 | 2019-06-30 23:30 | 42.4 | 4 | 291 | R | 138 | 64 | 98 | 74 | 0.1 | 3.9 | 11 | 85 | 559.18 | 719.48 | 679.48 | 689.18 | 160.3 |  |  | 30.3 | [12 empty] | 719.48 | 0.12 | 0.53 | 0.23
32 | 2019-06-09 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE019 | 1S-DL-YP-ETC-DVSE-2351-VSE019 | S/STN 2 SFS FLATE MVR -III:ID | TG-VSE019A-1 | 19502527 | 630 | 200 | 242 | 0.97 | 206 | 79 | 332 | 69 | 286 | 59 | 245 | 76 | 2019-06-11 22:30 | 34.5 | 6.9 | 336 | Y | 110 | 99 | 91 | 19 |  |  | 14.5 | 85.5 | 347.12 | 386.11 | 411.11 | 389.41 | 180.29 | 141.3 | 141.3 | 138 | [12 empty] | 527.41 | 0.19 | 0.5 | 0.33
33 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE019 | 1S-DL-YP-ETC-DVSE-2351-VSE019 | S/STN 2 SFS FLATE MVR -III:ID | TG-VSE019A-2 | 19502390 | 630 | 200 | 242 | 0.96 | 255 | 78 | 325 | 100 | 425 | 77 | 332 | 97 | 2019-06-10 15:00 | 66.7 | 17.5 | 447 | Y | 102 | 124 | 74 | 50 | 77.3 | 22.7 |  |  | 116.3 | 38.57 | 463.18 | 155 | 593.21 | 604.15 | 604.15 | 561.45 | 8.24 | 75.03 |  | 1.3 | [8 empty] | 718.15 | 1.45 | 0.61 | 0.4
34 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE019 | 1S-DL-YP-ETC-DVSE-2351-VSE019 | S/STN 2 SFS FLATE MVR -III:ID | TG-VSE019A-3 | 19506426 | 400 | 120 | 250 | 0.97 | 63 | 15 | 63 | 34 | 137 | 14 | 56 | 78 | 2019-06-05 23:00 | 19 | 1.8 | 158 | Y | 62 | 180 | 59 | 121 | 0.1 | 1 | 20.4 | 78.5 | 719.47 | 579.47 | 719.47 | 719.47 |  | 140 | 140 | [13 empty] | 719.47 | 0.13 | 0.51 | 0.16
35 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE020 | 1S-DL-YP-ETC-DVSE-2351-VSE020 | S/STN 3 SFS FLATE MVR -III:ID | TG-VSE020A-1 | 19502386 | 630 | 200 | 256 | 0.96 | 143 | 61 | 237 | 42 | 160 | 40 | 156 | 80 | 2019-06-14 | 36.8 | 6 | 257 | R | 117 | 97 | 85 | 32 |  |  | 16.2 | 83.8 | 597 | 710.3 | 717.3 | 699 | 123 | 9.3 | 9.3 | 21 | [12 empty] | 720 | 0 | 0.52 | 0.23
36 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE020 | 1S-DL-YP-ETC-DVSE-2351-VSE020 | S/STN 3 SFS FLATE MVR -III:ID | TG-VSE020A-2 | 19505824 | 630 | 200 | 244 | 0.98 | 138 | 42 | 169 | 36 | 149 | 60 | 249 | 91 | 2019-06-11 23:30 | 48.6 | 3.6 | 249 | B | 93 | 86 | 122 | 36 | 0.1 | 0.3 | 15.6 | 84 | 719 | 719.3 | 635 | 714 | 1 | 0.3 | 0.3 | 6 | [12 empty] | 720 | 0 | 0.52 | 0.22
37 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE021 | 1S-DL-YP-ETC-DVSE-2351-VSE021 | S/STN 4 SFS FLATE MVR - III:ID | TG-VSE021A-1 | 19502467 | 630 | 200 | 248 | 0.98 | 288 | 83 | 347 | 104 | 433 | 101 | 418 | 80 | 2019-06-02 23:30 | 58.9 | 9.7 | 459 | B | 97 | 98 | 105 | 8 |  |  | 23.4 | 76.6 | 260.26 | 233.16 | 215.16 | 229.56 | 429.3 | 458.4 | 458.4 | 451.3 | 29.3 | 27.3 | 78.3 | 38 | [8 empty] | 719.26 | 0.34 | 0.55 | 0.46
38 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE022 | 1S-DL-YP-ETC-DVSE-2351-VSE022 | S/STN 5 SFS FLATE NVR - III:ID | TG-VSE022A-1 | 19502469 | 630 | 200 | 243 | 0.98 | 169 | 51 | 215 | 65 | 269 | 52 | 216 | 53 | 2019-06-29 00:30 | 24.8 | 4.1 | 269 | Y | 88 | 105 | 107 | 19 |  | 1.7 | 55.2 | 43 | 645.46 | 598.46 | 607.47 | 621.46 | 74 | 121 | 121 | 98 | [12 empty] | 719.46 | 0.14 | 0.51 | 0.27
39 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE022 | 1S-DL-YP-ETC-DVSE-2351-VSE022 | S/STN 5 SFS FLATE NVR - III:ID | TG-VSE022A-2 | 19502468 | 630 | 200 | 246 | 0.98 | 159 | 50 | 211 | 48 | 202 | 60 | 257 | 51 | 2019-06-30 | 29.4 | 3.2 | 273 | B | 93 | 100 | 107 | 14 |  | 0.2 | 27.9 | 71.9 | 662.19 | 626.19 | 637.19 | 643.49 | 57 | 93 | 93 | 75.3 | [12 empty] | 719.19 | 0.41 | 0.51 | 0.25
40 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE023 | 1S-DL-YP-ETC-DVSE-2351-VSE023 | S/STN 7 SFS FLATE MVR - III:ID | TG-VSE023A-1 | 19502415 | 630 | 200 | 243 | 0.97 | 146 | 34 | 145 | 73 | 313 | 39 | 165 | 159 | 2019-06-30 23:30 | 24.4 | 4.6 | 313 | Y | 73 | 145 | 81 | 72 |  | 2.8 | 21.7 | 75.5 | 719.47 | 563.47 | 719.47 | 713.47 |  | 156 | 156 | 6 | [12 empty] | 719.47 | 0.13 | 0.46 | 0.23
41 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE023 | 1S-DL-YP-ETC-DVSE-2351-VSE023 | S/STN 7 SFS FLATE MVR - III:ID | TG-VSE023A-2 | 19502389 | 630 | 200 | 243 | 0.97 | 139 | 56 | 241 | 31 | 136 | 52 | 213 | 94 | 2019-06-02 23:30 | 31.7 | 2.8 | 269 | R | 129 | 55 | 116 | 74 | 99.1 | 0.1 | 0.1 | 0.6 | 572.43 | 719.43 | 631.43 | 706.13 | 147 |  |  | 13.3 | [12 empty] | 719.43 | 0.17 | 0.51 | 0.22
42 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE036 | 1S-DL-YP-ETC-DVSE-2351-VSE036 | SUBJI MANDI HARIJAN BASTI KNODLI:K | TG-VSE036A-1 | 19506914 | 990 | 320 | 242 | 0.97 | 1208 | 358 | 1615 | 453 | 2059 | 396 | 1770 | 390 | 2019-06-02 23:30 | 429.4 | 81 | 2059 | Y | 101 | 105 | 94 | 11 |  | 0.1 | 2.4 | 97.4 |  |  |  |  | 1 | 0.3 | 0.3 |  | 525.25 | 478.09 | 613.45 | 536.31 | 156.3 | 180.14 | 77.04 | 151.18 | 10.24 | 34.26 | 1 | 5.3 | 693.19 | 26.41 | 0.57 | 1.22
43 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE036 | 1S-DL-YP-ETC-DVSE-2351-VSE036 | SUBJI MANDI HARIJAN BASTI KNODLI:K | TG-VSE036A-2 | 19505314 | 990 | 320 | 241 | 0.97 | 1378 | 402 | 1720 | 473 | 2042 | 503 | 2176 | 406 | 2019-06-09 00:30 | 377.9 | 75.2 | 2176 | B | 100 | 96 | 103 | 7 | 0.1 | 0.2 | 24.3 | 75.4 |  |  |  |  | 24.04 | 6 | 6 | 12.04 | 439.59 | 515.58 | 447.23 | 470.4 | 158.51 | 123.56 | 157.2 | 151.4 | 36.17 | 13.17 | 41.36 | 24.47 | 659.11 | 60.49 | 0.5 | 1.39
44 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE037 | 1S-DL-YP-ETC-DVSE-2351-VSE037 | KNODLI VILL. PANCHYAT GHAR:PL | TG-VSE037A-1 | 19502838 | 990 | 320 | 235 | 0.98 | 794 | 199 | 859 | 357 | 1550 | 238 | 1010 | 630 | 2019-06-29 22:30 | 134 | 30.2 | 1572 | Y | 78 | 131 | 91 | 53 |  | 1.4 | 96.8 | 1.8 |  |  |  |  | 290.06 | 4.3 | 4.3 | 43.55 | 427 | 484.58 | 635.41 | 672.41 |  | 220.52 |  | 0.3 |  | 6.46 |  |  | 717.06 | 2.54 | 0.69 | 0.8
45 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE038 | 1S-DL-YP-ETC-DVSE-2351-VSE038 | KNODLI VILL. NEAR PR/SCHOOL:PL | TG-VSE038A-1 | 19505907 | 630 | 200 | 243 | 0.98 | 516 | 137 | 605 | 180 | 809 | 198 | 884 | 250 | 2019-06-02 23:30 | 158.2 | 16.2 | 884 | B | 86 | 104 | 110 | 24 | 0.1 | 0.3 | 12.2 | 87.4 | 0.3 | 0.3 |  |  | 347.26 | 112 | 112 | 154.3 | 345.47 | 580.13 | 591.43 | 538.43 |  | 1 | 2.3 | 0.3 |  |  |  |  | 693.43 | 26.17 | 0.59 | 0.82
46 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE038 | 1S-DL-YP-ETC-DVSE-2351-VSE038 | KNODLI VILL. NEAR PR/SCHOOL:PL | TG-VSE038A-2 | 19506428 | 630 | 200 | 243 | 0.98 | 781 | 273 | 1186 | 266 | 1179 | 242 | 1066 | 117 | 2019-06-27 20:30 | 186.6 | 21.6 | 1186 | R | 110 | 65 | 125 | 60 | 0.1 | 0.6 | 58 | 41.4 |  | 7.3 |  |  | 50 | 675.39 | 675.39 | 116.3 | 666.25 | 32.46 | 702.26 | 599.55 |  | 0.3 | 4.29 |  | 0.28 | 0.28 | 0.28 | 0.28 | 716.53 | 3.07 | 0.39 | 1.24
47 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE039 | 1S-DL-YP-ETC-DVSE-2351-VSE039 | KNODLI INDAL PUBLIC SCHOOL:PM | TG-VSE039A-1 | 19506640 | 400 | 120 | 250 | 0.97 | 433 | 152 | 632 | 163 | 676 | 118 | 483 | 175 | 2019-06-30 22:30 | 110.6 | 29 | 753 | Y | 99 | 112 | 90 | 22 | 1.2 | 7.5 | 42.6 | 48.7 | [8 empty] | 427.2 | 208.51 | 508.31 | 392.5 | 210.38 | 390.37 | 172.27 | 289.38 | 56.3 | 95 | 7.3 | 12 | 694.28 | 25.32 | 0.72 | 1.08
48 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE040 | 1S-DL-YP-ETC-DVSE-2351-VSE040 | D-BLK HARIJAN BASTI S. HOSP.:PL | TG-VSE040A-1 | 19504566 | 990 | 320 | 244 | 0.98 | 700 | 225 | 950 | 227 | 971 | 248 | 1047 | 88 | 2019-06-28 22:30 | 143.5 | 41.2 | 1065 | B | 93 | 103 | 104 | 11 |  | 8.4 | 58.5 | 33.1 |  |  |  |  | 96.33 | 32.3 | 32.3 | 39.05 | 619.36 | 683.39 | 659.15 | 677.04 | [8 empty] | 716.09 | 3.51 | 0.74 | 0.71
49 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE041 | 1S-DL-YP-ETC-DVSE-2351-VSE041 | A-BLK RAJBIR COLONY:PL | TG-VSE041A-1 | 19506206 | 990 | 320 | 238 | 0.97 | 405 | 136 | 601 | 111 | 485 | 158 | 698 | 185 | 2019-06-08 20:30 | 138.9 | 25.3 | 698 | B | 97 | 83 | 121 | 38 |  | 0.1 | 13.8 | 86.1 | 172.3 | 389 | 62 | 160.55 | 546.23 | 329.58 | 329.58 | 557.58 | 0.05 |  | 33.05 | 0.05 | [8 empty] | 718.58 | 1.02 | 0.58 | 0.41
50 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE041 | 1S-DL-YP-ETC-DVSE-2351-VSE041 | A-BLK RAJBIR COLONY:PL | TG-VSE041A-2 | 19505373 | 990 | 320 | 238 | 0.97 | 619 | 204 | 869 | 233 | 993 | 183 | 776 | 188 | 2019-06-29 23:30 | 197.1 | 42.2 | 1073 | Y | 102 | 116 | 82 | 34 |  |  | 1.1 | 98.9 |  |  | 2.3 |  | 241.4 | 85.3 | 85.3 | 253.4 | 464.49 | 620.59 | 202 | 452.49 | [8 empty] | 706.29 | 13.31 | 0.7 | 0.63
51 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE042 | 1S-DL-YP-ETC-DVSE-2351-VSE042 | B-BLK RAJBIR COLONY:PL | TG-VSE042A-1 | 19502732 | 990 | 320 | 234 | 0.98 | 763 | 212 | 912 | 286 | 1256 | 265 | 1160 | 307 | 2019-06-11 23:00 | 161.2 | 40.5 | 1318 | Y | 83 | 112 | 105 | 29 |  | 4.5 | 14.8 | 80.7 | 0.3 |  |  |  | 289.04 | 46.3 | 46.3 | 98.3 | 428.34 | 635.08 | 664.38 | 619.38 |  | 36.3 | 1.3 | [5 empty] | 718.08 | 1.52 | 0.67 | 0.77
52 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE042 | 1S-DL-YP-ETC-DVSE-2351-VSE042 | B-BLK RAJBIR COLONY:PL | TG-VSE042A-2 | 19505311 | 630 | 200 | 247 | 0.97 | 462 | 111 | 451 | 154 | 640 | 197 | 802 | 305 | 2019-06-09 | 156 | 30.8 | 802 | B | 87 | 101 | 112 | 25 | 0.1 | 0.2 | 25.6 | 74.1 | 0.3 |  |  |  | 561.07 | 342.35 | 342.35 | 351.35 | 156.32 | 375.34 | 532.09 | 366.34 |  |  | 0.3 | [5 empty] | 718.09 | 1.51 | 0.55 | 0.73
53 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE045 | 1S-DL-YP-ETC-DVSE-2351-VSE045 | GHARAOLI VILL. OLD:PL | TG-VSE045A-1 | 19502849 | 630 | 200 | 239 | 0.98 | 504 | 175 | 731 | 151 | 624 | 177 | 724 | 104 | 2019-06-13 23:00 | 99.8 | 28.5 | 809 | R | 101 | 97 | 102 | 5 |  | 3.6 | 8.9 | 87.5 |  |  |  |  | 75.42 | 26 | 26 | 30.42 | 608.39 | 689.21 | 687.21 | 685.39 | 32 | 1 | 5.3 | [5 empty] | 716.21 | 3.39 | 0.72 | 0.8
54 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE046 | 1S-DL-YP-ETC-DVSE-2351-VSE046 | GHARAOLI VILL. NEW:PL | TG-VSE046A-1 | 19502842 | 990 | 320 | 239 | 0.98 | 785 | 270 | 1108 | 241 | 998 | 274 | 1146 | 133 | 2019-06-13 23:00 | 138.4 | 39.7 | 1206 | R | 104 | 95 | 102 | 9 |  | 0.1 | 34.3 | 65.5 |  |  |  |  | 8.41 | 39.08 | 39.08 | 18.41 | 704.17 | 678.49 | 692.46 | 699.16 | 4.59 |  | 3.3 | [5 empty] | 717.57 | 2.03 | 0.73 | 0.79
55 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE140 | 1S-DL-YP-ETC-DVSE-2351-VSE140 | 480 EWS QTRS GHAROLI | TG-VSE140A-1 | 19504688 | 630 | 200 | 238 | 0.94 | 85 | 44 | 185 | 29 | 121 | 13 | 53 | 114 | 2019-06-01 22:00 | 37.3 | 3.2 | 201 | R | 149 | 102 | 49 | 100 |  |  | 7.9 | 92.1 | 707.15 | 716.45 | 716.45 | 716.45 | 9.3 | [15 empty] | 716.45 | 3.15 | 0.61 | 0.13
56 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE140 | 1S-DL-YP-ETC-DVSE-2351-VSE140 | 480 EWS QTRS GHAROLI | TG-VSE140A-2 | 19504733 | 630 | 200 | 243 | 0.97 | 221 | 53 | 227 | 84 | 364 | 83 | 362 | 136 | 2019-06-30 23:30 | 40.5 | 9.7 | 375 | B | 74 | 109 | 117 | 43 |  |  | 0.6 | 99.4 | 615.31 | 390.41 | 338.52 | 462.34 | 101.14 | 324.34 | 324.34 | 254.11 |  | 1.3 | 0.47 | [9 empty] | 716.45 | 3.15 | 0.53 | 0.35
57 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE142 | 1S-DL-YP-ETC-DVSE-2351-VSE142 | STN 3 GHAROLI DAIRY CL MVR PH-3:ID | TG-VSE142A-1 | 19504841 | 990 | 320 | 239 | 0.98 | 1052 | 333 | 1416 | 334 | 1440 | 385 | 1680 | 253 | 2019-06-30 23:30 | 167.1 | 53 | 1680 | B | 98 | 94 | 109 | 15 | 23.6 | 75.8 | 0.6 | [5 empty] | 14.27 | 35.27 | 35.27 | 16.27 | 557.03 | 580.03 | 511.1 | 554.14 | 139.41 | 101.11 | 162.04 | 139.3 | 6.3 | 1 | 36.3 | 7.3 | 717.41 | 2.19 | 0.62 | 1.06
58 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE142 | 1S-DL-YP-ETC-DVSE-2351-VSE142 | STN 3 GHAROLI DAIRY CL MVR PH-3:ID | TG-VSE142A-2 | 19502831 | 630 | 200 | 244 | 0.98 | 522 | 189 | 764 | 158 | 636 | 175 | 713 | 111 | 2019-06-11 23:30 | 89.7 | 34 | 805 | R | 112 | 87 | 102 | 25 |  | 0.2 | 80.8 | 19 |  |  |  |  | 11.3 | 133 | 133 | 36 | 660.24 | 586.54 | 657.54 | 676.54 | 48 |  | 16.3 | 7 |  |  |  |  | 719.54 | 0.06 | 0.68 | 0.83
59 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE143 | 1S-DL-YP-ETC-DVSE-2351-VSE143 | STN 4 GHAROLI DAIRY CL MVR PH-3:ID | TG-VSE143A-1 | 19503159 | 990 | 320 | 243 | 0.97 | 1001 | 425 | 1830 | 273 | 1147 | 303 | 1298 | 621 | 2019-06-02 23:00 | 189.9 | 60.4 | 1830 | R | 102 | 96 | 101 | 6 |  | 0.1 | 29.5 | 70.4 |  |  |  |  | 51.15 | 13.54 | 13.54 | 24.56 | 535.14 | 675.05 | 605.03 | 607.33 | 85 | 25.55 | 85.55 | 81.25 | 43.25 |  | 0.3 | 1 | 714.54 | 5.06 | 0.61 | 1.01
60 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE143 | 1S-DL-YP-ETC-DVSE-2351-VSE143 | STN 4 GHAROLI DAIRY CL MVR PH-3:ID | TG-VSE143A-2 | 19502843 | 630 | 200 | 236 | 0.98 | 666 | 231 | 1013 | 213 | 934 | 222 | 974 | 68 | 2019-06-30 23:00 | 98.4 | 28.1 | 1049 | R | 107 | 96 | 97 | 11 |  |  | 18.7 | 81.3 |  |  |  |  | 28.3 | 93.17 | 93.17 | 73.3 | 557.14 | 532.32 | 484.03 | 538.49 | 103.01 | 86.56 | 96.55 | 94.56 | 26 | 2 | 6.3 | 7.3 | 714.45 | 5.15 | 0.57 | 1.06
61 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE144 | 1S-DL-YP-ETC-DVSE-2351-VSE144 | STN 1 480 MIG MVR PH-3:ID | TG-VSE144A-1 | 19502432 | 630 | 200 | 238 | 0.98 | 228 | 68 | 299 | 90 | 397 | 70 | 310 | 93 | 2019-06-30 23:30 | 30.4 | 5.5 | 397 | Y | 91 | 117 | 92 | 26 |  |  | 4.4 | 95.6 | 577.3 | 479.29 | 606 | 549 | 140.24 | 238.08 | 238.08 | 168.54 |  | 0.17 | [10 empty] | 717.54 | 2.06 | 0.42 | 0.36
62 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE144 | 1S-DL-YP-ETC-DVSE-2351-VSE144 | STN 1 480 MIG MVR PH-3:ID | TG-VSE144A-2 | 19502379 | 630 | 200 | 238 | 0.98 | 196 | 55 | 243 | 78 | 345 | 62 | 273 | 91 | 2019-06-30 23:30 | 31.7 | 4.6 | 345 | Y | 82 | 124 | 94 | 42 |  |  | 3.2 | 96.8 | 676.09 | 493.17 | 627.17 | 596.47 | 41.25 | 224.17 | 224.17 | 120.47 | [12 empty] | 717.34 | 2.26 | 0.46 | 0.31
63 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE145 | 1S-DL-YP-ETC-DVSE-2351-VSE145 | STN 2 480 MIG MVR PH-3:ID | TG-VSE145A-1 | 19502383 | 630 | 200 | 244 | 0.97 | 184 | 66 | 275 | 50 | 207 | 68 | 284 | 72 | 2019-06-29 23:00 | 32.7 | 5.1 | 297 | B | 103 | 84 | 112 | 28 |  |  | 4.5 | 95.5 | 559.59 | 668.29 | 488.29 | 575.29 | 160 | 51.3 | 51.3 | 144.3 | [12 empty] | 719.59 | 0.01 | 0.5 | 0.29
64 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE145 | 1S-DL-YP-ETC-DVSE-2351-VSE145 | STN 2 480 MIG MVR PH-3:ID | TG-VSE145A-2 | 19502051 | 630 | 200 | 244 | 0.98 | 195 | 62 | 280 | 90 | 400 | 44 | 196 | 178 | 2019-06-10 23:00 | 33.6 | 6 | 400 | Y | 103 | 131 | 66 | 65 |  |  | 59.6 | 40.4 | 545.59 | 444.29 | 711.59 | 563.59 | 174 | 263 | 263 | 156 |  | 12.3 | [10 empty] | 719.59 | 0.01 | 0.47 | 0.31
65 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE149 | 1S-DL-YP-ETC-DVSE-2351-VSE149 | FLOOD CONTROL S/STN KONDLI BRIDGE:PM | TG-VSE149A-1 | 19506429 | 100 | 40 | 243 | 0.91 | 166 | 39 | 165 | 63 | 282 | 64 | 282 | 117 | 2019-06-30 09:00 | 122.3 | -1.9 | 282 | B | 65 | 77 | 158 | 93 | 60.9 | 20.2 | 13.6 | 5.4 | 650.18 | 645.48 | 634.18 | 646.48 | 20.3 | 24 | 24 | 23 | 12.3 | 13.3 | 15.3 | 13 | 2 | 2 | 2 | 2 | 15 | 15 | 15.3 | 15.3 | 718.15 | 1.45 | 0.06 | 1.66
66 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE156 | 1S-DL-YP-ETC-DVSE-2351-VSE156 | S/S 6 SFS FLAT MVR PH-3 VASUNDH ENCL:ID | TG-VSE156A-1 | 19502380 | 630 | 200 | 242 | 0.98 | 188 | 79 | 335 | 59 | 260 | 50 | 215 | 105 | 2019-06-30 23:30 | 41.4 | 4.6 | 335 | R | 113 | 90 | 97 | 23 | 5.1 | 7.9 | 7.1 | 79.8 | 482.11 | 586.41 | 551.41 | 545.11 | 237.3 | 133 | 133 | 174.3 | [12 empty] | 719.41 | 0.19 | 0.54 | 0.3
67 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE157 | 1S-DL-YP-ETC-DVSE-2351-VSE157 | S/S-1 C-BLK HARIZAN BASTI,MULLA CLY:PL | TG-VSE157A-1 | 19506535 | 990 | 320 | 242.1532 | 0.96634 | 877.7226 | 270.2477 | 1083.635 | 284.2234 | 1142.1934 | 323.2515 | 1288.4192 | 182.685 | 2019-06-11 06:30 | [15 empty] | 0 |  |  |  | 11.5 |  |  |  | 706.5 |  |  |  | 1 |  |  |  | 0 | 719 |  | 0.60202 | 0.88659
68 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE158 | 1S-DL-YP-ETC-DVSE-2351-VSE158 | S/STN-2 A1 PKT MVR-III:I/D | TG-VSE158A-1 | 19506224 | 630 | 200 | 248 | 0.96 | 476 | 167 | 705 | 123 | 512 | 186 | 778 | 238 | 2019-06-30 23:00 | 108.6 | 19 | 841 | B | 111 | 79 | 110 | 32 |  | 1 | 42 | 57 | 16.3 | 298.59 | 38 | 54.3 | 399.29 | 217.22 | 217.22 | 406.35 | 300.26 | 201.34 | 286.07 | 256.5 | 1.3 |  | 6 | [5 empty] | 717.55 | 2.05 | 0.48 | 0.75
69 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE163 | 1S-DL-YP-ETC-DVSE-2351-VSE163 | S/S-2 C-BLK HARIZAN BASTI,MULLA CLY:PL | TG-VSE163A-1 | 19506207 | 630 | 200 | 240 | 0.97 | 719 | 250 | 1121 | 232 | 1049 | 238 | 1067 | 65 | 2019-06-02 23:30 | 241.6 | 57.8 | 1121 | R | 115 | 90 | 95 | 25 | 0.2 | 0.4 | 20.5 | 78.9 |  | 62 |  |  |  | 0.3 | 0.3 |  | 280.33 | 457.22 | 545.22 | 476.22 | 312.49 | 172.59 | 148.29 | 215.29 | 101.59 | 2.3 | 1 | 3.3 | 695.21 | 24.39 | 0.64 | 1.14
70 | 2019-06-08 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE176 | 1S-DL-YP-ETC-DVSE-2351-VSE176 | S/STN NO-1 IFC PAPER MARKET MVR III | TG-VSE176A-2 | 19505813 | 400 | 120 | 248 | 0.94 | 114 | 59 | 250 | 25 | 108 | 30 | 127 | 133 | 2019-06-22 15:00 | 29.6 | -9.8 | 250 | R | 152 | 26 | 122 | 126 |  | 1.9 | 34.9 | 63.2 | 547.45 | 551.45 | 548.45 | 550.15 | 3.3 |  |  | 1.3 | 0.3 | [11 empty] | 551.45 | 0.15 | 0.18 | 0.29
71 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE182 | 1S-DL-YP-ETC-DVSE-2351-VSE182 | CNG STN-1 (NAHAR) IFC PAPER MKT GAJIPUR. | TG-VSE182A-1 | 19506210 | 990 | 320 | 246 | 0.68 | 514 | 168 | 700 | 175 | 734 | 170 | 714 | 29 | 2019-06-05 13:30 | 495 | -139.2 | 734 | Y | 97 | 102 | 101 | 5 |  |  | 21.7 | 78.3 | 541.03 | 535.33 | 538.03 | 539.33 | 89 | 5.3 | 5.3 | 6.3 | 64.57 | 153.57 | 147.57 | 148.57 | [8 empty] | 695 | 25 | 0.41 | 0.52
72 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE183 | 1S-DL-YP-ETC-DVSE-2351-VSE183 | SS-2 IFC PAPER MKT GAJIPUR MV-3 | TG-VSE183A-1 | 19506764 | 400 | 120 | 247 | 0.95 | 52 | 1 | 3 | 1 | 5 | 51 | 214 | 210 | 2019-06-25 10:30 | 25.3 | 1.3 | 214 | B | 6 | 13 | 281 | 275 |  | 0.1 | 3.7 | 96.3 | 708.16 | 708.16 | 613.48 | 708.16 | [16 empty] | 708.16 | 11.44 | 0.44 | 0.13
73 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE184 | 1S-DL-YP-ETC-DVSE-2351-VSE184 | SS-5 IFC PAPER MKT GAJIPUR MV-3 | TG-VSE184A-1 | 19505528 | 400 | 120 | 246 | 0.96 | 113 | 30 | 125 | 50 | 205 | 33 | 135 | 75 | 2019-06-14 15:00 | 48.8 | 6.2 | 238 | Y | 82 | 136 | 82 | 54 |  | 1.3 | 48.9 | 49.8 | 693.04 | 100.3 | 673.4 | 480.38 | 25.29 | 614.33 | 614.33 | 237.55 |  | 3.3 | [10 empty] | 718.33 | 1.27 | 0.67 | 0.28
74 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE185 | 1S-DL-YP-ETC-DVSE-2351-VSE185 | SS-6 IFC PAPER MKT GAJIPUR MV-3 | TG-VSE185A-1 | 19505916 | 630 | 200 | 247 | 0.91 | 17 | 17 | 69 | 0 | 0 | 0 | 0 | 69 | 2019-06-12 16:30 | 11.6 | -4.6 | 69 | R | 252 | 13 | 36 | 239 |  | 0.6 | 16.3 | 83.1 | 708.44 | 708.44 | 708.44 | 708.44 | [16 empty] | 708.44 | 11.16 | 0.18 | 0.03
75 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE186 | 1S-DL-YP-ETC-DVSE-2351-VSE186 | SS-7 IFC PAPER MKT GAJIPUR MV-3 | TG-VSE186A-1 | 19506714 | 400 | 120 | 245 | 0.81 | 63 | 34 | 133 | 27 | 106 | 2 | 9 | 113 | 2019-06-14 19:00 | 55.4 | -0.2 | 140 | R | 150 | 108 | 42 | 108 | 33.3 | 4.7 | 18.5 | 43.5 | 697.35 | 716.05 | 719.05 | 719.05 | 21.3 | 3 | 3 | [13 empty] | 719.05 | 0.55 | 0.38 | 0.16
76 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE187 | 1S-DL-YP-ETC-DVSE-2351-VSE187 | SS-8 IFC PAPER MKT GAJIPUR MV-3 | TG-VSE187A-2 | 19505538 | 630 | 200 | 247 | 0.88 | 44 | 3 | 13 | 3 | 12 | 38 | 153 | 140 | 2019-06-04 14:00 | 10.8 | -3.6 | 153 | B | 56 | 32 | 212 | 180 |  | 0.8 | 20.6 | 78.7 | 719.34 | 719.34 | 719.34 | 719.34 | [16 empty] | 719.34 | 0.26 | 0.32 | 0.07
77 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE188 | 1S-DL-YP-ETC-DVSE-2351-VSE188 | SS-9 IFC PAPER MKT GAJIPUR MV-3 | TG-VSE188A-1 | 19504939 | 400 | 120 | 247 | 0.82 | 80 | 26 | 104 | 25 | 100 | 30 | 120 | 18 | 2019-06-07 19:00 | 69.3 | -0.3 | 140 | R | 95 | 88 | 117 | 29 |  |  | 2.9 | 97.1 | 714.45 | 717.15 | 715.15 | 719.15 | 5 | 2.3 | 2.3 | 0.3 | [12 empty] | 719.45 | 0.15 | 0.33 | 0.2
78 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE189 | 1S-DL-YP-ETC-DVSE-2351-VSE189 | SS-10 IFC PAPER MKT GAJIPUR MV-3 | TG-VSE189A-1 | 19504829 | 400 | 120 | 247 | 0.95 | 35 | 12 | 48 | 12 | 48 | 12 | 48 | 1 | 2019-06-24 13:00 | 9.9 | -0.3 | 49 | R | 83 | 104 | 113 | 30 | 2.6 | 0.3 | 4.8 | 92.3 | 716.42 | 716.42 | 716.42 | 716.42 | [16 empty] | 716.42 | 3.18 | 0.11 | 0.09
79 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE190 | 1S-DL-YP-ETC-DVSE-2351-VSE190 | SS-11 IFC PAPER MKT GAJIPUR MV-3 | TG-VSE190A-1 | 19504791 | 400 | 120 | 246 | 0.94 | 67 | 16 | 65 | 29 | 114 | 22 | 86 | 43 | 2019-06-15 17:00 | 28.7 | 0.8 | 114 | Y | 60 | 120 | 120 | 60 |  |  | 40.6 | 59.4 | 719.46 | 719.16 | 719.46 | 719.46 |  | 0.3 | 0.3 | [13 empty] | 719.46 | 0.14 | 0.29 | 0.17
80 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE190 | 1S-DL-YP-ETC-DVSE-2351-VSE190 | SS-11 IFC PAPER MKT GAJIPUR MV-3 | TG-VSE190A-2 | 19506815 | 400 | 120 | 261 | 0.98 | 13 | 0 | 0 | 0 | 0 | 13 | 49 | 49 | 2019-06-24 15:30 | 9.8 | -0.4 | 50 | B | 0 | 0 | 300 | 300 | 0.1 | 0.3 | 8 | 91.7 | 719.46 | 719.46 | 719.46 | 719.46 | [16 empty] | 719.46 | 0.14 | 0.14 | 0.03
81 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE191 | 1S-DL-YP-ETC-DVSE-2351-VSE191 | SS-12 IFC PAPER MKT GAJIPUR MV-3 | TG-VSE191A-1 | 19505668 | 400 | 120 | 254 | 0.92 | 49 | 0 | 0 | 49 | 199 | 0 | 0 | 199 | 2019-06-06 13:00 | 19.4 | -0.4 | 199 | Y | 5 | 281 | 14 | 276 | 0.1 | 1.1 | 16.2 | 82.7 | 708.45 | 696.15 | 708.45 | 708.45 |  | 12.3 | 12.3 | [13 empty] | 708.45 | 11.15 | 0.22 | 0.12
82 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE192 | 1S-DL-YP-ETC-DVSE-2351-VSE192 | SS-13 IFC PAPER MKT GAJIPUR MV-3 | TG-VSE192A-1 | 19502846 | 400 | 120 | 247 | 0.93 | 23 | 20 | 86 | 0 | 1 | 2 | 9 | 81 | 2019-06-06 11:00 | 12.1 | -0.8 | 86 | R | 101 | 109 | 89 | 20 |  | 0.1 | 5.1 | 94.8 | 719.45 | 719.45 | 719.45 | 719.45 | [16 empty] | 719.45 | 0.15 | 0.25 | 0.06
83 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE193 | 1S-DL-YP-ETC-DVSE-2351-VSE193 | SS-14 IFC PAPER MKT GAJIPUR MV-3 | TG-VSE193A-2 | 19500217 | 400 | 120 | 245 | 0.99 | 19 | 15 | 62 | 3 | 12 | 0 | 1 | 56 | 2019-06-11 14:00 | 2.8 | -1.1 | 62 | R | 215 | 79 | 6 | 209 | 31.8 | 13.9 | 53.8 | 0.5 | 719.44 | 719.44 | 719.44 | 719.44 | [16 empty] | 719.44 | 0.16 | 0.26 | 0.05
84 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE203 | 1S-DL-YP-ETC-DVSE-2351-VSE203 | HPC,PETROL PUMP,IFC PAPER MKT.MVR-3 | TG-VSE203A-1 | 19504756 | 100 | 40 | 246 | 0.94 | 15 | 3 | 11 | 3 | 13 | 9 | 36 | 25 | 2019-06-25 19:00 | 5.8 | -0.2 | 36 | B | 77 | 81 | 142 | 65 |  |  | 15.9 | 84.1 | 695.44 | 695.44 | 657.16 | 695.44 | [16 empty] | 695.44 | 0.16 | 0.68 | 0.15
85 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE204 | 1S-DL-YP-ETC-DVSE-2351-VSE204 | DP MULLA COLONY,KIOSK | TG-VSE204A-1 | 19506225 | 400 | 120 | 248 | 0.77 | 12 | 5 | 18 | 4 | 18 | 3 | 11 | 7 | 2019-06-30 04:00 | 2.6 | -0.8 | 20 | R | 117 | 113 | 71 | 46 | 0.2 | 0.2 | 1.5 | 98.1 | 696.16 | 696.16 | 696.16 | 696.16 | [16 empty] | 696.16 | 23.44 | 0.51 | 0.03
86 | 2019-06-01 | 2019-06-14 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE207 | 1S-DL-YP-ETC-DVSE-2351-VSE207 | SSTN-10 A3 PKT LIG MVR-III:ID | TG-VSE207A-1 | 19505499 | 400 | 120 | 247 | 0.97 | 269 | 87 | 367 | 81 | 341 | 101 | 430 | 79 | 2019-06-03 01:00 | 46.4 | 15.4 | 430 | B | 95 | 87 | 118 | 31 |  |  | 4.6 | 95.4 | 25.3 | 87.3 | 6 | 19 | 209 | 149 | 149 | 202.3 | 88.11 | 86.11 | 135.41 | 101.11 | [8 empty] | 322.41 | 13.19 | 0.52 | 0.67
87 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE049 | 1S-DL-YP-ETC-DVSE-2351-VSE049 | S/STN 1 VASHUNDRA ENCLAVE:ID | TG-VSE049A-1 | 19504286 | 400 | 120 | 239 | 0.97 | 97 | 31 | 128 | 37 | 155 | 28 | 116 | 35 | 2019-06-01 11:00 | 26.2 | 0.3 | 158 | Y | 101 | 100 | 99 | 2 |  |  | 7.9 | 92.1 | 687.38 | 663.07 | 711.07 | 710.07 | 30.59 | 55.3 | 55.3 | 8.3 | [12 empty] | 718.37 | 1.23 | 0.44 | 0.24
88 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE052 | 1S-DL-YP-ETC-DVSE-2351-VSE052 | S/STN 4 VASHUNDRA ENCLAVE:ID | TG-VSE052A-1 | 19500981 | 400 | 120 | 235 | 0.99 | 24 | 2 | 8 | 19 | 83 | 3 | 14 | 72 | 2019-06-13 13:00 | 1.9 | -0.3 | 83 | Y | 35 | 235 | 29 | 206 |  | 1 | 60 | 39.1 | 719.26 | 719.26 | 719.26 | 719.26 | [16 empty] | 719.26 | 0.34 | 0.23 | 0.06
89 | 2019-06-04 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE053 | 1S-DL-YP-ETC-DVSE-2351-VSE053 | S/STN 5 VASHUNDRA ENCLAVE:ID | TG-VSE053A-1 | 19502617 | 400 | 120 | 241 | 0.96 | 8 | 0 | 0 | 4 | 17 | 3 | 13 | 16 | 2019-06-24 06:00 | 4.1 | -0.3 | 18 | Y | 0 | 142 | 158 | 158 |  |  | 11.4 | 88.6 | 646.09 | 646.09 | 646.09 | 646.09 | [16 empty] | 646.09 | 1.51 | 0.22 | 0.02
90 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE058 | 1S-DL-YP-ETC-DVSE-2351-VSE058 | S/S DALLUPURA GRID STREET LIGHT | TG-VSE058A-1 | 19505703 | 100 | 40 | 242 | 0.66 | 29 | 6 | 26 | 10 | 40 | 13 | 52 | 23 | 2019-06-06 18:30 | 26.9 | 0.8 | 52 | B | 51 | 88 | 162 | 111 |  |  | 10 | 90 | 706.4 | 692.14 | 376.45 | 691.14 | 1 | 15.26 | 15.26 | 16.26 | [12 empty] | 707.4 | 12.2 | 0.26 | 0.29
91 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE059 | 1S-DL-YP-ETC-DVSE-2351-VSE059 | GOVIND(DELHI PUNJABI)VASHUNDRA ENCL.:ID | TG-VSE059A-1 | 19500942 | 630 | 200 | 240 | 0.99 | 125 | 49 | 217 | 44 | 196 | 32 | 139 | 70 | 2019-06-29 23:00 | 14.3 | 1.4 | 224 | Y | 98 | 122 | 80 | 42 |  |  | 6.6 | 93.4 | 715.17 | 665.47 | 718.47 | 718.47 | 3.3 | 53 | 53 | [13 empty] | 718.47 | 1.13 | 0.55 | 0.2
92 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE059 | 1S-DL-YP-ETC-DVSE-2351-VSE059 | GOVIND(DELHI PUNJABI)VASHUNDRA ENCL.:ID | TG-VSE059A-2 | 19500941 | 630 | 200 | 235 | 0.98 | 105 | 28 | 120 | 37 | 161 | 40 | 172 | 47 | 2019-06-28 23:00 | 29.9 | 2.8 | 198 | B | 80 | 103 | 117 | 37 |  |  | 5.1 | 94.9 | 718.48 | 718.48 | 714.48 | 718.48 | [16 empty] | 718.48 | 1.12 | 0.58 | 0.17
93 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE060 | 1S-DL-YP-ETC-DVSE-2351-VSE060 | TRIVENI CGHS VASHUNDRA ENCLAVE:ID | TG-VSE060A-1 | 19505558 | 400 | 120 | 236 | 0.98 | 64 | 28 | 120 | 15 | 65 | 21 | 92 | 48 | 2019-06-03 01:00 | 15.2 | 1.4 | 135 | R | 125 | 58 | 117 | 67 | 0.1 | 0.1 | 8 | 91.8 | 702.48 | 708.18 | 706.48 | 708.18 | 5.3 | [15 empty] | 708.18 | 11.42 | 0.47 | 0.16
94 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE060 | 1S-DL-YP-ETC-DVSE-2351-VSE060 | TRIVENI CGHS VASHUNDRA ENCLAVE:ID | TG-VSE060A-2 | 19500954 | 400 | 120 | 241 | 0.99 | 70 | 38 | 164 | 19 | 83 | 14 | 59 | 95 | 2019-06-30 22:00 | 7.5 | -0.3 | 174 | R | 152 | 89 | 59 | 93 |  |  | 39.2 | 60.8 | 661.18 | 718.48 | 718.48 | 718.48 | 57.3 | [15 empty] | 718.48 | 1.12 | 0.46 | 0.18
95 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE061 | 1S-DL-YP-ETC-DVSE-2351-VSE061 | B-4 PARYATEN VIHAR S/STN 1:ID | TG-VSE061A-1 | 19500879 | 630 | 200 | 232.4679 | 0.98599 | 281.0271 | 93.1168 | 413.5399 | 86.4629 | 388.3528 | 101.4475 | 450.5372 | 54.1761 | 2019-06-11 23:30 | [15 empty] | 345 |  |  |  | 356 |  |  |  | 19 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.50663 | 0.44607
96 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE062 | 1S-DL-YP-ETC-DVSE-2351-VSE062 | B-4 PARYATEN VIHAR S/STN 2:ID | TG-VSE062A-1 | 19500876 | 630 | 200 | 231.9461 | 0.98263 | 297.2248 | 108.3024 | 494.6219 | 69.495 | 319.0626 | 119.4274 | 544.8578 | 205.3389 | 2019-06-30 23:30 | [15 empty] | 238 |  |  |  | 422 |  |  |  | 58 |  |  |  | 0 |  |  |  | 0 | 718 |  | 0.53797 | 0.47179
97 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE063 | 1S-DL-YP-ETC-DVSE-2351-VSE063 | DELUX S/STN 1:ID | TG-VSE063A-1 | 19500907 | 630 | 200 | 240 | 0.99 | 125 | 34 | 149 | 50 | 218 | 41 | 180 | 60 | 2019-06-11 23:00 | 10.6 | -4.6 | 218 | Y | 42 | 125 | 133 | 91 |  |  | 14.3 | 85.7 | 719.07 | 691.37 | 710.37 | 719.07 |  | 27.3 | 27.3 | [13 empty] | 719.07 | 0.53 | 0.45 | 0.2
98 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE063 | 1S-DL-YP-ETC-DVSE-2351-VSE063 | DELUX S/STN 1:ID | TG-VSE063A-2 | 19500906 | 630 | 200 | 241 | 0.98 | 106 | 35 | 150 | 36 | 157 | 35 | 148 | 8 | 2019-06-12 | 15.2 | 0.9 | 199 | B | 93 | 105 | 102 | 12 | 1.5 | 10.8 | 75.1 | 12.6 | 718.57 | 718.57 | 717.57 | 718.57 | [16 empty] | 718.57 | 1.03 | 0.49 | 0.17
99 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE064 | 1S-DL-YP-ETC-DVSE-2351-VSE064 | DELUX S/STN 2:ID | TG-VSE064A-1 | 19500965 | 400 | 120 | 240 | 0.97 | 113 | 47 | 200 | 22 | 94 | 44 | 189 | 101 | 2019-06-12 | 24.8 | 3 | 219 | R | 127 | 68 | 105 | 59 |  | 2.5 | 34.4 | 63.1 | 467.38 | 705.37 | 614.38 | 630.08 | 251.29 | 13.3 | 13.3 | 88.59 | [12 empty] | 719.07 | 0.53 | 0.49 | 0.28
100 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE064 | 1S-DL-YP-ETC-DVSE-2351-VSE064 | DELUX S/STN 2:ID | TG-VSE064A-2 | 19506599 | 400 | 120 | 240 | 0.98 | 98 | 42 | 179 | 32 | 137 | 25 | 108 | 62 | 2019-06-26 23:30 | 18.1 | 1.4 | 186 | R | 117 | 94 | 89 | 28 | 8.1 | 42.3 | 47.6 | 2 | 530.34 | 650.34 | 689.04 | 648.34 | 175.3 | 55.3 | 55.3 | 57.3 | [12 empty] | 706.04 | 13.56 | 0.52 | 0.25
101 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE065 | 1S-DL-YP-ETC-DVSE-2351-VSE065 | B-6 PARVATYA VIAHR VASHUNDRA ENCL.:ID | TG-VSE065A-1 | 19500963 | 400 | 120 | 241 | 0.98 | 55 | 21 | 91 | 14 | 60 | 19 | 81 | 27 | 2019-06-15 23:00 | 11.6 | 0.6 | 119 | B | 103 | 78 | 119 | 41 |  |  | 13.9 | 86.1 | 719.21 | 719.21 | 717.21 | 719.21 | [16 empty] | 719.21 | 0.39 | 0.5 | 0.14
102 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE065 | 1S-DL-YP-ETC-DVSE-2351-VSE065 | B-6 PARVATYA VIAHR VASHUNDRA ENCL.:ID | TG-VSE065A-2 | 19500962 | 400 | 120 | 241 | 0.97 | 91 | 37 | 157 | 39 | 169 | 15 | 65 | 99 | 2019-06-11 01:00 | 16.3 | 1.4 | 173 | Y | 126 | 118 | 56 | 70 |  |  | 19.7 | 80.3 | 591.28 | 619.28 | 719.28 | 689.28 | 128 | 100 | 100 | 30 | [12 empty] | 719.28 | 0.32 | 0.45 | 0.23
103 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE066 | 1S-DL-YP-ETC-DVSE-2351-VSE066 | ILA APPARTMENT VASHUNDRA ENCL.:ID | TG-VSE066A-1 | 19500998 | 400 | 120 | 241 | 0.99 | 79 | 0 | 0 | 34 | 145 | 45 | 189 | 171 | 2019-06-14 | 9.7 | 0.3 | 192 | B | 0 | 141 | 159 | 159 |  |  | 9.5 | 90.5 | 719.23 | 580.27 | 503.01 | 719.23 |  | 138.56 | 138.56 | [13 empty] | 719.23 | 0.37 | 0.53 | 0.2
104 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE066 | 1S-DL-YP-ETC-DVSE-2351-VSE066 | ILA APPARTMENT VASHUNDRA ENCL.:ID | TG-VSE066A-2 | 19503084 | 400 | 120 | 241 | 0.98 | 47 | 10 | 45 | 17 | 74 | 20 | 85 | 36 | 2019-06-02 22:30 | 9.1 | 0.8 | 100 | B | 57 | 98 | 145 | 88 |  |  | 6.3 | 93.7 | 719.23 | 719.23 | 719.23 | 719.23 | [16 empty] | 719.23 | 0.37 | 0.48 | 0.12
105 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE067 | 1S-DL-YP-ETC-DVSE-2351-VSE067 | B8 PARYATAN VIHAR:ID | TG-VSE067A-1 | 19500918 | 400 | 120 | 228 | 0.98 | 272 | 86 | 392 | 89 | 403 | 97 | 444 | 47 | 2019-06-30 23:30 | 33.7 | 8.8 | 449 | B | 102 | 97 | 100 | 5 |  |  | 14.3 | 85.7 | 131.38 | 133.11 | 124.15 | 123.18 | 376.23 | 403.16 | 403.16 | 394.43 | 211.25 | 182.59 | 202.55 | 201.25 | [8 empty] | 719.26 | 0.34 | 0.48 | 0.68
106 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE090 | 1S-DL-YP-ETC-DVSE-2351-VSE090 | MOD:ID | TG-VSE090A-1 | 19500372 | 630 | 200 | 240 | 0.97 | 193 | 49 | 206 | 59 | 251 | 86 | 364 | 141 | 2019-06-13 23:00 | 36.8 | 8.3 | 376 | B | 71 | 101 | 128 | 57 |  |  | 16 | 84 | 705.49 | 563.56 | 394.08 | 540.26 | 11.3 | 153.23 | 153.23 | 176.53 |  |  | 4.3 | [9 empty] | 717.19 | 2.41 | 0.52 | 0.31
107 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE090 | 1S-DL-YP-ETC-DVSE-2351-VSE090 | MOD:ID | TG-VSE090A-2 | 19500373 | 630 | 200 | 241 | 0.99 | 165 | 48 | 202 | 55 | 231 | 61 | 255 | 46 | 2019-06-13 23:30 | 19.3 | 3.2 | 301 | B | 91 | 100 | 109 | 18 |  | 0.2 | 31.2 | 68.6 | 659.2 | 647.2 | 582.09 | 635.2 | 58 | 70 | 70 | 82 | [12 empty] | 717.2 | 2.4 | 0.49 | 0.26
108 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE091 | 1S-DL-YP-ETC-DVSE-2351-VSE091 | LEIAH SISTR S/STN 2:ID | TG-VSE091A-1 | 19500964 | 400 | 120 | 240 | 0.96 | 93 | 31 | 136 | 32 | 137 | 30 | 127 | 9 | 2019-06-28 22:30 | 17.9 | 3.3 | 154 | Y | 104 | 110 | 86 | 24 |  |  | 82.2 | 17.8 | 671.58 | 614.02 | 713.58 | 682.28 | 47.3 | 105.26 | 105.26 | 37 | [12 empty] | 719.28 | 0.32 | 0.52 | 0.23
109 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE091 | 1S-DL-YP-ETC-DVSE-2351-VSE091 | LEIAH SISTR S/STN 2:ID | TG-VSE091A-2 | 19500909 | 400 | 120 | 242 | 0.98 | 95 | 36 | 158 | 31 | 135 | 27 | 116 | 36 | 2019-06-30 23:30 | 13.2 | 1.9 | 187 | R | 124 | 98 | 77 | 47 |  | 29.7 | 70.3 |  | 573.26 | 677.56 | 717.26 | 686.26 | 146 | 41.3 | 41.3 | 33 | [12 empty] | 719.26 | 0.34 | 0.47 | 0.24
110 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE092 | 1S-DL-YP-ETC-DVSE-2351-VSE092 | LEIAH SISTR S/STN 1:ID | TG-VSE092A-1 | 19500908 | 630 | 200 | 241 | 0.97 | 98 | 39 | 165 | 32 | 136 | 27 | 115 | 43 | 2019-06-10 01:00 | 18.9 | 2.3 | 181 | R | 120 | 96 | 84 | 36 |  |  | 32.5 | 67.5 | 717.27 | 719.27 | 719.27 | 719.27 | 2 | [15 empty] | 719.27 | 0.33 | 0.5 | 0.15
111 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE092 | 1S-DL-YP-ETC-DVSE-2351-VSE092 | LEIAH SISTR S/STN 1:ID | TG-VSE092A-2 | 19500910 | 630 | 200 | 241 | 0.98 | 136 | 44 | 192 | 48 | 212 | 43 | 188 | 22 | 2019-06-11 23:00 | 16.6 | 2.3 | 212 | Y | 93 | 112 | 95 | 19 |  |  | 48.4 | 51.6 | 717.27 | 704.27 | 712.27 | 717.57 | 2 | 15 | 15 | 1.3 | [12 empty] | 719.27 | 0.33 | 0.45 | 0.22
112 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE093 | 1S-DL-YP-ETC-DVSE-2351-VSE093 | CEL:ID | TG-VSE093A-1 | 19500895 | 400 | 120 | 240 | 0.97 | 187 | 83 | 356 | 48 | 204 | 56 | 238 | 137 | 2019-06-12 01:00 | 39.2 | 8.8 | 359 | R | 117 | 78 | 105 | 39 |  |  | 26.3 | 73.7 | 137.1 | 355.51 | 129.1 | 184.4 | 406.07 | 359.26 | 359.26 | 478.07 | 173.3 | 1.3 | 56 | 54 | [8 empty] | 716.47 | 3.13 | 0.57 | 0.47
113 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE094 | 1S-DL-YP-ETC-DVSE-2351-VSE094 | SAMARAT S/ST 1:ID | TG-VSE094A-1 | 19500999 | 630 | 200 | 234 | 0.98 | 214 | 73 | 326 | 77 | 343 | 65 | 286 | 51 | 2019-06-30 23:30 | 37.7 | 7.8 | 393 | Y | 107 | 105 | 88 | 19 |  |  | 21 | 79 | 373.01 | 402.01 | 526.27 | 435.31 | 346.21 | 314.21 | 314.21 | 283.51 |  | 3 | [10 empty] | 719.22 | 0.38 | 0.57 | 0.34
114 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE095 | 1S-DL-YP-ETC-DVSE-2351-VSE095 | SAMARAT S/STN 2:ID | TG-VSE095A-1 | 19500990 | 630 | 200 | 234 | 0.98 | 179 | 73 | 329 | 44 | 196 | 61 | 270 | 116 | 2019-06-11 23:00 | 20.7 | 4.6 | 329 | R | 117 | 74 | 109 | 43 |  |  | 48.3 | 51.7 | 514.57 | 713.26 | 546.57 | 598.56 | 204.29 | 6 | 6 | 120.3 | [12 empty] | 719.26 | 0.34 | 0.5 | 0.28
115 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE096 | 1S-DL-YP-ETC-DVSE-2351-VSE096 | ANUPAM:ID | TG-VSE096A-1 | 19500992 | 630 | 200 | 241 | 0.84 | 94 | 27 | 116 | 40 | 166 | 27 | 112 | 52 | 2019-06-02 01:00 | 72.2 | -2.8 | 166 | Y | 90 | 104 | 107 | 17 |  |  | 52.9 | 47.1 | 719.26 | 719.26 | 719.26 | 719.26 | [16 empty] | 719.26 | 0.34 | 0.57 | 0.15
116 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE096 | 1S-DL-YP-ETC-DVSE-2351-VSE096 | ANUPAM:ID | TG-VSE096A-2 | 19506884 | 630 | 200 | 242 | 0.98 | 106 | 52 | 227 | 26 | 115 | 27 | 116 | 111 | 2019-06-26 23:00 | 24.4 | 2.4 | 293 | R | 144 | 76 | 80 | 68 | 0.2 | 0.1 | 11.9 | 87.8 | 675.27 | 711.27 | 711.27 | 711.27 | 36 | [15 empty] | 711.27 | 8.33 | 0.54 | 0.17
117 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE097 | 1S-DL-YP-ETC-DVSE-2351-VSE097 | ABHINAV S/STN 1:ID | TG-VSE097A-1 | 19500997 | 630 | 200 | 241 | 0.98 | 84 | 17 | 75 | 33 | 145 | 34 | 149 | 73 | 2019-06-10 23:00 | 12.4 | 1.4 | 155 | Y | 82 | 114 | 105 | 32 |  |  | 58.3 | 41.7 | 719.26 | 719.26 | 719.26 | 719.26 | [16 empty] | 719.26 | 0.34 | 0.5 | 0.13
118 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE097 | 1S-DL-YP-ETC-DVSE-2351-VSE097 | ABHINAV S/STN 1:ID | TG-VSE097A-2 | 19500980 | 630 | 200 | 231 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [5 empty] | 5.2 | 32.7 | 45.2 | 16.8 | 695.44 | 695.44 | 695.44 | 695.44 | [16 empty] | 719.07 | 0.53 |  | 0
119 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE098 | 1S-DL-YP-ETC-DVSE-2351-VSE098 | ABHINAV S/STN 2:ID | TG-VSE098A-1 | 19502934 | 630 | 200 | 241 | 0.99 | 29 | 8 | 37 | 7 | 33 | 13 | 59 | 24 | 2019-06-10 23:30 | 3.2 | -0.5 | 65 | B | 90 | 75 | 135 | 60 |  |  | 7.2 | 92.8 | 719.27 | 719.27 | 719.27 | 719.27 | [16 empty] | 719.27 | 0.33 | 0.49 | 0.05
120 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE098 | 1S-DL-YP-ETC-DVSE-2351-VSE098 | ABHINAV S/STN 2:ID | TG-VSE098A-2 | 19500991 | 630 | 200 | 241 | 0.98 | 128 | 35 | 152 | 48 | 207 | 45 | 193 | 50 | 2019-06-30 23:00 | 17 | 1.4 | 215 | Y | 85 | 109 | 106 | 24 |  |  | 34.9 | 65.1 | 719.27 | 705.57 | 708.27 | 718.57 |  | 13.3 | 13.3 | 0.3 | [12 empty] | 719.27 | 0.33 | 0.48 | 0.2
121 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE100 | 1S-DL-YP-ETC-DVSE-2351-VSE100 | OVERSEES:ID | TG-VSE100A-1 | 19502019 | 400 | 120 | 241 | 0.98 | 137 | 47 | 202 | 60 | 260 | 31 | 131 | 111 | 2019-06-30 23:30 | 20.1 | 3.9 | 260 | Y | 100 | 119 | 80 | 39 |  |  | 51.2 | 48.8 | 445.57 | 339.31 | 589.27 | 472.01 | 273.3 | 372.26 | 372.26 | 247.26 |  | 7.3 | [10 empty] | 719.27 | 0.33 | 0.53 | 0.34
122 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE103 | 1S-DL-YP-ETC-DVSE-2351-VSE103 | ABLK NEW ASHOK NAGAR:ID | TG-VSE103A-1 | 19500836 | 990 | 320 | 235.5021 | 0.98958 | 1020.3621 | 341.4279 | 1514.7642 | 311.9477 | 1378.3478 | 366.9866 | 1631.4866 | 219.4457 | 2019-06-30 23:30 | [15 empty] | 0 |  |  |  | 7 |  |  |  | 528 |  |  |  | 182.5 |  |  |  | 2.5 | 720 |  | 0.67348 | 1.0307
123 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE103 | 1S-DL-YP-ETC-DVSE-2351-VSE103 | ABLK NEW ASHOK NAGAR:ID | TG-VSE103A-2 | 19500873 | 630 | 200 | 231.9042 | 0.99176 | 506.9606 | 154.4813 | 704.7824 | 191.0069 | 876.9429 | 161.4724 | 730.5454 | 160.8341 | 2019-06-02 22:30 | [15 empty] | 0 |  |  |  | 15 |  |  |  | 703.5 |  |  |  | 1.5 |  |  |  | 0 | 720 |  | 0.72468 | 0.8047
124 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE104 | 1S-DL-YP-ETC-DVSE-2351-VSE104 | ABLK (LOOP) NEW ASHOK NAGAR:ID | TG-VSE104A-1 | 19505992 | 990 | 320 | 237 | 0.98 | 1143 | 361 | 1633 | 395 | 1757 | 387 | 1730 | 113 | 2019-06-26 22:30 | 274.6 | 64.3 | 1769 | Y | 97 | 102 | 101 | 5 | 1.7 | 3.2 | 67.9 | 27.2 | [8 empty] | 400.52 | 306.52 | 326.25 | 353.52 | 242.32 | 315.5 | 304.47 | 281.2 | 52.37 | 73.19 | 64.49 | 60.49 | 696.01 | 23.59 | 0.7 | 1.15
125 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE104 | 1S-DL-YP-ETC-DVSE-2351-VSE104 | ABLK (LOOP) NEW ASHOK NAGAR:ID | TG-VSE104A-2 | 19505532 | 990 | 320 | 232 | 0.98 | 650 | 236 | 1077 | 209 | 945 | 204 | 932 | 139 | 2019-06-26 22:30 | 160.6 | 31.7 | 1077 | R | 105 | 99 | 96 | 9 | 0.1 | 0.3 | 28.8 | 70.9 |  |  |  |  | 175.56 | 188.56 | 188.56 | 218.53 | 542.41 | 529.41 | 449.45 | 499.44 | [8 empty] | 718.37 | 1.23 | 0.69 | 0.66
126 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE105 | 1S-DL-YP-ETC-DVSE-2351-VSE105 | B BLK NEW ASHOK NAGAR:ID | TG-VSE105A-1 | 19506128 | 990 | 320 | 232 | 0.99 | 948 | 289 | 1315 | 375 | 1707 | 284 | 1288 | 406 | 2019-06-09 23:30 | 214.1 | 44.8 | 1707 | Y | 94 | 109 | 97 | 15 | 0.1 | 0.1 | 15.2 | 84.6 | 0.27 |  |  |  | 35.57 | 1.3 | 1.3 | 10 | 677.14 | 689.53 | 697.17 | 699.47 | 4.3 | 20.45 | 8.51 | 8.21 |  | 6 |  |  | 718.08 | 1.52 | 0.61 | 0.96
127 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE105 | 1S-DL-YP-ETC-DVSE-2351-VSE105 | B BLK NEW ASHOK NAGAR:ID | TG-VSE105A-2 | 19505427 | 990 | 320 | 232 | 0.98 | 765 | 243 | 1078 | 264 | 1176 | 258 | 1167 | 94 | 2019-06-30 | 161.3 | 44.5 | 1307 | Y | 91 | 111 | 98 | 20 | 0.1 | 2.4 | 47.3 | 50.2 |  |  |  |  | 75.58 | 7.3 | 7.3 | 24.3 | 619.49 | 682.47 | 651.47 | 671.17 |  | 5.3 | [6 empty] | 695.47 | 24.13 | 0.71 | 0.77
128 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE106 | 1S-DL-YP-ETC-DVSE-2351-VSE106 | B1 BLK NEW ASHOK NAGAR:ID | TG-VSE106A-1 | 19500875 | 630 | 200 | 232.3974 | 0.9907 | 403.8376 | 114.2968 | 493.9788 | 139.65 | 609.6122 | 149.8908 | 650.3985 | 140.5378 | 2019-06-13 23:30 | [15 empty] | 0 |  |  |  | 298 |  |  |  | 421.5 |  |  |  | 0 |  |  |  | 0 | 719.5 |  | 0.67033 | 0.64101
129 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE106 | 1S-DL-YP-ETC-DVSE-2351-VSE106 | B1 BLK NEW ASHOK NAGAR:ID | TG-VSE106A-2 | 19505221 | 990 | 320 | 228 | 0.99 | 900 | 266 | 1222 | 310 | 1420 | 323 | 1479 | 233 | 2019-06-30 | 224.6 | 33.6 | 1479 | B | 90 | 104 | 106 | 16 | 0.1 | 0.1 | 10.3 | 89.5 |  |  |  |  | 70.16 | 18.3 | 18.3 | 19.3 | 616.55 | 589.14 | 598.2 | 624.44 | 7.2 | 86.47 | 91.11 | 50.17 |  |  |  |  | 694.31 | 25.29 | 0.67 | 0.91
130 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE107 | 1S-DL-YP-ETC-DVSE-2351-VSE107 | B2 BLK NEW ASHOK NAGAR:ID | TG-VSE107A-1 | 19500797 | 990 | 320 | 231.8136 | 0.98995 | 1222.6722 | 383.9311 | 1699.8631 | 426.4464 | 1913.4313 | 412.2947 | 1871.175 | 195.8887 | 2019-06-30 | [15 empty] | 0 |  |  |  | 0 |  |  |  | 464.5 |  |  |  | 206.5 |  |  |  | 48.5 | 719.5 |  | 0.62085 | 1.235
131 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE107 | 1S-DL-YP-ETC-DVSE-2351-VSE107 | B2 BLK NEW ASHOK NAGAR:ID | TG-VSE107A-2 | 19500303 | 990 | 320 | 236 | 0.98 | 1005 | 336 | 1477 | 292 | 1291 | 377 | 1681 | 338 | 2019-06-30 01:30 | 162.7 | 50.8 | 1681 | B | 106 | 88 | 105 | 18 |  |  | 23.6 | 76.4 |  |  |  |  | 5 | 73.54 | 73.54 | 22.59 | 602.5 | 641.16 | 577.57 | 643.51 | 107.5 | 1.12 | 120.44 | 48.5 | 0.42 |  | 2.12 | 0.42 | 716.22 | 3.38 | 0.6 | 1.01
132 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE108 | 1S-DL-YP-ETC-DVSE-2351-VSE108 | C2 BLK NEW ASHOK NAGAR:ID | TG-VSE108A-1 | 19500837 | 990 | 320 | 238.407 | 0.98775 | 846.8837 | 338.9342 | 1475.102 | 261.9922 | 1142.5242 | 245.9573 | 1065.119 | 377.2835 | 2019-06-01 | [15 empty] | 0 |  |  |  | 189.5 |  |  |  | 529 |  |  |  | 1.5 |  |  |  | 0 | 720 |  | 0.54004 | 0.85544
133 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE108 | 1S-DL-YP-ETC-DVSE-2351-VSE108 | C2 BLK NEW ASHOK NAGAR:ID | TG-VSE108A-2 | 19506902 | 630 | 200 | 238 | 0.99 | 708 | 234 | 1037 | 222 | 968 | 252 | 1101 | 115 | 2019-06-29 23:30 | 173.2 | 32 | 1180 | B | 99 | 92 | 109 | 17 | 0.1 | 0.1 | 23.4 | 76.4 |  |  |  |  | 14.25 | 18.3 | 18.3 | 6 | 493.31 | 539.26 | 419.31 | 498.26 | 171.44 | 134.44 | 188.25 | 165.44 | 24.48 | 11.48 | 96.32 | 34.18 | 704.28 | 15.32 | 0.63 | 1.12
134 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE109 | 1S-DL-YP-ETC-DVSE-2351-VSE109 | C3 BLK NEW ASHOK NAGAR:ID | TG-VSE109A-1 | 19506026 | 630 | 200 | 239 | 0.98 | 916 | 307 | 1330 | 329 | 1439 | 280 | 1206 | 202 | 2019-06-13 23:00 | 315.6 | 21.4 | 1439 | Y | 96 | 109 | 95 | 14 |  | 0.1 | 19.5 | 80.5 | 0.3 |  | 3 |  | 250.24 | 181.45 | 181.45 | 222.44 | 277.1 | 253.25 | 311.54 | 285.21 | 91.19 | 153.54 | 82.19 | 101.48 | 85.39 | 115.58 | 83.09 | 95.09 | 705.02 | 14.58 | 0.43 | 1.45
135 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE109 | 1S-DL-YP-ETC-DVSE-2351-VSE109 | C3 BLK NEW ASHOK NAGAR:ID | TG-VSE109A-2 | 19506757 | 990 | 320 | 239 | 0.98 | 842 | 284 | 1244 | 233 | 1017 | 325 | 1444 | 370 | 2019-06-29 23:30 | 206.1 | 24.3 | 1444 | B | 105 | 78 | 117 | 39 | 0.1 |  | 36.8 | 63.1 | 55.3 | 306 | 40.07 | 115 | 353.23 | 233.51 | 233.51 | 304.53 | 305.14 | 177.16 | 315.37 | 293.14 | 3 |  | 46 | 4 |  |  |  |  | 717.07 | 2.53 | 0.44 | 0.85
136 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE110 | 1S-DL-YP-ETC-DVSE-2351-VSE110 | C4 BLK NEW ASHOK NAGAR:ID | TG-VSE110A-1 | 19505530 | 630 | 200 | 239 | 0.98 | 728 | 233 | 1013 | 259 | 1141 | 237 | 1032 | 119 | 2019-06-12 | 206.4 | 30.8 | 1169 | Y | 97 | 107 | 97 | 10 | 0.1 | 0.2 | 24.3 | 75.4 |  |  |  |  | 19.16 | 2.19 | 2.19 | 1.49 | 542.07 | 501.4 | 599.39 | 558.09 | 139.3 | 168.45 | 92.15 | 131.45 | 17.5 | 45.59 | 20.3 | 27 | 718.43 | 1.17 | 0.58 | 1.16
137 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE110 | 1S-DL-YP-ETC-DVSE-2351-VSE110 | C4 BLK NEW ASHOK NAGAR:ID | TG-VSE110A-2 | 19505232 | 990 | 320 | 229 | 0.98 | 662 | 161 | 730 | 183 | 820 | 319 | 1453 | 682 | 2019-06-11 01:00 | 188.2 | 27.8 | 1453 | B | 89 | 91 | 121 | 32 |  | 0.4 | 32.2 | 67.4 | 2.3 | 7 | 0.3 | 2 | 456.02 | 435.25 | 435.25 | 338.05 | 236.34 | 252.41 | 432.47 | 355.01 |  |  | 38 | [5 empty] | 695.06 | 24.54 | 0.62 | 0.67
138 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE111 | 1S-DL-YP-ETC-DVSE-2351-VSE111 | C5 BLK NEW ASHOK NAGAR:ID | TG-VSE111A-1 | 19500846 | 990 | 320 | 241.9258 | 0.9831 | 927.2653 | 285.326 | 1230.7024 | 284.4857 | 1215.0237 | 357.4536 | 1543.3427 | 320.7672 | 2019-06-26 23:00 | [15 empty] | 0 |  |  |  | 358 |  |  |  | 335 |  |  |  | 23 |  |  |  | 0 | 716 |  | 0.47207 | 0.93663
139 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE111 | 1S-DL-YP-ETC-DVSE-2351-VSE111 | C5 BLK NEW ASHOK NAGAR:ID | TG-VSE111A-2 | 19500850 | 630 | 200 | 239.0847 | 0.98504 | 688.7085 | 219.9498 | 920.4074 | 231.2776 | 977.2153 | 237.4812 | 1000.5107 | 71.3665 | 2019-06-13 23:30 | [15 empty] | 0 |  |  |  | 48 |  |  |  | 463 |  |  |  | 172 |  |  |  | 36.5 | 719.5 |  | 0.63114 | 1.0932
140 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE112 | 1S-DL-YP-ETC-DVSE-2351-VSE112 | D BLK NEW ASHOK NAGAR:ID | TG-VSE112A-1 | 19506911 | 990 | 320 | 238 | 0.98 | 629 | 200 | 881 | 239 | 1060 | 190 | 846 | 199 | 2019-06-30 23:30 | 161.6 | 40.3 | 1060 | Y | 102 | 109 | 89 | 20 | 0.1 | 1.1 | 39.7 | 59.2 |  |  |  |  | 120 | 113.56 | 113.56 | 213.53 | 585.59 | 592.03 | 325.37 | 492.06 | [8 empty] | 705.59 | 14.01 | 0.71 | 0.64
141 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE112 | 1S-DL-YP-ETC-DVSE-2351-VSE112 | D BLK NEW ASHOK NAGAR:ID | TG-VSE112A-2 | 19505544 | 990 | 320 | 226 | 0.99 | 937 | 283 | 1312 | 353 | 1651 | 301 | 1418 | 301 | 2019-06-30 23:00 | 199.4 | 44.8 | 1665 | Y | 96 | 110 | 94 | 16 | 0.1 | 0.1 | 31.7 | 68.1 |  |  |  |  | 0.3 |  |  |  | 662.16 | 515.32 | 697.22 | 646.56 | 56.36 | 196.2 | 12.3 | 72.26 |  | 7.3 |  |  | 719.22 | 0.38 | 0.68 | 0.95
142 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE113 | 1S-DL-YP-ETC-DVSE-2351-VSE113 | E1 BLK NEW ASHOK NAGAR:ID | TG-VSE113A-1 | 19505322 | 990 | 320 | 244 | 0.98 | 774 | 269 | 1142 | 290 | 1214 | 215 | 901 | 284 | 2019-06-02 23:30 | 190.4 | 52.2 | 1254 | Y | 105 | 99 | 97 | 8 | 0.3 | 6.6 | 56.1 | 37 |  |  |  |  | 19 | 28 | 28 | 17 | 671.25 | 655.55 | 669.25 | 675.55 | 2.3 | 9 | [6 empty] | 692.55 | 27.05 | 0.71 | 0.78
143 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE113 | 1S-DL-YP-ETC-DVSE-2351-VSE113 | E1 BLK NEW ASHOK NAGAR:ID | TG-VSE113A-2 | 19506488 | 630 | 200 | 244 | 0.98 | 365 | 117 | 482 | 115 | 472 | 134 | 554 | 78 | 2019-06-28 23:30 | 89.2 | 20.2 | 561 | B | 103 | 94 | 103 | 9 |  | 0.1 | 12 | 87.9 |  |  | 0.3 |  | 253.46 | 405.44 | 405.44 | 278.46 | 464.28 | 312.3 | 456.28 | 439.28 | [8 empty] | 718.14 | 1.46 | 0.72 | 0.58
144 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE114 | 1S-DL-YP-ETC-DVSE-2351-VSE114 | E2 BLK NEW ASHOK NAGAR:ID | TG-VSE114A-1 | 19505994 | 630 | 200 | 241.804 | 0.98947 | 1034.8665 | 327.6259 | 1390.3664 | 380.7403 | 1656.5451 | 326.5002 | 1425.5784 | 250.4362 | 2019-06-27 21:30 | [15 empty] | 0 |  |  |  | 3.5 |  |  |  | 543 |  |  |  | 158 |  |  |  | 14.5 | 719 |  | 0.42781 | 1.6426
145 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE114 | 1S-DL-YP-ETC-DVSE-2351-VSE114 | E2 BLK NEW ASHOK NAGAR:ID | TG-VSE114A-2 | 19505522 | 400 | 120 | 235 | 0.99 | 513 | 170 | 769 | 181 | 822 | 162 | 733 | 78 | 2019-06-30 23:00 | 115.8 | 19.6 | 909 | Y | 104 | 104 | 92 | 12 | 0.2 | 0.9 | 59 | 39.9 | 0.54 | 1.02 | 0.49 | 0.25 |  |  |  |  | 369.11 | 372.38 | 512.22 | 429.3 | 244.34 | 223.45 | 140.29 | 191.58 | 100.17 | 117.31 | 61.16 | 93.03 | 714.56 | 5.04 | 0.61 | 1.28
146 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE115 | 1S-DL-YP-ETC-DVSE-2351-VSE115 | MCD TUBEWELL BLK NEW ASHOK NAGAR:PM | TG-VSE115A-1 | 19505266 | 400 | 120 | 241 | 0.95 | 119 | 38 | 159 | 52 | 214 | 29 | 120 | 82 | 2019-06-06 22:00 | 52.4 | 1.6 | 214 | Y | 109 | 97 | 94 | 15 |  | 0.2 | 8.1 | 91.6 | 387.5 | 534.45 | 525.44 | 450.49 | 329.54 | 182.59 | 182.59 | 266.55 | [12 empty] | 717.44 | 2.16 | 0.57 | 0.3
147 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE116 | 1S-DL-YP-ETC-DVSE-2351-VSE116 | S/STN . EAST END APTT:ID | TG-VSE116A-1 | 19500783 | 990 | 320 | 234.384 | 0.99183 | 135.2909 | 45.9219 | 203.1134 | 52.3854 | 230.7626 | 36.9835 | 162.5865 | 59.3923 | 2019-06-01 23:00 | [15 empty] | 718.5 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 718.5 |  | 0.5359 | 0.13666
148 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE116 | 1S-DL-YP-ETC-DVSE-2351-VSE116 | S/STN . EAST END APTT:ID | TG-VSE116A-2 | 19500782 | 630 | 200 | 240.5481 | 0.98628 | 98.5036 | 37.8991 | 164.614 | 36.5259 | 160.0888 | 24.0787 | 104.1692 | 58.3141 | 2019-06-07 22:30 | [15 empty] | 718.5 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 718.5 |  | 0.58139 | 0.15635
149 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE117 | 1S-DL-YP-ETC-DVSE-2351-VSE117 | S/STN 2 EAST END APTT:ID | TG-VSE117A-1 | 19500741 | 630 | 200 | 226.2902 | 0.99399 | 118.3435 | 28.7012 | 135.7865 | 44.5037 | 209.8635 | 45.1386 | 211.0268 | 74.6654 | 2019-06-10 22:30 | [15 empty] | 718.5 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 718.5 |  | 0.50444 | 0.18785
150 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE117 | 1S-DL-YP-ETC-DVSE-2351-VSE117 | S/STN 2 EAST END APTT:ID | TG-VSE117A-2 | 19500745 | 630 | 200 | 233.91 | 0.98384 | 111.1348 | 35.6611 | 153.3614 | 35.986 | 155.2191 | 39.4877 | 169.65 | 15.4437 | 2019-06-13 23:30 | [15 empty] | 718.5 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 718.5 |  | 0.5665 | 0.1764
151 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE118 | 1S-DL-YP-ETC-DVSE-2351-VSE118 | S/STN 3 EAST END APTT:ID | TG-VSE118A-1 | 19505445 | 630 | 200 | 240 | 0.98 | 215 | 79 | 360 | 80 | 340 | 55 | 239 | 112 | 2019-06-11 23:00 | 39.6 | 2.8 | 360 | R | 107 | 109 | 83 | 26 | 96.7 | 2.3 | 0.9 | 0.1 | 362.22 | 292.1 | 531.47 | 389.31 | 330.55 | 401.07 | 401.07 | 303.46 | [12 empty] | 693.17 | 26.43 | 0.58 | 0.34
152 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE118 | 1S-DL-YP-ETC-DVSE-2351-VSE118 | S/STN 3 EAST END APTT:ID | TG-VSE118A-2 | 19500806 | 630 | 200 | 239.1687 | 0.98962 | 214.9853 | 67.2875 | 295.5094 | 86.2693 | 378.1089 | 61.4285 | 267.6157 | 99.5225 | 2019-06-01 22:30 | [15 empty] | 420.5 |  |  |  | 297.5 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 718 |  | 0.57381 | 0.34125
153 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE119 | 1S-DL-YP-ETC-DVSE-2351-VSE119 | S/STN 4 EAST END APTT:ID | TG-VSE119A-1 | 19505186 | 630 | 200 | 242 | 0.99 | 137 | 49 | 214 | 47 | 203 | 41 | 176 | 34 | 2019-06-07 23:30 | 34.6 | 5.2 | 228 | R | 113 | 99 | 88 | 25 | 0.1 | 0.2 | 21.9 | 77.8 | 646.51 | 679.21 | 692.21 | 691.21 | 47.3 | 15 | 15 | 3 | [12 empty] | 694.21 | 25.39 | 0.58 | 0.22
154 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE119 | 1S-DL-YP-ETC-DVSE-2351-VSE119 | S/STN 4 EAST END APTT:ID | TG-VSE119A-2 | 19500738 | 630 | 200 | 239 | 0.98 | 148 | 43 | 188 | 51 | 224 | 54 | 239 | 46 | 2019-06-10 22:00 | 23 | 3.7 | 304 | B | 83 | 87 | 130 | 47 |  |  | 59 | 41 | 715.26 | 715.26 | 514.26 | 700.56 | 4 | 4 | 4 | 18.3 | [12 empty] | 719.26 | 0.34 | 0.55 | 0.24
155 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE120 | 1S-DL-YP-ETC-DVSE-2351-VSE120 | S/STN 5 EAST END APTT:ID | TG-VSE120A-1 | 19500799 | 630 | 200 | 239.1455 | 0.98258 | 207.8176 | 58.8261 | 253.9876 | 65.5754 | 286.2555 | 83.4162 | 364.8681 | 98.7817 | 2019-06-04 23:00 | [15 empty] | 470.5 |  |  |  | 248 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 718.5 |  | 0.55194 | 0.32987
156 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE120 | 1S-DL-YP-ETC-DVSE-2351-VSE120 | S/STN 5 EAST END APTT:ID | TG-VSE120A-2 | 19505908 | 630 | 200 | 241 | 0.98 | 159 | 44 | 190 | 59 | 250 | 56 | 237 | 54 | 2019-06-12 00:30 | 31 | 5.6 | 289 | Y | 93 | 107 | 100 | 14 | 0.1 | 0.1 | 10.9 | 88.9 | 660.58 | 553.18 | 602.28 | 606.28 | 32.5 | 140.3 | 140.3 | 87.2 | [12 empty] | 693.48 | 26.12 | 0.56 | 0.25
157 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE121 | 1S-DL-YP-ETC-DVSE-2351-VSE121 | S/STN 6 EAST END APTT:ID | TG-VSE121A-1 | 19500841 | 630 | 200 | 239.0036 | 0.98912 | 152.5585 | 49.2458 | 213.4717 | 52.918 | 229.3901 | 50.3947 | 220.6518 | 13.8077 | 2019-06-02 23:00 | [15 empty] | 673.5 |  |  |  | 45 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 718.5 |  | 0.54446 | 0.24216
158 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE121 | 1S-DL-YP-ETC-DVSE-2351-VSE121 | S/STN 6 EAST END APTT:ID | TG-VSE121A-2 | 19500739 | 630 | 200 | 239 | 0.99 | 127 | 40 | 175 | 37 | 161 | 50 | 219 | 52 | 2019-06-29 23:00 | 17.5 | 3.7 | 237 | B | 104 | 89 | 107 | 18 |  |  | 27.5 | 72.5 | 712.49 | 699.19 | 641.19 | 716.19 | 4 | 17.3 | 17.3 | 0.3 | [12 empty] | 716.49 | 3.11 | 0.61 | 0.2
159 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE122 | 1S-DL-YP-ETC-DVSE-2351-VSE122 | S/STN 7 EAST END APTT:ID | TG-VSE122A-1 | 19505832 | 630 | 200 | 236 | 0.98 | 44 | 15 | 65 | 14 | 59 | 15 | 65 | 6 | 2019-06-15 15:00 | 8.4 | 1 | 83 | R | 120 | 74 | 106 | 46 |  | 0.2 | 16.9 | 82.9 | 719.26 | 719.26 | 719.26 | 719.26 | [16 empty] | 719.26 | 0.34 | 0.57 | 0.07
160 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE122 | 1S-DL-YP-ETC-DVSE-2351-VSE122 | S/STN 7 EAST END APTT:ID | TG-VSE122A-2 | 19500800 | 630 | 200 | 234.1815 | 0.99532 | 105.4413 | 14.7487 | 66.4507 | 52.5126 | 235.8632 | 38.18 | 167.002 | 147.5687 | 2019-06-30 23:30 | [15 empty] | 720 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.50448 | 0.16737
161 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE123 | 1S-DL-YP-ETC-DVSE-2351-VSE123 | S/STN 8 EAST END APTT:ID | TG-VSE123A-1 | 19505292 | 630 | 200 | 242 | 0.99 | 142 | 51 | 216 | 40 | 172 | 51 | 219 | 46 | 2019-06-12 | 16.4 | 1.2 | 248 | B | 105 | 89 | 106 | 17 |  |  | 10.3 | 89.7 | 654.56 | 692.56 | 606.56 | 666.56 | 41 | 3 | 3 | 29 | [12 empty] | 695.56 | 24.04 | 0.51 | 0.23
162 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE123 | 1S-DL-YP-ETC-DVSE-2351-VSE123 | S/STN 8 EAST END APTT:ID | TG-VSE123A-2 | 19500771 | 630 | 200 | 239.6214 | 0.98414 | 78.6404 | 30.9057 | 132.6482 | 22.3846 | 95.7915 | 25.3501 | 109.3432 | 32.2892 | 2019-06-04 23:00 | [15 empty] | 720 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.51333 | 0.12483
163 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE124 | 1S-DL-YP-ETC-DVSE-2351-VSE124 | S/STN 9 EAST END APTT:ID | TG-VSE124A-1 | 19505254 | 630 | 200 | 234 | 0.99 | 209 | 80 | 355 | 61 | 268 | 68 | 304 | 76 | 2019-06-03 | 30.6 | 1.8 | 364 | R | 121 | 75 | 104 | 46 | 13.6 |  | 6.4 | 79.9 | 415.59 | 650.15 | 499.15 | 509.29 | 277.16 | 43 | 43 | 183.46 | [12 empty] | 693.15 | 26.45 | 0.47 | 0.33
164 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE125 | 1S-DL-YP-ETC-DVSE-2351-VSE125 | S/STN 10 EAST END APTT:ID | TG-VSE125A-1 | 19505706 | 630 | 200 | 241 | 0.98 | 196 | 87 | 376 | 50 | 216 | 59 | 258 | 144 | 2019-06-30 23:30 | 48.2 | -9.8 | 385 | R | 110 | 97 | 93 | 17 | 0.1 | 0.1 | 3.5 | 96.3 | 449.3 | 559.56 | 561.56 | 526.3 | 267.56 | 159.3 | 159.3 | 192.56 | 2 | [11 empty] | 719.26 | 0.34 | 0.52 | 0.31
165 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE126 | 1S-DL-YP-ETC-DVSE-2351-VSE126 | S/STN 11 EAST END APTT:ID | TG-VSE126A-1 | 19500794 | 630 | 200 | 233.699 | 0.99866 | 70.8484 | 23.4645 | 102.8423 | 27.1439 | 120.5485 | 20.24 | 89.0688 | 27.333 | 2019-06-09 22:00 | [15 empty] | 718 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 718 |  | 0.49081 | 0.11246
166 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE126 | 1S-DL-YP-ETC-DVSE-2351-VSE126 | S/STN 11 EAST END APTT:ID | TG-VSE126A-2 | 19500793 | 630 | 200 | 239.4718 | 0.99155 | 62.6544 | 26.7434 | 116.5086 | 16.5855 | 71.6809 | 19.3255 | 83.7725 | 40.1707 | 2019-06-30 22:00 | [15 empty] | 718 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 718 |  | 0.49225 | 0.099451
167 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE127 | 1S-DL-YP-ETC-DVSE-2351-VSE127 | NAGARJUNA S/STR 1:ID | TG-VSE127A-1 | 19500766 | 400 | 120 | 239 | 0.98 | 99 | 34 | 146 | 23 | 99 | 42 | 182 | 72 | 2019-06-03 | 21.3 | 1.9 | 228 | B | 97 | 75 | 128 | 53 |  |  | 9.6 | 90.4 | 638.32 | 715.32 | 447.33 | 650.33 | 78 | 1 | 1 | 65.59 | [12 empty] | 716.32 | 3.28 | 0.59 | 0.25
168 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE127 | 1S-DL-YP-ETC-DVSE-2351-VSE127 | NAGARJUNA S/STR 1:ID | TG-VSE127A-2 | 19505704 | 400 | 120 | 242 | 0.99 | 82 | 27 | 114 | 23 | 98 | 32 | 139 | 36 | 2019-06-08 01:00 | 13.2 | 0.5 | 166 | B | 86 | 89 | 125 | 39 | 0.1 | 0.4 | 22.6 | 76.9 | 700.07 | 704.37 | 603.37 | 704.37 | 5.3 | 1 | 1 | 1 | [12 empty] | 705.37 | 14.23 | 0.59 | 0.21
169 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE128 | 1S-DL-YP-ETC-DVSE-2351-VSE128 | NAGARJUNA S/STR 2:ID | TG-VSE128A-1 | 19500769 | 400 | 120 | 240 | 0.98 | 57 | 15 | 64 | 30 | 131 | 12 | 51 | 75 | 2019-06-30 22:00 | 9.4 | 0.3 | 137 | Y | 82 | 143 | 75 | 68 |  | 0.3 | 43.7 | 56 | 716.34 | 705.34 | 716.34 | 716.34 |  | 11 | 11 | [13 empty] | 716.34 | 3.26 | 0.57 | 0.14
170 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE128 | 1S-DL-YP-ETC-DVSE-2351-VSE128 | NAGARJUNA S/STR 2:ID | TG-VSE128A-2 | 19504912 | 400 | 120 | 241 | 0.98 | 83 | 31 | 133 | 27 | 115 | 25 | 109 | 22 | 2019-06-16 00:30 | 12.7 | 1.7 | 143 | B | 109 | 92 | 98 | 17 |  |  | 8.4 | 91.6 | 681.04 | 687.34 | 677.34 | 690.34 | 10 | 3.3 | 3.3 | 0.3 | [12 empty] | 714.45 | 5.15 | 0.54 | 0.21
171 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE129 | 1S-DL-YP-ETC-DVSE-2351-VSE129 | NAGARJUNA P/M:PM | TG-VSE129A-1 | 19506729 | 100 | 40 | 242 | 0.45 | 8 | 3 | 14 | 2 | 7 | 3 | 12 | 6 | 2019-06-15 19:00 | 6.9 | -7.6 | 26 | R | 55 | 113 | 132 | 77 | 0.1 | 1.4 | 22.4 | 76 | 707.05 | 707.05 | 707.05 | 707.05 | [16 empty] | 707.05 | 12.55 | 0.2 | 0.08
172 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE130 | 1S-DL-YP-ETC-DVSE-2351-VSE130 | S/STR 9 VASUNDHARA ENCLAVE:ID | TG-VSE130A-1 | 19500767 | 400 | 120 | 240 | 0.95 | 40 | 19 | 82 | 7 | 29 | 13 | 54 | 45 | 2019-06-15 15:30 | 21 | 1.1 | 84 | R | 174 | 12 | 114 | 162 |  | 0.1 | 63.4 | 36.5 | 716.34 | 716.34 | 716.34 | 716.34 | [16 empty] | 716.34 | 3.26 | 0.35 | 0.1
173 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE131 | 1S-DL-YP-ETC-DVSE-2351-VSE131 | INDIAN EXPRESS:ID | TG-VSE131A-1 | 19500768 | 400 | 120 | 239 | 0.99 | 69 | 24 | 100 | 30 | 125 | 16 | 68 | 50 | 2019-06-13 23:00 | 5.8 | 0.6 | 130 | Y | 106 | 111 | 83 | 28 |  |  | 15.8 | 84.2 | 716.35 | 711.05 | 716.35 | 716.35 |  | 5.3 | 5.3 | [13 empty] | 716.35 | 3.25 | 0.41 | 0.17
174 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE131 | 1S-DL-YP-ETC-DVSE-2351-VSE131 | INDIAN EXPRESS:ID | TG-VSE131A-2 | 19500791 | 400 | 120 | 240 | 0.98 | 55 | 16 | 70 | 16 | 70 | 23 | 98 | 28 | 2019-06-03 | 10.2 | 0.3 | 108 | B | 90 | 75 | 134 | 59 |  |  | 5.5 | 94.5 | 716.35 | 716.35 | 716.35 | 716.35 | [16 empty] | 716.35 | 3.25 | 0.45 | 0.14
175 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE132 | 1S-DL-YP-ETC-DVSE-2351-VSE132 | ALLAHABAD BANK CGHS:ID | TG-VSE132A-1 | 19505829 | 400 | 120 | 242 | 0.97 | 84 | 23 | 99 | 23 | 98 | 38 | 167 | 68 | 2019-06-02 23:30 | 21.1 | 1.9 | 167 | B | 91 | 76 | 132 | 56 |  | 0.1 | 15.5 | 84.4 | 703.26 | 706.56 | 543.3 | 704.26 | 3.3 |  |  | 2.3 | [12 empty] | 706.56 | 13.04 | 0.56 | 0.21
176 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE132 | 1S-DL-YP-ETC-DVSE-2351-VSE132 | ALLAHABAD BANK CGHS:ID | TG-VSE132A-2 | 19500770 | 400 | 120 | 240 | 0.98 | 85 | 19 | 83 | 21 | 94 | 45 | 198 | 110 | 2019-06-10 22:00 | 9.9 | 0.6 | 205 | B | 61 | 68 | 171 | 110 |  |  | 23.7 | 76.3 | 716.25 | 716.25 | 466.01 | 714.55 |  |  |  | 1.3 | [12 empty] | 716.25 | 3.35 | 0.49 | 0.21
177 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE133 | 1S-DL-YP-ETC-DVSE-2351-VSE133 | AIIMS:ID | TG-VSE133A-1 | 19500746 | 400 | 120 | 240.1335 | 0.97369 | 57.248 | 18.1951 | 77.8632 | 22.9595 | 98.1552 | 16.0934 | 67.4749 | 27.0275 | 2019-06-30 00:30 | [15 empty] | 718 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 718 |  | 0.5435 | 0.14312
178 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE133 | 1S-DL-YP-ETC-DVSE-2351-VSE133 | AIIMS:ID | TG-VSE133A-2 | 19505828 | 400 | 120 | 241 | 0.98 | 108 | 36 | 152 | 49 | 210 | 23 | 97 | 98 | 2019-06-29 23:30 | 22 | 3.5 | 210 | Y | 113 | 110 | 77 | 36 | 0.1 | 0.1 | 16 | 83.8 | 462.21 | 483.13 | 682.35 | 561.35 | 241.44 | 220.52 | 220.52 | 142.3 | [12 empty] | 704.05 | 15.55 | 0.57 | 0.27
179 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE134 | 1S-DL-YP-ETC-DVSE-2351-VSE134 | VISH WAKARMA ABH:ID | TG-VSE134A-1 | 19505827 | 630 | 200 | 242 | 0.99 | 115 | 44 | 188 | 37 | 157 | 35 | 151 | 34 | 2019-06-02 23:00 | 17.8 | -0.8 | 205 | R | 132 | 30 | 137 | 107 | 0.1 | 0.1 | 10.5 | 89.4 | 697.27 | 708.57 | 700.57 | 708.57 | 11.3 | [15 empty] | 708.57 | 11.03 | 0.44 | 0.18
180 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE134 | 1S-DL-YP-ETC-DVSE-2351-VSE134 | VISH WAKARMA ABH:ID | TG-VSE134A-2 | 19502363 | 630 | 200 | 241 | 0.98 | 133 | 41 | 178 | 54 | 235 | 38 | 161 | 68 | 2019-06-02 23:30 | 22.1 | 3.2 | 235 | Y | 93 | 113 | 95 | 20 |  |  | 26.2 | 73.8 | 691.02 | 659.32 | 694.32 | 691.32 | 4 | 35.3 | 35.3 | 3.3 | [12 empty] | 695.02 | 24.58 | 0.53 | 0.21
181 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE135 | 1S-DL-YP-ETC-DVSE-2351-VSE135 | NEW PROGESSIVE S/SM1:ID | TG-VSE135A-1 | 19500892 | 630 | 200 | 241 | 0.99 | 109 | 36 | 156 | 29 | 125 | 45 | 196 | 61 | 2019-06-11 | 16.6 | 0.9 | 209 | B | 92 | 87 | 122 | 35 |  |  | 4.9 | 95.1 | 717.21 | 717.21 | 695.51 | 717.21 | [16 empty] | 717.21 | 2.39 | 0.51 | 0.17
182 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE135 | 1S-DL-YP-ETC-DVSE-2351-VSE135 | NEW PROGESSIVE S/SM1:ID | TG-VSE135A-2 | 19500920 | 630 | 200 | 242 | 0.98 | 160 | 32 | 138 | 32 | 139 | 96 | 840 | 701 | 2019-06-30 23:00 | 22.1 | -3.7 | 844 | B | 87 | 80 | 133 | 53 | 71.1 | 26.1 | 2.9 |  | 710.5 | 712.2 | 589.5 | 703.2 | 1.3 |  |  | 9 |  |  | 6.3 | [9 empty] | 717.2 | 2.4 | 0.41 | 0.25
183 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE136 | 1S-DL-YP-ETC-DVSE-2351-VSE136 | NEW PROGESSIVE S/SM2:ID | TG-VSE136A-1 | 19500893 | 630 | 200 | 240 | 0.95 | 115 | 45 | 189 | 40 | 165 | 31 | 128 | 53 | 2019-06-13 23:30 | 56.1 | 6 | 206 | R | 105 | 114 | 82 | 32 |  |  | 4.5 | 95.5 | 711.52 | 712.22 | 717.22 | 717.22 | 5.3 | 5 | 5 | [13 empty] | 717.22 | 2.38 | 0.6 | 0.18
184 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE136 | 1S-DL-YP-ETC-DVSE-2351-VSE136 | NEW PROGESSIVE S/SM2:ID | TG-VSE136A-2 | 19500894 | 630 | 200 | 241 | 0.98 | 122 | 55 | 240 | 38 | 164 | 29 | 121 | 104 | 2019-06-01 | 17.5 | 1.8 | 244 | R | 126 | 100 | 74 | 52 | 0.1 | 0.4 | 65.4 | 34.2 | 692.51 | 710.51 | 716.51 | 716.51 | 24 | 6 | 6 | [13 empty] | 716.51 | 3.09 | 0.47 | 0.19
185 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE146 | 1S-DL-YP-ETC-DVSE-2351-VSE146 | PUNEET CGHS V. ENCLAVE:ID | TG-VSE146A-1 | 19504740 | 400 | 120 | 235 | 0.98 | 67 | 24 | 109 | 18 | 78 | 25 | 110 | 32 | 2019-06-11 23:30 | 13.5 | 0.3 | 129 | R | 111 | 93 | 96 | 18 |  |  | 13.3 | 86.7 | 718.27 | 719.27 | 719.27 | 719.27 | 1 | [15 empty] | 719.27 | 0.33 | 0.47 | 0.17
186 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE146 | 1S-DL-YP-ETC-DVSE-2351-VSE146 | PUNEET CGHS V. ENCLAVE:ID | TG-VSE146A-2 | 19504687 | 400 | 120 | 230 | 0.98 | 44 | 22 | 99 | 22 | 98 | 0 | 0 | 98 | 2019-06-16 | 7.2 | 0.6 | 102 | Y | 152 | 148 | 0 | 152 |  |  | 28.3 | 71.7 | 719.26 | 719.26 | 719.26 | 719.26 | [16 empty] | 719.26 | 0.34 | 0.44 | 0.11
187 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE153 | 1S-DL-YP-ETC-DVSE-2351-VSE153 | HABITAT CGHS VASUNDHARA ENCLAVE:ID | TG-VSE153A-1 | 19504251 | 630 | 200 | 241 | 0.99 | 144 | 51 | 218 | 41 | 178 | 52 | 220 | 41 | 2019-06-05 23:30 | 22.1 | -3.7 | 233 | R | 99 | 102 | 99 | 3 |  |  | 40.5 | 59.5 | 659.21 | 653.21 | 683.21 | 685.51 | 58 | 64 | 64 | 31.3 | [12 empty] | 717.21 | 2.39 | 0.6 | 0.23
188 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE153 | 1S-DL-YP-ETC-DVSE-2351-VSE153 | HABITAT CGHS VASUNDHARA ENCLAVE:ID | TG-VSE153A-2 | 19504257 | 630 | 200 | 241 | 0.98 | 129 | 63 | 276 | 37 | 160 | 29 | 123 | 137 | 2019-06-11 23:30 | 17 | 2.3 | 276 | R | 135 | 86 | 79 | 56 |  |  | 36 | 64 | 660.5 | 717.2 | 717.2 | 716.5 | 56.3 |  |  | 0.3 | [12 empty] | 717.2 | 2.4 | 0.48 | 0.2
189 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE154 | 1S-DL-YP-ETC-DVSE-2351-VSE154 | NIRAJ (PRYAG) CGHS VASHUNDRA ENCL:ID | TG-VSE154A-1 | 19505559 | 630 | 200 | 230 | 0.99 | 211 | 76 | 342 | 72 | 323 | 64 | 288 | 47 | 2019-06-01 23:30 | 26 | 4.2 | 342 | R | 103 | 99 | 98 | 5 | 0.1 |  | 22.5 | 77.4 | 516.53 | 532.53 | 536.23 | 529.53 | 200.54 | 184.54 | 184.54 | 187.54 | [12 empty] | 717.47 | 2.13 | 0.46 | 0.34
190 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE154 | 1S-DL-YP-ETC-DVSE-2351-VSE154 | NIRAJ (PRYAG) CGHS VASHUNDRA ENCL:ID | TG-VSE154A-2 | 19505560 | 630 | 200 | 230 | 0.99 | 205 | 71 | 317 | 59 | 261 | 75 | 336 | 67 | 2019-06-12 00:30 | 39.6 | 2.2 | 376 | B | 113 | 85 | 102 | 28 | 0.1 | 0.1 | 21.2 | 78.5 | 436.26 | 600.22 | 511.22 | 523.26 | 281.2 | 117.24 | 117.24 | 194.2 | [12 empty] | 717.46 | 2.14 | 0.5 | 0.33
191 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE165 | 1S-DL-YP-ETC-DVSE-2351-VSE165 | MAHESH C.G.H.S. VASUNDHRA ENCLAVE :I/D | TG-VSE165A-1 | 19504289 | 630 | 200 | 230 | 0.99 | 111 | 29 | 129 | 11 | 49 | 71 | 319 | 240 | 2019-06-30 | 6.4 | -1.8 | 319 | B | 81 | 41 | 178 | 137 |  |  | 20.7 | 79.3 | 719.26 | 719.26 | 515.26 | 719.26 | [16 empty] | 719.26 | 0.34 | 0.53 | 0.18
192 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE165 | 1S-DL-YP-ETC-DVSE-2351-VSE165 | MAHESH C.G.H.S. VASUNDHRA ENCLAVE :I/D | TG-VSE165A-2 | 19506136 | 630 | 200 | 230 | 0.99 | 140 | 36 | 161 | 37 | 169 | 67 | 299 | 134 | 2019-06-03 | 68.6 | 3.6 | 315 | B | 92 | 71 | 137 | 66 | 0.1 |  | 9 | 90.9 | 700.26 | 706.56 | 401.56 | 693.56 | 6.3 |  |  | 13 | [12 empty] | 706.56 | 13.04 | 0.63 | 0.22
193 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE166 | 1S-DL-YP-ETC-DVSE-2351-VSE166 | POLICE COMPUTER CGHS V.ENCL.:PACKAGE S/S | TG-VSE166A-1 | 19506898 | 990 | 320 | 236 | 0.97 | 106 | 39 | 174 | 38 | 168 | 28 | 127 | 45 | 2019-06-11 23:00 | 26.2 | 2.6 | 179 | Y | 102 | 104 | 94 | 10 | 0.1 | 0.8 | 8.1 | 91.1 | 711.27 | 711.27 | 711.27 | 711.27 | [16 empty] | 711.27 | 8.33 | 0.54 | 0.11
194 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE210 | 1S-DL-YP-ETC-DVSE-2351-VSE210 | Dutt Bhawan (AIFODE) | TG-VSE210A-1 | 19505122 | 100 | 40 | 241 | 0.98 | 15 | 0 | 0 | 15 | 64 | 0 | 1 | 63 | 2019-06-30 01:30 | 6.3 | -5.8 | 64 | Y | 0 | 283 | 17 | 283 |  | 0.4 | 20.5 | 79 | 708.04 | 582.26 | 708.04 | 708.04 |  | 124.08 | 124.08 |  |  | 1.3 | [10 empty] | 708.04 | 11.56 | 0.3 | 0.15
195 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE213 | 1S-DL-YP-ETC-DVSE-2351-VSE213 | DMRC Staff Qtrs New Ashok Nagar | TG-VSE213A-1 | 19506315 | 990 | 320 | 242 | 0.97 | 266 | 88 | 368 | 90 | 376 | 87 | 367 | 8 | 2019-06-22 10:00 | 192.6 | -3.8 | 376 | Y | 93 | 101 | 106 | 13 | 0.1 |  | 9.8 | 90.2 | 708.29 | 708.29 | 708.29 | 708.29 | 1.3 | 1.3 | 1.3 | 1.3 | [12 empty] | 709.59 | 10.01 | 0.21 | 0.27
196 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE024 | 1S-DL-YP-ETC-DVSE-2351-VSE024 | S/STN 2 MIXED HOUSING MVR-III:ID | TG-VSE024A-1 | 19502347 | 630 | 200 | 248 | 0.98 | 177 | 39 | 161 | 79 | 327 | 59 | 246 | 144 | 2019-06-30 23:00 | 24.4 | 4.1 | 403 | Y | 55 | 148 | 97 | 93 |  |  | 77.1 | 22.9 | 719.54 | 472.29 | 618.3 | 620.59 |  | 241 | 241 | 98.55 |  | 6.25 | [10 empty] | 719.54 | 0.06 | 0.44 | 0.28
197 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE024 | 1S-DL-YP-ETC-DVSE-2351-VSE024 | S/STN 2 MIXED HOUSING MVR-III:ID | TG-VSE024A-2 | 19502341 | 630 | 200 | 240 | 0.98 | 176 | 51 | 220 | 71 | 304 | 54 | 233 | 79 | 2019-06-29 23:00 | 21.6 | 1.4 | 304 | Y | 95 | 105 | 100 | 10 |  |  | 0.5 | 99.5 | 602 | 555.3 | 611 | 583 | 117.54 | 164.24 | 164.24 | 136.54 | [12 empty] | 719.54 | 0.06 | 0.5 | 0.28
198 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE025 | 1S-DL-YP-ETC-DVSE-2351-VSE025 | S/STN 3 MIXED HOUSING MVR-III:ID | TG-VSE025A-1 | 19505964 | 630 | 200 | 248 | 0.98 | 112 | 40 | 159 | 34 | 135 | 38 | 150 | 21 | 2019-06-12 | 27.4 | 2.4 | 212 | B | 91 | 93 | 115 | 24 | 1.4 | 23.2 | 61.6 | 13.7 | 697 | 697 | 695.3 | 697 | [16 empty] | 697 | 23 | 0.5 | 0.18
199 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE025 | 1S-DL-YP-ETC-DVSE-2351-VSE025 | S/STN 3 MIXED HOUSING MVR-III:ID | TG-VSE025A-2 | 19502344 | 630 | 200 | 241 | 0.98 | 113 | 34 | 146 | 27 | 116 | 52 | 216 | 89 | 2019-06-30 23:00 | 14.3 | 0.9 | 221 | B | 97 | 84 | 118 | 34 | 96.4 | 0.1 | 1.3 | 2.2 | 719.3 | 720 | 693 | 720 | 0.3 | [15 empty] | 720 | 0 | 0.48 | 0.18
200 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE026 | 1S-DL-YP-ETC-DVSE-2351-VSE026 | S/STN 4 MIXED HOUSING MVR-III:ID | TG-VSE026A-1 | 19502342 | 630 | 200 | 242 | 0.93 | 71 | 24 | 98 | 19 | 79 | 28 | 116 | 32 | 2019-06-11 00:30 | 38.2 | 0.5 | 133 | B | 102 | 73 | 125 | 52 |  |  | 22.5 | 77.5 | 718.19 | 718.19 | 718.19 | 718.19 | [16 empty] | 718.19 | 1.41 | 0.44 | 0.11
201 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE026 | 1S-DL-YP-ETC-DVSE-2351-VSE026 | S/STN 4 MIXED HOUSING MVR-III:ID | TG-VSE026A-2 | 19506312 | 630 | 200 | 242 | 0.98 | 110 | 13 | 52 | 19 | 78 | 79 | 333 | 270 | 2019-06-30 03:00 | 35.2 | 1.4 | 333 | B | 63 | 91 | 147 | 84 | 1.8 | 16.4 | 65.3 | 16.5 | 710.53 | 710.53 | 672.53 | 710.53 | [16 empty] | 710.53 | 9.07 | 0.44 | 0.18
202 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE027 | 1S-DL-YP-ETC-DVSE-2351-VSE027 | S/STN 5 MIXED HOUSING MVR-III:ID | TG-VSE027A-1 | 19502381 | 630 | 200 | 246 | 0.99 | 146 | 56 | 231 | 42 | 174 | 48 | 202 | 50 | 2019-06-11 23:30 | 12.9 | -7.4 | 255 | R | 110 | 81 | 109 | 29 |  |  | 31.4 | 68.6 | 613.41 | 713.11 | 654.11 | 686.11 | 102 | 2.3 | 2.3 | 29.3 | [12 empty] | 715.41 | 4.19 | 0.5 | 0.23
203 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE027 | 1S-DL-YP-ETC-DVSE-2351-VSE027 | S/STN 5 MIXED HOUSING MVR-III:ID | TG-VSE027A-2 | 19502348 | 630 | 200 | 246 | 0.97 | 92 | 8 | 35 | 34 | 142 | 49 | 216 | 158 | 2019-06-11 23:00 | 13.8 | 2.3 | 230 | B | 22 | 109 | 170 | 148 | 100 |  |  |  | 715.4 | 715.4 | 673.1 | 715.4 | [16 empty] | 715.4 | 4.2 | 0.45 | 0.15
204 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE028 | 1S-DL-YP-ETC-DVSE-2351-VSE028 | S/STN 6 MIXED HOUSING MVR-III:ID | TG-VSE028A-1 | 19502438 | 630 | 200 | 240 | 0.98 | 173 | 60 | 260 | 55 | 224 | 58 | 249 | 31 | 2019-06-30 23:30 | 23.9 | 6.9 | 295 | B | 86 | 92 | 122 | 36 | 48.8 | 11.9 | 33 | 6.3 | 661.36 | 687.06 | 564.26 | 641.36 | 54 | 28.3 | 28.3 | 74 | [12 empty] | 715.36 | 4.24 | 0.46 | 0.27
205 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE028 | 1S-DL-YP-ETC-DVSE-2351-VSE028 | S/STN 6 MIXED HOUSING MVR-III:ID | TG-VSE028A-2 | 19502346 | 630 | 200 | 240 | 0.98 | 99 | 32 | 141 | 23 | 98 | 44 | 189 | 79 | 2019-06-02 22:30 | 17.5 | 3.2 | 204 | B | 96 | 90 | 114 | 24 |  |  | 68.1 | 31.9 | 715.4 | 715.4 | 697.4 | 715.4 | [16 empty] | 715.4 | 4.2 | 0.55 | 0.16
206 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE029 | 1S-DL-YP-ETC-DVSE-2351-VSE029 | S/STN 7 MIXED HOUSING MVR-III:ID | TG-VSE029A-1 | 19502437 | 630 | 200 | 246 | 0.98 | 175 | 43 | 180 | 83 | 349 | 50 | 212 | 155 | 2019-06-26 22:30 | 30.8 | 7.8 | 353 | Y | 77 | 139 | 84 | 62 |  |  | 10.6 | 89.4 | 696.54 | 322.56 | 645.3 | 595.3 | 16.3 | 389.58 | 389.58 | 117.54 |  | 0.3 | [10 empty] | 713.24 | 6.36 | 0.55 | 0.28
207 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE029 | 1S-DL-YP-ETC-DVSE-2351-VSE029 | S/STN 7 MIXED HOUSING MVR-III:ID | TG-VSE029A-2 | 19502345 | 630 | 200 | 246 | 0.98 | 159 | 49 | 205 | 63 | 262 | 47 | 199 | 60 | 2019-06-09 | 26.2 | 2.8 | 303 | Y | 96 | 122 | 82 | 40 |  |  | 3.2 | 96.8 | 651.5 | 561.5 | 709.18 | 644.5 | 62.58 | 152.58 | 152.58 | 69.58 | [12 empty] | 714.48 | 5.12 | 0.46 | 0.25
208 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE030 | 1S-DL-YP-ETC-DVSE-2351-VSE030 | S/STN 8 MIXED HOUSING MVR III:ID | TG-VSE030A-1 | 19503038 | 630 | 200 | 235 | 0.98 | 89 | 18 | 79 | 36 | 157 | 34 | 148 | 74 | 2019-06-29 23:30 | 16.6 | 2.3 | 176 | B | 81 | 132 | 87 | 51 |  |  | 37.4 | 62.6 | 715.41 | 715.41 | 715.41 | 715.41 | [16 empty] | 715.41 | 4.19 | 0.6 | 0.14
209 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE030 | 1S-DL-YP-ETC-DVSE-2351-VSE030 | S/STN 8 MIXED HOUSING MVR III:ID | TG-VSE030A-2 | 19502439 | 630 | 200 | 241 | 0.98 | 176 | 73 | 318 | 54 | 232 | 49 | 210 | 98 | 2019-06-11 22:30 | 21.2 | 3.2 | 318 | R | 133 | 89 | 79 | 54 |  |  | 35 | 65 | 525.41 | 648.11 | 680.11 | 620.11 | 190 | 67.3 | 67.3 | 95.3 | [12 empty] | 715.41 | 4.19 | 0.45 | 0.28
210 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE031 | 1S-DL-YP-ETC-DVSE-2351-VSE031 | S/STN 9 MIXED HOUSING MVR III:ID | TG-VSE031A-1 | 19502440 | 990 | 320 | 238 | 0.98 | 728 | 290 | 1263 | 236 | 1015 | 202 | 857 | 354 | 2019-06-30 23:30 | 130.3 | 43.4 | 1263 | R | 112 | 103 | 85 | 27 |  | 7.9 | 91.9 | 0.2 |  |  | 7.3 |  | 250 | 315 | 315 | 340.3 | 460.16 | 404.46 | 255.46 | 379.16 | 9.3 | [7 empty] | 719.46 | 0.14 | 0.59 | 0.74
211 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE031 | 1S-DL-YP-ETC-DVSE-2351-VSE031 | S/STN 9 MIXED HOUSING MVR III:ID | TG-VSE031A-2 | 19506129 | 630 | 200 | 239 | 0.98 | 629 | 260 | 1119 | 179 | 750 | 190 | 801 | 347 | 2019-06-30 03:00 | 217.8 | 25.4 | 1119 | R | 106 | 101 | 93 | 13 | 0.1 | 0.4 | 56.6 | 42.9 | 0.3 | 0.3 | 3 |  | 223 | 236.3 | 236.3 | 248 | 414.3 | 441.59 | 388.29 | 428.29 | 57.45 | 16.46 | 8.16 | 19.46 | 0.3 | 0.3 |  |  | 696.15 | 23.45 | 0.49 | 1
212 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE032 | 1S-DL-YP-ETC-DVSE-2351-VSE032 | S/STN 10 MIXED HOUSING MVR III:ID | TG-VSE032A-1 | 19502349 | 630 | 200 | 240 | 0.98 | 161 | 37 | 155 | 75 | 320 | 50 | 213 | 144 | 2019-06-30 23:30 | 21.2 | 4.1 | 320 | Y | 68 | 132 | 100 | 64 |  |  | 13.4 | 86.6 | 716.18 | 576.48 | 703.48 | 696.48 |  | 139.3 | 139.3 | 19.3 | [12 empty] | 716.18 | 3.42 | 0.42 | 0.26
213 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE032 | 1S-DL-YP-ETC-DVSE-2351-VSE032 | S/STN 10 MIXED HOUSING MVR III:ID | TG-VSE032A-2 | 19506127 | 630 | 200 | 247 | 0.98 | 153 | 44 | 180 | 33 | 138 | 75 | 312 | 157 | 2019-06-30 23:00 | 48.8 | 4.2 | 375 | B | 68 | 83 | 149 | 81 | 0.1 |  | 16.6 | 83.2 | 708.11 | 708.41 | 469.13 | 682.13 | 1 | 0.3 | 0.3 | 26.58 |  |  | 0.3 | [9 empty] | 709.11 | 10.49 | 0.49 | 0.24
214 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE033 | 1S-DL-YP-ETC-DVSE-2351-VSE033 | S/STN B- BLK NEW KNODLI:ID | TG-VSE033A-1 | 19504187 | 630 | 200 | 246 | 0.97 | 401 | 151 | 619 | 129 | 533 | 120 | 493 | 111 | 2019-06-30 | 94.8 | 27.6 | 650 | R | 109 | 101 | 90 | 19 |  |  | 32.8 | 67.2 |  | 1 | 1 |  | 142.3 | 210 | 210 | 203.3 | 577.02 | 508.32 | 389.15 | 516.02 | [8 empty] | 719.32 | 0.28 | 0.71 | 0.64
215 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE033 | 1S-DL-YP-ETC-DVSE-2351-VSE033 | S/STN B- BLK NEW KNODLI:ID | TG-VSE033A-2 | 19502954 | 630 | 200 | 245 | 0.98 | 438 | 125 | 528 | 150 | 636 | 163 | 685 | 139 | 2019-06-30 00:30 | 81 | 18.4 | 689 | Y | 88 | 111 | 102 | 23 |  |  | 19.7 | 80.3 |  |  |  |  | 357.18 | 122 | 122 | 206.18 | 362.3 | 597.48 | 528.3 | 513.3 | [8 empty] | 719.48 | 0.12 | 0.67 | 0.69
216 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE033 | 1S-DL-YP-ETC-DVSE-2351-VSE033 | S/STN B- BLK NEW KNODLI:ID | TG-VSE033A-3 | 19505676 | 630 | 200 | 244 | 0.98 | 406 | 137 | 573 | 149 | 622 | 120 | 505 | 103 | 2019-06-30 21:00 | 84.2 | 20 | 645 | Y | 105 | 106 | 89 | 17 | 0.2 | 0.2 | 10.4 | 89.2 | 6.3 | 4 | 49 | 6 | 400.19 | 365.19 | 365.19 | 452.49 | 301.58 | 339.28 | 124.58 | 249.58 | [8 empty] | 708.47 | 11.13 | 0.57 | 0.64
217 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE034 | 1S-DL-YP-ETC-DVSE-2351-VSE034 | S/STN C- BLK NEW KNODLI:ID | TG-VSE034A-1 | 19505982 | 630 | 200 | 254 | 0.95 | 315 | 96 | 393 | 117 | 472 | 102 | 413 | 71 | 2019-06-30 23:30 | 152.6 | 26.6 | 562 | B | 86 | 109 | 105 | 23 |  | 0.3 | 19.9 | 79.7 | 19.3 | 0.3 | 0.3 | 0.3 | 604.45 | 373.3 | 373.3 | 469 | 95 | 345.15 | 309.45 | 249.45 | [8 empty] | 719.15 | 0.45 | 0.73 | 0.5
218 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE034 | 1S-DL-YP-ETC-DVSE-2351-VSE034 | S/STN C- BLK NEW KNODLI:ID | TG-VSE034A-2 | 19502435 | 630 | 200 | 241 | 0.98 | 487 | 142 | 609 | 168 | 717 | 177 | 762 | 137 | 2019-06-29 23:30 | 104.4 | 26.7 | 770 | B | 87 | 109 | 105 | 22 |  | 0.1 | 9 | 90.9 |  |  |  |  | 169.3 | 13.3 | 13.3 | 35 | 549.34 | 704.34 | 693.34 | 684.04 |  | 1 | 3 | [5 empty] | 719.04 | 0.56 | 0.7 | 0.77
219 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE034 | 1S-DL-YP-ETC-DVSE-2351-VSE034 | S/STN C- BLK NEW KNODLI:ID | TG-VSE034A-3 | 19506424 | 630 | 200 | 244 | 0.99 | 348 | 108 | 443 | 153 | 636 | 86 | 351 | 251 | 2019-06-01 20:30 | 23.6 | -27.8 | 636 | Y | 99 | 132 | 69 | 63 | 3.2 | 7.4 | 49.5 | 39.8 | 7.3 | 2 | 108.3 | 10 | 298.3 | 139 | 139 | 288 | 111.59 | 276.59 | 7.3 | 119.59 | [8 empty] | 707.59 | 12.01 | 0.64 | 0.55
220 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE035 | 1S-DL-YP-ETC-DVSE-2351-VSE035 | S/STN D-BLK NEW KNODLI:ID | TG-VSE035A-1 | 19505444 | 400 | 120 | 248 | 0.96 | 187 | 77 | 314 | 56 | 230 | 54 | 224 | 87 | 2019-06-02 18:30 | 96.7 | 4.6 | 325 | R | 124 | 77 | 100 | 47 | 0.2 | 0.1 | 9.3 | 90.3 | 256.36 | 528.27 | 404.27 | 476.27 | 387.21 | 164.3 | 164.3 | 213 | 51.3 | 2.3 | 2 | 6 | [8 empty] | 695.27 | 24.33 | 0.42 | 0.47
221 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE035 | 1S-DL-YP-ETC-DVSE-2351-VSE035 | S/STN D-BLK NEW KNODLI:ID | TG-VSE035A-2 | 19505985 | 400 | 120 | 245 | 0.97 | 377 | 111 | 442 | 142 | 564 | 124 | 491 | 107 | 2019-06-13 22:30 | 102.5 | 25.4 | 589 | Y | 92 | 110 | 98 | 18 | 0.1 | 0.1 | 10.4 | 89.4 |  |  |  |  | 48.3 | 3 | 3 | 12.3 | 634.58 | 394.44 | 604.58 | 570.58 | 35.3 | 309.44 | 98.3 | 135.3 |  | 11.3 |  |  | 718.58 | 1.02 | 0.72 | 0.94
222 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE047 | 1S-DL-YP-ETC-DVSE-2351-VSE047 | STAFF QUT. SEW. P/STN. KNODLI:ID | TG-VSE047A-1 | 19502836 | 400 | 120 | 235 | 0.98 | 76 | 26 | 125 | 28 | 130 | 21 | 92 | 36 | 2019-06-10 23:00 | 8 | 1.4 | 141 | Y | 103 | 114 | 83 | 31 | 100 |  |  |  | 719.27 | 700.27 | 719.27 | 719.27 |  | 19 | 19 | [13 empty] | 719.27 | 0.33 | 0.49 | 0.19
223 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE048 | 1S-DL-YP-ETC-DVSE-2351-VSE048 | DALLUPURA VILL. DURGA PARK:ID | TG-VSE048A-1 | 19505213 | 990 | 320 | 238 | 0.99 | 800 | 227 | 953 | 211 | 895 | 363 | 1558 | 636 | 2019-06-14 00:30 | 229.4 | 32.3 | 1558 | B | 100 | 99 | 101 | 2 | 0.1 | 0.4 | 17.7 | 81.8 |  |  |  |  | 23.5 | 19.3 | 19.3 | 17.3 | 668.12 | 672.02 | 658.32 | 675.02 | 1 | 1.3 | 7 | 0.3 |  |  | 0.3 |  | 693.02 | 26.58 | 0.69 | 0.81
224 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE048 | 1S-DL-YP-ETC-DVSE-2351-VSE048 | DALLUPURA VILL. DURGA PARK:ID | TG-VSE048A-2 | 19505346 | 630 | 200 | 250 | 0.98 | 856 | 248 | 1012 | 296 | 1222 | 312 | 1287 | 249 | 2019-06-30 12:30 | 187 | 35.8 | 1361 | Y | 100 | 104 | 95 | 9 | 0.1 | 0.3 | 25.1 | 74.6 |  |  |  |  | 32.3 | 11 | 11 | 12.3 | 578.41 | 616.39 | 650.13 | 647.45 | 80.09 | 63.11 | 18.07 | 30.35 | 0.43 | 1.13 | 0.43 | 1.13 | 692.03 | 27.57 | 0.46 | 1.36
225 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE050 | 1S-DL-YP-ETC-DVSE-2351-VSE050 | S/STN 2 VASHUNDRA ENCLAVE:ID | TG-VSE050A-1 | 19502018 | 990 | 320 | 238 | 0.99 | 618 | 218 | 965 | 220 | 969 | 181 | 788 | 179 | 2019-06-27 22:30 | 89.1 | 5.9 | 969 | Y | 98 | 94 | 108 | 14 |  |  | 11.5 | 88.5 | 9 | 10 | 6 | 6.3 | 263.02 | 324.04 | 324.04 | 211.11 | 445.26 | 383.24 | 594.34 | 499.47 | [8 empty] | 717.28 | 2.32 | 0.69 | 0.62
226 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE050 | 1S-DL-YP-ETC-DVSE-2351-VSE050 | S/STN 2 VASHUNDRA ENCLAVE:ID | TG-VSE050A-2 | 19506767 | 990 | 320 | 240 | 0.99 | 543 | 215 | 883 | 247 | 1035 | 81 | 337 | 636 | 2019-06-26 06:30 | 127 | 2.9 | 1035 | Y | 117 | 74 | 109 | 43 | 0.1 | 0.1 | 2.3 | 97.5 | 261.08 | 662.57 | 343.56 | 453.05 | 449.19 | 47.3 | 47.3 | 257.22 | 0.3 | 0.3 |  | 0.3 | [8 empty] | 710.57 | 9.03 | 0.34 | 0.55
227 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE051 | 1S-DL-YP-ETC-DVSE-2351-VSE051 | S/STN 3 VASHUNDRA ENCLAVE:ID | TG-VSE051A-1 | 19502368 | 400 | 120 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [7 empty] | 0.1 | 99.9 | 719.25 | 719.25 | 719.25 | 719.25 | [16 empty] | 719.25 | 0.35 |  | 0
228 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE054 | 1S-DL-YP-ETC-DVSE-2351-VSE054 | S/STN 6 VASHUNDRA ENCLAVE:ID | TG-VSE054A-1 | 19500878 | 630 | 200 | 240 | 0.96 | 197 | 45 | 187 | 89 | 372 | 63 | 267 | 161 | 2019-06-14 12:00 | 47.8 | 8.7 | 372 | Y | 77 | 134 | 88 | 57 |  |  | 8.7 | 91.3 | 633.46 | 334.53 | 520.23 | 443.23 | 85.41 | 381.04 | 381.04 | 276.04 |  | 3.3 | [10 empty] | 719.27 | 0.33 | 0.51 | 0.31
229 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE054 | 1S-DL-YP-ETC-DVSE-2351-VSE054 | S/STN 6 VASHUNDRA ENCLAVE:ID | TG-VSE054A-2 | 19500880 | 630 | 200 | 245 | 0.95 | 148 | 62 | 254 | 37 | 152 | 50 | 205 | 88 | 2019-06-29 12:30 | 36.3 | 7.8 | 254 | R | 127 | 66 | 107 | 61 |  |  | 0.9 | 99.1 | 618.15 | 719.45 | 693.45 | 714.45 | 101.3 |  |  | 5 | [12 empty] | 719.45 | 0.15 | 0.41 | 0.24
230 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE055 | 1S-DL-YP-ETC-DVSE-2351-VSE055 | S/STN 8 VASHUNDRA ENCLAVE:ID | TG-VSE055A-1 | 19505281 | 400 | 120 | 249 | 0.96 | 214 | 110 | 453 | 49 | 196 | 56 | 231 | 241 | 2019-06-01 11:30 | 64.3 | 10.2 | 453 | R | 119 | 107 | 74 | 45 |  | 2.5 | 31.1 | 66.4 | 4 | 104 | 384.38 | 80 | 507.07 | 419.56 | 419.56 | 521.55 | 197.41 | 185.22 | 29.07 | 107.23 | 0.3 | [7 empty] | 709.18 | 10.42 | 0.56 | 0.54
231 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE056 | 1S-DL-YP-ETC-DVSE-2351-VSE056 | INOD-VERMAN PETROLIUM P/PUMP:PM | TG-VSE056A-1 | 19504359 | 400 | 120 | 248 | 0.98 | 33 | 14 | 54 | 9 | 36 | 10 | 38 | 17 | 2019-06-29 18:30 | 1.9 | -32.6 | 54 | R | 87 | 62 | 151 | 89 |  | 0.1 | 49.4 | 50.5 | 717.38 | 717.38 | 717.38 | 717.38 | [16 empty] | 717.38 | 2.22 | 0.21 | 0.08
232 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE057 | 1S-DL-YP-ETC-DVSE-2351-VSE057 | BPS+ IOC P/PUMP NOIDA RD DALLUPURA:PL:ID | TG-VSE057A-1 | 19506474 | 400 | 120 | 249 | 0.88 | 87 | 20 | 79 | 32 | 130 | 35 | 139 | 56 | 2019-06-27 19:30 | 63.8 | -0.7 | 165 | B | 64 | 112 | 124 | 60 | 0.1 | 2.1 | 53.1 | 44.7 | 708.3 | 690 | 688.3 | 707.3 |  | 18.3 | 18.3 | 1 | [12 empty] | 708.3 | 11.3 | 0.39 | 0.22
233 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE068 | 1S-DL-YP-ETC-DVSE-2351-VSE068 | LAHORE:ID | TG-VSE068A-1 | 19500919 | 400 | 120 | 240 | 0.97 | 66 | 24 | 103 | 35 | 147 | 8 | 32 | 100 | 2019-06-30 01:00 | 14.9 | 1.9 | 147 | Y | 101 | 143 | 56 | 87 |  |  | 3.1 | 96.9 | 718.55 | 686.55 | 719.25 | 719.25 | 0.3 | 32.3 | 32.3 | [13 empty] | 719.25 | 0.35 | 0.49 | 0.17
234 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE068 | 1S-DL-YP-ETC-DVSE-2351-VSE068 | LAHORE:ID | TG-VSE068A-2 | 19500916 | 400 | 120 | 241 | 0.98 | 71 | 33 | 140 | 15 | 62 | 23 | 98 | 68 | 2019-06-05 23:30 | 8.8 | 1.4 | 140 | R | 99 | 87 | 113 | 26 |  |  | 9.1 | 90.9 | 713.54 | 719.24 | 718.24 | 719.24 | 5.3 | [15 empty] | 719.24 | 0.36 | 0.47 | 0.18
235 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE069 | 1S-DL-YP-ETC-DVSE-2351-VSE069 | INDIAN NAVAL:ID | TG-VSE069A-1 | 19500891 | 400 | 120 | 241 | 0.97 | 79 | 30 | 128 | 23 | 99 | 26 | 107 | 26 | 2019-06-01 12:00 | 26.8 | 1.4 | 136 | R | 129 | 100 | 71 | 58 |  | 0.1 | 44.1 | 55.8 | 712.55 | 718.55 | 719.25 | 719.25 | 6.3 | 0.3 | 0.3 | [13 empty] | 719.25 | 0.35 | 0.4 | 0.2
236 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE069 | 1S-DL-YP-ETC-DVSE-2351-VSE069 | INDIAN NAVAL:ID | TG-VSE069A-2 | 19500917 | 400 | 120 | 241 | 0.98 | 90 | 46 | 197 | 21 | 92 | 24 | 102 | 101 | 2019-06-30 23:30 | 14.4 | 2.8 | 205 | R | 135 | 65 | 100 | 70 |  |  | 5.9 | 94.1 | 518.59 | 719.25 | 717.55 | 691.55 | 200.26 |  |  | 27.3 | [12 empty] | 719.25 | 0.35 | 0.5 | 0.23
237 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE071 | 1S-DL-YP-ETC-DVSE-2351-VSE071 | DAINIK JANYAG CGHS:ID | TG-VSE071A-1 | 19502365 | 400 | 120 | 251 | 0.98 | 83 | 21 | 83 | 36 | 157 | 26 | 114 | 64 | 2019-06-10 23:30 | 12.1 | 1.7 | 157 | Y | 72 | 121 | 107 | 49 | 72.5 | 0.3 | 17.9 | 9.3 | 719.27 | 677.57 | 712.57 | 718.57 |  | 41.3 | 41.3 | 0.3 | [12 empty] | 719.27 | 0.33 | 0.44 | 0.21
238 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE071 | 1S-DL-YP-ETC-DVSE-2351-VSE071 | DAINIK JANYAG CGHS:ID | TG-VSE071A-2 | 19502362 | 400 | 120 | 242 | 0.98 | 58 | 18 | 76 | 17 | 74 | 23 | 98 | 23 | 2019-06-26 22:30 | 11.6 | 1.1 | 100 | Y | 105 | 96 | 100 | 9 |  |  | 18.1 | 81.9 | 719.27 | 719.27 | 719.27 | 719.27 | [16 empty] | 719.27 | 0.33 | 0.5 | 0.14
239 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE072 | 1S-DL-YP-ETC-DVSE-2351-VSE072 | CAPITAL CGHS:ID | TG-VSE072A-1 | 19502007 | 630 | 200 | 235 | 0.98 | 166 | 71 | 318 | 59 | 264 | 35 | 156 | 142 | 2019-06-11 | 24.4 | 5.5 | 318 | R | 115 | 114 | 72 | 43 |  |  | 6.6 | 93.4 | 535.27 | 531.27 | 719.27 | 636.27 | 184 | 188 | 188 | 83 | [12 empty] | 719.27 | 0.33 | 0.55 | 0.26
240 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE072 | 1S-DL-YP-ETC-DVSE-2351-VSE072 | CAPITAL CGHS:ID | TG-VSE072A-2 | 19502017 | 630 | 200 | 247 | 0.97 | 198 | 68 | 290 | 67 | 291 | 63 | 269 | 21 | 2019-06-10 22:30 | 31.7 | 7.4 | 312 | R | 114 | 88 | 98 | 26 |  |  | 1.9 | 98.1 | 435.58 | 575.58 | 543.58 | 527.28 | 283.3 | 143.3 | 143.3 | 192 | [12 empty] | 719.28 | 0.32 | 0.51 | 0.31
241 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE073 | 1S-DL-YP-ETC-DVSE-2351-VSE073 | DOCTORS S/STR 1:ID | TG-VSE073A-1 | 19502020 | 400 | 120 | 241 | 0.98 | 68 | 25 | 107 | 15 | 64 | 29 | 124 | 53 | 2019-06-29 23:00 | 18.5 | 1.9 | 130 | B | 99 | 65 | 136 | 71 |  |  | 2.8 | 97.2 | 716.5 | 717.2 | 707.2 | 717.2 | 0.3 | [15 empty] | 717.2 | 2.4 | 0.48 | 0.17
242 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE073 | 1S-DL-YP-ETC-DVSE-2351-VSE073 | DOCTORS S/STR 1:ID | TG-VSE073A-2 | 19502006 | 400 | 120 | 235 | 0.97 | 73 | 42 | 182 | 31 | 136 | 0 | 0 | 164 | 2019-06-08 23:00 | 15.2 | 0.8 | 182 | R | 153 | 147 | 0 | 153 | 100 |  |  |  | 609.57 | 645.41 | 717.41 | 717.41 | 107.44 | 72 | 72 | [13 empty] | 717.41 | 2.19 | 0.49 | 0.18
243 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE074 | 1S-DL-YP-ETC-DVSE-2351-VSE074 | DOCTORS S/S II CGHS:ID | TG-VSE074A-1 | 19502001 | 400 | 120 | 241 | 0.99 | 79 | 19 | 80 | 27 | 115 | 32 | 136 | 49 | 2019-06-30 15:00 | 7.5 | 1.1 | 157 | B | 64 | 106 | 130 | 66 |  |  | 40.2 | 59.8 | 717.4 | 703.1 | 636.1 | 717.4 |  | 14.3 | 14.3 | [13 empty] | 717.4 | 2.2 | 0.51 | 0.2
244 | 2019-06-02 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE074 | 1S-DL-YP-ETC-DVSE-2351-VSE074 | DOCTORS S/S II CGHS:ID | TG-VSE074A-2 | 19502009 | 400 | 120 | 240 | 0.97 | 107 | 32 | 137 | 36 | 155 | 39 | 167 | 26 | 2019-06-09 22:30 | 28.7 | 5 | 167 | B | 103 | 92 | 105 | 13 |  |  | 1.2 | 98.8 | 595.09 | 658.09 | 586.09 | 652.39 | 98.3 | 35.3 | 35.3 | 41 | [12 empty] | 693.39 | 2.21 | 0.55 | 0.27
245 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE075 | 1S-DL-YP-ETC-DVSE-2351-VSE075 | NEW DELHI CGHS:ID | TG-VSE075A-1 | 19502043 | 630 | 200 | 241 | 0.98 | 221 | 76 | 326 | 70 | 303 | 76 | 328 | 24 | 2019-06-29 23:30 | 33.1 | 5.1 | 344 | Y | 101 | 97 | 103 | 6 |  |  | 28.5 | 71.5 | 472.38 | 471.08 | 440.28 | 471.58 | 245.01 | 246.31 | 246.31 | 245.41 | [12 empty] | 717.39 | 2.21 | 0.53 | 0.35
246 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE076 | 1S-DL-YP-ETC-DVSE-2351-VSE076 | HIGH LAND CGHS:ID | TG-VSE076A-1 | 19502399 | 630 | 200 | 235 | 0.98 | 73 | 23 | 100 | 27 | 119 | 24 | 103 | 18 | 2019-06-15 23:30 | 14.3 | 0.5 | 125 | Y | 99 | 94 | 107 | 13 |  |  | 26 | 74 | 719.25 | 719.25 | 719.25 | 719.25 | [16 empty] | 719.25 | 0.35 | 0.56 | 0.12
247 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE076 | 1S-DL-YP-ETC-DVSE-2351-VSE076 | HIGH LAND CGHS:ID | TG-VSE076A-2 | 19500702 | 630 | 200 | 240 | 0.98 | 101 | 50 | 217 | 23 | 98 | 28 | 122 | 109 | 2019-06-11 23:30 | 16.1 | 2.3 | 224 | R | 140 | 79 | 81 | 61 |  | 0.2 | 6.7 | 93.1 | 706.56 | 719.26 | 719.26 | 719.26 | 12.3 | [15 empty] | 719.26 | 0.34 | 0.5 | 0.16
248 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE077 | 1S-DL-YP-ETC-DVSE-2351-VSE077 | MANSARA CGHS:ID | TG-VSE077A-1 | 19502049 | 400 | 120 | 239 | 0.97 | 96 | 28 | 116 | 38 | 157 | 30 | 122 | 39 | 2019-06-05 20:00 | 37.8 | 3.9 | 179 | Y | 109 | 110 | 81 | 29 |  |  | 5.6 | 94.4 | 556.25 | 596.55 | 705.55 | 664.25 | 163 | 122.3 | 122.3 | 55 | [12 empty] | 719.25 | 0.35 | 0.59 | 0.24
249 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE077 | 1S-DL-YP-ETC-DVSE-2351-VSE077 | MANSARA CGHS:ID | TG-VSE077A-2 | 19502042 | 400 | 120 | 234 | 0.98 | 88 | 23 | 99 | 30 | 144 | 35 | 155 | 51 | 2019-06-11 23:00 | 11.9 | 1.7 | 172 | B | 74 | 98 | 128 | 54 | 100 |  |  |  | 717.55 | 691.55 | 563.55 | 705.25 | 1.3 | 27.3 | 27.3 | 14 | [12 empty] | 719.25 | 0.35 | 0.51 | 0.22
250 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE078 | 1S-DL-YP-ETC-DVSE-2351-VSE078 | ABHIMAYU S/STN 1 CGHS:ID | TG-VSE078A-1 | 19502397 | 630 | 200 | 234 | 0.99 | 122 | 44 | 193 | 26 | 115 | 52 | 232 | 103 | 2019-06-30 22:30 | 14.3 | 0.9 | 259 | B | 101 | 70 | 129 | 59 |  |  | 9.2 | 90.8 | 711.25 | 719.25 | 660.25 | 719.25 | 8 | [15 empty] | 719.25 | 0.35 | 0.48 | 0.19
251 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE078 | 1S-DL-YP-ETC-DVSE-2351-VSE078 | ABHIMAYU S/STN 1 CGHS:ID | TG-VSE078A-2 | 19502398 | 400 | 120 | 235 | 0.97 | 67 | 17 | 74 | 20 | 88 | 31 | 136 | 56 | 2019-06-01 23:30 | 16.6 | 1.1 | 136 | B | 73 | 114 | 113 | 41 | 0.3 | 0.5 | 22.8 | 76.4 | 719.25 | 717.55 | 712.25 | 719.25 |  | 1.3 | 1.3 | [13 empty] | 719.25 | 0.35 | 0.55 | 0.17
252 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE079 | 1S-DL-YP-ETC-DVSE-2351-VSE079 | ABHIMANYU S/STR 2:ID | TG-VSE079A-1 | 19506471 | 400 | 120 | 241 | 0.98 | 98 | 34 | 145 | 29 | 126 | 35 | 154 | 25 | 2019-06-02 23:30 | 18.4 | 1.7 | 170 | B | 103 | 90 | 108 | 18 | 0.1 | 0.1 | 9.9 | 89.9 | 626.19 | 688.19 | 625.19 | 663.19 | 82 | 20 | 20 | 45 | [12 empty] | 708.19 | 11.41 | 0.49 | 0.25
253 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE079 | 1S-DL-YP-ETC-DVSE-2351-VSE079 | ABHIMANYU S/STR 2:ID | TG-VSE079A-2 | 19506475 | 630 | 200 | 241 | 0.99 | 89 | 56 | 257 | 18 | 75 | 14 | 61 | 188 | 2019-06-16 03:00 | 22.2 | 0.8 | 257 | R | 103 | 120 | 77 | 43 | 0.1 |  | 8.7 | 91.2 | 707.55 | 708.25 | 708.25 | 708.25 | 0.3 | [15 empty] | 708.25 | 11.35 | 0.44 | 0.14
254 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE080 | 1S-DL-YP-ETC-DVSE-2351-VSE080 | SOOCHANA:ID | TG-VSE080A-1 | 19502451 | 400 | 120 | 241 | 0.98 | 88 | 30 | 131 | 33 | 143 | 25 | 109 | 29 | 2019-06-11 | 18.2 | 1.7 | 177 | Y | 108 | 118 | 75 | 43 |  |  | 1.4 | 98.6 | 687.25 | 640.55 | 719.25 | 708.25 | 32 | 78.3 | 78.3 | 11 | [12 empty] | 719.25 | 0.35 | 0.5 | 0.22
255 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE080 | 1S-DL-YP-ETC-DVSE-2351-VSE080 | SOOCHANA:ID | TG-VSE080A-2 | 19502453 | 400 | 120 | 241 | 0.98 | 127 | 47 | 202 | 46 | 199 | 34 | 143 | 58 | 2019-06-12 00:30 | 22.1 | 2.5 | 217 | Y | 118 | 109 | 73 | 45 |  | 0.1 | 2.2 | 97.8 | 455.41 | 474.11 | 682.04 | 527.07 | 261.18 | 242.48 | 242.48 | 189.52 | [12 empty] | 716.59 | 3.01 | 0.49 | 0.32
256 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE081 | 1S-DL-YP-ETC-DVSE-2351-VSE081 | NEW PRAGATI SHEEL:ID | TG-VSE081A-1 | 19502457 | 630 | 200 | 229 | 0.99 | 119 | 43 | 196 | 23 | 103 | 54 | 246 | 126 | 2019-06-10 23:30 | 13.3 | 1.4 | 249 | B | 108 | 58 | 134 | 76 |  |  | 32.3 | 67.7 | 700.56 | 719.26 | 665.56 | 719.26 | 18.3 | [15 empty] | 719.26 | 0.34 | 0.5 | 0.19
257 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE081 | 1S-DL-YP-ETC-DVSE-2351-VSE081 | NEW PRAGATI SHEEL:ID | TG-VSE081A-2 | 19502459 | 630 | 200 | 229 | 0.99 | 162 | 48 | 220 | 67 | 308 | 46 | 210 | 93 | 2019-06-30 23:30 | 17.9 | 1.8 | 350 | Y | 98 | 135 | 66 | 69 |  |  | 25.9 | 74.1 | 670.25 | 498.25 | 714.55 | 644.55 | 49 | 221 | 221 | 74.3 | [12 empty] | 719.25 | 0.35 | 0.49 | 0.26
258 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE082 | 1S-DL-YP-ETC-DVSE-2351-VSE082 | MANGAL:ID | TG-VSE082A-1 | 19502456 | 630 | 200 | 234 | 0.99 | 127 | 41 | 181 | 37 | 162 | 48 | 208 | 40 | 2019-06-13 23:30 | 14.7 | 2.3 | 214 | B | 102 | 98 | 100 | 4 |  |  | 5.1 | 94.9 | 715.51 | 718.21 | 697.21 | 718.21 | 3 | 0.3 | 0.3 | 0.3 | [12 empty] | 718.51 | 1.09 | 0.52 | 0.2
259 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE082 | 1S-DL-YP-ETC-DVSE-2351-VSE082 | MANGAL:ID | TG-VSE082A-2 | 19502455 | 630 | 200 | 229 | 0.99 | 133 | 37 | 166 | 44 | 201 | 52 | 234 | 59 | 2019-06-10 | 15.2 | 1.8 | 267 | B | 92 | 89 | 120 | 31 |  |  | 9.3 | 90.7 | 719.25 | 715.55 | 648.25 | 717.25 |  | 3.3 | 3.3 | 2 | [12 empty] | 719.25 | 0.35 | 0.52 | 0.21
260 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE082 | 1S-DL-YP-ETC-DVSE-2351-VSE082 | MANGAL:ID | TG-VSE082A-3 | 19502460 | 630 | 200 | 229 | 0.99 | 140 | 40 | 183 | 52 | 237 | 48 | 219 | 48 | 2019-06-30 23:30 | 15.6 | 1.4 | 246 | B | 99 | 90 | 111 | 21 |  |  | 31 | 69 | 693.55 | 701.55 | 664.55 | 703.25 | 25.3 | 17.3 | 17.3 | 16 | [12 empty] | 719.25 | 0.35 | 0.51 | 0.22
261 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE082 | 1S-DL-YP-ETC-DVSE-2351-VSE082 | MANGAL:ID | TG-VSE082A-4 | 19502452 | 630 | 200 | 229 | 0.98 | 103 | 39 | 178 | 31 | 139 | 33 | 150 | 35 | 2019-06-11 23:30 | 21.2 | 1.4 | 188 | B | 81 | 105 | 114 | 33 |  |  | 18.7 | 81.3 | 719.26 | 719.26 | 718.56 | 719.26 | [16 empty] | 719.26 | 0.34 | 0.59 | 0.16
262 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE083 | 1S-DL-YP-ETC-DVSE-2351-VSE083 | SHANTI DOOT:ID | TG-VSE083A-1 | 19504133 | 630 | 200 | 240 | 0.97 | 86 | 18 | 78 | 37 | 163 | 31 | 134 | 75 | 2019-06-12 | 19.8 | 2.3 | 171 | Y | 57 | 124 | 118 | 67 |  |  | 4.4 | 95.6 | 719.25 | 719.25 | 719.25 | 719.25 | [16 empty] | 719.25 | 0.35 | 0.52 | 0.14
263 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE083 | 1S-DL-YP-ETC-DVSE-2351-VSE083 | SHANTI DOOT:ID | TG-VSE083A-2 | 19505826 | 630 | 200 | 238 | 0.98 | 30 | 16 | 70 | 0 | 0 | 14 | 59 | 65 | 2019-06-01 22:30 | 5.6 | 0.2 | 76 | R | 151 | 0 | 149 | 151 | 68.9 | 29.7 | 1.4 |  | 709.26 | 709.26 | 709.26 | 709.26 | [16 empty] | 709.26 | 10.34 | 0.5 | 0.05
264 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE084 | 1S-DL-YP-ETC-DVSE-2351-VSE084 | FANCY:ID | TG-VSE084A-1 | 19502044 | 630 | 200 | 235 | 0.99 | 69 | 12 | 52 | 30 | 129 | 28 | 120 | 73 | 2019-06-15 23:30 | 7.4 | 0.5 | 129 | Y | 42 | 137 | 121 | 95 |  |  | 1.5 | 98.5 | 717.4 | 717.4 | 717.4 | 717.4 | [16 empty] | 717.4 | 2.2 | 0.47 | 0.11
265 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE084 | 1S-DL-YP-ETC-DVSE-2351-VSE084 | FANCY:ID | TG-VSE084A-2 | 19502050 | 630 | 200 | 235 | 0.98 | 98 | 32 | 138 | 24 | 106 | 42 | 181 | 66 | 2019-06-13 23:30 | 21.2 | 0.9 | 202 | B | 87 | 88 | 125 | 38 |  |  | 8.2 | 91.8 | 717.41 | 717.41 | 713.11 | 717.41 | [16 empty] | 717.41 | 2.19 | 0.49 | 0.16
266 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE085 | 1S-DL-YP-ETC-DVSE-2351-VSE085 | CITY:ID | TG-VSE085A-1 | 19505426 | 630 | 200 | 238 | 0.97 | 253 | 116 | 495 | 57 | 246 | 79 | 339 | 218 | 2019-06-09 | 102.4 | 8 | 495 | R | 126 | 67 | 106 | 59 |  | 0.2 | 19.5 | 80.3 | 243.02 | 605.28 | 395.48 | 434.17 | 435.26 | 104.3 | 104.3 | 275.11 | 31.3 |  | 2 | 0.3 | [8 empty] | 709.58 | 10.02 | 0.49 | 0.4
267 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE086 | 1S-DL-YP-ETC-DVSE-2351-VSE086 | ABUL FAZAL:ID | TG-VSE086A-1 | 19502840 | 630 | 200 | 249 | 0.96 | 246 | 94 | 379 | 73 | 294 | 79 | 316 | 76 | 2019-06-30 02:00 | 67.6 | 12.4 | 392 | R | 120 | 84 | 95 | 36 |  | 0.1 | 8.6 | 91.3 | 102.3 | 409.11 | 289.54 | 233.11 | 573.41 | 310 | 310 | 486 | 43 |  | 0.3 | [9 empty] | 719.11 | 0.49 | 0.6 | 0.39
268 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE087 | 1S-DL-YP-ETC-DVSE-2351-VSE087 | ANEKANT:ID | TG-VSE087A-1 | 19502378 | 400 | 120 | 250 | 0.98 | 100 | 49 | 200 | 34 | 141 | 17 | 68 | 115 | 2019-06-30 | 17.4 | 1.4 | 200 | R | 136 | 94 | 70 | 66 |  | 0.5 | 13.2 | 86.3 | 500.42 | 668.12 | 718.42 | 668.12 | 218.3 | 51 | 51 | 51 | [12 empty] | 719.12 | 0.48 | 0.51 | 0.25
269 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE087 | 1S-DL-YP-ETC-DVSE-2351-VSE087 | ANEKANT:ID | TG-VSE087A-2 | 19502376 | 400 | 120 | 250 | 0.98 | 88 | 19 | 81 | 36 | 150 | 32 | 131 | 62 | 2019-06-29 23:30 | 13.5 | 1.7 | 162 | Y | 80 | 119 | 101 | 39 |  |  | 12 | 88 | 719.11 | 618.41 | 664.41 | 706.41 |  | 100.3 | 100.3 | 12.3 | [12 empty] | 719.11 | 0.49 | 0.53 | 0.22
270 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE088 | 1S-DL-YP-ETC-DVSE-2351-VSE088 | NDSE. (SRINIKETAN):ID | TG-VSE088A-1 | 19502835 | 400 | 120 | 249 | 0.97 | 119 | 62 | 251 | 40 | 167 | 17 | 68 | 159 | 2019-06-03 00:30 | 22.6 | 2.8 | 259 | R | 138 | 103 | 59 | 79 |  | 5.1 | 42.5 | 52.5 | 365.41 | 550.41 | 719.11 | 557.11 | 328 | 168.3 | 168.3 | 162 | 25.3 | [11 empty] | 719.11 | 0.49 | 0.53 | 0.3
271 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE088 | 1S-DL-YP-ETC-DVSE-2351-VSE088 | NDSE. (SRINIKETAN):ID | TG-VSE088A-2 | 19506814 | 400 | 120 | 250 | 0.98 | 91 | 29 | 116 | 34 | 133 | 28 | 110 | 21 | 2019-06-09 02:00 | 34.7 | 1.1 | 156 | B | 112 | 71 | 117 | 46 | 0.2 | 0.7 | 17.9 | 81.2 | 636.11 | 710.11 | 574.41 | 691.11 | 75 | 1 | 1 | 20 | [12 empty] | 711.11 | 8.49 | 0.5 | 0.23
272 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE089 | 1S-DL-YP-ETC-DVSE-2351-VSE089 | HINDON:ID | TG-VSE089A-1 | 19506131 | 630 | 200 | 244 | 0.98 | 112 | 36 | 153 | 36 | 151 | 39 | 165 | 13 | 2019-06-01 23:30 | 36.6 | 4.2 | 223 | Y | 89 | 104 | 107 | 18 | 0.1 | 0.2 | 20.1 | 79.7 | 710.49 | 709.19 | 710.49 | 710.49 |  | 1.3 | 1.3 | [13 empty] | 710.49 | 9.11 | 0.55 | 0.18
273 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE089 | 1S-DL-YP-ETC-DVSE-2351-VSE089 | HINDON:ID | TG-VSE089A-2 | 19506473 | 630 | 200 | 244 | 0.97 | 135 | 64 | 270 | 34 | 140 | 37 | 156 | 123 | 2019-06-11 23:00 | 48.4 | 2.6 | 270 | R | 126 | 89 | 86 | 40 |  | 0.2 | 15.7 | 84.1 | 564.19 | 709.49 | 710.19 | 704.49 | 146 | 0.3 | 0.3 | 5.3 | [12 empty] | 710.19 | 9.41 | 0.53 | 0.21
274 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE099 | 1S-DL-YP-ETC-DVSE-2351-VSE099 | MANAVASTHALI S/STN:ID | TG-VSE099A-1 | 19500374 | 630 | 200 | 240 | 0.97 | 119 | 39 | 166 | 39 | 168 | 41 | 173 | 6 | 2019-06-30 01:00 | 22.1 | 4.1 | 207 | B | 110 | 89 | 102 | 21 |  |  | 1.1 | 98.9 | 715.09 | 717.09 | 699.09 | 717.39 | 2.3 | 0.3 | 0.3 | [13 empty] | 717.39 | 2.21 | 0.57 | 0.19
275 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE099 | 1S-DL-YP-ETC-DVSE-2351-VSE099 | MANAVASTHALI S/STN:ID | TG-VSE099A-2 | 19502005 | 630 | 200 | 240 | 0.98 | 165 | 55 | 235 | 62 | 262 | 48 | 201 | 53 | 2019-06-15 23:00 | 25.8 | 5.5 | 298 | Y | 98 | 115 | 87 | 28 |  |  | 15.5 | 84.5 | 650.08 | 518.08 | 686.08 | 619.38 | 67.3 | 199.3 | 199.3 | 98 | [12 empty] | 717.38 | 2.22 | 0.52 | 0.26
276 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE137 | 1S-DL-YP-ETC-DVSE-2351-VSE137 | VISHAL:ID | TG-VSE137A-1 | 19506730 | 400 | 120 | 241 | 0.97 | 101 | 40 | 172 | 26 | 109 | 35 | 152 | 56 | 2019-06-30 23:30 | 22 | 4.9 | 173 | R | 101 | 90 | 109 | 19 |  | 0.1 | 32.2 | 67.7 | 580.57 | 646.47 | 596.47 | 617.47 | 124.5 | 59 | 59 | 88 | [12 empty] | 705.47 | 14.13 | 0.52 | 0.25
277 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE137 | 1S-DL-YP-ETC-DVSE-2351-VSE137 | VISHAL:ID | TG-VSE137A-2 | 19505245 | 400 | 120 | 242 | 0.98 | 41 | 11 | 49 | 16 | 70 | 14 | 59 | 18 | 2019-06-11 23:00 | 17.4 | 0.2 | 85 | Y | 92 | 141 | 67 | 74 |  | 0.2 | 15.5 | 84.3 | 706.11 | 706.11 | 706.11 | 706.11 | [16 empty] | 706.11 | 13.49 | 0.52 | 0.1
278 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE148 | 1S-DL-YP-ETC-DVSE-2351-VSE148 | NAV JAGRITI CGHS VASUNDHARA ENCLAVE:ID | TG-VSE148A-1 | 19505850 | 400 | 120 | 229 | 0.98 | 110 | 44 | 204 | 33 | 154 | 33 | 150 | 52 | 2019-06-11 | 24 | 1.1 | 242 | R | 118 | 98 | 84 | 34 | 0.1 | 0.1 | 6.8 | 93 | 484.27 | 594.27 | 653.27 | 595.27 | 223 | 113.3 | 113.3 | 112.3 | 0.3 | [11 empty] | 707.57 | 12.03 | 0.52 | 0.28
279 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE148 | 1S-DL-YP-ETC-DVSE-2351-VSE148 | NAV JAGRITI CGHS VASUNDHARA ENCLAVE:ID | TG-VSE148A-2 | 19505849 | 400 | 120 | 231 | 0.99 | 108 | 30 | 137 | 42 | 190 | 36 | 163 | 45 | 2019-06-09 23:30 | 18.4 | 1.6 | 205 | Y | 91 | 110 | 99 | 19 | 0.1 | 0.1 | 24.9 | 75 | 663.57 | 530.27 | 578.57 | 591.27 | 44 | 177.3 | 177.3 | 116.3 | [12 empty] | 707.57 | 12.03 | 0.51 | 0.27
280 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE164 | 1S-DL-YP-ETC-DVSE-2351-VSE164 | S/STN-7 VASUNDHRA ENCL. MVR-III :PM(SOM) | TG-VSE164A-1 | 19506313 | 400 | 120 | 247 | 0.9 | 58 | 18 | 75 | 20 | 83 | 19 | 80 | 7 | 2019-06-10 13:30 | 32.2 | -0.6 | 97 | Y | 98 | 89 | 113 | 24 |  | 0.2 | 13.1 | 86.7 | 711.04 | 711.04 | 711.04 | 711.04 | [16 empty] | 711.04 | 8.56 | 0.37 | 0.14
281 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE167 | 1S-DL-YP-ETC-DVSE-2351-VSE167 | MCD SCHOOL VASUNDHARA ENCLAVE:PM | TG-VSE167A-1 | 19504252 | 100 | 40 | 241 | 0.98 | 38 | 12 | 49 | 10 | 40 | 16 | 66 | 23 | 2019-06-06 08:00 | 9.4 | -2.1 | 73 | B | 87 | 94 | 118 | 31 |  |  | 28.7 | 71.3 | 698.25 | 702.25 | 653.25 | 698.25 | 21 | 17 | 17 | 21 |  |  | 9 | [9 empty] | 719.25 | 0.35 | 0.21 | 0.38
282 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE172 | 1S-DL-YP-ETC-DVSE-2351-VSE172 | DALLUPURA HARIZAN BASTI SUB STN. | TG-VSE172A-1 | 19500842 | 630 | 200 | 235.1541 | 0.98883 | 618.4301 | 236.7289 | 1032.3531 | 198.3688 | 869.4286 | 183.3324 | 789.2052 | 214.5939 | 2019-06-30 22:30 | [15 empty] | 1 |  |  |  | 5 |  |  |  | 583.5 |  |  |  | 130 |  |  |  | 0 | 719.5 |  | 0.69739 | 0.98164
283 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE172 | 1S-DL-YP-ETC-DVSE-2351-VSE172 | DALLUPURA HARIZAN BASTI SUB STN. | TG-VSE172A-2 | 19505698 | 630 | 200 | 244 | 0.99 | 570 | 164 | 670 | 164 | 663 | 242 | 997 | 331 | 2019-06-21 23:00 | 116.8 | 10 | 1102 | B | 90 | 93 | 117 | 27 | 0.3 | 1 | 41.8 | 56.9 | 3 | 5 |  |  | 47.46 | 53.33 | 53.33 | 20 | 662.22 | 654.35 | 541.44 | 680.16 | 4 | 4 | 161.54 | 16.52 |  |  | 5 |  | 717.08 | 2.52 | 0.66 | 0.91
284 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE172 | 1S-DL-YP-ETC-DVSE-2351-VSE172 | DALLUPURA HARIZAN BASTI SUB STN. | TG-VSE172A-3 | 19505589 | 630 | 200 | 239 | 0.98 | 444 | 124 | 541 | 154 | 680 | 165 | 723 | 165 | 2019-06-13 11:00 | 127.8 | 15.6 | 744 | R | 113 | 97 | 89 | 24 | 0.1 | 0.1 | 16.4 | 83.5 | 0.29 | 1.59 | 1.29 | 0.29 | 56.3 | 188.04 | 188.04 | 138.55 | 660.46 | 528.12 | 425.51 | 578.51 | 0.3 | [7 empty] | 718.15 | 1.45 | 0.67 | 0.7
285 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE194 | 1S-DL-YP-ETC-DVSE-2351-VSE194 | SS-Vardhman Plaza Market V.Encl | TG-VSE194A-1 | 19504991 | 630 | 200 | 230 | 0.98 | 102 | 33 | 148 | 35 | 157 | 34 | 149 | 8 | 2019-06-26 12:00 | 8.7 | 0.5 | 179 | Y | 96 | 91 | 113 | 22 |  |  | 10.1 | 89.9 | 719.25 | 719.25 | 719.25 | 719.25 | [16 empty] | 719.25 | 0.35 | 0.28 | 0.16
286 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE194 | 1S-DL-YP-ETC-DVSE-2351-VSE194 | SS-Vardhman Plaza Market V.Encl | TG-VSE194A-2 | 19504997 | 630 | 200 | 230 | 0.97 | 202 | 71 | 314 | 71 | 312 | 59 | 258 | 55 | 2019-06-14 12:00 | 35 | 6 | 325 | R | 114 | 83 | 104 | 31 |  |  | 7.3 | 92.7 | 551.38 | 674.24 | 625.36 | 623.36 | 167.45 | 44.59 | 44.59 | 95.47 | [12 empty] | 719.23 | 0.37 | 0.32 | 0.32
287 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE196 | 1S-DL-YP-ETC-DVSE-2351-VSE196 | Fire Station Dallupura MVR-3 | TG-VSE196A-1 | 19506314 | 400 | 120 | 248 | 0.96 | 25 | 4 | 16 | 17 | 69 | 4 | 18 | 52 | 2019-06-28 21:00 | 7 | -0.7 | 69 | Y | 39 | 176 | 86 | 137 |  | 0.2 | 55.5 | 44.3 | 708.3 | 708.3 | 708.3 | 708.3 | [16 empty] | 708.3 | 11.3 | 0.37 | 0.06
288 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE197 | 1S-DL-YP-ETC-DVSE-2351-VSE197 | SHEED RAJGURU WOMENS COLLEGE V. ENCL. | TG-VSE197A-1 | 19505243 | 400 | 120 | 242 | 0.99 | 31 | 9 | 38 | 6 | 25 | 16 | 68 | 38 | 2019-06-30 23:00 | 8.4 | -0.2 | 71 | B | 148 | 94 | 58 | 90 | 0.1 | 0.1 | 4.5 | 95.3 | 708.41 | 708.41 | 708.41 | 708.41 | [16 empty] | 708.41 | 11.19 | 0.34 | 0.08
289 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE198 | 1S-DL-YP-ETC-DVSE-2351-VSE198 | 1350 EWS DDA QUARTER NEW KONDLI MVR--3 | TG-VSE198A-1 | 19505983 | 630 | 200 | 250 | 0.96 | 255 | 105 | 434 | 68 | 277 | 83 | 340 | 136 | 2019-06-30 20:30 | 171 | 6.6 | 434 | R | 149 | 63 | 88 | 86 |  | 1.1 | 33.2 | 65.7 | 344.29 | 650.29 | 617.59 | 548.59 | 325.3 | 58 | 58 | 159 | 38.3 |  | 0.3 | 0.3 | [8 empty] | 708.29 | 11.31 | 0.38 | 0.41
290 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE198 | 1S-DL-YP-ETC-DVSE-2351-VSE198 | 1350 EWS DDA QUARTER NEW KONDLI MVR--3 | TG-VSE198A-2 | 19505984 | 630 | 200 | 250 | 0.97 | 243 | 56 | 225 | 91 | 369 | 95 | 388 | 155 | 2019-06-11 23:30 | 70.4 | 10 | 424 | B | 66 | 111 | 123 | 57 | 0.2 | 4 | 12 | 83.8 | 531.46 | 224.05 | 156.3 | 304.05 | 175.53 | 458.34 | 458.34 | 403.34 |  | 25 | 85.23 | [9 empty] | 707.39 | 12.21 | 0.6 | 0.39
291 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE208 | 1S-DL-YP-ETC-DVSE-2351-VSE208 | NEW ASHOK NAGAR POLICE STATION S/STN | TG-VSE208A-1 | 19506765 | 400 | 120 | 249 | 0.95 | 55 | 27 | 112 | 15 | 62 | 13 | 52 | 56 | 2019-06-30 23:30 | 16 | 1.1 | 112 | R | 126 | 97 | 77 | 49 | 0.1 | 0.4 | 21.6 | 77.8 | 707.3 | 708 | 708 | 708 | 0.3 | [15 empty] | 708 | 12 | 0.47 | 0.14
292 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE217 | 1S-DL-YP-ETC-DVSE-2351-VSE217 | Vidhata Apartment,Dallupura Village | TG-VSE217A-1 | 19506430 | 400 | 120 | 239 | 0.99 | 119 | 67 | 291 | 26 | 113 | 26 | 109 | 180 | 2019-06-03 00:30 | 15 | 0.7 | 296 | R | 123 | 89 | 89 | 34 |  | 0.6 | 48.2 | 51.1 | 353.21 | 533.51 | 590.21 | 463.51 | 321.3 | 176 | 176 | 246 | 35 | [11 empty] | 709.51 | 10.09 | 0.59 | 0.3