## Loading Condition > 80%
MIS Report of Distribution Transformer - Jun19
Jun19 1241 MAYUR VIHAR III (Loading Condition > 80% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE008 | 1S-DL-YP-ETC-DVSE-2351-VSE008 | S/STN 9 A2 PKT MVR - III:ID | TG-VSE008A-2 | 19502404 | 630 | 200 | 244 | 0.97 | 550 | 175 | 728 | 215 | 908 | 160 | 666 | 218 | 2019-06-29 23:30 | 107.6 | 28.5 | 908 | Y | 95 | 114 | 91 | 23 |  |  | 20.7 | 79.3 | 44.3 | 7.3 | 25.58 | 18 | 398.15 | 327.45 | 327.45 | 393.45 | 271.58 | 335.28 | 262.34 | 301.58 | 3.36 | 46.36 |  | 4.36 |  | 1 |  |  | 718.19 | 1.41 | 0.47 | 0.87
2 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE011 | 1S-DL-YP-ETC-DVSE-2351-VSE011 | S/STN B5 DDA JANTA FLATE:ID | TG-VSE011A-1 | 19506212 | 400 | 120 | 251 | 0.95 | 369 | 109 | 442 | 142 | 578 | 119 | 486 | 120 | 2019-06-30 23:00 | 98.2 | 29.4 | 601 | Y | 84 | 115 | 101 | 31 |  | 0.2 | 9.4 | 90.4 | 5 | 1.3 |  |  | 395.46 | 217.46 | 217.46 | 294.16 | 295 | 357 | 376 | 369.3 | 0.3 | 105 | 37.3 | 32.3 |  | 15 |  |  | 696.16 | 23.44 | 0.52 | 0.92
3 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE013 | 1S-DL-YP-ETC-DVSE-2351-VSE013 | S/STN 4 B-8 DDA JANTA FLAT:ID | TG-VSE013A-2 | 19503774 | 400 | 120 | 239 | 0.97 | 257 | 123 | 532 | 61 | 265 | 73 | 312 | 247 | 2019-06-28 23:30 | 50.8 | 18.8 | 546 | R | 137 | 76 | 87 | 61 |  | 0.1 | 15.4 | 84.6 | 3 | 164.15 | 54.3 | 33 | 199.15 | 512.59 | 512.59 | 402.45 | 480.59 | 42.3 | 151.59 | 283.59 | 36.3 | [7 empty] | 719.44 | 0.16 | 0.57 | 0.64
4 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE014 | 1S-DL-YP-ETC-DVSE-2351-VSE014 | S/STN C-1 PKT DDA JANTA FLAT:ID | TG-VSE014A-1 | 19506899 | 630 | 200 | 245 | 0.97 | 527 | 211 | 873 | 143 | 593 | 173 | 718 | 243 | 2019-06-02 | 137.8 | 25 | 897 | R | 105 | 93 | 101 | 12 | 0.1 | 0.2 | 10.8 | 88.8 |  |  | 0.3 |  | 162.16 | 223.31 | 223.31 | 136.45 | 486.03 | 478.33 | 616.01 | 567.25 | 57.51 | 4.3 | 7.24 | 2.24 | 0.24 |  |  |  | 706.34 | 13.26 | 0.61 | 0.84
5 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE015 | 1S-DL-YP-ETC-DVSE-2351-VSE015 | S/STN C-2 PKT DDA JANTA FLAT:ID | TG-VSE015A-1 | 19502405 | 630 | 200 | 243 | 0.97 | 661 | 226 | 949 | 242 | 1025 | 193 | 819 | 181 | 2019-06-30 23:00 | 132.9 | 46.9 | 1025 | Y | 104 | 104 | 92 | 12 |  |  | 31.4 | 68.6 |  |  |  |  | 24.25 | 27.25 | 27.25 | 33.25 | 550.28 | 537.58 | 577.1 | 556.58 | 130.3 | 124.3 | 68.41 | 123 | 13.41 | 29.11 |  | 5.41 | 719.04 | 0.56 | 0.6 | 1.05
6 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE037 | 1S-DL-YP-ETC-DVSE-2351-VSE037 | KNODLI VILL. PANCHYAT GHAR:PL | TG-VSE037A-1 | 19502838 | 990 | 320 | 235 | 0.98 | 794 | 199 | 859 | 357 | 1550 | 238 | 1010 | 630 | 2019-06-29 22:30 | 134 | 30.2 | 1572 | Y | 78 | 131 | 91 | 53 |  | 1.4 | 96.8 | 1.8 |  |  |  |  | 290.06 | 4.3 | 4.3 | 43.55 | 427 | 484.58 | 635.41 | 672.41 |  | 220.52 |  | 0.3 |  | 6.46 |  |  | 717.06 | 2.54 | 0.69 | 0.8
7 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE042 | 1S-DL-YP-ETC-DVSE-2351-VSE042 | B-BLK RAJBIR COLONY:PL | TG-VSE042A-1 | 19502732 | 990 | 320 | 234 | 0.98 | 763 | 212 | 912 | 286 | 1256 | 265 | 1160 | 307 | 2019-06-11 23:00 | 161.2 | 40.5 | 1318 | Y | 83 | 112 | 105 | 29 |  | 4.5 | 14.8 | 80.7 | 0.3 |  |  |  | 289.04 | 46.3 | 46.3 | 98.3 | 428.34 | 635.08 | 664.38 | 619.38 |  | 36.3 | 1.3 | [5 empty] | 718.08 | 1.52 | 0.67 | 0.77
8 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE045 | 1S-DL-YP-ETC-DVSE-2351-VSE045 | GHARAOLI VILL. OLD:PL | TG-VSE045A-1 | 19502849 | 630 | 200 | 239 | 0.98 | 504 | 175 | 731 | 151 | 624 | 177 | 724 | 104 | 2019-06-13 23:00 | 99.8 | 28.5 | 809 | R | 101 | 97 | 102 | 5 |  | 3.6 | 8.9 | 87.5 |  |  |  |  | 75.42 | 26 | 26 | 30.42 | 608.39 | 689.21 | 687.21 | 685.39 | 32 | 1 | 5.3 | [5 empty] | 716.21 | 3.39 | 0.72 | 0.8
9 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE142 | 1S-DL-YP-ETC-DVSE-2351-VSE142 | STN 3 GHAROLI DAIRY CL MVR PH-3:ID | TG-VSE142A-2 | 19502831 | 630 | 200 | 244 | 0.98 | 522 | 189 | 764 | 158 | 636 | 175 | 713 | 111 | 2019-06-11 23:30 | 89.7 | 34 | 805 | R | 112 | 87 | 102 | 25 |  | 0.2 | 80.8 | 19 |  |  |  |  | 11.3 | 133 | 133 | 36 | 660.24 | 586.54 | 657.54 | 676.54 | 48 |  | 16.3 | 7 |  |  |  |  | 719.54 | 0.06 | 0.68 | 0.83
10 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE143 | 1S-DL-YP-ETC-DVSE-2351-VSE143 | STN 4 GHAROLI DAIRY CL MVR PH-3:ID | TG-VSE143A-2 | 19502843 | 630 | 200 | 236 | 0.98 | 666 | 231 | 1013 | 213 | 934 | 222 | 974 | 68 | 2019-06-30 23:00 | 98.4 | 28.1 | 1049 | R | 107 | 96 | 97 | 11 |  |  | 18.7 | 81.3 |  |  |  |  | 28.3 | 93.17 | 93.17 | 73.3 | 557.14 | 532.32 | 484.03 | 538.49 | 103.01 | 86.56 | 96.55 | 94.56 | 26 | 2 | 6.3 | 7.3 | 714.45 | 5.15 | 0.57 | 1.06
11 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE106 | 1S-DL-YP-ETC-DVSE-2351-VSE106 | B1 BLK NEW ASHOK NAGAR:ID | TG-VSE106A-2 | 19505221 | 990 | 320 | 228 | 0.99 | 900 | 266 | 1222 | 310 | 1420 | 323 | 1479 | 233 | 2019-06-30 | 224.6 | 33.6 | 1479 | B | 90 | 104 | 106 | 16 | 0.1 | 0.1 | 10.3 | 89.5 |  |  |  |  | 70.16 | 18.3 | 18.3 | 19.3 | 616.55 | 589.14 | 598.2 | 624.44 | 7.2 | 86.47 | 91.11 | 50.17 |  |  |  |  | 694.31 | 25.29 | 0.67 | 0.91
12 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE107 | 1S-DL-YP-ETC-DVSE-2351-VSE107 | B2 BLK NEW ASHOK NAGAR:ID | TG-VSE107A-2 | 19500303 | 990 | 320 | 236 | 0.98 | 1005 | 336 | 1477 | 292 | 1291 | 377 | 1681 | 338 | 2019-06-30 01:30 | 162.7 | 50.8 | 1681 | B | 106 | 88 | 105 | 18 |  |  | 23.6 | 76.4 |  |  |  |  | 5 | 73.54 | 73.54 | 22.59 | 602.5 | 641.16 | 577.57 | 643.51 | 107.5 | 1.12 | 120.44 | 48.5 | 0.42 |  | 2.12 | 0.42 | 716.22 | 3.38 | 0.6 | 1.01
13 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE109 | 1S-DL-YP-ETC-DVSE-2351-VSE109 | C3 BLK NEW ASHOK NAGAR:ID | TG-VSE109A-2 | 19506757 | 990 | 320 | 239 | 0.98 | 842 | 284 | 1244 | 233 | 1017 | 325 | 1444 | 370 | 2019-06-29 23:30 | 206.1 | 24.3 | 1444 | B | 105 | 78 | 117 | 39 | 0.1 |  | 36.8 | 63.1 | 55.3 | 306 | 40.07 | 115 | 353.23 | 233.51 | 233.51 | 304.53 | 305.14 | 177.16 | 315.37 | 293.14 | 3 |  | 46 | 4 |  |  |  |  | 717.07 | 2.53 | 0.44 | 0.85
14 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE110 | 1S-DL-YP-ETC-DVSE-2351-VSE110 | C4 BLK NEW ASHOK NAGAR:ID | TG-VSE110A-2 | 19505232 | 990 | 320 | 229 | 0.98 | 662 | 161 | 730 | 183 | 820 | 319 | 1453 | 682 | 2019-06-11 01:00 | 188.2 | 27.8 | 1453 | B | 89 | 91 | 121 | 32 |  | 0.4 | 32.2 | 67.4 | 2.3 | 7 | 0.3 | 2 | 456.02 | 435.25 | 435.25 | 338.05 | 236.34 | 252.41 | 432.47 | 355.01 |  |  | 38 | [5 empty] | 695.06 | 24.54 | 0.62 | 0.67
15 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE112 | 1S-DL-YP-ETC-DVSE-2351-VSE112 | D BLK NEW ASHOK NAGAR:ID | TG-VSE112A-2 | 19505544 | 990 | 320 | 226 | 0.99 | 937 | 283 | 1312 | 353 | 1651 | 301 | 1418 | 301 | 2019-06-30 23:00 | 199.4 | 44.8 | 1665 | Y | 96 | 110 | 94 | 16 | 0.1 | 0.1 | 31.7 | 68.1 |  |  |  |  | 0.3 |  |  |  | 662.16 | 515.32 | 697.22 | 646.56 | 56.36 | 196.2 | 12.3 | 72.26 |  | 7.3 |  |  | 719.22 | 0.38 | 0.68 | 0.95
16 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE031 | 1S-DL-YP-ETC-DVSE-2351-VSE031 | S/STN 9 MIXED HOUSING MVR III:ID | TG-VSE031A-2 | 19506129 | 630 | 200 | 239 | 0.98 | 629 | 260 | 1119 | 179 | 750 | 190 | 801 | 347 | 2019-06-30 03:00 | 217.8 | 25.4 | 1119 | R | 106 | 101 | 93 | 13 | 0.1 | 0.4 | 56.6 | 42.9 | 0.3 | 0.3 | 3 |  | 223 | 236.3 | 236.3 | 248 | 414.3 | 441.59 | 388.29 | 428.29 | 57.45 | 16.46 | 8.16 | 19.46 | 0.3 | 0.3 |  |  | 696.15 | 23.45 | 0.49 | 1
17 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE035 | 1S-DL-YP-ETC-DVSE-2351-VSE035 | S/STN D-BLK NEW KNODLI:ID | TG-VSE035A-2 | 19505985 | 400 | 120 | 245 | 0.97 | 377 | 111 | 442 | 142 | 564 | 124 | 491 | 107 | 2019-06-13 22:30 | 102.5 | 25.4 | 589 | Y | 92 | 110 | 98 | 18 | 0.1 | 0.1 | 10.4 | 89.4 |  |  |  |  | 48.3 | 3 | 3 | 12.3 | 634.58 | 394.44 | 604.58 | 570.58 | 35.3 | 309.44 | 98.3 | 135.3 |  | 11.3 |  |  | 718.58 | 1.02 | 0.72 | 0.94
18 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE048 | 1S-DL-YP-ETC-DVSE-2351-VSE048 | DALLUPURA VILL. DURGA PARK:ID | TG-VSE048A-2 | 19505346 | 630 | 200 | 250 | 0.98 | 856 | 248 | 1012 | 296 | 1222 | 312 | 1287 | 249 | 2019-06-30 12:30 | 187 | 35.8 | 1361 | Y | 100 | 104 | 95 | 9 | 0.1 | 0.3 | 25.1 | 74.6 |  |  |  |  | 32.3 | 11 | 11 | 12.3 | 578.41 | 616.39 | 650.13 | 647.45 | 80.09 | 63.11 | 18.07 | 30.35 | 0.43 | 1.13 | 0.43 | 1.13 | 692.03 | 27.57 | 0.46 | 1.36
19 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | VASUNDHARA ENCLAVE | 1241 | VSE172 | 1S-DL-YP-ETC-DVSE-2351-VSE172 | DALLUPURA HARIZAN BASTI SUB STN. | TG-VSE172A-2 | 19505698 | 630 | 200 | 244 | 0.99 | 570 | 164 | 670 | 164 | 663 | 242 | 997 | 331 | 2019-06-21 23:00 | 116.8 | 10 | 1102 | B | 90 | 93 | 117 | 27 | 0.3 | 1 | 41.8 | 56.9 | 3 | 5 |  |  | 47.46 | 53.33 | 53.33 | 20 | 662.22 | 654.35 | 541.44 | 680.16 | 4 | 4 | 161.54 | 16.52 |  |  | 5 |  | 717.08 | 2.52 | 0.66 | 0.91

## Loading Condition > 100%
MIS Report of Distribution Transformer - Jun19
Jun19 1241 MAYUR VIHAR III (Loading Condition > 100% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE004 | 1S-DL-YP-ETC-DVSE-2351-VSE004 | S/STN 5 A2 PKT MVR-III:ID | TG-VSE004A-2 | 19503533 | 400 | 120 | 238 | 0.97 | 440 | 172 | 781 | 165 | 744 | 103 | 455 | 309 | 2019-06-03 01:00 | 64.9 | 19.9 | 781 | R | 112 | 107 | 81 | 31 | 0.5 | 34.2 | 65.1 | 0.2 | 9.59 | 11.59 | 19.25 | 10.59 | 221.29 | 253.49 | 253.49 | 268.58 | 357.2 | 339.3 | 306.35 | 366.51 | 91.3 | 95.3 | 1 | 68.55 | 37.05 | 16.35 |  | 1.4 | 717.23 | 2.37 | 0.45 | 1.1
2 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE012 | 1S-DL-YP-ETC-DVSE-2351-VSE012 | S/STN 3 B-7 DDA JANTA FLAT:ID | TG-VSE012A-1 | 19502420 | 400 | 120 | 246 | 0.96 | 477 | 197 | 833 | 104 | 433 | 176 | 751 | 366 | 2019-06-30 22:30 | 86.9 | 36.4 | 833 | R | 110 | 75 | 115 | 40 |  | 8.3 | 79.8 | 11.9 |  |  |  |  | 105.16 | 340.59 | 340.59 | 135.15 | 415.43 | 378.3 | 463.43 | 450.14 | 111.3 |  | 105.3 | 111 | 87 |  | 90 | 23 | 719.29 | 0.31 | 0.49 | 1.19
3 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE036 | 1S-DL-YP-ETC-DVSE-2351-VSE036 | SUBJI MANDI HARIJAN BASTI KNODLI:K | TG-VSE036A-2 | 19505314 | 990 | 320 | 241 | 0.97 | 1378 | 402 | 1720 | 473 | 2042 | 503 | 2176 | 406 | 2019-06-09 00:30 | 377.9 | 75.2 | 2176 | B | 100 | 96 | 103 | 7 | 0.1 | 0.2 | 24.3 | 75.4 |  |  |  |  | 24.04 | 6 | 6 | 12.04 | 439.59 | 515.58 | 447.23 | 470.4 | 158.51 | 123.56 | 157.2 | 151.4 | 36.17 | 13.17 | 41.36 | 24.47 | 659.11 | 60.49 | 0.5 | 1.39
4 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE036 | 1S-DL-YP-ETC-DVSE-2351-VSE036 | SUBJI MANDI HARIJAN BASTI KNODLI:K | TG-VSE036A-1 | 19506914 | 990 | 320 | 242 | 0.97 | 1208 | 358 | 1615 | 453 | 2059 | 396 | 1770 | 390 | 2019-06-02 23:30 | 429.4 | 81 | 2059 | Y | 101 | 105 | 94 | 11 |  | 0.1 | 2.4 | 97.4 |  |  |  |  | 1 | 0.3 | 0.3 |  | 525.25 | 478.09 | 613.45 | 536.31 | 156.3 | 180.14 | 77.04 | 151.18 | 10.24 | 34.26 | 1 | 5.3 | 693.19 | 26.41 | 0.57 | 1.22
5 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE039 | 1S-DL-YP-ETC-DVSE-2351-VSE039 | KNODLI INDAL PUBLIC SCHOOL:PM | TG-VSE039A-1 | 19506640 | 400 | 120 | 250 | 0.97 | 433 | 152 | 632 | 163 | 676 | 118 | 483 | 175 | 2019-06-30 22:30 | 110.6 | 29 | 753 | Y | 99 | 112 | 90 | 22 | 1.2 | 7.5 | 42.6 | 48.7 | [8 empty] | 427.2 | 208.51 | 508.31 | 392.5 | 210.38 | 390.37 | 172.27 | 289.38 | 56.3 | 95 | 7.3 | 12 | 694.28 | 25.32 | 0.72 | 1.08
6 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE142 | 1S-DL-YP-ETC-DVSE-2351-VSE142 | STN 3 GHAROLI DAIRY CL MVR PH-3:ID | TG-VSE142A-1 | 19504841 | 990 | 320 | 239 | 0.98 | 1052 | 333 | 1416 | 334 | 1440 | 385 | 1680 | 253 | 2019-06-30 23:30 | 167.1 | 53 | 1680 | B | 98 | 94 | 109 | 15 | 23.6 | 75.8 | 0.6 | [5 empty] | 14.27 | 35.27 | 35.27 | 16.27 | 557.03 | 580.03 | 511.1 | 554.14 | 139.41 | 101.11 | 162.04 | 139.3 | 6.3 | 1 | 36.3 | 7.3 | 717.41 | 2.19 | 0.62 | 1.06
7 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE143 | 1S-DL-YP-ETC-DVSE-2351-VSE143 | STN 4 GHAROLI DAIRY CL MVR PH-3:ID | TG-VSE143A-1 | 19503159 | 990 | 320 | 243 | 0.97 | 1001 | 425 | 1830 | 273 | 1147 | 303 | 1298 | 621 | 2019-06-02 23:00 | 189.9 | 60.4 | 1830 | R | 102 | 96 | 101 | 6 |  | 0.1 | 29.5 | 70.4 |  |  |  |  | 51.15 | 13.54 | 13.54 | 24.56 | 535.14 | 675.05 | 605.03 | 607.33 | 85 | 25.55 | 85.55 | 81.25 | 43.25 |  | 0.3 | 1 | 714.54 | 5.06 | 0.61 | 1.01
8 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE163 | 1S-DL-YP-ETC-DVSE-2351-VSE163 | S/S-2 C-BLK HARIZAN BASTI,MULLA CLY:PL | TG-VSE163A-1 | 19506207 | 630 | 200 | 240 | 0.97 | 719 | 250 | 1121 | 232 | 1049 | 238 | 1067 | 65 | 2019-06-02 23:30 | 241.6 | 57.8 | 1121 | R | 115 | 90 | 95 | 25 | 0.2 | 0.4 | 20.5 | 78.9 |  | 62 |  |  |  | 0.3 | 0.3 |  | 280.33 | 457.22 | 545.22 | 476.22 | 312.49 | 172.59 | 148.29 | 215.29 | 101.59 | 2.3 | 1 | 3.3 | 695.21 | 24.39 | 0.64 | 1.14
9 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE104 | 1S-DL-YP-ETC-DVSE-2351-VSE104 | ABLK (LOOP) NEW ASHOK NAGAR:ID | TG-VSE104A-1 | 19505992 | 990 | 320 | 237 | 0.98 | 1143 | 361 | 1633 | 395 | 1757 | 387 | 1730 | 113 | 2019-06-26 22:30 | 274.6 | 64.3 | 1769 | Y | 97 | 102 | 101 | 5 | 1.7 | 3.2 | 67.9 | 27.2 | [8 empty] | 400.52 | 306.52 | 326.25 | 353.52 | 242.32 | 315.5 | 304.47 | 281.2 | 52.37 | 73.19 | 64.49 | 60.49 | 696.01 | 23.59 | 0.7 | 1.15
10 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE108 | 1S-DL-YP-ETC-DVSE-2351-VSE108 | C2 BLK NEW ASHOK NAGAR:ID | TG-VSE108A-2 | 19506902 | 630 | 200 | 238 | 0.99 | 708 | 234 | 1037 | 222 | 968 | 252 | 1101 | 115 | 2019-06-29 23:30 | 173.2 | 32 | 1180 | B | 99 | 92 | 109 | 17 | 0.1 | 0.1 | 23.4 | 76.4 |  |  |  |  | 14.25 | 18.3 | 18.3 | 6 | 493.31 | 539.26 | 419.31 | 498.26 | 171.44 | 134.44 | 188.25 | 165.44 | 24.48 | 11.48 | 96.32 | 34.18 | 704.28 | 15.32 | 0.63 | 1.12
11 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE109 | 1S-DL-YP-ETC-DVSE-2351-VSE109 | C3 BLK NEW ASHOK NAGAR:ID | TG-VSE109A-1 | 19506026 | 630 | 200 | 239 | 0.98 | 916 | 307 | 1330 | 329 | 1439 | 280 | 1206 | 202 | 2019-06-13 23:00 | 315.6 | 21.4 | 1439 | Y | 96 | 109 | 95 | 14 |  | 0.1 | 19.5 | 80.5 | 0.3 |  | 3 |  | 250.24 | 181.45 | 181.45 | 222.44 | 277.1 | 253.25 | 311.54 | 285.21 | 91.19 | 153.54 | 82.19 | 101.48 | 85.39 | 115.58 | 83.09 | 95.09 | 705.02 | 14.58 | 0.43 | 1.45
12 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE110 | 1S-DL-YP-ETC-DVSE-2351-VSE110 | C4 BLK NEW ASHOK NAGAR:ID | TG-VSE110A-1 | 19505530 | 630 | 200 | 239 | 0.98 | 728 | 233 | 1013 | 259 | 1141 | 237 | 1032 | 119 | 2019-06-12 | 206.4 | 30.8 | 1169 | Y | 97 | 107 | 97 | 10 | 0.1 | 0.2 | 24.3 | 75.4 |  |  |  |  | 19.16 | 2.19 | 2.19 | 1.49 | 542.07 | 501.4 | 599.39 | 558.09 | 139.3 | 168.45 | 92.15 | 131.45 | 17.5 | 45.59 | 20.3 | 27 | 718.43 | 1.17 | 0.58 | 1.16
13 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE114 | 1S-DL-YP-ETC-DVSE-2351-VSE114 | E2 BLK NEW ASHOK NAGAR:ID | TG-VSE114A-2 | 19505522 | 400 | 120 | 235 | 0.99 | 513 | 170 | 769 | 181 | 822 | 162 | 733 | 78 | 2019-06-30 23:00 | 115.8 | 19.6 | 909 | Y | 104 | 104 | 92 | 12 | 0.2 | 0.9 | 59 | 39.9 | 0.54 | 1.02 | 0.49 | 0.25 |  |  |  |  | 369.11 | 372.38 | 512.22 | 429.3 | 244.34 | 223.45 | 140.29 | 191.58 | 100.17 | 117.31 | 61.16 | 93.03 | 714.56 | 5.04 | 0.61 | 1.28