## Complete Report
MIS Report of Distribution Transformer - Jun19
Jun19 1241 MAYUR VIHAR III (Complete Report)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE182 | 1S-DL-YP-ETC-DVSE-2351-VSE182 | CNG STN-1 (NAHAR) IFC PAPER MKT GAJIPUR. | TG-VSE182A-1 | 19506210 | 990 | 320 | 246 | 0.68 | 514 | 168 | 700 | 175 | 734 | 170 | 714 | 29 | 2019-06-05 13:30 | 495 | -139.2 | 734 | Y | 97 | 102 | 101 | 5 |  |  | 21.7 | 78.3 | 541.03 | 535.33 | 538.03 | 539.33 | 89 | 5.3 | 5.3 | 6.3 | 64.57 | 153.57 | 147.57 | 148.57 | [8 empty] | 695 | 25 | 0.41 | 0.52
2 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE186 | 1S-DL-YP-ETC-DVSE-2351-VSE186 | SS-7 IFC PAPER MKT GAJIPUR MV-3 | TG-VSE186A-1 | 19506714 | 400 | 120 | 245 | 0.81 | 63 | 34 | 133 | 27 | 106 | 2 | 9 | 113 | 2019-06-14 19:00 | 55.4 | -0.2 | 140 | R | 150 | 108 | 42 | 108 | 33.3 | 4.7 | 18.5 | 43.5 | 697.35 | 716.05 | 719.05 | 719.05 | 21.3 | 3 | 3 | [13 empty] | 719.05 | 0.55 | 0.38 | 0.16
3 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE188 | 1S-DL-YP-ETC-DVSE-2351-VSE188 | SS-9 IFC PAPER MKT GAJIPUR MV-3 | TG-VSE188A-1 | 19504939 | 400 | 120 | 247 | 0.82 | 80 | 26 | 104 | 25 | 100 | 30 | 120 | 18 | 2019-06-07 19:00 | 69.3 | -0.3 | 140 | R | 95 | 88 | 117 | 29 |  |  | 2.9 | 97.1 | 714.45 | 717.15 | 715.15 | 719.15 | 5 | 2.3 | 2.3 | 0.3 | [12 empty] | 719.45 | 0.15 | 0.33 | 0.2
4 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | MVR-III | 1241 | VSE204 | 1S-DL-YP-ETC-DVSE-2351-VSE204 | DP MULLA COLONY,KIOSK | TG-VSE204A-1 | 19506225 | 400 | 120 | 248 | 0.77 | 12 | 5 | 18 | 4 | 18 | 3 | 11 | 7 | 2019-06-30 04:00 | 2.6 | -0.8 | 20 | R | 117 | 113 | 71 | 46 | 0.2 | 0.2 | 1.5 | 98.1 | 696.16 | 696.16 | 696.16 | 696.16 | [16 empty] | 696.16 | 23.44 | 0.51 | 0.03
5 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE058 | 1S-DL-YP-ETC-DVSE-2351-VSE058 | S/S DALLUPURA GRID STREET LIGHT | TG-VSE058A-1 | 19505703 | 100 | 40 | 242 | 0.66 | 29 | 6 | 26 | 10 | 40 | 13 | 52 | 23 | 2019-06-06 18:30 | 26.9 | 0.8 | 52 | B | 51 | 88 | 162 | 111 |  |  | 10 | 90 | 706.4 | 692.14 | 376.45 | 691.14 | 1 | 15.26 | 15.26 | 16.26 | [12 empty] | 707.4 | 12.2 | 0.26 | 0.29
6 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE096 | 1S-DL-YP-ETC-DVSE-2351-VSE096 | ANUPAM:ID | TG-VSE096A-1 | 19500992 | 630 | 200 | 241 | 0.84 | 94 | 27 | 116 | 40 | 166 | 27 | 112 | 52 | 2019-06-02 01:00 | 72.2 | -2.8 | 166 | Y | 90 | 104 | 107 | 17 |  |  | 52.9 | 47.1 | 719.26 | 719.26 | 719.26 | 719.26 | [16 empty] | 719.26 | 0.34 | 0.57 | 0.15
7 | 2019-06-01 | 2019-06-30 23:30 | MAYUR VIHAR III | NEW ASHOK NAGAR | 1241 | VSE129 | 1S-DL-YP-ETC-DVSE-2351-VSE129 | NAGARJUNA P/M:PM | TG-VSE129A-1 | 19506729 | 100 | 40 | 242 | 0.45 | 8 | 3 | 14 | 2 | 7 | 3 | 12 | 6 | 2019-06-15 19:00 | 6.9 | -7.6 | 26 | R | 55 | 113 | 132 | 77 | 0.1 | 1.4 | 22.4 | 76 | 707.05 | 707.05 | 707.05 | 707.05 | [16 empty] | 707.05 | 12.55 | 0.2 | 0.08