## Complete Report
MIS Report of Distribution Transformer - Jun19
Jun19 1250 YAMUNA VIHAR (Complete Report)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM001 | 1S-DL-YP-ETC-DYVR-2402-YAM001 | C-4 YAMUNA VIHAR:PL | TG-YAM001A-1 | 19506333 | 990 | 320 | 244 | 0.97 | 1005 | 316 | 1339 | 264 | 1112 | 425 | 1825 | 632 | 2019-06-11 23:30 | 267.2 | 73 | 1825 | B | 105 | 91 | 105 | 14 | 0.5 | 1.9 | 13.1 | 84.5 |  |  |  |  | 129.02 | 240.32 | 240.32 | 155.02 | 529.3 | 448.17 | 513.1 | 511.04 | 31.17 | 1 | 31.11 | 23.13 |  |  | 15.58 | 0.3 | 689.49 | 30.11 | 0.5 | 1.01
2 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM002 | 1S-DL-YP-ETC-DYVR-2402-YAM002 | C-5 YAMUNA VIHAR:PG | TG-YAM002A-1 | 19503727 | 990 | 320 | 245 | 0.97 | 677 | 290 | 1210 | 193 | 840 | 194 | 809 | 387 | 2019-06-11 23:30 | 135.4 | 39.7 | 1244 | R | 119 | 88 | 93 | 31 | 75.7 | 18.3 | 5.5 | 0.5 | 7.31 | 38.31 | 22.01 | 14.01 | 331.14 | 520.53 | 520.53 | 452.14 | 361.47 | 156.58 | 191.15 | 250.07 | 15.5 | [7 empty] | 716.22 | 3.38 | 0.54 | 0.68
3 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM003 | 1S-DL-YP-ETC-DYVR-2402-YAM003 | C-6, YAMUNA VIHAR:PG | TG-YAM003A-1 | 19503253 | 990 | 320 | 241 | 0.97 | 1093 | 341 | 1454 | 360 | 1518 | 393 | 1663 | 186 | 2019-06-12 | 213.4 | 53 | 1663 | B | 107 | 96 | 97 | 11 |  | 0.1 | 66.6 | 33.3 |  | 0.3 | 2 |  | 170.58 | 250.22 | 250.22 | 222.48 | 422.07 | 371.39 | 378.46 | 390.43 | 85.4 | 77.08 | 69.27 | 80.1 | 35.26 | 14.32 | 25 | 20.3 | 714.11 | 5.49 | 0.49 | 1.1
4 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM003 | 1S-DL-YP-ETC-DYVR-2402-YAM003 | C-6, YAMUNA VIHAR:PG | TG-YAM003A-2 | 19503252 | 990 | 320 | 242 | 0.97 | 967 | 396 | 1691 | 314 | 1325 | 257 | 1088 | 526 | 2019-06-29 23:30 | 146.5 | 36.1 | 1766 | R | 117 | 98 | 85 | 32 |  |  | 43.9 | 56.1 | 3.3 | 17 | 124.2 | 21.3 | 348.47 | 449.16 | 449.16 | 429.16 | 328.29 | 239 | 185.01 | 250.3 | 24 | 13.3 |  | 17.3 | 14 |  |  |  | 718.46 | 1.14 | 0.39 | 0.98
5 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM005 | 1S-DL-YP-ETC-DYVR-2402-YAM005 | C-7, YAMUNA VIHAR:ID | TG-YAM005A-1 | 19500622 | 630 | 200 | 250 | 0.97 | 385 | 143 | 588 | 140 | 581 | 102 | 534 | 51 | 2019-06-11 23:30 | 99.4 | 12.9 | 626 | Y | 91 | 109 | 100 | 18 | 3.8 | 0.6 | 24.4 | 71.3 | 6 | 3 | 6.32 | 2.3 | 509.59 | 319.21 | 319.21 | 424.29 | 200.16 | 393.54 | 285.16 | 289.16 | [8 empty] | 716.15 | 3.45 | 0.63 | 0.61
6 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM005 | 1S-DL-YP-ETC-DYVR-2402-YAM005 | C-7, YAMUNA VIHAR:ID | TG-YAM005A-2 | 19506506 | 990 | 200 | 243.9028 | 0.97399 | 1024.4402 | 382.7983 | 1627.2672 | 301.5334 | 1259.7486 | 340.1085 | 1429.748 | 318.5777 | 2019-06-12 | [15 empty] | 0.5 |  |  |  | 128.5 |  |  |  | 525.5 |  |  |  | 63.5 |  |  |  | 1.5 | 719.5 |  | 0.53628 | 1.0348
7 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM006 | 1S-DL-YP-ETC-DYVR-2402-YAM006 | C-7/2, YAMUNA VIHAR:ID | TG-YAM006A-1 | 19500646 | 400 | 120 | 241.9969 | 0.93861 | 102.2563 | 20.9633 | 86.6395 | 52.5082 | 219.3051 | 28.7848 | 118.4025 | 119.98 | 2019-06-13 16:00 | [15 empty] | 674.5 |  |  |  | 43.5 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 718 |  | 0.48192 | 0.25564
8 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM006 | 1S-DL-YP-ETC-DYVR-2402-YAM006 | C-7/2, YAMUNA VIHAR:ID | TG-YAM006A-2 | 19502948 | 630 | 200 | 240 | 0.98 | 552 | 213 | 908 | 156 | 672 | 183 | 750 | 208 | 2019-06-12 00:30 | 90.6 | 25.8 | 1105 | B | 115 | 82 | 103 | 33 | 99.5 | 0.5 |  |  |  | 2 | 0.47 |  | 72.44 | 349.01 | 349.01 | 178.39 | 561.21 | 365.04 | 451.29 | 514 | 71 |  | 42.37 | 23.26 | 11 |  | 19.48 |  | 716.05 | 3.55 | 0.58 | 0.88
9 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM007 | 1S-DL-YP-ETC-DYVR-2402-YAM007 | C-8 YAMUNA VIHAR:ID | TG-YAM007A-1 | 19503237 | 990 | 320 | 245 | 0.97 | 960 | 313 | 1287 | 336 | 1392 | 311 | 1285 | 106 | 2019-06-30 23:30 | 172.2 | 42.7 | 1408 | Y | 97 | 110 | 93 | 17 | 4.9 | 0.5 | 55.5 | 39.1 | 1 |  | 1 | 0.3 | 50.52 | 31 | 31 | 46.29 | 143.28 | 144.2 | 137.52 | 146.51 | 19 | 37 | 10.3 | 20.3 |  | 2 |  |  | 712.58 | 7.02 | 0.56 | 0.97
10 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM007 | 1S-DL-YP-ETC-DYVR-2402-YAM007 | C-8 YAMUNA VIHAR:ID | TG-YAM007A-2 | 19503239 | 990 | 320 | 247 | 0.98 | 745 | 205 | 835 | 267 | 1096 | 273 | 1126 | 278 | 2019-06-30 23:00 | 140.6 | 33.9 | 1272 | B | 86 | 99 | 115 | 29 |  | 0.8 | 54.3 | 44.9 | 1.58 | 4.3 | 1.28 | 1.28 | 397.13 | 296.41 | 296.41 | 275.13 | 318.03 | 414.33 | 563.27 | 440.33 |  | 1.3 | 14.3 | [5 empty] | 717.14 | 2.46 | 0.6 | 0.75
11 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM007 | 1S-DL-YP-ETC-DYVR-2402-YAM007 | C-8 YAMUNA VIHAR:ID | TG-YAM007A-3 | 19506256 | 630 | 200 | 247 | 0.97 | 441 | 122 | 519 | 169 | 720 | 150 | 626 | 174 | 2019-06-07 00:30 | 117.4 | -6.8 | 720 | Y | 116 | 111 | 73 | 43 | 0.1 | 0.1 | 24.2 | 75.6 | 35.07 | 59.37 | 324.54 | 83.37 | 463.43 | 444.58 | 444.58 | 479.43 | 204.3 | 198.45 | 16 | 140.3 | 0.3 | 0.3 | [6 empty] | 703.5 | 16.1 | 0.44 | 0.7
12 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM008 | 1S-DL-YP-ETC-DYVR-2402-YAM008 | C-11 YAMUNA VIHAR:ID | TG-YAM008A-1 | 19500554 | 630 | 200 | 259 | 0.98 | 525 | 180 | 704 | 209 | 830 | 135 | 529 | 262 | 2019-06-30 00:30 | 95.2 | 23.9 | 830 | Y | 100 | 121 | 78 | 43 |  | 18.3 | 79.9 | 1.8 | 0.3 |  | 21.21 |  | 313.36 | 115.08 | 115.08 | 326.36 | 397.13 | 571.49 | 182.13 | 389.13 | 5.3 | 29.52 |  | 1 |  |  |  |  | 716.49 | 3.11 | 0.52 | 0.83
13 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM008 | 1S-DL-YP-ETC-DYVR-2402-YAM008 | C-11 YAMUNA VIHAR:ID | TG-YAM008A-2 | 19500543 | 990 | 320 | 241 | 0.97 | 772 | 340 | 1482 | 259 | 1116 | 173 | 740 | 642 | 2019-06-03 | 132.5 | 36.1 | 1582 | R | 113 | 103 | 84 | 29 |  |  | 14.9 | 85.1 | 6.3 | 9.51 | 17.3 | 7.3 | 295.07 | 348.11 | 348.11 | 363.07 | 373.22 | 358.47 | 203.24 | 346.12 | 40.2 |  |  |  | 1.3 |  |  |  | 716.49 | 3.11 | 0.53 | 0.78
14 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM009 | 1S-DL-YP-ETC-DYVR-2402-YAM009 | C-12, YAMUNA VIHAR:ID | TG-YAM009A-1 | 19501815 | 990 | 320 | 235 | 0.98 | 488 | 183 | 775 | 149 | 638 | 156 | 667 | 125 | 2019-06-09 00:30 | 89.8 | 12.5 | 855 | R | 113 | 89 | 99 | 24 |  | 0.2 | 75.8 | 24 | 51.3 | 249.29 | 158 | 132.3 | 522.36 | 430.21 | 430.21 | 500.41 | 142.27 | 36.43 | 78.33 | 83.22 | [8 empty] | 716.33 | 3.27 | 0.57 | 0.49
15 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM009 | 1S-DL-YP-ETC-DYVR-2402-YAM009 | C-12, YAMUNA VIHAR:ID | TG-YAM009A-2 | 19505309 | 400 | 120 | 235 | 0.98 | 368 | 167 | 749 | 104 | 453 | 97 | 428 | 309 | 2019-06-12 | 101.9 | 17.8 | 896 | R | 120 | 86 | 94 | 34 | 0.1 | 0.5 | 56.5 | 42.9 |  | 1 |  |  | 57.3 | 273.22 | 273.22 | 157.31 | 506.11 | 416.5 | 491.02 | 515.29 | 118.39 | 1.51 | 2.3 | 20.03 | 10.43 |  | 0.3 |  | 693.03 | 26.57 | 0.57 | 0.92
16 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM010 | 1S-DL-YP-ETC-DYVR-2402-YAM010 | B-1 YAMUNA VIHAR:ID | TG-YAM010A-1 | 19503454 | 990 | 320 | 241 | 0.97 | 526 | 187 | 809 | 159 | 681 | 180 | 780 | 116 | 2019-06-30 01:00 | 105.2 | 36.8 | 832 | B | 108 | 92 | 100 | 16 |  |  | 28.6 | 71.4 | 29.29 | 51.53 | 42.54 | 26.1 | 511.44 | 642.41 | 642.41 | 584.48 | 175.28 | 22.07 | 150.13 | 105.43 | [8 empty] | 716.41 | 3.19 | 0.59 | 0.53
17 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM010 | 1S-DL-YP-ETC-DYVR-2402-YAM010 | B-1 YAMUNA VIHAR:ID | TG-YAM010A-2 | 19503451 | 990 | 320 | 247 | 0.98 | 633 | 170 | 705 | 237 | 995 | 226 | 948 | 270 | 2019-06-29 23:30 | 100.1 | 33.1 | 1139 | Y | 82 | 119 | 99 | 37 |  | 1.8 | 86.1 | 12.1 | 14.33 |  | 0.3 |  | 511.48 | 153.57 | 153.57 | 312.57 | 190.19 | 561.43 | 350.36 | 403.43 |  | 1 | [6 empty] | 716.4 | 3.2 | 0.66 | 0.64
18 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM011 | 1S-DL-YP-ETC-DYVR-2402-YAM011 | B-2 YAMUNA VIHAR:PL | TG-YAM011A-1 | 19503247 | 990 | 320 | 240 | 0.98 | 918 | 370 | 1608 | 304 | 1309 | 244 | 1055 | 479 | 2019-06-29 23:00 | 163.4 | 70.7 | 1608 | R | 112 | 107 | 81 | 31 |  |  | 29.4 | 70.6 |  |  | 0.3 |  | 25.3 | 19 | 19 | 40 | 539.32 | 601.46 | 520.24 | 611.35 | 124.37 | 97 |  | 66.11 | 28.07 |  |  |  | 717.46 | 2.14 | 0.63 | 0.93
19 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM012 | 1S-DL-YP-ETC-DYVR-2402-YAM012 | B-4 YAMUNA VIHAR:ID | TG-YAM012A-1 | 19506327 | 990 | 320 | 248 | 0.97 | 593 | 197 | 835 | 205 | 866 | 191 | 811 | 48 | 2019-06-30 23:30 | 159.7 | 37.4 | 878 | B | 92 | 111 | 98 | 19 | 0.3 | 0.1 | 48.6 | 51 | 91.4 | 13.3 | 59.17 | 37.3 | 476.5 | 442 | 442 | 489.3 | 133.23 | 246.23 | 169.23 | 174.53 | [8 empty] | 701.53 | 18.07 | 0.55 | 0.6
20 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM012 | 1S-DL-YP-ETC-DYVR-2402-YAM012 | B-4 YAMUNA VIHAR:ID | TG-YAM012A-2 | 19503453 | 990 | 320 | 252 | 0.98 | 1044 | 348 | 1376 | 386 | 1548 | 310 | 1235 | 272 | 2019-06-10 01:30 | 220.1 | -23.6 | 1548 | Y | 104 | 100 | 96 | 8 |  |  | 6.3 | 93.7 |  |  |  |  | 19 | 35.3 | 35.3 | 29 | 576.55 | 569.25 | 591.15 | 581.55 | 110.3 | 99.57 | 67.4 | 100.28 | 6.57 | 8.3 |  | 1.59 | 713.22 | 6.38 | 0.58 | 1.05
21 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM013 | 1S-DL-YP-ETC-DYVR-2402-YAM013 | B-5 YAMUNA VIHAR:PL | TG-YAM013A-1 | 19503244 | 990 | 320 | 253 | 0.97 | 655 | 106 | 426 | 310 | 1259 | 238 | 963 | 731 | 2019-06-30 | 131.7 | 40.5 | 1259 | Y | 57 | 130 | 113 | 73 |  |  | 1.3 | 98.7 | 437.12 | 7 | 17 | 49.3 | 279.18 | 351.14 | 351.14 | 467.42 | 2 | 344.16 | 281.18 | 201.18 |  | 16 | [6 empty] | 718.3 | 1.3 | 0.52 | 0.66
22 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM013 | 1S-DL-YP-ETC-DYVR-2402-YAM013 | B-5 YAMUNA VIHAR:PL | TG-YAM013A-2 | 19506326 | 990 | 320 | 236 | 0.98 | 277 | 53 | 252 | 110 | 420 | 114 | 522 | 236 | 2019-06-02 23:00 | 61.4 | 10.6 | 552 | B | 64 | 99 | 137 | 73 | 94.2 | 5.6 | 0.2 |  | 717.37 | 556.44 | 411.48 | 584.44 | 1 | 161.53 | 161.53 | 133.53 | [12 empty] | 718.37 | 1.23 | 0.52 | 0.28
23 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM014 | 1S-DL-YP-ETC-DYVR-2402-YAM014 | DTC DEPOT YAMUNA VIHAR NO-2:ID | TG-YAM014A-1 | 19506719 | 630 | 200 | 245 | 0.97 | 509 | 74 | 314 | 236 | 1015 | 199 | 909 | 655 | 2019-06-01 19:00 | 166.2 | 39 | 1015 | Y | 70 | 128 | 102 | 58 | 0.3 | 6.7 | 60.9 | 32.1 | 4.3 |  |  |  | 537.45 | 16.58 | 16.58 | 137.25 | 168 | 648.47 | 551.46 | 572.2 |  | 44 | 3.3 | 0.3 |  | 0.3 |  |  | 710.15 | 9.45 | 0.6 | 0.81
24 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM015 | 1S-DL-YP-ETC-DYVR-2402-YAM015 | PUMPING STATION BHAJAN PURA :ID | TG-YAM015A-1 | 19504082 | 990 | 320 | 257 | 0.97 | 1166 | 412 | 1677 | 386 | 1565 | 368 | 1501 | 155 | 2019-06-01 22:30 | 291.5 | 90.5 | 1677 | R | 105 | 100 | 95 | 10 |  | 0.1 | 22.7 | 77.2 |  |  |  |  | 3 | 7 | 7 | 6.3 | 366.15 | 417.41 | 440.27 | 407.53 | 267.58 | 245.43 | 212.49 | 264.31 | 76.51 | 43.4 | 30.5 | 35.1 | 714.04 | 5.56 | 0.63 | 1.18
25 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM016 | 1S-DL-YP-ETC-DYVR-2402-YAM016 | POLICE STATION., BHAJAN PURA:ID | TG-YAM016A-1 | 19502193 | 400 | 200 | 254 | 0.97 | 137 | 25 | 101 | 66 | 298 | 46 | 187 | 171 | 2019-06-30 23:00 | 24.4 | 5.5 | 298 | Y | 57 | 147 | 95 | 90 | 5.7 | 2.5 | 46.7 | 45.1 | 703.43 | 201.15 | 493.32 | 481.28 | 14.3 | 449.43 | 449.43 | 236.45 |  | 67.15 | [10 empty] | 718.13 | 1.47 | 0.52 | 0.34
26 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM016 | 1S-DL-YP-ETC-DYVR-2402-YAM016 | POLICE STATION., BHAJAN PURA:ID | TG-YAM016A-2 | 19506051 | 400 | 120 | 243 | 0.98 | 64 | 16 | 63 | 19 | 76 | 29 | 116 | 48 | 2019-06-11 07:00 | 26 | -0.8 | 156 | B | 79 | 79 | 142 | 63 |  |  | 3.6 | 96.4 | 702.14 | 701.44 | 690.44 | 702.14 |  | 0.3 | 0.3 | [13 empty] | 702.14 | 17.46 | 0.48 | 0.16
27 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM017 | 1S-DL-YP-ETC-DYVR-2402-YAM017 | C-BLOCK GALI NO7 BHAJAN PURA:PL | TG-YAM017A-1 | 19502144 | 1600 | 500 | 241 | 0.97 | 1608 | 495 | 2096 | 452 | 1919 | 661 | 2819 | 826 | 2019-06-01 00:30 | 323.2 | 92 | 2819 | B | 103 | 89 | 108 | 19 |  |  | 5.7 | 94.3 |  | 0.3 |  |  | 124.48 | 232.37 | 232.37 | 148.05 | 540.14 | 466.05 | 482.36 | 525.18 | 36.54 | 2.44 | 89.43 | 28.05 |  |  | 6.06 | 0.28 | 701.56 | 18.04 | 0.53 | 1
28 | 2019-06-01 | 2019-06-07 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM018 | 1S-DL-YP-ETC-DYVR-2402-YAM018 | K-BLOCK GHONDA:ID | TG-YAM018A-1 | 19503720 | 990 | 320 | 256.0241 | 0.96318 | 358.9012 | 158.5136 | 619.7749 | 114.8278 | 444.9655 | 85.5598 | 328.9117 | 253.6022 | 2019-06-05 23:30 | [15 empty] | 27.5 |  |  |  | 139 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 166.5 |  | 0.68469 | 0.36253
29 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM018 | 1S-DL-YP-ETC-DYVR-2402-YAM018 | K-BLOCK GHONDA:ID | TG-YAM018A-2 | 19506573 | 630 | 200 | 247 | 0.96 | 607 | 233 | 937 | 213 | 856 | 161 | 647 | 259 | 2019-06-16 03:00 | 179 | 36.2 | 984 | R | 107 | 106 | 87 | 20 | 0.4 | 1.2 | 41 | 57.4 | 0.3 | 0.3 | 2 | 0.3 | 184.53 | 187.44 | 187.44 | 216.26 | 477.14 | 477.36 | 304.59 | 462.11 | 19.35 | 18.11 | 0.38 | 6.22 | 3.17 | 1.28 |  |  | 685.29 | 34.31 | 0.49 | 0.96
30 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM018 | 1S-DL-YP-ETC-DYVR-2402-YAM018 | K-BLOCK GHONDA:ID | TG-YAM018A-3 | 19506826 | 630 | 200 | 243.4227 | 0.97196 | 1148.6508 | 422.1685 | 1785.5963 | 415.9515 | 1762.1332 | 310.5307 | 1283.8744 | 490.4115 | 2019-06-10 00:30 | [15 empty] | 5.5 |  |  |  | 38 |  |  |  | 347 |  |  |  | 75 |  |  |  | 221.5 | 687 |  | 0.44373 | 1.8233
31 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM019 | 1S-DL-YP-ETC-DYVR-2402-YAM019 | DISPENSERY BHAJAN PURA:PL | TG-YAM019A-1 | 19502203 | 990 | 320 | 247 | 0.97 | 1465 | 446 | 1860 | 480 | 2000 | 538 | 2239 | 332 | 2019-06-01 01:00 | 290.7 | 83.9 | 2273 | B | 94 | 94 | 111 | 17 |  | 0.4 | 12.6 | 87 |  |  |  |  | 2 | 1.3 | 1.3 |  | 376.19 | 394.53 | 225.18 | 316.03 | 203.12 | 166.26 | 216.01 | 209.51 | 113.48 | 132.3 | 254 | 169.25 | 695.19 | 24.41 | 0.58 | 1.48
32 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM019 | 1S-DL-YP-ETC-DYVR-2402-YAM019 | DISPENSERY BHAJAN PURA:PL | TG-YAM019A-2 | 19506331 | 990 | 320 | 257 | 0.96 | 1158 | 372 | 1426 | 388 | 1499 | 398 | 1528 | 91 | 2019-06-01 01:00 | 395.5 | 89.6 | 1759 | Y | 96 | 100 | 104 | 8 | 0.1 | 0.1 | 1.7 | 98.1 |  |  |  |  | 40.56 | 16 | 16 | 17.3 | 498.39 | 503.3 | 498.1 | 502.3 | 116.55 | 121.59 | 121.37 | 123.36 | 25.37 | 40.38 | 51.2 | 38.31 | 682.07 | 37.53 | 0.58 | 1.17
33 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM020 | 1S-DL-YP-ETC-DYVR-2402-YAM020 | D-BLOCK, SANJAY MOHALLA:K | TG-YAM020A-1 | 19505851 | 990 | 320 | 257 | 0.96 | 908 | 289 | 1147 | 304 | 1199 | 314 | 1251 | 90 | 2019-06-30 00:30 | 298.2 | 106.2 | 1477 | Y | 98 | 108 | 94 | 14 | 0.1 | 0.1 | 19.6 | 80.3 |  |  |  |  | 24.58 | 20 | 20 | 29.58 | 657.22 | 571.35 | 542.52 | 616.22 | 16.3 | 99.45 | 68.3 | 52.3 |  | 7.3 |  |  | 698.5 | 21.1 | 0.66 | 0.92
34 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM020 | 1S-DL-YP-ETC-DYVR-2402-YAM020 | D-BLOCK, SANJAY MOHALLA:K | TG-YAM020A-2 | 19506598 | 630 | 200 | 258 | 0.94 | 761 | 222 | 897 | 328 | 1354 | 212 | 862 | 475 | 2019-06-01 01:00 | 232.2 | 29 | 1354 | Y | 80 | 103 | 117 | 37 | 0.1 | 0.7 | 43.3 | 55.9 | 131.19 |  | 4.3 | 5 | 412.58 | 396.27 | 396.27 | 423.44 | 147 | 294.5 | 403.05 | 262.33 | 0.04 |  | 0.04 | 0.04 | 0.02 | 0.06 | 0.02 | 0.02 | 691.23 | 28.37 | 0.32 | 1.21
35 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM021 | 1S-DL-YP-ETC-DYVR-2402-YAM021 | NOOR-E-ILLAHI:K | TG-YAM021A-1 | 19505649 | 990 | 320 | 253 | 0.96 | 708 | 234 | 958 | 225 | 929 | 249 | 1031 | 91 | 2019-06-02 21:00 | 272 | 74.6 | 1031 | B | 101 | 93 | 106 | 13 | 0.3 |  | 18.8 | 80.9 | 3.59 | 3.59 | 3.59 | 3.59 | 141.04 | 210.55 | 210.55 | 111.35 | 564.48 | 494.57 | 634.56 | 594.17 | [8 empty] | 709.51 | 10.09 | 0.66 | 0.71
36 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM021 | 1S-DL-YP-ETC-DYVR-2402-YAM021 | NOOR-E-ILLAHI:K | TG-YAM021A-2 | 19500192 | 990 | 320 | 241 | 0.97 | 1344 | 450 | 1882 | 428 | 1773 | 466 | 1943 | 149 | 2019-06-11 01:30 | 278.2 | 141.3 | 1948 | B | 101 | 95 | 104 | 9 |  | 0.1 | 18.6 | 81.4 | 4 | 4 | 4 | 4 |  |  |  |  | 96.24 | 162.52 | 52.24 | 91.54 | 340.21 | 387.55 | 327.12 | 361.52 | 275.03 | 161.01 | 332.12 | 258.02 | 715.48 | 4.12 | 0.7 | 1.36
37 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM021 | 1S-DL-YP-ETC-DYVR-2402-YAM021 | NOOR-E-ILLAHI:K | TG-YAM021A-3 | 19502220 | 990 | 320 | 245 | 0.96 | 890 | 323 | 1360 | 250 | 1033 | 317 | 1327 | 312 | 2019-06-11 02:00 | 213.4 | 64 | 1360 | R | 117 | 82 | 101 | 35 | 57.4 | 26.1 | 15.4 | 1.1 | 3.3 | 3.3 | 3.3 | 3.3 | 0.3 | 64.24 | 64.24 | 2.3 | 570.46 | 647.47 | 671.09 | 700.38 | 140.55 |  | 27.02 | 9.03 |  |  |  |  | 715.41 | 4.19 | 0.68 | 0.9
38 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM022 | 1S-DL-YP-ETC-DYVR-2402-YAM022 | ABDUL HAMID MARG:PL | TG-YAM022A-1 | 19505062 | 990 | 320 | 258 | 0.95 | 597 | 207 | 825 | 205 | 815 | 186 | 741 | 79 | 2019-06-29 23:00 | 179.6 | 67 | 846 | R | 102 | 104 | 94 | 10 |  |  | 1.7 | 98.3 |  |  |  |  | 299.03 | 253.33 | 253.33 | 304.03 | 418.25 | 463.55 | 302.3 | 413.25 | [8 empty] | 717.28 | 2.32 | 0.69 | 0.6
39 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM022 | 1S-DL-YP-ETC-DYVR-2402-YAM022 | ABDUL HAMID MARG:PL | TG-YAM022A-2 | 19505325 | 630 | 200 | 247 | 0.96 | 165 | 59 | 245 | 53 | 218 | 53 | 219 | 26 | 2019-06-30 01:00 | 58 | 14.8 | 317 | Y | 109 | 107 | 84 | 25 | 0.3 |  | 25.5 | 74.2 | 378.29 | 413.34 | 667.29 | 498.59 | 333.3 | 298.25 | 298.25 | 213 | [12 empty] | 711.59 | 8.01 | 0.69 | 0.26
40 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM024 | 1S-DL-YP-ETC-DYVR-2402-YAM024 | SCHOOL MOHAN PURI | TG-YAM024A-1 | 19503718 | 990 | 320 | 245 | 0.96 | 758 | 255 | 1072 | 283 | 1197 | 220 | 929 | 232 | 2019-06-11 | 170.8 | 69.2 | 1203 | Y | 99 | 115 | 87 | 28 |  | 28.3 | 25 | 46.7 |  |  |  |  | 127.25 | 46.59 | 46.59 | 129.55 | 591.02 | 658.45 | 385.32 | 588.32 |  | 12.43 | [6 empty] | 718.27 | 1.33 | 0.64 | 0.77
41 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM025 | 1S-DL-YP-ETC-DYVR-2402-YAM025 | GHONDA CHOWK:K | TG-YAM025A-1 | 19505509 | 630 | 200 | 251 | 0.97 | 535 | 173 | 703 | 184 | 753 | 178 | 731 | 43 | 2019-06-29 12:00 | 198.8 | 6.4 | 759 | B | 112 | 96 | 92 | 20 |  |  | 7.1 | 92.9 |  | 0.3 | 5 |  | 102.26 | 290.29 | 290.29 | 249.49 | 594.09 | 405.36 | 330.57 | 446.46 | 4 | 4 | 5.3 | 4 |  |  |  |  | 700.35 | 19.25 | 0.55 | 0.85
42 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM025 | 1S-DL-YP-ETC-DYVR-2402-YAM025 | GHONDA CHOWK:K | TG-YAM025A-2 | 19504714 | 990 | 320 | 249 | 0.98 | 865 | 294 | 1222 | 315 | 1294 | 257 | 1060 | 208 | 2019-06-29 16:00 | 189.9 | 47.1 | 1654 | Y | 100 | 116 | 84 | 32 | 0.5 |  | 50.6 | 48.9 | 4.05 | 4.05 | 0.3 | 0.3 | 14 | 3 | 3 | 15.05 | 676.43 | 518.2 | 655.07 | 683.48 | 21.48 | 183.57 | 1.3 | 17.13 |  | 7.14 |  |  | 716.36 | 3.24 | 0.7 | 0.87
43 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM025 | 1S-DL-YP-ETC-DYVR-2402-YAM025 | GHONDA CHOWK:K | TG-YAM025A-3 | 19503250 | 990 | 320 | 241 | 0.97 | 983 | 353 | 1488 | 348 | 1501 | 282 | 1187 | 308 | 2019-06-01 23:30 | 223.7 | 82.4 | 1501 | Y | 104 | 97 | 99 | 7 | 0.1 | 13.3 | 66.9 | 19.7 | [8 empty] | 516.54 | 605.08 | 580.23 | 577.22 | 194.13 | 108.59 | 133.44 | 139.15 | 5.3 | 2.3 | 1.3 |  | 716.37 | 3.23 | 0.71 | 0.99
44 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM025 | 1S-DL-YP-ETC-DYVR-2402-YAM025 | GHONDA CHOWK:K | TG-YAM025A-4 | 19505878 | 630 | 200 | 246 | 0.97 | 383 | 83 | 351 | 113 | 467 | 187 | 830 | 433 | 2019-06-30 14:30 | 106 | 24.6 | 830 | B | 81 | 103 | 116 | 35 | 0.2 | 0.1 | 25.8 | 73.9 | 9.59 |  |  | 1 | 632.49 | 360.48 | 360.48 | 397.18 | 59.01 | 341.01 | 460.29 | 303.31 |  |  | 0.3 | [5 empty] | 701.49 | 18.11 | 0.64 | 0.61
45 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM027 | 1S-DL-YP-ETC-DYVR-2402-YAM027 | CHET RAM MAUJ PUR:PL | TG-YAM027A-1 | 19502189 | 990 | 320 | 244 | 0.96 | 1340 | 495 | 2107 | 382 | 1612 | 463 | 1956 | 439 | 2019-06-30 03:00 | 284.1 | 134 | 2107 | R | 113 | 87 | 100 | 26 | 45.9 | 26.5 | 15.5 | 12 | [8 empty] | 172 | 479.53 | 368.25 | 340.29 | 277.28 | 172.29 | 220.25 | 229.02 | 253.36 | 50.42 | 114.14 | 133.33 | 703.04 | 16.56 | 0.62 | 1.35
46 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM027 | 1S-DL-YP-ETC-DYVR-2402-YAM027 | CHET RAM MAUJ PUR:PL | TG-YAM027A-2 | 19502235 | 990 | 320 | 248 | 0.97 | 1332 | 391 | 1649 | 491 | 2100 | 451 | 1907 | 392 | 2019-06-30 03:30 | 276 | 135.4 | 2100 | Y | 97 | 102 | 101 | 5 |  |  | 46.2 | 53.8 | [8 empty] | 374.25 | 348.26 | 344.26 | 353.56 | 248.07 | 212.47 | 232.51 | 237.05 | 80.33 | 141.52 | 125.48 | 112.04 | 703.05 | 16.55 | 0.61 | 1.35
47 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM027 | 1S-DL-YP-ETC-DYVR-2402-YAM027 | CHET RAM MAUJ PUR:PL | TG-YAM027A-3 | 19505259 | 630 | 200 | 243 | 0.97 | 672 | 221 | 988 | 219 | 957 | 232 | 1022 | 57 | 2019-06-11 01:00 | 155 | 45.6 | 1156 | B | 83 | 112 | 104 | 29 |  | 0.2 | 39.3 | 60.4 |  |  |  |  | 96 | 0.3 | 0.3 | 12 | 574.49 | 528.28 | 525.09 | 593.57 | 9.09 | 144.57 | 104.47 | 72.44 | 0.37 | 6.4 | 28.09 | 1.54 | 680.35 | 39.25 | 0.59 | 1.07
48 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM028 | 1S-DL-YP-ETC-DYVR-2402-YAM028 | SUBJI MANDI-1 MAUJ PUR | TG-YAM028A-1 | 19506745 | 1600 | 500 | 239 | 0.97 | 1717 | 582 | 2515 | 607 | 2592 | 528 | 2265 | 296 | 2019-06-30 01:30 | 466.5 | 124.5 | 2800 | Y | 96 | 109 | 94 | 15 | 0.3 | 0.1 | 20.3 | 79.2 |  |  |  |  | 38.5 | 16.2 | 16.2 | 27.5 | 586.48 | 510.35 | 593.53 | 563.04 | 58.43 | 114.03 | 53.34 | 94.51 | 4.43 | 48.06 |  | 3.19 | 689.04 | 30.56 | 0.57 | 1.07
49 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM029 | 1S-DL-YP-ETC-DYVR-2402-YAM029 | SUBJI MANDI-2 MAUJ PUR:PL | TG-YAM029A-1 | 19501764 | 990 | 320 | 249 | 0.96 | 688 | 244 | 982 | 227 | 915 | 217 | 878 | 91 | 2019-06-30 | 203.9 | 39 | 1043 | Y | 101 | 95 | 104 | 9 | 0 | 0.8 | 50.8 | 48.4 | 0 | 0 | 0 | 0 | 93.11 | 179.53 | 179.53 | 92.41 | 612.34 | 525.52 | 664.59 | 613.04 | [8 empty] | 705.45 | 14.15 | 0.71 | 0.69
50 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM030 | 1S-DL-YP-ETC-DYVR-2402-YAM030 | BABU RAM CHOWK MAUJ PUR:PL | TG-YAM030A-1 | 19502197 | 990 | 320 | 246 | 0.97 | 750 | 252 | 1051 | 243 | 998 | 255 | 1063 | 60 | 2019-06-02 16:30 | 207.6 | 34.6 | 1099 | B | 98 | 99 | 103 | 5 |  |  | 21.5 | 78.5 | 0.3 | 1 | 1 | 1 | 111.05 | 68.2 | 68.2 | 71.05 | 598.36 | 640.51 | 654.16 | 638.06 |  |  | 0.3 | [5 empty] | 710.11 | 9.49 | 0.67 | 0.76
51 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM030 | 1S-DL-YP-ETC-DYVR-2402-YAM030 | BABU RAM CHOWK MAUJ PUR:PL | TG-YAM030A-2 | 19503728 | 990 | 200 | 247 | 0.98 | 761 | 261 | 1091 | 239 | 1005 | 260 | 1099 | 91 | 2019-06-29 23:30 | 171.6 | 33.1 | 1231 | R | 103 | 94 | 102 | 9 | 0.5 | 13.8 | 68.8 | 17 |  |  |  |  | 37.25 | 98.24 | 98.24 | 57.54 | 669.14 | 612.28 | 638.13 | 652.58 | 4.13 |  | 2.15 | [5 empty] | 710.52 | 9.08 | 0.69 | 0.77
52 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM031 | 1S-DL-YP-ETC-DYVR-2402-YAM031 | SANDHYA PUBLIC SCHOOL:PL | TG-YAM031A-1 | 19504743 | 990 | 200 | 239 | 0.97 | 1043 | 366 | 1657 | 347 | 1573 | 330 | 1497 | 139 | 2019-06-29 17:30 | 210.7 | 81.9 | 1842 | R | 116 | 90 | 94 | 26 |  | 0.6 | 25.3 | 74.1 | [5 empty] | 4 | 4 |  | 342.21 | 642.46 | 637.23 | 575.23 | 285.02 | 64.3 | 72.23 | 129.53 | 85.53 | 2 | 3.3 | 8 | 713.16 | 6.44 | 0.67 | 1.05
53 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM031 | 1S-DL-YP-ETC-DYVR-2402-YAM031 | SANDHYA PUBLIC SCHOOL:PL | TG-YAM031A-2 | 19505485 | 400 | 120 | 252 | 0.95 | 375 | 79 | 326 | 128 | 536 | 167 | 701 | 326 | 2019-06-03 15:00 | 141.5 | 40.6 | 850 | Y | 59 | 105 | 136 | 77 | 0.2 | 9.2 | 66.8 | 23.8 |  |  |  |  | 539.51 | 2.3 | 2.3 | 1 | 154.41 | 627.56 | 325.38 | 668.2 |  | 63.36 | 267.22 | 25.12 |  | 0.3 | 101.32 |  | 694.32 | 25.28 | 0.65 | 0.94
54 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM033 | 1S-DL-YP-ETC-DYVR-2402-YAM033 | SUBHASH MOHALLA NO-1:PL | TG-YAM033A-1 | 19506704 | 990 | 320 | 250 | 0.96 | 1213 | 441 | 1818 | 405 | 1653 | 367 | 1495 | 280 | 2019-06-05 23:30 | 386.2 | 120.3 | 1984 | R | 108 | 101 | 91 | 17 | 0.3 | 0.4 | 44.6 | 54.7 | [8 empty] | 343.25 | 432.58 | 537.08 | 452.41 | 225.12 | 167.17 | 146.07 | 162.34 | 125.38 | 94 | 11 | 79 | 694.15 | 25.45 | 0.62 | 1.23
55 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM034 | 1S-DL-YP-ETC-DYVR-2402-YAM034 | SUBHASH MOHALLA NO.-2:PL | TG-YAM034A-1 | 19500611 | 990 | 320 | 244.9288 | 0.97155 | 935.594 | 311.6341 | 1272.2355 | 299.8014 | 1215.9371 | 324.1585 | 1308.621 | 80.8817 | 2019-06-01 23:00 | [15 empty] | 0 |  |  |  | 1.5 |  |  |  | 652 |  |  |  | 64.5 |  |  |  | 0 | 718 |  | 0.6882 | 0.94504
56 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM034 | 1S-DL-YP-ETC-DYVR-2402-YAM034 | SUBHASH MOHALLA NO.-2:PL | TG-YAM034A-2 | 19502153 | 990 | 320 | 251 | 0.96 | 1036 | 355 | 1397 | 306 | 1195 | 375 | 1484 | 257 | 2019-06-11 00:30 | 259.8 | 94.9 | 1571 | B | 109 | 83 | 107 | 26 |  | 2.9 | 96.7 | 0.3 | [5 empty] | 19.01 | 19.01 | 1 | 437.17 | 647.45 | 471.47 | 561.46 | 259.52 | 49.23 | 209.59 | 148.53 | 19 |  | 33.53 | 4.3 | 716.09 | 3.51 | 0.67 | 1.05
57 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM034 | 1S-DL-YP-ETC-DYVR-2402-YAM034 | SUBHASH MOHALLA NO.-2:PL | TG-YAM034A-3 | 19506006 | 400 | 120 | 253 | 0.97 | 371 | 160 | 652 | 160 | 669 | 51 | 207 | 454 | 2019-06-28 04:00 | 129 | 17.4 | 669 | Y | 122 | 103 | 74 | 48 | 0.2 |  | 2.3 | 97.4 | 0.3 |  | 12.02 |  | 74.28 | 301.13 | 301.13 | 295.11 | 617.43 | 389.58 | 55 | 397.3 |  | 1.3 |  | 0.3 | 0.3 | 0.3 |  |  | 693.11 | 26.49 | 0.45 | 0.93
58 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM035 | 1S-DL-YP-ETC-DYVR-2402-YAM035 | SUBHASH MOHALLA NO-4:PL | TG-YAM035A-1 | 19501017 | 990 | 320 | 247 | 0.97 | 690 | 215 | 895 | 237 | 996 | 238 | 990 | 98 | 2019-06-30 | 181.8 | 66.2 | 1038 | B | 97 | 103 | 101 | 6 |  |  | 8.7 | 91.3 |  |  |  |  | 54.55 | 36.28 | 36.28 | 37.55 | 640.09 | 658.36 | 648.39 | 657.09 | [8 empty] | 717.4 | 2.2 | 0.74 | 0.7
59 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM036 | 1S-DL-YP-ETC-DYVR-2402-YAM036 | VIJAY PARK KIOSK:K | TG-YAM036A-1 | 19505577 | 630 | 200 | 245 | 0.97 | 670 | 132 | 555 | 201 | 868 | 337 | 1426 | 764 | 2019-06-27 00:30 | 214.6 | 64 | 1426 | B | 73 | 99 | 128 | 55 | 0.6 | 26 | 73.3 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 87.07 | 1 | 1 |  | 527.4 | 492.13 | 189 | 478.49 | 0.24 | 116.3 | 263 | 131.15 |  | 5.28 | 163.11 | 5.07 | 693.59 | 26.01 | 0.65 | 1.06
60 | 2019-06-12 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM036 | 1S-DL-YP-ETC-DYVR-2402-YAM036 | VIJAY PARK KIOSK:K | TG-YAM036A-2 | 19505778 | 990 | 200 | 258 | 0.96 | 1279 | 498 | 2000 | 450 | 1787 | 331 | 1301 | 620 | 2019-06-30 00:30 | 345.4 | 142.6 | 2000 | R | 94 | 102 | 105 | 11 | 0.1 | 0.8 | 37.3 | 61.8 | 2.3 | 2.3 | 2.3 | 2.3 | 0.3 |  |  |  | 289.55 | 217.57 | 169 | 232 | 103.46 | 163.29 | 230.34 | 166.33 | 30.54 | 43.39 | 25.31 | 26.32 | 427.35 | 28.25 | 0.61 | 1.29
61 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM037 | 1S-DL-YP-ETC-DYVR-2402-YAM037 | VIJAY PARK GALI NO-14:PL | TG-YAM037A-1 | 19502141 | 990 | 320 | 249 | 0.97 | 719 | 229 | 952 | 285 | 1190 | 204 | 842 | 308 | 2019-06-11 | 164.1 | 60.4 | 1190 | Y | 104 | 113 | 84 | 29 |  | 0.1 | 31 | 68.9 | 1 | 1 | 5 | 1 | 265 | 226 | 226 | 320 | 446.14 | 483.27 | 203.43 | 391.14 |  | 1.47 | [6 empty] | 712.14 | 7.46 | 0.59 | 0.73
62 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM037 | 1S-DL-YP-ETC-DYVR-2402-YAM037 | VIJAY PARK GALI NO-14:PL | TG-YAM037A-2 | 19502139 | 990 | 320 | 232 | 0.97 | 484 | 154 | 695 | 163 | 730 | 166 | 748 | 47 | 2019-06-10 23:30 | 101.6 | 30.9 | 752 | Y | 100 | 100 | 100 | 0 |  |  | 16.5 | 83.5 | 114.15 | 135.3 | 129 | 115.3 | 539.59 | 522.02 | 522.02 | 542.45 | 55.37 | 52.19 | 50.39 | 51.36 | [8 empty] | 709.51 | 10.09 | 0.56 | 0.49
63 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM038 | 1S-DL-YP-ETC-DYVR-2402-YAM038 | VIJAY PARK SHIV SADHAN MANDIR:PL | TG-YAM038A-1 | 19505446 | 990 | 320 | 251 | 0.96 | 1068 | 456 | 1773 | 255 | 1014 | 356 | 1409 | 657 | 2019-06-12 | 323.8 | 71.7 | 1773 | R | 121 | 72 | 107 | 49 | 43.4 | 45.1 | 10.3 | 1.3 | 0.42 | 0.36 | 0.36 | 0.12 |  | 81.26 | 81.26 | 0.3 | 297.45 | 627.39 | 452.12 | 548.06 | 261.51 | 0.3 | 228.33 | 147.53 | 149.53 |  | 28.5 | 13.3 | 710.41 | 9.19 | 0.66 | 1.08
64 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM039 | 1S-DL-YP-ETC-DYVR-2402-YAM039 | VIJAY PARK NEAR NURSARY:PL | TG-YAM039A-1 | 19505323 | 630 | 200 | 258 | 0.97 | 806 | 278 | 1180 | 276 | 1165 | 253 | 1058 | 115 | 2019-06-29 01:30 | 237.8 | 49.4 | 1272 | Y | 105 | 115 | 79 | 36 | 0.2 | 0.4 | 22.1 | 77.3 |  |  |  |  | 4.51 |  |  | 3 | 426.19 | 340.11 | 554.16 | 481.42 | 170.07 | 195.25 | 47.48 | 141.02 | 103.35 | 169.16 | 25.36 | 79.08 | 704.52 | 15.08 | 0.58 | 1.28
65 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM039 | 1S-DL-YP-ETC-DYVR-2402-YAM039 | VIJAY PARK NEAR NURSARY:PL | TG-YAM039A-2 | 19505873 | 400 | 120 | 252 | 0.97 | 459 | 141 | 568 | 171 | 701 | 147 | 597 | 121 | 2019-06-01 01:00 | 115.6 | 8 | 778 | Y | 118 | 58 | 124 | 66 | 1.4 | 2.2 | 32.3 | 64.1 |  | 534.05 |  |  | 55.32 | 1.3 | 1.3 | 305.01 | 623.53 | 100.51 | 566.45 | 356.46 | 24.57 | 38.41 | 67.08 | 30.5 | 0.29 | 29.44 | 7.29 | 12.14 | 704.51 | 15.09 | 0.41 | 1.15
66 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM040 | 1S-DL-YP-ETC-DYVR-2402-YAM040 | VIJAY PARK ADARSH MOHALLA;PL | TG-YAM040A-1 | 19505645 | 1600 | 500 | 243 | 0.96 | 1023 | 383 | 1655 | 273 | 1153 | 367 | 1593 | 474 | 2019-06-11 23:30 | 300 | 84 | 1716 | B | 99 | 83 | 118 | 35 | 0.2 | 1.7 | 62.6 | 35.5 | 11.54 | 87.24 | 1.24 | 8.54 | 519.24 | 536.44 | 536.44 | 518.19 | 179.58 | 87.08 | 290.35 | 184.03 | [8 empty] | 711.16 | 8.44 | 0.54 | 0.64
67 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM041 | 1S-DL-YP-ETC-DYVR-2402-YAM041 | NALA NO.4 MAUJPUR:PL | TG-YAM041A-1 | 19503438 | 990 | 320 | 257 | 0.96 | 1171 | 376 | 1502 | 423 | 1668 | 373 | 1481 | 177 | 2019-06-12 | 257.6 | 95.7 | 1694 | Y | 94 | 108 | 98 | 14 |  | 0.2 | 64.6 | 35.2 |  |  |  |  | 22.52 | 2.3 | 2.3 | 10.52 | 547.46 | 431.15 | 526.57 | 505.28 | 126.1 | 202.45 | 160.14 | 164.33 | 16.26 | 76.44 | 15.11 | 32.21 | 713.14 | 6.46 | 0.59 | 1.18
68 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM041 | 1S-DL-YP-ETC-DYVR-2402-YAM041 | NALA NO.4 MAUJPUR:PL | TG-YAM041A-2 | 19505866 | 630 | 200 | 257 | 0.97 | 719 | 304 | 1228 | 192 | 748 | 223 | 890 | 426 | 2019-06-12 | 217.4 | 48.8 | 1228 | R | 94 | 102 | 104 | 10 | 1 | 3.2 | 36.1 | 59.7 |  |  |  |  | 69.01 | 18.3 | 18.3 | 28.01 | 573.37 | 584.44 | 531.45 | 567.44 | 39.14 | 58.57 | 96.27 | 94.25 | 11.49 | 31.3 | 27.59 | 3.31 | 693.41 | 26.19 | 0.54 | 1.14
69 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM042 | 1S-DL-YP-ETC-DYVR-2402-YAM042 | SETH BHAGWAN DAS MAUJ PUR:PL | TG-YAM042A-1 | 19506033 | 990 | 320 | 250 | 0.96 | 937 | 255 | 1028 | 396 | 1625 | 286 | 1148 | 546 | 2019-06-12 00:30 | 296.3 | 83.8 | 1657 | Y | 86 | 115 | 99 | 29 | 0.3 | 2 | 59.5 | 38.2 |  |  |  |  | 79 | 5 | 5 | 16 | 636.27 | 550.19 | 678.37 | 659.18 | 1.3 | 134.29 | 17.2 | 41.39 |  | 27.09 |  |  | 716.57 | 3.03 | 0.63 | 0.95
70 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM043 | 1S-DL-YP-ETC-DYVR-2402-YAM043 | CRESENT PUBLIC SCHOOL MAUJ PUR:PL | TG-YAM043A-1 | 19503717 | 990 | 320 | 250 | 0.97 | 1026 | 336 | 1358 | 390 | 1578 | 300 | 1200 | 329 | 2019-06-30 03:30 | 216.4 | 48.6 | 1585 | Y | 92 | 115 | 93 | 23 |  | 1.4 | 48.7 | 49.9 |  |  |  |  | 130.01 | 13.3 | 13.3 | 43.58 | 553.26 | 561.28 | 616.11 | 626.32 | 24.2 | 114.29 | 11.48 | 37.17 | 0.28 | 18.48 |  | 0.28 | 708.15 | 11.45 | 0.55 | 1.04
71 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM043 | 1S-DL-YP-ETC-DYVR-2402-YAM043 | CRESENT PUBLIC SCHOOL MAUJ PUR:PL | TG-YAM043A-2 | 19506512 | 630 | 200 | 241 | 0.95 | 704 | 251 | 1142 | 223 | 994 | 229 | 1041 | 132 | 2019-06-03 | 211 | 69.4 | 1197 | B | 110 | 106 | 83 | 27 | 1.5 | 14.3 | 66.5 | 17.7 |  |  |  |  | 1.3 | 1.3 | 1.3 | 8.3 | 428.1 | 453.22 | 358.12 | 492.15 | 216.32 | 208.33 | 93.11 | 180.29 | 47.36 | 30.23 | 12.29 | 12.34 | 693.48 | 26.12 | 0.6 | 1.12
72 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM044 | 1S-DL-YP-ETC-DYVR-2402-YAM044 | ZAMALO KA BAGH MAUJ PUR:PL | TG-YAM044A-1 | 19505148 | 990 | 200 | 253 | 0.98 | 289 | 61 | 241 | 144 | 574 | 84 | 337 | 296 | 2019-06-28 12:00 | 95 | -61 | 578 | Y | 110 | 153 | 37 | 116 |  |  | 34.8 | 65.2 | 694.4 | 501.06 | 693.4 | 690.4 |  | 191.34 | 191.34 | 4 |  | 2 | [10 empty] | 694.4 | 25.2 | 0.33 | 0.29
73 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM044 | 1S-DL-YP-ETC-DYVR-2402-YAM044 | ZAMALO KA BAGH MAUJ PUR:PL | TG-YAM044A-2 | 19505170 | 990 | 320 | 251 | 0.97 | 988 | 322 | 1365 | 401 | 1699 | 265 | 1097 | 522 | 2019-06-02 02:00 | 221.1 | 54.4 | 1699 | Y | 103 | 111 | 86 | 25 | 0.6 | 8.6 | 68.4 | 22.3 |  |  | 1 |  | 8.3 | 3.58 | 3.58 | 5.3 | 547.08 | 486.1 | 660.24 | 589.38 | 134 | 167.3 | 10.3 | 99.3 | 5 | 37 |  |  | 694.38 | 25.22 | 0.65 | 1
74 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM045 | 1S-DL-YP-ETC-DYVR-2402-YAM045 | VIJAY MOHALLA GALI NO 11:PL | TG-YAM045A-1 | 19503437 | 990 | 320 | 241 | 0.96 | 1061 | 356 | 1487 | 347 | 1456 | 358 | 1519 | 55 | 2019-06-03 03:00 | 256.1 | 123.6 | 1610 | B | 102 | 97 | 101 | 5 | 3.7 | 6.4 | 39.2 | 50.7 | [8 empty] | 478.33 | 541.47 | 511.01 | 510.36 | 212.19 | 151.28 | 185.14 | 184.39 | 22.23 | 20 | 17 | 18 | 713.15 | 6.45 | 0.68 | 1.07
75 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM046 | 1S-DL-YP-ETC-DYVR-2402-YAM046 | VILLAGE GARHI MANDU (YAMUNA BED):K | TG-YAM046A-1 | 19505800 | 630 | 200 | 251 | 0.97 | 474 | 145 | 623 | 156 | 691 | 173 | 761 | 120 | 2019-06-30 14:30 | 160.4 | 35.8 | 1128 | B | 93 | 74 | 134 | 60 | 0.4 | 0.2 | 8.3 | 91.1 | 0.3 | 12.52 |  |  | 282.01 | 496 | 496 | 246.31 | 417.02 | 190.41 | 539.22 | 453.02 |  |  | 120.11 |  |  |  | 2 |  | 699.33 | 20.27 | 0.61 | 0.75
76 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM046 | 1S-DL-YP-ETC-DYVR-2402-YAM046 | VILLAGE GARHI MANDU (YAMUNA BED):K | TG-YAM046A-2 | 19505484 | 630 | 200 | 259 | 0.97 | 427 | 138 | 552 | 134 | 528 | 155 | 615 | 78 | 2019-06-30 | 132 | 24.4 | 888 | Y | 111 | 92 | 97 | 19 | 1.3 | 2.6 | 77.7 | 18.5 | 12 | 2 | 1.3 | 1 | 87 | 364.54 | 364.54 | 208.54 | 601.28 | 324.04 | 392.34 | 490.34 |  | 6 | 0.3 |  |  | 3.3 |  |  | 700.28 | 19.32 | 0.65 | 0.68
77 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM047 | 1S-DL-YP-ETC-DYVR-2402-YAM047 | C-3 YAMUNA VIHAR:PG | TG-YAM047A-1 | 19505211 | 990 | 320 | 243 | 0.97 | 494 | 221 | 937 | 150 | 629 | 123 | 517 | 376 | 2019-06-30 | 109.8 | 28.8 | 949 | R | 121 | 103 | 76 | 45 | 0.4 | 0.8 | 81.2 | 17.6 | 4 | 9.15 | 109.12 | 12.45 | 355.41 | 526.15 | 526.15 | 569.45 | 335.32 | 159.43 | 0.3 | 112.43 | [8 empty] | 695.13 | 24.47 | 0.66 | 0.5
78 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM048 | 1S-DL-YP-ETC-DYVR-2402-YAM048 | C- 9 YAMUNA VIHAR:PG | TG-YAM048A-1 | 19504378 | 990 | 320 | 251 | 0.96 | 1178 | 351 | 1375 | 509 | 2016 | 318 | 1263 | 704 | 2019-06-11 03:30 | 292.9 | 84.6 | 2073 | Y | 88 | 130 | 81 | 49 |  | 1 | 85 | 14.1 |  |  |  |  | 117.27 | 1.3 | 1.3 | 28.27 | 467.55 | 347.22 | 562.03 | 513.09 | 113.58 | 170.44 | 40.33 | 126.24 | 17.13 | 196.57 |  | 48.33 | 716.33 | 3.27 | 0.56 | 1.19
79 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM049 | 1S-DL-YP-ETC-DYVR-2402-YAM049 | C-10 YAMUNA VIHAR:PG | TG-YAM049A-1 | 19506417 | 990 | 320 | 241 | 0.97 | 636 | 224 | 964 | 211 | 905 | 201 | 865 | 87 | 2019-06-29 23:00 | 159 | 39.7 | 1100 | Y | 92 | 100 | 108 | 16 | 0.3 | 0.1 | 4.2 | 95.4 | 96.58 | 39 | 16.43 | 29.3 | 439.05 | 477.03 | 477.03 | 481.16 | 159.01 | 179.01 | 213.48 | 184.18 | [8 empty] | 695.04 | 24.56 | 0.52 | 0.64
80 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM051 | 1S-DL-YP-ETC-DYVR-2402-YAM051 | COMMUNITY CENTER, NEAR MTNL OFFICE | TG-YAM051A-1 | 19505877 | 400 | 120 | 249 | 0.98 | 167 | 52 | 209 | 62 | 250 | 53 | 213 | 39 | 2019-06-09 15:00 | 100.8 | -9.5 | 250 | Y | 92 | 113 | 95 | 21 | 0.2 |  | 5.9 | 93.9 | 609.46 | 556.46 | 596.16 | 596.16 | 91.48 | 144.18 | 144.18 | 107.48 | 3.3 | 4 | 0.3 | 1 | [8 empty] | 705.04 | 14.56 | 0.31 | 0.42
81 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM053 | 1S-DL-YP-ETC-DYVR-2402-YAM053 | MOHANPURI NO-2 OUTSIDE SCHOOL | TG-YAM053A-1 | 19504374 | 630 | 200 | 237 | 0.98 | 773 | 254 | 1115 | 289 | 1276 | 231 | 1020 | 225 | 2019-06-11 | 130.2 | 51.5 | 1276 | Y | 107 | 106 | 87 | 20 |  |  | 3.6 | 96.4 | 0.05 | 0.05 | 0.05 | 0.05 |  |  |  |  | 318.25 | 395.25 | 614.51 | 463.56 | 322.01 | 219.1 | 99.58 | 203 | 77.14 | 103.05 | 1.51 | 50.44 | 717.45 | 2.15 | 0.62 | 1.23
82 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM053 | 1S-DL-YP-ETC-DYVR-2402-YAM053 | MOHANPURI NO-2 OUTSIDE SCHOOL | TG-YAM053A-2 | 19506332 | 400 | 120 | 233 | 0.97 | 370 | 110 | 511 | 132 | 613 | 128 | 594 | 94 | 2019-06-05 13:30 | 118.3 | 23.4 | 634 | B | 104 | 66 | 130 | 64 | 1.1 | 52.3 | 46.6 | 0.1 |  | 6 |  |  | 26 | 463.24 | 463.24 | 25 | 670.31 | 231.07 | 555.27 | 675.31 | 4.3 | 0.3 | 139.34 | 0.3 |  |  | 2.3 |  | 701.01 | 18.59 | 0.58 | 0.93
83 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM054 | 1S-DL-YP-ETC-DYVR-2402-YAM054 | SUBHASH MOHALLA NO.-3:PL | TG-YAM054A-1 | 19502226 | 990 | 320 | 257 | 0.96 | 871 | 308 | 1241 | 297 | 1199 | 266 | 1076 | 149 | 2019-06-30 23:00 | 203.1 | 76.5 | 1272 | R | 104 | 98 | 99 | 6 |  | 0.1 | 9.8 | 90.1 |  |  |  |  | 19.38 | 58.35 | 58.35 | 35.35 | 633.42 | 635.15 | 649.2 | 651.15 | 62 | 21.3 | 19 | 28.3 |  |  |  |  | 715.2 | 4.4 | 0.66 | 0.88
84 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM054 | 1S-DL-YP-ETC-DYVR-2402-YAM054 | SUBHASH MOHALLA NO.-3:PL | TG-YAM054A-2 | 19502194 | 630 | 200 | 238 | 0.97 | 470 | 131 | 565 | 176 | 760 | 163 | 700 | 173 | 2019-06-30 | 101.2 | 35.4 | 772 | Y | 90 | 102 | 107 | 17 |  |  | 18.9 | 81.1 | 0.3 | 0.3 | 0.3 | 0.3 | 322.2 | 261.33 | 261.33 | 235.55 | 392.27 | 446.44 | 532.51 | 478.52 |  | 6.3 | 2.3 | [5 empty] | 715.17 | 4.43 | 0.62 | 0.75
85 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM055 | 1S-DL-YP-ETC-DYVR-2402-YAM055 | VILLAGE GARHI MANDU KHADAR | TG-YAM055A-1 | 19506825 | 630 | 200 | 256 | 0.94 | 382 | 117 | 458 | 150 | 587 | 114 | 439 | 139 | 2019-06-13 16:30 | 237 | -7.8 | 630 | Y | 92 | 128 | 80 | 48 |  | 0.6 | 45.6 | 53.8 | 68.3 | 12 | 298.12 | 38.3 | 564.54 | 401.32 | 401.32 | 546.59 | 62.58 | 282.5 | 57.55 | 110.53 | [8 empty] | 696.22 | 23.38 | 0.5 | 0.61
86 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM060 | 1S-DL-YP-ETC-DYVR-2402-YAM060 | C-1, YVR NEAR ANAND SAGAR | TG-YAM060A-1 | 19506311 | 630 | 200 | 241 | 0.99 | 710 | 237 | 972 | 227 | 928 | 246 | 1002 | 64 | 2019-06-14 11:30 | 231.6 | 19 | 1388 | B | 108 | 87 | 106 | 21 | 0.4 | 0.2 | 23.9 | 75.5 |  |  |  |  | 11.02 | 109.31 | 109.31 | 24.02 | 482.12 | 462.39 | 468.08 | 511.38 | 153.26 | 123.27 | 137.27 | 138.57 | 58.27 | 9.3 | 72.3 | 30.3 | 705.07 | 14.53 | 0.59 | 1.13
87 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM061 | 1S-DL-YP-ETC-DYVR-2402-YAM061 | WZB-KHAJOORI FLYOVER T-Pt.(S.B. FLYOVER) | TG-YAM061A-1 | 19506698 | 400 | 120 | 246 | 0.99 | 36 | 7 | 26 | 19 | 70 | 11 | 41 | 38 | 2019-06-18 01:30 | 24.8 | -33.6 | 85 | Y | 67 | 147 | 86 | 80 |  | 0.1 | 3.4 | 96.5 | 696.49 | 696.49 | 696.49 | 696.49 | [16 empty] | 696.49 | 23.11 | 0.3 | 0.09
88 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM066 | 1S-DL-YP-ETC-DYVR-2402-YAM066 | PUMPING STATION BHAJANPURA NO-2 | TG-YAM066A-1 | 19506496 | 630 | 200 | 258 | 0.97 | 471 | 180 | 691 | 123 | 470 | 168 | 650 | 203 | 2019-06-30 14:00 | 129.4 | 28 | 813 | R | 110 | 92 | 98 | 18 | 0.2 | 0.1 | 22.6 | 77.1 | 5.42 | 5.42 | 8.42 | 5.42 | 129 | 272.17 | 272.17 | 178.57 | 553.24 | 424.07 | 445.43 | 517.27 | 14 |  | 0.3 | [5 empty] | 702.06 | 17.54 | 0.62 | 0.75
89 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO001 | 1S-DL-YP-ETC-DYVR-2404-GHO001 | A BLOCK BHAJANPURA GALI NO. -3:PL | TG-GHO001A-1 | 19504886 | 990 | 320 | 245 | 0.97 | 898 | 287 | 1205 | 356 | 1499 | 254 | 1059 | 388 | 2019-06-30 00:30 | 200.2 | 58.1 | 1499 | Y | 99 | 110 | 91 | 19 |  |  | 10.8 | 89.2 |  |  |  |  | 220.38 | 172.23 | 172.23 | 207.38 | 467.27 | 442.24 | 470.08 | 488.57 | 29.41 | 101.11 |  | 21.11 |  | 1.48 |  |  | 717.46 | 2.14 | 0.56 | 0.91
90 | 2019-06-01 | 2019-06-26 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO002 | 1S-DL-YP-ETC-DYVR-2404-GHO002 | B BLOCK BHAJANPURA:K | TG-GHO002A-1 | 19501767 | 990 | 320 | 243 | 0.99 | 1101 | 356 | 1492 | 372 | 1589 | 373 | 1583 | 94 | 2019-06-08 14:00 | 239.9 | 14 | 1755 | B | 87 | 108 | 105 | 21 | 0.2 | 15.4 | 83.7 | 0.7 | 8.55 | 8.55 | 8.55 | 8.55 | 141.44 | 42.17 | 42.17 | 81.5 | 369.21 | 387.14 | 355.19 | 371.24 | 59.39 | 125.05 | 109.24 | 112.18 | 6.51 | 22.59 | 39.02 | 12.03 | 602.07 | 21.53 | 0.56 | 1.11
91 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO002 | 1S-DL-YP-ETC-DYVR-2404-GHO002 | B BLOCK BHAJANPURA:K | TG-GHO002A-2 | 19506334 | 990 | 320 | 237.6274 | 0.97662 | 1265.9065 | 445.525 | 1989.6617 | 405.0761 | 1791.5796 | 415.3053 | 1848.2655 | 176.6956 | 2019-06-29 23:00 | [15 empty] | 11.5 |  |  |  | 21.5 |  |  |  | 472.5 |  |  |  | 156.5 |  |  |  | 42 | 704 |  | 0.54207 | 1.2787
92 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO002 | 1S-DL-YP-ETC-DYVR-2404-GHO002 | B BLOCK BHAJANPURA:K | TG-GHO002A-3 | 19504179 | 990 | 320 | 244 | 0.97 | 1251 | 421 | 1821 | 413 | 1779 | 417 | 1802 | 36 | 2019-06-02 23:30 | 247.3 | 42 | 1848 | R | 87 | 96 | 117 | 30 |  | 0.1 | 45 | 54.9 | 9.45 | 9.12 | 9.08 | 9.12 | 200.15 | 113.51 | 113.51 | 63.05 | 409.13 | 473.53 | 473.42 | 524.06 | 51.39 | 77.22 | 152.01 | 76.29 | 18.54 | 15.28 | 45.46 | 16.54 | 689.46 | 30.14 | 0.47 | 1.26
93 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO003 | 1S-DL-YP-ETC-DYVR-2404-GHO003 | D BLOCK BHAJANPURA:K | TG-GHO003A-1 | 19503712 | 990 | 320 | 245 | 0.97 | 1020 | 360 | 1530 | 318 | 1355 | 343 | 1447 | 152 | 2019-06-29 23:30 | 210.5 | 72.9 | 1533 | B | 103 | 99 | 98 | 5 |  | 0.1 | 34.9 | 65 |  |  |  |  | 26.27 | 32 | 32 | 26 | 552.5 | 578.17 | 584.47 | 575.47 | 120.37 | 108.07 | 92.07 | 112.37 | 19 | 0.3 | 6 | 4.3 | 718.54 | 1.06 | 0.6 | 1.03
94 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO003 | 1S-DL-YP-ETC-DYVR-2404-GHO003 | D BLOCK BHAJANPURA:K | TG-GHO003A-2 | 19504884 | 990 | 320 | 243 | 0.97 | 1023 | 328 | 1397 | 382 | 1640 | 313 | 1321 | 289 | 2019-06-29 23:30 | 222.3 | 81.7 | 1640 | Y | 99 | 111 | 90 | 21 |  |  | 37.4 | 62.6 |  |  |  |  | 2 | 0.3 | 0.3 | 2.3 | 647.07 | 568.1 | 675.07 | 655.37 | 69.12 | 144.1 | 15.42 | 59.39 |  | 5.29 |  | 0.33 | 718.19 | 1.41 | 0.62 | 1.03
95 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO003 | 1S-DL-YP-ETC-DYVR-2404-GHO003 | D BLOCK BHAJANPURA:K | TG-GHO003A-3 | 19501785 | 990 | 320 | 243 | 0.97 | 1020 | 324 | 1366 | 342 | 1443 | 354 | 1492 | 110 | 2019-06-30 02:00 | 200.9 | 70.7 | 1551 | B | 86 | 100 | 114 | 28 |  |  | 5.9 | 94.1 |  |  |  |  | 118.23 | 17.3 | 17.3 | 21.53 | 590.13 | 641.36 | 548.38 | 631.43 | 9.42 | 58.5 | 140.1 | 64.2 |  | 0.22 | 18.3 | 0.22 | 718.18 | 1.42 | 0.59 | 1.03
96 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO004 | 1S-DL-YP-ETC-DYVR-2404-GHO004 | 4 PUSTA BHATI WALA:PL | TG-GHO004A-1 | 19506335 | 630 | 200 | 237 | 0.97 | 463 | 143 | 638 | 184 | 805 | 136 | 602 | 188 | 2019-06-29 23:00 | 152.6 | 48.6 | 809 | Y | 90 | 118 | 92 | 28 | 0.5 | 43.1 | 56.2 | 0.2 |  |  |  |  | 173 | 3 | 3 | 40.3 | 544.38 | 697.43 | 567.18 | 677.08 |  | 16.55 | [6 empty] | 717.38 | 2.22 | 0.69 | 0.73
97 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO005 | 1S-DL-YP-ETC-DYVR-2404-GHO005 | MOTHER DAIRY B BLOCK GAMRI:PL | TG-GHO005A-1 | 19505390 | 990 | 320 | 235 | 0.97 | 398 | 166 | 731 | 134 | 587 | 98 | 432 | 259 | 2019-06-29 23:30 | 116.5 | 35.8 | 794 | R | 117 | 99 | 85 | 32 | 0.2 | 0.1 | 40.8 | 58.9 | 8 | 44 | 165.42 | 20.3 | 624.36 | 654.06 | 654.06 | 680.06 | 68.3 | 3 |  | 0.3 | [8 empty] | 701.06 | 18.54 | 0.67 | 0.4
98 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO006 | 1S-DL-YP-ETC-DYVR-2404-GHO006 | SOUTH GAMRI KIOSK:K | TG-GHO006A-1 | 19505178 | 990 | 320 | 243 | 0.97 | 546 | 155 | 660 | 213 | 906 | 179 | 768 | 213 | 2019-06-11 19:00 | 192 | 53.4 | 919 | Y | 87 | 121 | 92 | 34 |  | 0.2 | 10.8 | 89 | 15.3 |  | 1.3 |  | 633.57 | 261.23 | 261.23 | 580.34 | 46.3 | 434.34 | 34.57 | 115.23 | [8 empty] | 695.57 | 24.03 | 0.63 | 0.55
99 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO006 | 1S-DL-YP-ETC-DYVR-2404-GHO006 | SOUTH GAMRI KIOSK:K | TG-GHO006A-2 | 19505655 | 990 | 320 | 240 | 0.98 | 898 | 291 | 1259 | 270 | 1175 | 337 | 1474 | 267 | 2019-06-29 23:00 | 302.7 | 68.5 | 1528 | B | 99 | 94 | 107 | 13 | 0.1 | 0.3 | 17.2 | 82.4 |  |  |  |  | 1.29 | 16.3 | 16.3 | 1.3 | 685.32 | 692.58 | 610.3 | 677.58 | 32.27 | 10 | 103.28 | 40 |  |  | 2.3 |  | 719.28 | 0.32 | 0.68 | 0.91
100 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO007 | 1S-DL-YP-ETC-DYVR-2404-GHO007 | GAMRHI VILLAGE:PL | TG-GHO007A-1 | 19502639 | 630 | 200 | 244 | 0.97 | 599 | 196 | 830 | 176 | 747 | 228 | 965 | 191 | 2019-06-30 00:30 | 119.1 | 35.4 | 982 | B | 101 | 75 | 124 | 49 |  |  | 51.2 | 48.8 |  |  |  |  | 60.3 | 444.17 | 444.17 | 73.47 | 618.24 | 264.37 | 547.2 | 607.37 | 34 | 4 | 142.12 | 31.3 |  |  | 17.22 |  | 712.54 | 7.06 | 0.57 | 0.95
101 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO007 | 1S-DL-YP-ETC-DYVR-2404-GHO007 | GAMRHI VILLAGE:PL | TG-GHO007A-2 | 19506047 | 990 | 320 | 238 | 0.97 | 922 | 296 | 1295 | 306 | 1331 | 320 | 1390 | 83 | 2019-06-01 | 259.5 | 83.5 | 1587 | B | 93 | 102 | 105 | 12 | 0.1 | 0.1 | 25.3 | 74.5 |  |  |  |  | 10 |  |  |  | 651.55 | 616.4 | 555.55 | 636.25 | 30 | 74.45 | 127 | 56 | 0.3 | 1 | 9.3 |  | 692.25 | 27.35 | 0.71 | 0.93
102 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO008 | 1S-DL-YP-ETC-DYVR-2404-GHO008 | GAMRI KIOSK:K | TG-GHO008A-1 | 19506830 | 1600 | 500 | 243 | 0.97 | 1217 | 362 | 1489 | 394 | 1645 | 462 | 1918 | 376 | 2019-06-11 23:30 | 360.5 | 45.5 | 2132 | B | 94 | 103 | 103 | 9 | 0.1 | 2.2 | 75.2 | 22.5 | 0.3 | 0.3 | 0.3 | 0.3 | 28.2 | 14.3 | 14.3 | 19 | 672.02 | 685.22 | 640.27 | 681.22 |  | 0.3 | 26.28 | [5 empty] | 700.52 | 19.08 | 0.72 | 0.76
103 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO009 | 1S-DL-YP-ETC-DYVR-2404-GHO009 | ARVIND NAGAR PRIMARY SCHOOL GAUTAM VIHAR:PL | TG-GHO009A-1 | 19506005 | 990 | 320 | 248 | 0.97 | 969 | 366 | 1489 | 289 | 1173 | 314 | 1268 | 281 | 2019-06-12 | 238.1 | 86.7 | 1666 | R | 112 | 89 | 99 | 23 | 0.3 | 0.9 | 63 | 35.9 |  |  |  |  | 46.55 | 49.37 | 49.37 | 35.55 | 483.55 | 636.1 | 545.12 | 595.59 | 136.34 | 13 | 76.23 | 66.53 | 31.23 |  | 2.3 |  | 698.47 | 21.13 | 0.6 | 0.98
104 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO009 | 1S-DL-YP-ETC-DYVR-2404-GHO009 | ARVIND NAGAR PRIMARY SCHOOL GAUTAM VIHAR:PL | TG-GHO009A-2 | 19501821 | 990 | 320 | 235 | 0.97 | 680 | 231 | 1009 | 177 | 761 | 271 | 1172 | 358 | 2019-06-11 23:00 | 122.2 | 46.4 | 1209 | B | 91 | 99 | 111 | 20 |  | 0.2 | 32.8 | 67 | 8.54 |  |  |  | 420.14 | 236.55 | 236.55 | 338.55 | 284.38 | 476.51 | 432.11 | 374.51 |  |  | 8.23 | [5 empty] | 713.46 | 6.14 | 0.63 | 0.69
105 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO009 | 1S-DL-YP-ETC-DYVR-2404-GHO009 | ARVIND NAGAR PRIMARY SCHOOL GAUTAM VIHAR:PL | TG-GHO009A-3 | 19506522 | 630 | 200 | 244 | 0.98 | 297 | 98 | 406 | 46 | 190 | 153 | 635 | 386 | 2019-06-11 | 77.6 | 10.4 | 703 | B | 125 | 57 | 117 | 68 | 0.2 | 2 | 80.5 | 17.3 | 4 | 632.53 | 64.15 | 81.55 | 568.53 | 65.53 | 65.53 | 600.21 | 125.53 |  | 110.04 | 16.3 | [8 empty] | 698.46 | 21.14 | 0.56 | 0.47
106 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO010 | 1S-DL-YP-ETC-DYVR-2404-GHO010 | GAUTAM VIHAR KIOSK:K | TG-GHO010A-1 | 19501769 | 990 | 320 | 253 | 0.96 | 1072 | 305 | 1214 | 350 | 1412 | 417 | 1680 | 405 | 2019-06-10 23:30 | 253.9 | 97.2 | 1772 | B | 84 | 97 | 119 | 35 |  | 5.2 | 91.1 | 3.7 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 0.3 | 632.53 | 429.32 | 93.04 | 332.07 | 79.39 | 250.51 | 344.01 | 351.16 |  | 32.09 | 276.57 | 30.09 | 715.32 | 4.28 | 0.74 | 1.08
107 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO010 | 1S-DL-YP-ETC-DYVR-2404-GHO010 | GAUTAM VIHAR KIOSK:K | TG-GHO010A-2 | 19505118 | 990 | 320 | 249 | 0.97 | 871 | 289 | 1172 | 292 | 1181 | 289 | 1169 | 11 | 2019-06-09 23:30 | 224.3 | 73.9 | 1401 | B | 101 | 98 | 101 | 3 | 0.1 | 1.4 | 18.4 | 80.1 | 0.24 | 0.24 | 0.24 | 0.24 | 17.41 | 45.31 | 45.31 | 20.41 | 631.14 | 608.07 | 638.29 | 641 | 49.08 | 43.3 | 44.27 | 36.22 |  | 0.55 | 1.55 |  | 698.27 | 21.33 | 0.69 | 0.88
108 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO011 | 1S-DL-YP-ETC-DYVR-2404-GHO011 | JAI PRAKASH NO-1:PL | TG-GHO011A-1 | 19501819 | 990 | 320 | 235 | 0.97 | 957 | 326 | 1438 | 332 | 1478 | 299 | 1325 | 137 | 2019-06-29 23:30 | 172.2 | 76.5 | 1511 | Y | 101 | 103 | 96 | 7 |  | 2.2 | 77.2 | 20.7 | 0.06 | 0.06 | 0.06 | 0.06 |  | 1 | 1 |  | 657.25 | 628.26 | 686.29 | 661.55 | 59 | 85.29 | 28.26 | 54.3 |  | 1.3 |  |  | 716.31 | 3.29 | 0.65 | 0.97
109 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO012 | 1S-DL-YP-ETC-DYVR-2404-GHO012 | JAI PRAKASH NO-2:PL | TG-GHO012A-1 | 19506116 | 990 | 320 | 234 | 0.98 | 1043 | 283 | 1262 | 389 | 1749 | 371 | 1671 | 452 | 2019-06-29 23:30 | 318.1 | 72 | 1971 | Y | 83 | 115 | 102 | 32 | 0.1 | 2.9 | 20.1 | 76.8 |  |  |  |  | 1.3 |  |  |  | 690.58 | 297.29 | 525.53 | 558.1 | 5.3 | 300.29 | 157.33 | 132.48 |  | 100 | 14.32 | 7 | 697.58 | 22.02 | 0.69 | 1.05
110 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO013 | 1S-DL-YP-ETC-DYVR-2404-GHO013 | KARTAR NAGAR HOTEL WALA:PL | TG-GHO013A-1 | 19501723 | 990 | 320 | 242 | 0.97 | 1116 | 378 | 1634 | 344 | 1471 | 394 | 1711 | 213 | 2019-06-10 23:30 | 256.9 | 99.4 | 1714 | B | 98 | 99 | 103 | 5 |  | 0.9 | 82.6 | 16.5 | [8 empty] | 481.4 | 461.16 | 406.28 | 451.01 | 189.53 | 209.47 | 244.23 | 215.02 | 45.27 | 45.57 | 66.09 | 50.57 | 717 | 3 | 0.69 | 1.13
111 | 2019-06-20 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO014 | 1S-DL-YP-ETC-DYVR-2404-GHO014 | 3.5 PUSTA KARTAR NAGAR:K | TG-GHO014A-1 | 19505486 | 630 | 200 | 248 | 0.97 | 700 | 219 | 922 | 230 | 968 | 251 | 1063 | 125 | 2019-06-29 23:30 | 190 | 62.4 | 1263 | Y | 93 | 107 | 101 | 14 | 0.2 | 1.1 | 61.3 | 37.5 | [8 empty] | 195.03 | 146.33 | 178.03 | 174.03 | 40.47 | 62.3 | 52.43 | 52.3 | 1.3 | 28.17 | 6.34 | 10.47 | 237.2 | 26.4 | 0.66 | 1.11
112 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO014 | 1S-DL-YP-ETC-DYVR-2404-GHO014 | 3.5 PUSTA KARTAR NAGAR:K | TG-GHO014A-2 | 19504173 | 630 | 200 | 247 | 0.97 | 555 | 175 | 737 | 206 | 878 | 174 | 734 | 142 | 2019-06-29 23:30 | 114.5 | 47.8 | 878 | Y | 106 | 106 | 88 | 18 |  | 2.5 | 74.9 | 22.6 | 0.3 | 0.3 | 0.3 | 0.3 | 7.3 | 43.3 | 43.3 | 19 | 699.12 | 616.42 | 528.19 | 682.12 | 4 | 50.3 | 1 | 9.3 |  |  |  |  | 711.12 | 8.48 | 0.63 | 0.88
113 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO015 | 1S-DL-YP-ETC-DYVR-2404-GHO015 | JAGJEET NAGAR KIOSK:K | TG-GHO015A-1 | 19506721 | 990 | 320 | 255 | 0.97 | 1021 | 360 | 1465 | 312 | 1264 | 349 | 1420 | 183 | 2019-06-29 23:30 | 316.2 | 49 | 1504 | B | 110 | 94 | 95 | 16 | 0.9 | 0.4 | 35.6 | 63.2 | 7.01 | 7.01 | 1.3 | 1 | 3 | 4.3 | 4.3 | 10.01 | 455.29 | 608.31 | 570.33 | 561.01 | 196.16 | 68.47 | 103.46 | 113.17 | 27.33 | 0.3 | 7.3 | 4 | 689.19 | 30.41 | 0.66 | 1.03
114 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO015 | 1S-DL-YP-ETC-DYVR-2404-GHO015 | JAGJEET NAGAR KIOSK:K | TG-GHO015A-2 | 19506046 | 990 | 320 | 247 | 0.97 | 1237 | 368 | 1510 | 414 | 1693 | 456 | 1879 | 320 | 2019-06-01 07:30 | 393.9 | 75.5 | 1879 | B | 96 | 94 | 110 | 16 | 1 | 0.4 | 6.2 | 92.3 | 1 | 6.58 | 1.3 | 1 | 4 | 4.07 | 4.07 | 4 | 426.25 | 438.21 | 182.52 | 368.02 | 215.09 | 208.08 | 352.5 | 263.32 | 45.46 | 34.46 | 145.33 | 55.46 | 692.2 | 27.4 | 0.64 | 1.25
115 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO015 | 1S-DL-YP-ETC-DYVR-2404-GHO015 | JAGJEET NAGAR KIOSK:K | TG-GHO015A-3 | 19506495 | 990 | 320 | 234 | 0.97 | 927 | 316 | 1396 | 289 | 1283 | 322 | 1437 | 138 | 2019-06-06 00:30 | 269.4 | 54.1 | 1604 | Y | 111 | 91 | 98 | 20 | 0.1 | 0.8 | 13.9 | 85.1 | 1 | 1.03 | 1 | 1 | 2.24 | 36.21 | 36.21 | 15.24 | 578.41 | 635.07 | 632.05 | 642.54 | 109.43 | 19.47 | 28.19 | 33.3 | 1 | 0.3 |  |  | 692.48 | 27.12 | 0.64 | 0.94
116 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO016 | 1S-DL-YP-ETC-DYVR-2404-GHO016 | 3 RD JAGJEET NAGAR :PL | TG-GHO016A-1 | 19506707 | 990 | 200 | 242 | 0.98 | 904 | 290 | 1222 | 248 | 1029 | 365 | 1554 | 460 | 2019-06-25 18:30 | 236.4 | -1.2 | 1570 | B | 119 | 84 | 97 | 35 | 0.1 | 1.3 | 44 | 54.6 | 51.3 | 41.29 | 361.47 | 50 | 3 | 378.2 | 378.2 | 316.17 | 633.01 | 268.16 | 150.56 | 306.57 | 2 | 1.26 | 148.12 | 16.17 |  |  | 6.06 |  | 689.31 | 30.29 | 0.51 | 0.91
117 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO017 | 1S-DL-YP-ETC-DYVR-2404-GHO017 | VIJAY COLONY:PL | TG-GHO017A-1 | 19505799 | 990 | 320 | 236 | 0.98 | 1398 | 511 | 2325 | 481 | 2251 | 406 | 1841 | 452 | 2019-06-30 | 256 | -13.1 | 2325 | R | 91 | 119 | 90 | 29 | 0.5 | 8 | 81.9 | 9.7 | 0.3 | 0.3 | 83.3 | 0.3 | 39.13 | 3.3 | 3.3 | 73.3 | 641.04 | 519.56 | 590.17 | 582.47 | 33.3 | 176.08 | 35.56 | 57.56 | 2.17 | 16.3 | 1.21 | 1.51 | 716.34 | 3.26 | 0.43 | 1.41
118 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO018 | 1S-DL-YP-ETC-DYVR-2404-GHO018 | USMANPUR PUSTA NO-2:PL | TG-GHO018A-1 | 19506644 | 630 | 200 | 244 | 0.95 | 544 | 127 | 535 | 291 | 1198 | 126 | 524 | 669 | 2019-06-15 16:00 | 205.4 | 10.6 | 1198 | Y | 90 | 116 | 95 | 26 | 0.1 | 0.1 | 55.2 | 44.6 | 0.3 | 0.3 | 0.3 | 0.3 | 14 |  |  | 1.3 | 668.38 | 503.13 | 655.44 | 678.38 | 7 | 178.25 | 13.3 | 9.3 |  | 8 |  |  | 690.08 | 29.52 | 0.72 | 0.86
119 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO018 | 1S-DL-YP-ETC-DYVR-2404-GHO018 | USMANPUR PUSTA NO-2:PL | TG-GHO018A-2 | 19504176 | 630 | 200 | 237 | 0.98 | 546 | 153 | 668 | 138 | 605 | 255 | 1121 | 488 | 2019-06-27 23:30 | 102.6 | 42.8 | 1121 | B | 82 | 82 | 136 | 54 |  | 0.1 | 9.3 | 90.5 |  |  |  |  | 51.26 | 33.56 | 33.56 |  | 660.42 | 678.12 | 276.52 | 705.38 |  |  | 370.28 | 6.3 |  |  | 64.48 |  | 712.08 | 7.52 | 0.71 | 0.87
120 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO019 | 1S-DL-YP-ETC-DYVR-2404-GHO019 | KHADDEY WALI MASJID:PM | TG-GHO019A-1 | 19506336 | 630 | 200 | 244 | 0.97 | 935 | 315 | 1341 | 340 | 1456 | 279 | 1189 | 233 | 2019-06-22 01:30 | 325.6 | 85.6 | 1456 | Y | 103 | 106 | 91 | 15 | 0.1 | 0.2 | 4.1 | 95.7 | [8 empty] | 55.52 | 61.18 | 183.39 | 79.1 | 247.11 | 237.16 | 331.44 | 289.24 | 394.39 | 399.08 | 182.19 | 329.08 | 697.42 | 22.18 | 0.67 | 1.48
121 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO020 | 1S-DL-YP-ETC-DYVR-2404-GHO020 | MONI BABA MANDIR:K | TG-GHO020A-1 | 19504129 | 990 | 320 | 240 | 0.97 | 1086 | 419 | 1906 | 309 | 1379 | 358 | 1613 | 457 | 2019-06-30 23:30 | 231.8 | 97.9 | 1906 | R | 111 | 86 | 103 | 25 |  | 4.3 | 83.6 | 12.1 | 1.3 | 1.3 | 1.3 | 1.3 |  | 13 | 13 | 1.3 | 407.56 | 616.53 | 460.5 | 503.49 | 206.56 | 81.58 | 173.26 | 179.54 | 96.59 |  | 71.05 | 26.38 | 713.21 | 6.39 | 0.65 | 1.1
122 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO020 | 1S-DL-YP-ETC-DYVR-2404-GHO020 | MONI BABA MANDIR:K | TG-GHO020A-2 | 19500582 | 630 | 200 | 233.989 | 0.97019 | 836.1671 | 213.0083 | 893.0792 | 318.2256 | 1360.4617 | 304.9332 | 1288.4318 | 435.8546 | 2019-06-29 23:30 | [15 empty] | 0 |  |  |  | 1 |  |  |  | 348 |  |  |  | 229 |  |  |  | 140.5 | 718.5 |  | 0.62563 | 1.3272
123 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO020 | 1S-DL-YP-ETC-DYVR-2404-GHO020 | MONI BABA MANDIR:K | TG-GHO020A-3 | 19506337 | 990 | 320 | 233.947 | 0.97598 | 1022.5369 | 311.7354 | 1382.0507 | 393.8928 | 1799.9124 | 316.9087 | 1422.8382 | 399.0345 | 2019-06-29 23:00 | [15 empty] | 0 |  |  |  | 8 |  |  |  | 593.5 |  |  |  | 115 |  |  |  | 2.5 | 719 |  | 0.61898 | 1.0329
124 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO021 | 1S-DL-YP-ETC-DYVR-2404-GHO021 | R BLOCK BRAHAMPURI:PL | TG-GHO021A-1 | 19505894 | 990 | 320 | 236 | 0.96 | 861 | 217 | 924 | 372 | 1619 | 272 | 1153 | 614 | 2019-06-11 00:30 | 314.6 | 67.2 | 1629 | Y | 81 | 116 | 103 | 35 | 15.7 | 3.8 | 40 | 40.5 | 0.3 | 0.3 | 1.3 | 0.3 | 30.3 | 1.3 | 1.3 | 3.3 | 455.53 | 301.05 | 442.21 | 462.51 | 1.12 | 171.23 | 31.44 | 21.14 |  | 13.37 |  |  | 698.45 | 21.15 | 0.73 | 0.87
125 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO023 | 1S-DL-YP-ETC-DYVR-2404-GHO023 | BRAMPURI NO-6 NEAR MANDIR:PL | TG-GHO023A-1 | 19502174 | 990 | 320 | 238 | 0.97 | 942 | 314 | 1328 | 302 | 1270 | 327 | 1367 | 84 | 2019-06-03 | 214.2 | 46.4 | 1549 | Y | 97 | 102 | 101 | 5 |  | 1.9 | 58.1 | 40 |  | 2 | 1 |  | 5 | 0.3 | 0.3 | 2 | 561.48 | 530.39 | 561.13 | 573.39 | 147.53 | 178.02 | 151.28 | 139.02 |  | 3.3 |  |  | 714.41 | 5.19 | 0.75 | 0.95
126 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO024 | 1S-DL-YP-ETC-DYVR-2404-GHO024 | X BL BRAHAMPURI RAMNIWAS WALA:PL | TG-GHO024A-1 | 19506904 | 990 | 320 | 241 | 0.97 | 943 | 383 | 1674 | 291 | 1269 | 268 | 1149 | 476 | 2019-06-09 23:30 | 280.3 | 45.4 | 1759 | R | 116 | 89 | 95 | 27 | 1.1 | 1.3 | 89.3 | 8.3 | 5.53 |  | 5.53 |  |  | 9 | 9 | 5.16 | 443.08 | 668.09 | 639.36 | 618.43 | 219.28 | 21.36 | 51.46 | 75.16 | 30.46 | 0.3 |  |  | 699.15 | 20.45 | 0.7 | 0.95
127 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO024 | 1S-DL-YP-ETC-DYVR-2404-GHO024 | X BL BRAHAMPURI RAMNIWAS WALA:PL | TG-GHO024A-2 | 19503177 | 990 | 320 | 249 | 0.97 | 433 | 188 | 793 | 123 | 513 | 121 | 508 | 283 | 2019-06-29 23:00 | 103.8 | 47.8 | 871 | Y | 97 | 110 | 93 | 17 |  | 3.5 | 66.9 | 29.6 | 7.3 | 9.24 | 1.3 |  | 529.55 | 350.49 | 350.49 | 682.38 | 181 | 358.12 | 14 | 35.47 | [8 empty] | 718.25 | 1.35 | 0.78 | 0.44
128 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO024 | 1S-DL-YP-ETC-DYVR-2404-GHO024 | X BL BRAHAMPURI RAMNIWAS WALA:PL | TG-GHO024A-3 | 19506049 | 630 | 200 | 242 | 0.98 | 452 | 168 | 726 | 128 | 551 | 156 | 675 | 157 | 2019-06-29 23:00 | 124.8 | 30.6 | 896 | R | 111 | 86 | 103 | 25 | 0.1 | 5.3 | 80.3 | 14.3 |  |  |  |  | 9.3 | 172.28 | 172.28 | 32 | 689.33 | 528.35 | 662.03 | 669.03 | 2 | [7 empty] | 701.03 | 18.57 | 0.71 | 0.72
129 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO025 | 1S-DL-YP-ETC-DYVR-2404-GHO025 | X BL BRAHAMPURI KHATTEY WALA:PL | TG-GHO025A-1 | 19503713 | 990 | 320 | 239 | 0.98 | 896 | 330 | 1467 | 269 | 1198 | 297 | 1304 | 234 | 2019-06-29 22:30 | 231.1 | 20.6 | 1467 | R | 108 | 85 | 107 | 23 | 0.2 | 4 | 82.8 | 13 |  | 118.42 |  |  |  | 2.3 | 2.3 | 5.22 | 506.26 | 435.3 | 527.42 | 535.2 | 51.16 | 1 | 27.3 | 17 |  |  |  |  | 557.42 | 42.18 | 0.65 | 0.9
130 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO025 | 1S-DL-YP-ETC-DYVR-2404-GHO025 | X BL BRAHAMPURI KHATTEY WALA:PL | TG-GHO025A-2 | 19506248 | 630 | 200 | 261 | 0.97 | 487 | 186 | 701 | 168 | 639 | 133 | 501 | 177 | 2019-06-11 13:00 | 162 | 35.8 | 825 | R | 112 | 105 | 83 | 29 |  | 1.7 | 76.6 | 21.7 | 0.01 | 0.01 | 0.01 | 0.01 | 129.22 | 68.56 | 68.56 | 66.26 | 538.46 | 617.1 | 168.16 | 619.4 | 17.58 |  | 10.27 | [5 empty] | 686.07 | 33.53 | 0.62 | 0.77
131 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO026 | 1S-DL-YP-ETC-DYVR-2404-GHO026 | X BL BRAHAMPURI BHISHAM WALA:PL | TG-GHO026A-1 | 19504986 | 990 | 320 | 240 | 0.97 | 963 | 299 | 1198 | 324 | 1352 | 340 | 1412 | 191 | 2019-06-29 23:00 | 195 | 69.2 | 1460 | B | 86 | 109 | 104 | 23 | 78.4 | 21.6 | [6 empty] | 33.3 |  |  | 7 | 665.46 | 582.51 | 602.51 | 630.36 | 16.25 | 132.5 | 105.5 | 78.05 |  |  | 2 |  | 715.41 | 4.19 | 0.65 | 0.97
132 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO027 | 1S-DL-YP-ETC-DYVR-2404-GHO027 | BRAMPURI GALI NO-1:PL | TG-GHO027A-1 | 19502175 | 990 | 320 | 246 | 0.96 | 588 | 237 | 967 | 151 | 610 | 199 | 800 | 309 | 2019-06-01 01:00 | 164.9 | 44.2 | 967 | R | 114 | 83 | 103 | 31 |  |  | 26.6 | 73.4 |  | 2.3 |  |  | 167.09 | 548.3 | 548.3 | 328.29 | 547.22 | 163.31 | 438.06 | 386.02 | [8 empty] | 714.31 | 5.29 | 0.69 | 0.59
133 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO028 | 1S-DL-YP-ETC-DYVR-2404-GHO028 | AMBEDKAR BASTI GHONDA:PL | TG-GHO028A-1 | 19505171 | 990 | 320 | 245 | 0.95 | 1069 | 333 | 1372 | 347 | 1442 | 389 | 1609 | 210 | 2019-06-01 17:30 | 369.6 | 67.8 | 1674 | Y | 89 | 109 | 102 | 20 | 0.8 | 6.2 | 49.3 | 43.7 |  | 0.3 | 0.04 |  | 70.12 | 83.15 | 83.15 | 57.17 | 498.35 | 354.32 | 444.57 | 460 | 31 | 134.3 | 81.21 | 78 | 1 | 28 | 15 | 5.3 | 600.47 | 47.13 | 0.56 | 1.08
134 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO028 | 1S-DL-YP-ETC-DYVR-2404-GHO028 | AMBEDKAR BASTI GHONDA:PL | TG-GHO028A-2 | 19506338 | 630 | 200 | 246 | 0.95 | 575 | 165 | 698 | 178 | 755 | 232 | 974 | 252 | 2019-06-01 14:30 | 200 | 51.8 | 1146 | B | 90 | 89 | 121 | 32 |  | 1.1 | 30.4 | 68.5 | 0.3 | 0.3 | 0.3 | 0.3 | 53.16 | 140.08 | 140.08 | 25.12 | 510.2 | 410.58 | 365.16 | 505.54 | 4 | 16.3 | 153.42 | 36.3 |  |  | 39 |  | 568.06 | 55.54 | 0.64 | 0.91
135 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO029 | 1S-DL-YP-ETC-DYVR-2404-GHO029 | TIKONA PARK GAMRI:PL | TG-GHO029A-1 | 19501814 | 990 | 320 | 249 | 0.97 | 751 | 288 | 1152 | 187 | 748 | 277 | 1105 | 383 | 2019-06-27 17:30 | 221.5 | 16.2 | 1157 | B | 120 | 82 | 98 | 38 |  | 3.6 | 53 | 43.4 | 1.59 | 2.3 | 6 |  | 61.12 | 430.01 | 430.01 | 156.41 | 643.16 | 278.26 | 453.18 | 554.16 | 4.3 |  | 3.29 | [5 empty] | 710.57 | 9.03 | 0.61 | 0.76
136 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO029 | 1S-DL-YP-ETC-DYVR-2404-GHO029 | TIKONA PARK GAMRI:PL | TG-GHO029A-2 | 19505066 | 630 | 200 | 238 | 0.97 | 506 | 166 | 729 | 142 | 616 | 199 | 876 | 225 | 2019-06-29 15:30 | 130.2 | 19.3 | 899 | B | 96 | 83 | 121 | 38 |  | 3.1 | 42.9 | 54 | 2.3 | 6.5 | 0.3 | 0.3 | 189.41 | 204.13 | 204.13 | 21.01 | 501.46 | 499.54 | 645.04 | 688.56 | 17 |  | 64.53 | 0.3 |  |  | 0.3 |  | 710.57 | 9.03 | 0.67 | 0.8
137 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO030 | 1S-DL-YP-ETC-DYVR-2404-GHO030 | NANAKSAR GURUDWARA:PM | TG-GHO030A-1 | 19505142 | 100 | 40 | 229 | 0.96 | 36 | 3 | 18 | 11 | 46 | 21 | 90 | 63 | 2019-06-30 17:30 | 15.3 | 0.8 | 90 | B | 59 | 128 | 113 | 69 | 100 |  |  |  | 696.47 | 607.49 | 634.49 | 660.19 |  | 84.28 | 84.28 | 36.28 |  | 4.3 | 5.3 | [9 empty] | 697.11 | 22.49 | 0.09 | 0.36
138 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO031 | 1S-DL-YP-ETC-DYVR-2404-GHO031 | MTNL 4 PUSTA:PL | TG-GHO031A-1 | 19505482 | 630 | 200 | 235 | 0.98 | 464 | 153 | 664 | 197 | 861 | 114 | 494 | 319 | 2019-06-12 | 125 | 35.6 | 861 | Y | 97 | 127 | 76 | 51 | 0.2 | 2.9 | 93.8 | 3.1 | 3.3 | 3.3 | 3.3 | 3.3 | 215.23 | 7 | 7 | 121.25 | 484.51 | 660.14 | 193.27 | 578.49 |  | 33 | [6 empty] | 703.44 | 16.16 | 0.65 | 0.74
139 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO031 | 1S-DL-YP-ETC-DYVR-2404-GHO031 | MTNL 4 PUSTA:PL | TG-GHO031A-2 | 19505305 | 990 | 320 | 228.9477 | 0.98015 | 728.3718 | 264.1784 | 1220.2234 | 247.5506 | 1128.307 | 216.6428 | 991.6819 | 199.1811 | 2019-06-29 23:00 | [15 empty] | 0 |  |  |  | 71.5 |  |  |  | 645.5 |  |  |  | 0 |  |  |  | 0 | 717 |  | 0.68339 | 0.73573
140 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO034 | 1S-DL-YP-ETC-DYVR-2404-GHO034 | 3.5 PUSTA PUMP HOUSE:PL | TG-GHO034A-1 | 19506578 | 630 | 200 | 242 | 0.97 | 431 | 173 | 728 | 155 | 636 | 102 | 421 | 273 | 2019-06-26 16:00 | 156.8 | 31.6 | 778 | R | 121 | 107 | 72 | 49 | 0.1 | 18.6 | 77.3 | 4.1 |  |  | 5 |  | 18 | 82 | 82 | 135.3 | 672.41 | 617.58 | 85.54 | 564.28 | 9.17 | [7 empty] | 699.58 | 20.02 | 0.68 | 0.68
141 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO035 | 1S-DL-YP-ETC-DYVR-2404-GHO035 | BALLU KA TUBEWELL | TG-GHO035A-1 | 19504732 | 990 | 200 | 227 | 0.97 | 875 | 269 | 1179 | 332 | 1465 | 274 | 1212 | 272 | 2019-06-29 23:00 | 190.4 | 63.5 | 1465 | Y | 91 | 107 | 102 | 16 |  |  | 34.1 | 65.9 |  |  |  |  | 53.44 | 8 | 8 | 10.3 | 657.16 | 631.26 | 686 | 680.3 | 4 | 74.34 | 20.3 | 24 |  | 1 |  |  | 715 | 5 | 0.68 | 0.88
142 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO038 | 1S-DL-YP-ETC-DYVR-2404-GHO038 | MAIN BRAHMPURI RD GALI NO.7:PM | TG-GHO038A-1 | 19504532 | 990 | 320 | 242 | 0.97 | 932 | 208 | 870 | 367 | 1549 | 357 | 1522 | 666 | 2019-06-03 00:30 | 214.2 | 61.1 | 1588 | Y | 79 | 113 | 108 | 34 |  | 0.6 | 11.6 | 87.8 | 1.3 | 1.3 | 1.3 | 1.3 | 74.24 |  |  | 3.3 | 639 | 511.45 | 567.45 | 632.15 |  | 176.23 | 138.39 | 77.39 |  | 25.16 | 6 |  | 714.54 | 5.06 | 0.68 | 0.94
143 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO040 | 1S-DL-YP-ETC-DYVR-2404-GHO040 | MAIN BRAHMPURI RD GALI NO.19:PM | TG-GHO040A-1 | 19506050 | 630 | 200 | 245 | 0.96 | 774 | 239 | 1016 | 244 | 1032 | 291 | 1243 | 219 | 2019-06-30 01:30 | 205 | 70.2 | 1436 | Y | 93 | 104 | 103 | 11 | 0.4 | 0.1 | 5.1 | 94.4 | [8 empty] | 487.14 | 297.31 | 346.34 | 362.26 | 212.47 | 325.26 | 285.29 | 307.05 | 16.19 | 93.23 | 84.17 | 46.49 | 716.2 | 3.4 | 0.65 | 1.23
144 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO041 | 1S-DL-YP-ETC-DYVR-2404-GHO041 | MAIN BRAHMPURI RD GALI NO. 24 | TG-GHO041A-1 | 19505946 | 400 | 120 | 247 | 0.98 | 317 | 125 | 516 | 93 | 403 | 99 | 428 | 103 | 2019-06-01 17:00 | 73.7 | -9.5 | 635 | B | 100 | 92 | 108 | 16 | 91.4 | 0.6 | 1.8 | 6.2 |  |  |  |  | 27.52 | 74.59 | 74.59 | 20.3 | 664.28 | 643.18 | 700.47 | 697.47 | 25.57 |  | 10.3 |  |  |  | 0.3 |  | 718.17 | 1.43 | 0.72 | 0.79
145 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO042 | 1S-DL-YP-ETC-DYVR-2404-GHO042 | MAIN BRAHMPURI RD GALI NO. 23:PM | TG-GHO042A-1 | 19505995 | 990 | 320 | 246 | 0.96 | 1071 | 362 | 1477 | 390 | 1583 | 320 | 1304 | 244 | 2019-06-26 02:00 | 359.7 | 88 | 1785 | R | 102 | 105 | 93 | 12 | 0.4 | 0.1 | 8.7 | 90.8 | 1.3 | 1.3 | 1.3 | 1.3 | 5 | 1.3 | 1.3 | 4 | 397.46 | 373.31 | 557.45 | 432.31 | 244.54 | 246.39 | 128.42 | 240.41 | 44.47 | 70.47 | 0.3 | 15.15 | 693.57 | 26.03 | 0.7 | 1.08
146 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO045 | 1S-DL-YP-ETC-DYVR-2404-GHO045 | PANJABI COLONY GAMRI | TG-GHO045A-1 | 19506673 | 400 | 120 | 245 | 0.97 | 237 | 165 | 685 | 36 | 144 | 36 | 144 | 541 | 2019-06-19 12:00 | 67.9 | 17.8 | 685 | R | 78 | 128 | 94 | 50 | 0.1 | 2.6 | 78.8 | 18.5 | 39.3 | 2.3 | 13.3 | 2.3 | 605.2 | 182.26 | 182.26 | 364.2 | 56 | 507.54 | 272.3 | 334.3 |  | 8.3 |  |  | 0.3 |  |  |  | 701.2 | 18.4 | 0.67 | 0.59
147 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO052 | 1S-DL-YP-ETC-DYVR-2404-GHO052 | C BLOCK USHMANPUR | TG-GHO052A-1 | 19505430 | 630 | 200 | 248 | 0.98 | 490 | 196 | 789 | 97 | 383 | 197 | 784 | 404 | 2019-06-06 04:30 | 182.4 | 28.6 | 878 | R | 128 | 56 | 116 | 72 | 0.2 | 13.3 | 81.6 | 4.9 |  | 41.26 |  |  | 16 | 655.04 | 655.04 | 145.46 | 632.3 | 1.37 | 643.06 | 552.21 | 49.37 |  | 5.37 | [5 empty] | 698.07 | 21.53 | 0.6 | 0.78
148 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO054 | 1S-DL-YP-ETC-DYVR-2404-GHO054 | D-BLOCK GAMRI EXTR S/ST | TG-GHO054A-1 | 19505519 | 990 | 320 | 239 | 0.97 | 636 | 202 | 836 | 239 | 1006 | 195 | 820 | 179 | 2019-06-14 19:30 | 169.3 | 48 | 1047 | Y | 94 | 113 | 93 | 20 | 0.1 | 5.8 | 64.8 | 29.3 | 2.3 | 1 | 1 | 1 | 369.58 | 163.57 | 163.57 | 284.28 | 345.24 | 552.55 | 331.17 | 432.24 | [8 empty] | 717.52 | 2.08 | 0.66 | 0.64
149 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO054 | 1S-DL-YP-ETC-DYVR-2404-GHO054 | D-BLOCK GAMRI EXTR S/ST | TG-GHO054A-2 | 19505777 | 630 | 200 | 244 | 0.97 | 642 | 130 | 517 | 274 | 1104 | 237 | 979 | 536 | 2019-06-30 06:30 | 203 | 64.2 | 1142 | Y | 100 | 111 | 89 | 22 | 1.3 | 9.3 | 63.5 | 25.9 |  |  |  |  | 0.02 | 1.3 | 1.3 |  | 657.53 | 506.17 | 676.27 | 643.04 | 54.53 | 170.03 | 16.02 | 69.25 | 0.3 | 35.28 | 0.19 | 0.49 | 713.18 | 6.42 | 0.64 | 1.02
150 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO055 | 1S-DL-YP-ETC-DYVR-2404-GHO055 | II Pusta Usmanpur Village Khaddar | TG-GHO055A-1 | 19506045 | 630 | 200 | 234 | 0.98 | 187 | 47 | 202 | 59 | 253 | 81 | 354 | 135 | 2019-06-27 15:30 | 64 | 12.4 | 451 | R | 111 | 93 | 95 | 18 |  | 1.5 | 45.3 | 53.2 | 180.37 | 332.25 | 394.55 | 158.3 | 527.02 | 382.12 | 382.12 | 556.07 | 6.58 |  | 8.3 | [9 empty] | 714.37 | 5.23 | 0.74 | 0.3
151 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO056 | 1S-DL-YP-ETC-DYVR-2404-GHO056 | A BLOCK BHAJANPURA GALI NO. -2:P/M | TG-GHO056A-1 | 19506048 | 630 | 200 | 245 | 0.97 | 662 | 306 | 1429 | 136 | 611 | 220 | 971 | 710 | 2019-06-30 14:30 | 248.4 | 42.4 | 1440 | R | 128 | 72 | 99 | 56 | 0.4 | 0.6 | 13.6 | 85.4 |  | 1.3 |  |  | 4.27 | 359.01 | 359.01 | 76.39 | 503.31 | 333.57 | 493.51 | 575.08 | 128.49 |  | 66.08 | 40.56 | 57.41 |  | 4.37 | 1.45 | 694.28 | 25.32 | 0.52 | 1.05
152 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO059 | 1S-DL-YP-ETC-DYVR-2404-GHO059 | DJB RAINY WELL-W-II, NEAR NANAKSAR WZB. | TG-GHO059A-1 | 19506627 | 400 | 120 | 252 | 0.9 | 159 | 54 | 210 | 53 | 207 | 53 | 206 | 4 | 2019-06-14 18:30 | 116.9 | -0.1 | 210 | R | 113 | 96 | 91 | 22 |  | 0.4 | 5.2 | 94.4 | 643.35 | 645.35 | 645.35 | 644.05 | 53.16 | 51.46 | 51.46 | 53.16 | 0.3 | [11 empty] | 697.21 | 22.39 | 0.07 | 0.4
153 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO060 | 1S-DL-YP-ETC-DYVR-2404-GHO060 | PAHADI HOTEL NALA | TG-GHO060A-1 | 19506816 | 630 | 200 | 241 | 0.97 | 476 | 194 | 852 | 142 | 610 | 140 | 597 | 249 | 2019-06-11 18:30 | 157.6 | 27.8 | 852 | R | 114 | 88 | 98 | 26 | 0.4 | 5.6 | 92.6 | 1.5 | 0.3 | 3 | 1.3 | 0.3 | 11.3 | 223.57 | 223.57 | 29.3 | 690.15 | 477.16 | 612.13 | 674.13 | 1.58 |  | 0.3 | [5 empty] | 704.13 | 15.47 | 0.64 | 0.76
154 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO062 | 1S-DL-YP-ETC-DYVR-2404-GHO062 | B-BLOCK BHAJANPURA NALA | TG-GHO062A-1 | 19506886 | 630 | 200 | 240 | 0.98 | 430 | 137 | 587 | 141 | 606 | 152 | 654 | 60 | 2019-06-30 | 132.4 | 22.4 | 696 | R | 105 | 85 | 110 | 25 | 0.3 | 0.1 | 1.2 | 98.4 | 9.3 | 60.54 | 2 | 6.3 | 395.54 | 488 | 488 | 439.24 | 294.39 | 151.09 | 363.09 | 254.09 | [8 empty] | 700.03 | 19.57 | 0.55 | 0.68
155 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | YAM032 | 1S-DL-YP-ETC-DYVR-2402-YAM032 | GAMRI ROAD PUMP HOUSE:PL | TG-YAM032A-1 | 19505578 | 630 | 200 | 252 | 0.97 | 438 | 123 | 510 | 216 | 911 | 99 | 411 | 459 | 2019-06-10 23:00 | 105.4 | 37.2 | 911 | Y | 99 | 121 | 80 | 41 | 0.2 | 0.1 | 15.7 | 84 |  |  |  |  | 242.45 | 94.51 | 94.51 | 214.49 | 460.29 | 589.23 | 209.55 | 488.25 |  | 17.3 |  |  |  | 1.3 |  |  | 703.14 | 16.46 | 0.66 | 0.69
156 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | YAM032 | 1S-DL-YP-ETC-DYVR-2402-YAM032 | GAMRI ROAD PUMP HOUSE:PL | TG-YAM032A-2 | 19505820 | 990 | 320 | 253 | 0.98 | 949 | 361 | 1458 | 347 | 1419 | 242 | 958 | 482 | 2019-06-12 12:00 | 425.6 | 41.6 | 1570 | Y | 90 | 121 | 89 | 32 | 0.3 | 3.7 | 48.6 | 47.5 |  |  |  |  | 124.3 |  |  | 16 | 579.44 | 539.19 | 642.49 | 692.14 | 15 | 169.25 |  | 11.3 | 0.3 | 11 |  |  | 719.44 | 0.16 | 0.62 | 0.96
157 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM010 | 1S-DL-YP-ETC-DYVR-2401-SLM010 | RISHI KARDOM MARG:PL | TG-SLM010A-1 | 19503434 | 990 | 320 | 229 | 0.98 | 778 | 188 | 803 | 361 | 1561 | 229 | 962 | 692 | 2019-06-30 | 141.3 | 52.3 | 1561 | Y | 80 | 119 | 101 | 39 |  | 2.5 | 67.7 | 29.8 |  |  |  |  | 156.37 | 4 | 4 | 12 | 559.39 | 611.02 | 708.16 | 704.16 |  | 99.14 | 0.3 |  |  | 2 |  |  | 716.16 | 3.44 | 0.72 | 0.79
158 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM011 | 1S-DL-YP-ETC-DYVR-2401-SLM011 | BRAHMPURI NO-I:PL | TG-SLM011A-1 | 19506454 | 990 | 320 | 240 | 0.96 | 881 | 332 | 1363 | 298 | 1203 | 251 | 1024 | 293 | 2019-06-26 18:00 | 257.3 | 16.3 | 1363 | R | 97 | 106 | 97 | 9 | 2.6 | 3.2 | 74.1 | 20 | 12.4 | 12.4 | 6 | 12.4 | 1.3 |  |  |  | 454.25 | 422.39 | 478.49 | 469.24 | 30.54 | 64.4 | 8 | 17.55 | 0.3 |  |  |  | 568.51 | 55.09 | 0.71 | 0.89
159 | 2019-06-01 | 2019-06-26 10:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM011 | 1S-DL-YP-ETC-DYVR-2401-SLM011 | BRAHMPURI NO-I:PL | TG-SLM011A-2 | 19506643 | 630 | 200 | 251.9784 | 0.9636 | 579.4609 | 210.1796 | 840.6848 | 188.6873 | 750.3373 | 180.5939 | 712.627 | 113.9815 | 2019-06-02 00:30 | [15 empty] | 0 |  |  |  | 0 |  |  |  | 6.5 |  |  |  | 129 |  |  |  | 273.5 | 409 |  | 0.73728 | 0.91978
160 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM013 | 1S-DL-YP-ETC-DYVR-2401-SLM013 | OUTSIDE KOTHI ZAFRABAD:PL | TG-SLM013A-1 | 19502308 | 990 | 320 | 243 | 0.97 | 821 | 213 | 852 | 307 | 1229 | 301 | 1194 | 361 | 2019-06-30 03:00 | 189.2 | 33.9 | 1229 | Y | 89 | 110 | 100 | 21 |  |  | 43.4 | 56.6 | 0.3 |  | 0.3 | 0.3 | 63 | 12.3 | 12.3 | 26 | 651 | 678.35 | 673.11 | 687 |  | 23.25 | 9.49 | 1 |  |  |  |  | 714.3 | 5.3 | 0.67 | 0.83
161 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM013 | 1S-DL-YP-ETC-DYVR-2401-SLM013 | OUTSIDE KOTHI ZAFRABAD:PL | TG-SLM013A-2 | 19506525 | 630 | 200 | 251 | 0.96 | 335 | 60 | 236 | 88 | 348 | 187 | 745 | 464 | 2019-06-30 01:00 | 120.4 | 35.4 | 745 | B | 75 | 108 | 117 | 42 | 0.1 | 0.6 | 17.8 | 81.5 | 99.27 | 0.3 | 1 |  | 585.47 | 501.39 | 501.39 | 630.38 | 5.55 | 189 | 337.21 | 60.31 |  |  | 1.48 | [5 empty] | 691.09 | 28.51 | 0.65 | 0.53
162 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM014 | 1S-DL-YP-ETC-DYVR-2401-SLM014 | INSIDE KOTHI ZAFRABAD:PL | TG-SLM014A-1 | 19503430 | 990 | 320 | 245 | 0.97 | 537 | 139 | 584 | 244 | 1021 | 154 | 647 | 409 | 2019-06-01 21:30 | 138.4 | 5.9 | 1034 | Y | 99 | 103 | 98 | 5 |  |  | 26.8 | 73.2 | 1 | 2 | 1 | 0.3 | 488.18 | 456.58 | 456.58 | 459.15 | 228.46 | 259.06 | 235.29 | 258.19 | [8 empty] | 718.04 | 1.56 | 0.7 | 0.54
163 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM014 | 1S-DL-YP-ETC-DYVR-2401-SLM014 | INSIDE KOTHI ZAFRABAD:PL | TG-SLM014A-2 | 19503729 | 990 | 320 | 238 | 0.96 | 882 | 320 | 1321 | 246 | 1009 | 316 | 1310 | 307 | 2019-06-30 00:30 | 209.8 | 87.6 | 1352 | R | 104 | 90 | 106 | 16 |  | 2.5 | 57.2 | 40.2 |  |  |  |  | 9.3 | 45 | 45 | 9 | 668.04 | 665.39 | 663.51 | 691.34 | 40.3 | 7.25 | 52.13 | 17.3 |  |  |  |  | 718.04 | 1.56 | 0.68 | 0.89
164 | 2019-06-17 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM015 | 1S-DL-YP-ETC-DYVR-2401-SLM015 | KHATTA ROAD NO 66 ZAFRABAD:PL | TG-SLM015A-1 | 19505169 | 990 | 320 | 253 | 0.96 | 847 | 249 | 1004 | 299 | 1191 | 299 | 1194 | 188 | 2019-06-30 | 251.8 | 1 | 1527 | B | 97 | 104 | 99 | 7 | 0.5 | 0.8 | 35.9 | 62.8 | 1 | 1 | 1 | 1 | 17 | 4.3 | 4.3 | 10.3 | 286.04 | 285.05 | 273.02 | 290.53 | 5.18 | 18.47 | 10 | 6.59 |  |  | 0.3 |  | 309.22 | 26.38 | 0.72 | 0.86
165 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM015 | 1S-DL-YP-ETC-DYVR-2401-SLM015 | KHATTA ROAD NO 66 ZAFRABAD:PL | TG-SLM015A-2 | 19506711 | 990 | 320 | 239 | 0.97 | 983 | 335 | 1329 | 323 | 1282 | 325 | 1315 | 42 | 2019-06-29 23:30 | 244.2 | 31.7 | 1666 | Y | 109 | 102 | 89 | 20 | 32.7 | 0.4 | 28.6 | 38.3 | 0.3 | 21.4 | 12.3 | 0.3 | 0.3 | 27.3 | 27.3 | 24.4 | 311.38 | 325.4 | 418.4 | 391.03 | 156.17 | 100.35 | 8.29 | 63.12 | 10.3 | 4 |  |  | 689.28 | 30.32 | 0.67 | 0.99
166 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM016 | 1S-DL-YP-ETC-DYVR-2401-SLM016 | OUTSIDE SCHOOL ZAFRABAD:PL | TG-SLM016A-1 | 19505290 | 990 | 320 | 238 | 0.96 | 775 | 254 | 1081 | 221 | 931 | 301 | 1306 | 327 | 2019-06-03 01:00 | 213.1 | 44.8 | 1306 | B | 101 | 94 | 105 | 11 | 0.3 | 3.4 | 59.3 | 37 | 1 | 0.3 |  |  | 29 | 40.3 | 40.3 | 23 | 656.17 | 652.46 | 671.16 | 670.46 | 7.29 |  | 5.3 | [5 empty] | 693.46 | 26.14 | 0.71 | 0.78
167 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM016 | 1S-DL-YP-ETC-DYVR-2401-SLM016 | OUTSIDE SCHOOL ZAFRABAD:PL | TG-SLM016A-2 | 19505654 | 990 | 320 | 260 | 0.96 | 648 | 123 | 477 | 345 | 1353 | 180 | 699 | 789 | 2019-06-29 17:00 | 208.6 | -1.3 | 1365 | Y | 51 | 135 | 114 | 84 | 0.2 | 2.3 | 57.2 | 40.4 | 330.21 | 7 | 8 | 7 | 371.08 | 57.55 | 57.55 | 343.48 |  | 620.37 | 501.1 | 350.41 |  | 14.46 |  |  |  | 1.11 |  |  | 701.29 | 18.31 | 0.61 | 0.65
168 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM017 | 1S-DL-YP-ETC-DYVR-2401-SLM017 | NALA NO 1 SEELAMPUR:PL | TG-SLM017A-1 | 19505092 | 990 | 320 | 243 | 0.96 | 633 | 220 | 891 | 212 | 853 | 202 | 821 | 61 | 2019-06-03 01:30 | 154.6 | 67.8 | 891 | R | 103 | 99 | 98 | 5 | 0.1 | 0.1 | 21.9 | 78 |  |  |  |  | 390.14 | 440.5 | 440.5 | 440.21 | 296.37 | 246.01 | 214.37 | 246.3 | [8 empty] | 686.51 | 33.09 | 0.6 | 0.64
169 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM017 | 1S-DL-YP-ETC-DYVR-2401-SLM017 | NALA NO 1 SEELAMPUR:PL | TG-SLM017A-2 | 19505652 | 990 | 320 | 237 | 0.97 | 787 | 285 | 1279 | 229 | 1019 | 273 | 1219 | 236 | 2019-06-29 23:30 | 236.8 | 71.7 | 1831 | B | 107 | 90 | 103 | 17 | 0.2 | 0.5 | 45.7 | 53.7 |  |  |  |  | 3.3 | 25.56 | 25.56 | 5 | 517.31 | 528.42 | 538.38 | 549.38 | 33.37 |  | 12.3 |  |  |  | 0.3 |  | 687.21 | 32.39 | 0.75 | 0.8
170 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM017 | 1S-DL-YP-ETC-DYVR-2401-SLM017 | NALA NO 1 SEELAMPUR:PL | TG-SLM017A-3 | 19506702 | 630 | 200 | 244 | 0.96 | 494 | 166 | 672 | 177 | 720 | 151 | 609 | 96 | 2019-06-11 07:00 | 94.6 | 18.6 | 720 | Y | 104 | 119 | 77 | 42 |  | 2.6 | 57 | 40.4 | 54.53 | 11 | 381.25 | 41.5 | 639.48 | 634.34 | 634.34 | 656.21 | 4 | 52.37 | 1 | 0.3 |  | 0.3 | [6 empty] | 698.41 | 21.19 | 0.33 | 0.78
171 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM018 | 1S-DL-YP-ETC-DYVR-2401-SLM018 | SBI WELCOME:ID | TG-SLM018A-1 | 19506718 | 990 | 320 | 251 | 0.96 | 917 | 310 | 1253 | 291 | 1167 | 316 | 1257 | 88 | 2019-06-01 23:00 | 308.5 | 60.2 | 1385 | R | 110 | 91 | 98 | 19 |  |  | 19.7 | 80.3 |  |  |  |  | 1.19 | 11.28 | 11.28 | 3.19 | 569.15 | 686.06 | 663.39 | 666.15 | 134.12 | 11.12 | 41.48 | 39.12 | 4 |  |  |  | 708.46 | 11.14 | 0.71 | 0.93
172 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM018 | 1S-DL-YP-ETC-DYVR-2401-SLM018 | SBI WELCOME:ID | TG-SLM018A-2 | 19505886 | 990 | 320 | 259 | 0.96 | 826 | 383 | 1592 | 359 | 1450 | 84 | 334 | 1194 | 2019-06-07 15:30 | 261.4 | 55.4 | 1592 | R | 113 | 102 | 86 | 27 | 0.3 | 0.1 | 6.7 | 92.9 | 0.3 | 1 | 2 | 0.3 | 112.31 | 228.04 | 228.04 | 238.41 | 594.48 | 479.15 | 197.02 | 469.08 | 0.3 |  |  | 0.26 | 0.26 | 0.26 |  |  | 708.45 | 11.15 | 0.51 | 0.83
173 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM018 | 1S-DL-YP-ETC-DYVR-2401-SLM018 | SBI WELCOME:ID | TG-SLM018A-3 | 19506642 | 630 | 200 | 246 | 0.96 | 355 | 129 | 513 | 117 | 461 | 109 | 435 | 69 | 2019-06-01 22:00 | 110.4 | 31.6 | 577 | R | 116 | 105 | 80 | 36 |  | 0.1 | 13.9 | 86 | 0.3 | 0.3 | 12.39 | 0.3 | 138.01 | 256.19 | 256.19 | 361.34 | 556.29 | 438.11 | 81.11 | 332.56 | [8 empty] | 695 | 25 | 0.7 | 0.56
174 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM019 | 1S-DL-YP-ETC-DYVR-2401-SLM019 | PHOTO CHOCK WELCOME:PL | TG-SLM019A-1 | 19505807 | 990 | 320 | 259 | 0.96 | 1242 | 415 | 1747 | 428 | 1789 | 398 | 1655 | 118 | 2019-06-24 20:30 | 223.4 | 56.6 | 2537 | R | 113 | 88 | 99 | 25 | 0.2 | 0.6 | 10.8 | 88.3 |  | 2 |  |  | 210.16 | 436.38 | 436.38 | 315.08 | 453.49 | 267.42 | 360.38 | 391.12 | 34.4 | 0.3 | 4.19 | 0.3 | 9.03 | 0.58 | 0.3 | 0.58 | 707.48 | 12.12 | 0.35 | 1.25
175 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM019 | 1S-DL-YP-ETC-DYVR-2401-SLM019 | PHOTO CHOCK WELCOME:PL | TG-SLM019A-2 | 19505086 | 990 | 320 | 246 | 0.96 | 1005 | 327 | 1403 | 319 | 1359 | 360 | 1532 | 156 | 2019-06-30 00:30 | 212.7 | 73.6 | 1532 | B | 105 | 97 | 99 | 8 |  |  | 1.5 | 98.5 |  |  |  |  | 36.32 | 84.46 | 84.46 | 52.58 | 614.27 | 590.03 | 620.4 | 617.49 | 55.29 | 32.09 | 27.25 | 35.42 | 0.3 |  | 0.59 | 0.29 | 706.58 | 13.02 | 0.57 | 1.02
176 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM019 | 1S-DL-YP-ETC-DYVR-2401-SLM019 | PHOTO CHOCK WELCOME:PL | TG-SLM019A-3 | 19506059 | 630 | 200 | 253 | 0.97 | 420 | 175 | 703 | 102 | 409 | 143 | 575 | 255 | 2019-06-20 19:30 | 167.2 | 22.6 | 703 | R | 135 | 74 | 91 | 61 | 0.1 | 0.2 | 13 | 86.7 |  | 274.28 | 152.02 | 34.42 | 298 | 388.28 | 388.28 | 519.07 | 408.35 | 44.01 | 133.35 | 153.08 | 0.22 | [7 empty] | 706.57 | 13.03 | 0.49 | 0.67
177 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM020 | 1S-DL-YP-ETC-DYVR-2401-SLM020 | Z-2 BLOCK WELCOME:PL | TG-SLM020A-1 | 19506530 | 630 | 200 | 240 | 0.96 | 447 | 153 | 693 | 154 | 705 | 140 | 631 | 69 | 2019-06-30 22:30 | 165.2 | 39.6 | 705 | Y | 115 | 100 | 84 | 31 | 0.1 | 0.1 | 15.7 | 84.1 | 0.29 | 0.29 | 2.29 | 0.29 | 134.31 | 298 | 298 | 283.55 | 563.37 | 400.08 | 173.19 | 414.13 | [8 empty] | 698.37 | 21.23 | 0.6 | 0.71
178 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM020 | 1S-DL-YP-ETC-DYVR-2401-SLM020 | Z-2 BLOCK WELCOME:PL | TG-SLM020A-2 | 19500583 | 990 | 320 | 233 | 0.97 | 916 | 298 | 1284 | 276 | 1184 | 342 | 1476 | 257 | 2019-06-01 00:30 | 213.4 | 35.3 | 1480 | B | 98 | 94 | 108 | 14 |  |  | 5 | 95 | 0.3 |  | 0.3 | 0.3 | 34.48 | 45.46 | 45.46 | 14.48 | 643.17 | 644.49 | 661.01 | 663.47 | 13.38 | 1.38 | 25.55 | 13.08 |  |  | 0.47 |  | 715.4 | 4.2 | 0.61 | 0.93
179 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM021 | 1S-DL-YP-ETC-DYVR-2401-SLM021 | KABOOTER MARKET WELCOME:ID | TG-SLM021A-1 | 19506754 | 990 | 320 | 246 | 0.95 | 606 | 236 | 966 | 195 | 784 | 176 | 711 | 227 | 2019-06-01 01:00 | 186.6 | 65.6 | 1140 | Y | 105 | 98 | 97 | 8 | 0.4 |  | 16.1 | 83.6 |  |  |  |  | 251.23 | 329.49 | 329.49 | 301.53 | 445.05 | 366.39 | 361.56 | 394.35 | [8 empty] | 696.28 | 23.32 | 0.68 | 0.61
180 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM021 | 1S-DL-YP-ETC-DYVR-2401-SLM021 | KABOOTER MARKET WELCOME:ID | TG-SLM021A-2 | 19500609 | 990 | 320 | 237 | 0.96 | 1084 | 397 | 1701 | 272 | 1148 | 415 | 1797 | 607 | 2019-06-03 01:30 | 276 | 89.8 | 1847 | B | 100 | 104 | 96 | 8 | 0.2 | 3.5 | 17 | 79.3 |  | 2.3 |  |  | 1 | 3.3 | 3.3 | 2.3 | 573.41 | 506.47 | 572.38 | 581.41 | 112.28 | 186.48 | 80.07 | 117.58 | 26.48 | 14.22 | 52.12 | 11.48 | 713.57 | 6.03 | 0.64 | 1.09
181 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM021 | 1S-DL-YP-ETC-DYVR-2401-SLM021 | KABOOTER MARKET WELCOME:ID | TG-SLM021A-3 | 19505892 | 630 | 200 | 253 | 0.96 | 468 | 177 | 719 | 175 | 719 | 116 | 473 | 247 | 2019-06-03 | 130.8 | 57.4 | 734 | R | 109 | 109 | 82 | 27 |  | 0.1 | 1.6 | 98.2 |  |  |  |  | 31.53 | 27.3 | 27.3 | 58.3 | 654.25 | 664.08 | 382.32 | 638.08 | 10.2 | 5 | [6 empty] | 696.38 | 23.22 | 0.68 | 0.74
182 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM022 | 1S-DL-YP-ETC-DYVR-2401-SLM022 | BAGHWALI MASJID WELCOME:PL | TG-SLM022A-1 | 19503421 | 630 | 200 | 239 | 0.96 | 375 | 120 | 512 | 127 | 537 | 128 | 542 | 27 | 2019-06-02 | 79.6 | 29.9 | 596 | B | 73 | 114 | 113 | 41 |  | 0.2 | 36.5 | 63.3 | 303.27 | 22.25 | 19.24 | 7.57 | 341.03 | 362.34 | 362.34 | 561 | 64.31 | 324.02 | 301.16 | 140.04 | [8 empty] | 709.01 | 10.59 | 0.57 | 0.6
183 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM022 | 1S-DL-YP-ETC-DYVR-2401-SLM022 | BAGHWALI MASJID WELCOME:PL | TG-SLM022A-2 | 19503704 | 990 | 320 | 240 | 0.96 | 482 | 146 | 597 | 145 | 591 | 192 | 792 | 198 | 2019-06-03 18:30 | 120 | 50 | 797 | B | 101 | 77 | 122 | 45 |  |  | 37.5 | 62.5 | 3.2 | 102.03 | 0.3 | 0.3 | 603.3 | 577.2 | 577.2 | 628.33 | 102.1 | 29.37 | 469.56 | 79.57 | [8 empty] | 709 | 11 | 0.71 | 0.49
184 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM023 | 1S-DL-YP-ETC-DYVR-2401-SLM023 | DOUBLE STOREY WELCOME:PL | TG-SLM023A-1 | 19505885 | 630 | 200 | 241 | 0.96 | 320 | 150 | 644 | 54 | 229 | 116 | 497 | 364 | 2019-06-26 | 102.4 | 30.6 | 645 | R | 130 | 57 | 112 | 73 | 0.1 | 0.5 | 23.3 | 76.1 | 1 | 351.22 | 1 | 2 | 234.26 | 360.39 | 360.39 | 558.22 | 476.35 |  | 322.56 | 151.39 | [8 empty] | 712.01 | 7.59 | 0.69 | 0.51
185 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM024 | 1S-DL-YP-ETC-DYVR-2401-SLM024 | DSIDC WELCOME:PL | TG-SLM024A-1 | 19502287 | 630 | 200 | 239 | 0.98 | 233 | 85 | 352 | 79 | 334 | 69 | 294 | 51 | 2019-06-04 11:30 | 93.8 | -35.9 | 352 | R | 95 | 113 | 93 | 20 |  | 49.9 | 47.9 | 2.2 | 429.58 | 344.44 | 464.53 | 414.59 | 283.44 | 369.28 | 369.28 | 299.13 | 0.3 | [11 empty] | 714.12 | 5.48 | 0.49 | 0.37
186 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM030 | 1S-DL-YP-ETC-DYVR-2401-SLM030 | E BLOCK SEELAMPUR:K | TG-SLM030A-1 | 19505407 | 990 | 320 | 253 | 0.96 | 568 | 194 | 763 | 236 | 922 | 138 | 538 | 335 | 2019-06-02 00:30 | 188.2 | 55 | 1094 | Y | 99 | 125 | 76 | 49 | 0.3 | 0.7 | 24.1 | 75 |  |  | 1 |  | 298.27 | 37.09 | 37.09 | 264.49 | 411.34 | 672.22 | 53.36 | 445.12 |  | 0.3 | [6 empty] | 710.01 | 9.59 | 0.73 | 0.57
187 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM030 | 1S-DL-YP-ETC-DYVR-2401-SLM030 | E BLOCK SEELAMPUR:K | TG-SLM030A-2 | 19506349 | 990 | 320 | 254 | 0.96 | 187 | 35 | 134 | 24 | 92 | 129 | 605 | 494 | 2019-06-01 19:00 | 53.4 | 10.9 | 605 | B | 56 | 66 | 178 | 122 | 8.9 | 2.3 | 15 | 73.8 | 710.03 | 710.03 | 235.29 | 710.03 | [16 empty] | 710.03 | 9.57 | 0.64 | 0.19
188 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM031 | 1S-DL-YP-ETC-DYVR-2401-SLM031 | CHAUHAN BANGAR NO 2:PL | TG-SLM031A-1 | 19503011 | 990 | 320 | 250 | 0.95 | 742 | 271 | 1070 | 268 | 1050 | 203 | 793 | 268 | 2019-06-30 | 246.6 | 89.8 | 1110 | R | 106 | 106 | 87 | 19 |  | 0.1 | 23.9 | 76.1 |  |  |  |  | 16 | 5 | 5 | 14.39 | 690.47 | 704 | 615.1 | 696.38 | 4.3 | 2.17 | [6 empty] | 711.17 | 8.43 | 0.72 | 0.75
189 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM031 | 1S-DL-YP-ETC-DYVR-2401-SLM031 | CHAUHAN BANGAR NO 2:PL | TG-SLM031A-2 | 19505893 | 990 | 320 | 250 | 0.95 | 704 | 222 | 885 | 209 | 830 | 273 | 1107 | 254 | 2019-06-29 23:30 | 231 | 55.7 | 1181 | B | 89 | 91 | 119 | 30 | 0.2 | 2.9 | 62.3 | 34.5 | 0.3 |  |  | 0.3 | 241.27 | 174.2 | 174.2 | 82.44 | 453.16 | 520.53 | 675.47 | 611.59 |  |  | 5.26 | [5 empty] | 695.13 | 24.47 | 0.68 | 0.71
190 | 2019-06-12 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM032 | 1S-DL-YP-ETC-DYVR-2401-SLM032 | MERCURY CHOWK SEELAMPUR:PL | TG-SLM032A-1 | 19506905 | 990 | 320 | 259 | 0.95 | 486 | 179 | 714 | 135 | 537 | 172 | 685 | 164 | 2019-06-30 | 183.4 | 40 | 986 | B | 100 | 88 | 113 | 25 | 0.2 | 0.1 | 1.2 | 98.5 | 1 | 2 | 0.3 | 0.3 | 330.38 | 418.07 | 418.07 | 356.36 | 93.35 | 5.06 | 186.24 | 68.07 | [8 empty] | 425.13 | 30.47 | 0.71 | 0.49
191 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM032 | 1S-DL-YP-ETC-DYVR-2401-SLM032 | MERCURY CHOWK SEELAMPUR:PL | TG-SLM032A-2 | 19506032 | 630 | 200 | 240.3955 | 0.97743 | 313.2231 | 157.7716 | 686.7099 | 47.555 | 193.7621 | 107.8964 | 451.4684 | 427.0531 | 2019-06-01 19:00 | [15 empty] | 14 |  |  |  | 681 |  |  |  | 22.5 |  |  |  | 0 |  |  |  | 0 | 717.5 |  | 0.6047 | 0.49718
192 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM044 | 1S-DL-YP-ETC-DYVR-2401-SLM044 | CHAUHAN BANGAR GALI NO 10:PL | TG-SLM044A-1 | 19505063 | 990 | 320 | 236 | 0.97 | 515 | 155 | 636 | 200 | 827 | 160 | 657 | 182 | 2019-06-28 18:00 | 161.2 | 31.6 | 1045 | B | 92 | 95 | 113 | 21 |  | 0.6 | 49.9 | 49.5 | 2 | 12 | 1 | 0.3 | 584.16 | 485.53 | 485.53 | 457.57 | 124.35 | 212.58 | 396.15 | 252.24 | [8 empty] | 710.51 | 9.09 | 0.72 | 0.52
193 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM044 | 1S-DL-YP-ETC-DYVR-2401-SLM044 | CHAUHAN BANGAR GALI NO 10:PL | TG-SLM044A-2 | 19502301 | 990 | 320 | 246 | 0.96 | 658 | 254 | 1072 | 219 | 916 | 184 | 763 | 268 | 2019-06-02 | 203.9 | 30.2 | 1072 | R | 121 | 74 | 105 | 47 |  |  | 47.1 | 52.9 |  | 248.08 |  | 2 | 46.59 | 50.36 | 50.36 | 296.18 | 663.15 | 411.3 | 593.09 | 411.56 | [8 empty] | 710.14 | 9.46 | 0.65 | 0.66
194 | 2019-06-01 | 2019-06-20 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM044 | 1S-DL-YP-ETC-DYVR-2401-SLM044 | CHAUHAN BANGAR GALI NO 10:PL | TG-SLM044A-3 | 19502234 | 990 | 320 | 236 | 0.97 | 864 | 314 | 1401 | 233 | 1019 | 317 | 1351 | 360 | 2019-06-02 00:30 | 189.2 | 69.9 | 1449 | R | 111 | 86 | 103 | 25 | 42.4 | 22.1 | 23.3 | 12.2 |  |  | 1 |  | 1 | 54.03 | 54.03 | 1 | 404.42 | 408.33 | 397.4 | 448.4 | 56.54 |  | 53.24 | 12.56 |  |  |  |  | 462.36 | 17.24 | 0.7 | 0.87
195 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM044 | 1S-DL-YP-ETC-DYVR-2401-SLM044 | CHAUHAN BANGAR GALI NO 10:PL | TG-SLM044A-4 | 19504045 | 990 | 320 | 250 | 0.96 | 810 | 255 | 1052 | 271 | 1115 | 283 | 1187 | 117 | 2019-06-01 23:30 | 181.1 | -28.7 | 1187 | B | 64 | 121 | 115 | 57 | 37.1 | 11.8 | 10.5 | 40.6 | 308.07 |  | 3.3 | 0.3 | 12 | 11.43 | 11.43 | 223.4 | 340.36 | 646.36 | 629.34 | 436.07 |  | 2.24 | 1.24 | 0.26 |  |  |  |  | 710.59 | 9.01 | 0.57 | 0.82
196 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM044 | 1S-DL-YP-ETC-DYVR-2401-SLM044 | CHAUHAN BANGAR GALI NO 10:PL | TG-SLM044A-5 | 19505205 | 990 | 320 | 240 | 0.97 | 791 | 268 | 1171 | 254 | 1116 | 269 | 1178 | 59 | 2019-06-30 | 207.7 | 63.4 | 1502 | R | 109 | 88 | 102 | 21 | 0.2 |  | 35.2 | 64.6 |  |  |  |  | 1.3 | 88.4 | 88.4 | 16 | 680.39 | 598.53 | 658.39 | 671.33 | 4.54 |  | 2 |  | 0.3 |  |  |  | 687.33 | 32.27 | 0.68 | 0.8
197 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM045 | 1S-DL-YP-ETC-DYVR-2401-SLM045 | POLICE STATION SEELAMPUR:ID | TG-SLM045A-1 | 19504278 | 400 | 120 | 248 | 0.97 | 56 | 19 | 77 | 20 | 80 | 17 | 70 | 9 | 2019-06-01 23:00 | 16.3 | 1.1 | 128 | Y | 80 | 117 | 103 | 37 |  |  | 6.2 | 93.8 | 711.59 | 703.33 | 711.59 | 711.59 |  | 8.26 | 8.26 | [13 empty] | 711.59 | 8.01 | 0.49 | 0.14
198 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM048 | 1S-DL-YP-ETC-DYVR-2401-SLM048 | DCP OFFICE WELLCOME:PL | TG-SLM048A-1 | 19505999 | 990 | 320 | 238 | 0.96 | 484 | 103 | 448 | 199 | 875 | 181 | 790 | 392 | 2019-06-05 00:30 | 133.4 | 43.5 | 990 | Y | 67 | 121 | 112 | 54 | 0.1 | 0.1 | 17.9 | 81.8 | 328.51 | 3 | 5 | 19 | 370.19 | 443.18 | 443.18 | 570.18 |  | 252.52 | 174.22 | 109.52 | [8 empty] | 699.1 | 20.5 | 0.64 | 0.49
199 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM053 | 1S-DL-YP-ETC-DYVR-2401-SLM053 | OPP CHAUHAN BANGAR GALI NO 14:PM | TG-SLM053A-1 | 19505307 | 990 | 320 | 230 | 0.97 | 762 | 254 | 1121 | 255 | 1126 | 253 | 1127 | 6 | 2019-06-02 | 171.8 | 65.6 | 1271 | Y | 103 | 101 | 96 | 7 | 0.1 | 0.1 | 22.4 | 77.5 |  |  |  |  | 42.3 | 61.19 | 61.19 | 54.19 | 648.27 | 629.08 | 591.19 | 636.38 |  | 0.3 | [6 empty] | 690.57 | 29.03 | 0.65 | 0.77
200 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM055 | 1S-DL-YP-ETC-DYVR-2401-SLM055 | OPP OM SWEET BRAHAMPURI ROAD:PM | TG-SLM055A-1 | 19505120 | 630 | 200 | 242 | 0.98 | 412 | 126 | 529 | 98 | 407 | 188 | 793 | 342 | 2019-06-02 00:30 | 125 | 22.8 | 979 | B | 95 | 62 | 143 | 81 | 0.1 | 10.6 | 77.4 | 11.9 |  | 45.24 |  |  | 231.51 | 600.56 | 600.56 | 159.53 | 457.37 | 43.08 | 654.42 | 529.35 |  |  | 34.16 |  |  |  | 0.3 |  | 689.28 | 30.32 | 0.69 | 0.65
201 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM056 | 1S-DL-YP-ETC-DYVR-2401-SLM056 | OPP MAZAR BRAHMPURI ROAD:PM | TG-SLM056A-1 | 19506254 | 400 | 120 | 235 | 0.96 | 409 | 128 | 546 | 146 | 629 | 135 | 585 | 72 | 2019-06-30 03:30 | 168.6 | 37.7 | 773 | Y | 91 | 122 | 87 | 35 | 0.2 | 12.7 | 72 | 15.1 | 1 | 1 | 1 | 1 | 13.3 |  |  |  | 659.22 | 347.4 | 670.52 | 616.34 | 19.52 | 281.54 | 8 | 75.18 |  | 63.1 | 0.22 | 0.52 | 693.44 | 26.16 | 0.65 | 1.02
202 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM057 | 1S-DL-YP-ETC-DYVR-2401-SLM057 | CHAUHAN BANGAR GALI NO 5:PL | TG-SLM057A-1 | 19505374 | 990 | 320 | 236 | 0.97 | 967 | 283 | 1193 | 352 | 1517 | 332 | 1429 | 290 | 2019-06-01 00:30 | 267.5 | 83.2 | 1579 | B | 91 | 106 | 103 | 15 | 0.3 | 2.5 | 32.1 | 65.1 |  |  |  |  | 10.3 | 2 | 2 | 2 | 682.28 | 618.41 | 616.19 | 656.1 | 18.45 | 85.47 | 92.39 | 53.33 |  | 5.15 | 2.15 |  | 711.43 | 8.17 | 0.66 | 0.98
203 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM057 | 1S-DL-YP-ETC-DYVR-2401-SLM057 | CHAUHAN BANGAR GALI NO 5:PL | TG-SLM057A-2 | 19506438 | 630 | 200 | 262 | 0.96 | 423 | 173 | 691 | 188 | 767 | 61 | 242 | 492 | 2019-06-29 23:00 | 129 | 49.6 | 832 | R | 133 | 115 | 52 | 81 | 0.2 | 6.5 | 85.9 | 7.3 | 1 | 1 | 76.13 | 1 | 4 | 14.05 | 14.05 | 68.25 | 640.38 | 677.59 | 3 | 625.09 | 47.56 | 1.3 |  |  | 1 |  |  |  | 694.34 | 25.26 | 0.72 | 0.67
204 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM058 | 1S-DL-YP-ETC-DYVR-2401-SLM058 | OPP CHUHAN BANGAR GALI NO.22:PM | TG-SLM058A-1 | 19502311 | 400 | 120 | 235 | 0.98 | 243 | 86 | 385 | 69 | 304 | 89 | 398 | 88 | 2019-06-01 16:00 | 69.6 | 8 | 531 | B | 88 | 83 | 129 | 46 | 0.2 | 15.6 | 70.7 | 13.5 | 8 | 7 |  |  | 511.43 | 568.18 | 568.18 | 393.15 | 197.5 | 142.15 | 624.05 | 324.18 |  |  | 13 | [5 empty] | 717.33 | 2.27 | 0.66 | 0.61
205 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM059 | 1S-DL-YP-ETC-DYVR-2401-SLM059 | JANTA COLONY NO-1 | TG-SLM059A-1 | 19504855 | 630 | 200 | 238 | 0.96 | 443 | 160 | 663 | 173 | 731 | 110 | 457 | 247 | 2019-06-01 21:30 | 111.3 | 39.6 | 794 | Y | 116 | 109 | 75 | 41 |  | 0.3 | 22.8 | 76.9 | 0.3 | 0.3 | 9.3 | 0.3 | 116 | 270.2 | 270.2 | 381.39 | 570.34 | 412.44 | 45.39 | 304.55 |  | 3.3 | [6 empty] | 709.57 | 10.03 | 0.57 | 0.7
206 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM060 | 1S-DL-YP-ETC-DYVR-2401-SLM060 | JANTA COLONY NO-2 | TG-SLM060A-1 | 19506052 | 400 | 120 | 243 | 0.96 | 342 | 104 | 416 | 99 | 405 | 139 | 555 | 144 | 2019-06-01 03:00 | 108.7 | 39.7 | 577 | B | 99 | 98 | 103 | 5 | 25.4 | 32.7 | 30 | 12 | 0.21 | 0.21 | 0.21 | 0.21 | 4.3 | 13.15 | 13.15 | 2.3 | 685.31 | 674.16 | 627.3 | 682.14 | 2.3 | 5 | 44.14 | 7.47 |  |  | 8.17 |  | 692.52 | 27.08 | 0.67 | 0.86
207 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM061 | 1S-DL-YP-ETC-DYVR-2401-SLM061 | JANTA COLONY NO-3 | TG-SLM061A-1 | 19505809 | 630 | 200 | 244 | 0.96 | 591 | 225 | 912 | 185 | 759 | 181 | 743 | 162 | 2019-06-02 18:30 | 150.2 | 0.4 | 954 | R | 102 | 104 | 94 | 10 | 0.2 | 0.6 | 13.9 | 85.2 | 1.3 | 1.47 | 2.12 | 1.3 | 18.59 | 5.25 | 5.25 | 9.42 | 671.09 | 700.57 | 642.14 | 698.56 | 18 | 2.29 | 7.25 | 0.3 | 1 |  |  |  | 710.38 | 9.22 | 0.6 | 0.94
208 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM069 | 1S-DL-YP-ETC-DYVR-2401-SLM069 | TAJ COLONY | TG-SLM069A-1 | 19506675 | 400 | 120 | 246 | 0.97 | 83 | 26 | 109 | 19 | 80 | 37 | 152 | 63 | 2019-06-02 14:00 | 22.9 | 2.2 | 192 | B | 103 | 100 | 98 | 5 | 0.1 |  | 17.3 | 82.6 | 690.12 | 697.42 | 685.12 | 698.12 | 8.3 | 1 | 1 | 0.3 | [12 empty] | 698.42 | 21.18 | 0.59 | 0.21
209 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM070 | 1S-DL-YP-ETC-DYVR-2401-SLM070 | INSIDE ZAFRABAD SCHOOL | TG-SLM070A-1 | 19505804 | 990 | 320 | 239 | 0.97 | 666 | 234 | 1023 | 175 | 757 | 256 | 1125 | 329 | 2019-06-01 23:30 | 208.6 | 57 | 1125 | B | 109 | 80 | 111 | 31 | 0.1 | 3 | 58.1 | 38.8 | 1 | 1 | 1 | 1 | 95.59 | 534.05 | 534.05 | 177.22 | 618.32 | 180.26 | 621.33 | 537.09 | [8 empty] | 715.31 | 4.29 | 0.66 | 0.67
210 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM072 | 1S-DL-YP-ETC-DYVR-2401-SLM072 | G.K.PATROL PUMP | TG-SLM072A-1 | 19505947 | 100 | 40 | 245 | 0.89 | 34 | 13 | 50 | 9 | 33 | 13 | 50 | 17 | 2019-06-30 09:30 | 20.8 | 1.6 | 63 | B | 109 | 90 | 100 | 19 |  | 0.7 | 18.4 | 80.9 | 402.57 | 637.35 | 442.04 | 543.43 | 296.08 | 61.3 | 61.3 | 155.22 |  |  | 1 | [9 empty] | 699.05 | 20.55 | 0.52 | 0.34
211 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM073 | 1S-DL-YP-ETC-DYVR-2401-SLM073 | ARORA BLDG GALI-24 CHAUHAN | TG-SLM073A-1 | 19506061 | 630 | 200 | 255 | 0.96 | 534 | 169 | 660 | 197 | 780 | 168 | 665 | 117 | 2019-06-30 03:30 | 212 | 11.2 | 799 | R | 96 | 94 | 110 | 16 | 0.1 | 0.2 | 48.8 | 50.9 | 2 | 2 | 2 | 2 | 31 | 36.3 | 36.3 | 10 | 652.05 | 651.53 | 658.23 | 677.23 | 6.4 | 1.22 | 28.22 | 2.22 |  |  |  |  | 691.45 | 28.15 | 0.68 | 0.85
212 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM074 | 1S-DL-YP-ETC-DYVR-2401-SLM074 | BANARASHI CLINIC RISHI KARDAM | TG-SLM074A-1 | 19504177 | 1600 | 500 | 237 | 0.97 | 689 | 261 | 1088 | 228 | 952 | 200 | 825 | 228 | 2019-06-29 23:30 | 165.6 | 57.5 | 1088 | R | 108 | 105 | 87 | 21 |  |  | 33.2 | 66.8 | 1.3 | 2.3 | 40 | 6.3 | 657.28 | 678.21 | 678.21 | 694.08 | 57.2 | 35.27 | 0.2 | 15.4 | [8 empty] | 716.18 | 3.42 | 0.71 | 0.43
213 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM075 | 1S-DL-YP-ETC-DYVR-2401-SLM075 | AGGRAWAL SWEET BHRAHPURI ROAD | TG-SLM075A-1 | 19506060 | 990 | 320 | 237 | 0.98 | 466 | 122 | 511 | 167 | 711 | 177 | 744 | 218 | 2019-06-30 03:30 | 175 | 27.8 | 805 | Y | 78 | 113 | 109 | 35 | 0.1 |  | 6.2 | 93.7 | 45.3 | 1 | 0.3 | 1 | 670.33 | 486.32 | 486.32 | 666.4 |  | 228.31 | 162.52 | 48.23 | [8 empty] | 716.03 | 3.57 | 0.7 | 0.47
214 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM076 | 1S-DL-YP-ETC-DYVR-2401-SLM076 | NALA NO 5 SEELAMPUR:PL | TG-SLM076A-1 | 19505111 | 630 | 200 | 249 | 0.96 | 541 | 200 | 804 | 179 | 734 | 162 | 655 | 129 | 2019-06-18 03:30 | 108 | 12 | 804 | R | 90 | 79 | 130 | 51 | 2.9 | 0.3 | 36.3 | 60.6 | 443.11 | 575.21 | 77.1 | 276.43 | 249.27 | 117.17 | 117.17 | 416.25 | 0.3 | 0.3 | 5.55 |  | 0.25 | 0.25 |  | 0.25 |  |  |  |  | 693.33 | 26.27 | 0.24 | 0.86
215 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM078 | 1S-DL-YP-ETC-DYVR-2401-SLM078 | JANTA COLONY NO4:PL | TG-SLM078A-1 | 19505308 | 630 | 200 | 247 | 0.96 | 304 | 109 | 434 | 42 | 166 | 153 | 618 | 393 | 2019-06-02 02:30 | 75.4 | 21 | 618 | B | 102 | 56 | 142 | 86 | 0.1 | 3.7 | 67.2 | 29.1 | 57.37 | 615.03 | 4.15 | 30.41 | 572.3 | 75.51 | 75.51 | 631.43 | 60.47 |  | 379.51 | 28.3 | [8 empty] | 690.54 | 29.06 | 0.61 | 0.48
216 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM078 | 1S-DL-YP-ETC-DYVR-2401-SLM078 | JANTA COLONY NO4:PL | TG-SLM078A-2 | 19505557 | 630 | 200 | 245 | 0.96 | 445 | 132 | 547 | 176 | 728 | 137 | 569 | 171 | 2019-06-30 12:30 | 140.2 | 37.4 | 762 | Y | 77 | 130 | 93 | 53 | 0.2 | 0.1 | 2.6 | 97.2 | 0.41 |  | 0.17 |  | 539.52 | 2 | 2 | 87.19 | 173.52 | 707.08 | 497.26 | 627.06 |  | 5.17 | [6 empty] | 714.25 | 5.35 | 0.65 | 0.71
217 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM079 | 1S-DL-YP-ETC-DYVR-2401-SLM079 | JANTA COLONY NO-5:PL | TG-SLM079A-1 | 19505204 | 630 | 200 | 245 | 0.95 | 374 | 187 | 735 | 68 | 264 | 119 | 468 | 409 | 2019-06-12 03:30 | 121 | 27.2 | 735 | R | 93 | 82 | 125 | 43 | 0.1 | 0.1 | 46 | 53.8 | 5.3 | 1.38 | 28.29 | 3.38 | 469.12 | 650.45 | 650.45 | 326.25 | 217.46 | 40.35 | 593.24 | 362.55 | 0.3 | [7 empty] | 692.58 | 27.02 | 0.67 | 0.59
218 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM079 | 1S-DL-YP-ETC-DYVR-2401-SLM079 | JANTA COLONY NO-5:PL | TG-SLM079A-2 | 19506014 | 400 | 120 | 251 | 0.96 | 258 | 57 | 217 | 117 | 454 | 83 | 322 | 206 | 2019-06-13 19:00 | 83.8 | 21.4 | 596 | Y | 71 | 139 | 90 | 68 | 0.2 | 2 | 62.9 | 34.9 | 10.41 |  | 1.41 |  | 598.18 | 11 | 11 | 165.43 | 79.04 | 660.11 | 341.49 | 522.2 |  | 16.22 |  |  |  | 0.3 |  |  | 688.03 | 31.57 | 0.67 | 0.64
219 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM080 | 1S-DL-YP-ETC-DYVR-2401-SLM080 | JANTA COLONY NO-6:PL | TG-SLM080A-1 | 19506247 | 630 | 200 | 238 | 0.96 | 481 | 173 | 737 | 127 | 536 | 182 | 782 | 227 | 2019-06-30 12:30 | 155.6 | 45.2 | 785 | B | 101 | 95 | 104 | 9 |  | 0.2 | 13.5 | 86.3 |  |  |  |  | 40.24 | 75.09 | 75.09 | 31.58 | 652.29 | 618.14 | 682.53 | 661.25 | 0.3 |  | 1 | [5 empty] | 693.23 | 26.37 | 0.71 | 0.76
220 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM081 | 1S-DL-YP-ETC-DYVR-2401-SLM081 | JANTA COLONY NO-7:PL | TG-SLM081A-1 | 19506664 | 630 | 200 | 239 | 0.97 | 413 | 125 | 502 | 139 | 564 | 149 | 607 | 92 | 2019-06-01 03:00 | 107.6 | 0.2 | 621 | R | 103 | 90 | 107 | 17 |  | 0.1 | 34 | 65.9 | 3 | 2 | 2 | 2 | 102.17 | 329.55 | 329.55 | 114.29 | 593.1 | 366.32 | 622.36 | 581.58 | [8 empty] | 698.27 | 21.33 | 0.7 | 0.66
221 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM081 | 1S-DL-YP-ETC-DYVR-2401-SLM081 | JANTA COLONY NO-7:PL | TG-SLM081A-2 | 19502710 | 630 | 200 | 247 | 0.96 | 202 | 52 | 209 | 98 | 399 | 52 | 211 | 190 | 2019-06-02 20:00 | 52.4 | 20.7 | 423 | Y | 80 | 141 | 80 | 61 |  |  | 4.5 | 95.5 | 579.19 | 29.22 | 536.2 | 234.11 | 137.42 | 629.17 | 629.17 | 482.5 |  | 58.22 | [10 empty] | 717.01 | 2.59 | 0.67 | 0.32
222 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM104 | 1S-DL-YP-ETC-DYVR-2401-SLM104 | Fire Brigade Shastri Park Shastri Park | TG-SLM104A-1 | 19502305 | 400 | 120 | 245 | 0.99 | 15 | 7 | 30 | 3 | 14 | 4 | 18 | 14 | 2019-06-28 21:30 | 6.6 | -0.8 | 30 | R | 112 | 93 | 95 | 19 | 7.7 | 0.4 | 23 | 68.9 | 719.45 | 719.45 | 719.45 | 719.45 | [16 empty] | 719.45 | 0.15 | 0.31 | 0.04
223 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM111 | 1S-DL-YP-ETC-DYVR-2401-SLM111 | MCD OFFICE,KESHAV CHOWK | TG-SLM111A-1 | 19505109 | 400 | 120 | 264 | 0.99 | 302 | 120 | 481 | 82 | 326 | 100 | 384 | 135 | 2019-06-26 14:00 | 65 | -14.8 | 481 | R | 113 | 82 | 105 | 31 | 79.8 | 20.1 | 0.1 |  | 207 | 229 | 205.3 | 207.3 | 310.54 | 336.52 | 336.52 | 333.22 | 163.46 | 137.44 | 182.41 | 162.44 | 21.56 |  | 1 | [5 empty] | 703.36 | 16.24 | 0.39 | 0.76
224 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM128 | 1S-DL-YP-ETC-DYVR-2401-SLM128 | E-BLOCK NALA SEELAMPUR | TG-SLM128A-1 | 19506062 | 630 | 200 | 234 | 0.97 | 430 | 88 | 358 | 112 | 468 | 230 | 998 | 592 | 2019-06-28 07:00 | 141.4 | 35.4 | 998 | B | 99 | 102 | 99 | 3 | 0.1 | 0.2 | 44 | 55.6 |  |  |  |  | 85.33 | 78.01 | 78.01 | 64.5 | 609.25 | 616.57 | 615.1 | 630.08 | [6 empty] | 0.3 |  | 694.58 | 25.02 | 0.71 | 0.68
225 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM131 | 1S-DL-YP-ETC-DYVR-2401-SLM131 | EDMC Shahadara Jheel | TG-SLM131A-1 | 19506629 | 400 | 120 | 237 | 0.94 | 456 | 140 | 624 | 167 | 731 | 149 | 664 | 94 | 2019-06-17 22:30 | 4 | -347.9 | 731 | Y | 102 | 94 | 104 | 10 | 0.1 | 0.1 | 19.2 | 80.7 | 702.35 | 702.35 | 702.35 | 702.35 | [12 empty] | 0.3 | 0.3 | 0.3 | 0.3 | 703.05 | 16.55 | 0.02 | 1.14
226 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM001 | 1S-DL-YP-ETC-DYVR-2401-SLM001 | USMAN PUR KIOSK:K | TG-SLM001A-1 | 19502886 | 990 | 320 | 242 | 0.98 | 935 | 314 | 1340 | 293 | 1248 | 327 | 1402 | 134 | 2019-06-27 23:00 | 167.8 | 53.7 | 1518 | Y | 99 | 97 | 104 | 7 |  |  | 20.6 | 79.4 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 7.3 | 7.3 | 0.3 | 650.21 | 627.46 | 634.55 | 654.53 | 59.25 | 73 | 75.21 | 55.23 |  | 2.3 |  |  | 711.16 | 8.44 | 0.7 | 0.94
227 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM001 | 1S-DL-YP-ETC-DYVR-2401-SLM001 | USMAN PUR KIOSK:K | TG-SLM001A-2 | 19506418 | 630 | 200 | 236 | 0.98 | 751 | 209 | 911 | 269 | 1189 | 272 | 1188 | 277 | 2019-06-14 | 195.8 | 12.8 | 1218 | B | 104 | 103 | 93 | 11 | 0.1 | 0.4 | 18.8 | 80.7 | 1 | 1 | 153.56 | 1 | 2 | 2 | 2 | 9 | 511.04 | 499.2 | 319.17 | 517.15 | 166.08 | 154.2 | 130.55 | 124.47 | 14.08 | 37.4 | 89.59 | 42.18 | 694.2 | 25.4 | 0.58 | 1.19
228 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM002 | 1S-DL-YP-ETC-DYVR-2401-SLM002 | MCD FLATS NO 1 SHASTRI PARK:ID | TG-SLM002A-1 | 19506674 | 630 | 200 | 247 | 0.96 | 379 | 153 | 647 | 199 | 808 | 27 | 110 | 633 | 2019-06-17 22:30 | 82.2 | 8 | 808 | Y | 84 | 134 | 82 | 52 | 0.1 |  | 17.6 | 82.4 | 390.55 | 111.29 | 438.25 | 280.01 | 152.3 | 381.56 | 381.56 | 263.24 | 0.3 | 50 |  | 0.3 |  | 0.3 | [6 empty] | 697.45 | 22.15 | 0.34 | 0.6
229 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM003 | 1S-DL-YP-ETC-DYVR-2401-SLM003 | MCD FLATE NO.2 SHASTRI PARK:ID | TG-SLM003A-1 | 19506476 | 400 | 120 | 237 | 0.97 | 334 | 72 | 314 | 144 | 631 | 119 | 517 | 278 | 2019-06-29 23:30 | 97.1 | 2.3 | 677 | B | 108 | 32 | 160 | 128 | 0.3 | 0.1 | 4.5 | 95.1 | 17 | 591.09 |  | 19.3 | 307.09 | 4.38 | 4.38 | 409.33 | 375.38 | 75 | 545.45 | 267.44 |  | 23 | 91.58 | 3 |  | 6 | 1.46 |  | 699.47 | 20.13 | 0.46 | 0.84
230 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM004 | 1S-DL-YP-ETC-DYVR-2401-SLM004 | MCD FLATS NO 3 SHASTRI PARK:ID | TG-SLM004A-1 | 19506771 | 400 | 120 | 232 | 0.98 | 133 | 34 | 153 | 99 | 454 | 0 | 0 | 400 | 2019-06-02 00:30 | 35.2 | 0.8 | 454 | Y | 76 | 224 | 0 | 224 | 0.1 | 0.2 | 42.5 | 57.2 | 638.44 | 82.08 | 698.46 | 550.19 | 60.02 | 398.04 | 398.04 | 148.27 |  | 218.34 | [10 empty] | 698.46 | 21.14 | 0.46 | 0.33
231 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM005 | 1S-DL-YP-ETC-DYVR-2401-SLM005 | GAUTAM PURI NO.1:PL | TG-SLM005A-1 | 19506608 | 990 | 320 | 248 | 0.96 | 1018 | 309 | 1299 | 353 | 1465 | 356 | 1501 | 186 | 2019-06-03 14:30 | 352.3 | 104.6 | 1810 | Y | 90 | 106 | 104 | 16 | 0.3 | 0.1 | 27.6 | 72 |  |  |  |  | 3.3 |  |  | 0.3 | 654.59 | 477 | 474.3 | 554.3 | 43.57 | 216.26 | 218.57 | 144.26 |  | 9 | 8.59 | 3 | 702.26 | 17.34 | 0.69 | 1.03
232 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM006 | 1S-DL-YP-ETC-DYVR-2401-SLM006 | GAUTAM PURI NO.2:K | TG-SLM006A-1 | 19500633 | 630 | 200 | 236 | 0.96 | 398 | 163 | 700 | 137 | 591 | 98 | 420 | 245 | 2019-06-02 23:30 | 115 | 38.6 | 700 | R | 114 | 104 | 82 | 32 |  | 0.1 | 2.5 | 97.4 |  |  | 1 |  | 38.54 | 140.11 | 140.11 | 128.1 | 676.43 | 575.26 | 256.37 | 587.27 | [8 empty] | 715.37 | 4.23 | 0.73 | 0.63
233 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM006 | 1S-DL-YP-ETC-DYVR-2401-SLM006 | GAUTAM PURI NO.2:K | TG-SLM006A-2 | 19503148 | 630 | 200 | 243 | 0.98 | 363 | 100 | 431 | 155 | 667 | 108 | 458 | 224 | 2019-06-11 23:30 | 65.3 | 18.9 | 677 | Y | 86 | 97 | 117 | 31 |  | 0.3 | 78.9 | 20.8 | 3.31 | 0.3 | 3.53 | 3.31 | 605.49 | 437.03 | 437.03 | 381.47 | 106.17 | 278.04 | 522.59 | 330.19 | [8 empty] | 715.37 | 4.23 | 0.69 | 0.58
234 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM007 | 1S-DL-YP-ETC-DYVR-2401-SLM007 | BHAGAT SINGH MOHALLA:PL | TG-SLM007A-1 | 19504172 | 990 | 320 | 242 | 0.97 | 858 | 281 | 1231 | 282 | 1241 | 295 | 1294 | 59 | 2019-06-30 23:00 | 216.4 | 69.2 | 1311 | Y | 96 | 103 | 100 | 7 |  |  | 59.1 | 40.9 |  |  |  |  | 59.49 | 39.1 | 39.1 | 31.4 | 626.39 | 635.13 | 668.26 | 657.13 | 27 | 39.05 | 18.3 | 24.35 |  |  |  |  | 713.28 | 6.32 | 0.64 | 0.87
235 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM025 | 1S-DL-YP-ETC-DYVR-2401-SLM025 | J BLOCK SEELAMPUR:K | TG-SLM025A-1 | 19504705 | 630 | 200 | 246 | 0.96 | 275 | 78 | 316 | 101 | 410 | 96 | 396 | 88 | 2019-06-29 23:00 | 75 | 23.5 | 429 | B | 76 | 115 | 109 | 39 |  |  | 30.1 | 69.9 | 321.37 | 3 | 7.3 | 24 | 397.39 | 627.32 | 627.32 | 680.46 |  | 88.44 | 45.59 | 14.3 | [8 empty] | 719.16 | 0.44 | 0.66 | 0.44
236 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM025 | 1S-DL-YP-ETC-DYVR-2401-SLM025 | J BLOCK SEELAMPUR:K | TG-SLM025A-2 | 19503186 | 630 | 200 | 233 | 0.97 | 434 | 153 | 643 | 120 | 508 | 162 | 687 | 162 | 2019-06-30 00:30 | 86.9 | 37.3 | 735 | B | 106 | 89 | 105 | 17 |  |  | 19.5 | 80.5 | 1.3 | 1.3 | 1.3 | 1.3 | 101.5 | 306.03 | 306.03 | 166.13 | 615.56 | 411.43 | 561.34 | 551.33 | [8 empty] | 719.16 | 0.44 | 0.68 | 0.69
237 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM025 | 1S-DL-YP-ETC-DYVR-2401-SLM025 | J BLOCK SEELAMPUR:K | TG-SLM025A-3 | 19503152 | 990 | 320 | 240 | 0.96 | 474 | 139 | 578 | 140 | 580 | 195 | 817 | 238 | 2019-06-29 23:30 | 145 | 45.6 | 836 | B | 93 | 89 | 118 | 29 |  |  | 21.9 | 78.1 | 7.3 | 30 | 2.3 | 7 | 686.18 | 667.48 | 667.48 | 613.19 | 25 | 21 | 291.26 | 98.29 | [8 empty] | 718.48 | 1.12 | 0.68 | 0.48
238 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM025 | 1S-DL-YP-ETC-DYVR-2401-SLM025 | J BLOCK SEELAMPUR:K | TG-SLM025A-4 | 19504769 | 400 | 120 | 239 | 0.96 | 162 | 60 | 250 | 37 | 154 | 64 | 267 | 106 | 2019-06-29 23:00 | 48.6 | 17.1 | 278 | B | 107 | 72 | 121 | 49 |  | 0.3 | 48.4 | 51.3 | 2 | 203.16 |  | 5 | 658.33 | 516.16 | 516.16 | 713.32 | 58.59 |  | 181.27 | 1 | [8 empty] | 719.32 | 0.28 | 0.74 | 0.4
239 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM026 | 1S-DL-YP-ETC-DYVR-2401-SLM026 | K BLOCK SEELAMPUR :PL | TG-SLM026A-1 | 19504717 | 990 | 320 | 238 | 0.96 | 705 | 259 | 1100 | 190 | 793 | 256 | 1074 | 295 | 2019-06-29 23:30 | 175.9 | 56.7 | 1100 | R | 101 | 93 | 106 | 13 |  | 0.1 | 39.1 | 60.9 |  |  |  |  | 109.43 | 240.25 | 240.25 | 136.06 | 605.15 | 474.33 | 616.23 | 578.52 | [8 empty] | 714.58 | 5.02 | 0.68 | 0.71
240 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM026 | 1S-DL-YP-ETC-DYVR-2401-SLM026 | K BLOCK SEELAMPUR :PL | TG-SLM026A-2 | 19503638 | 990 | 320 | 239 | 0.97 | 733 | 260 | 1114 | 255 | 1101 | 218 | 933 | 174 | 2019-06-03 | 185.5 | 55.9 | 1129 | Y | 100 | 110 | 90 | 20 |  |  | 33.5 | 66.5 | 1.27 | 0.27 | 0.27 | 0.27 | 140.14 | 50.21 | 50.21 | 98.52 | 572.51 | 663.14 | 455.33 | 615.43 | 0.3 | 1 | [6 empty] | 715.02 | 4.58 | 0.67 | 0.74
241 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM027 | 1S-DL-YP-ETC-DYVR-2401-SLM027 | H BLOCK SEELAMPUR:PL | TG-SLM027A-1 | 19505107 | 990 | 320 | 238 | 0.97 | 764 | 278 | 1160 | 229 | 948 | 258 | 1089 | 187 | 2019-06-29 23:30 | 222.1 | 67.5 | 1349 | B | 88 | 95 | 117 | 29 | 0.2 | 5.7 | 58.6 | 35.5 |  |  |  |  | 169.31 | 77.39 | 77.39 | 37.48 | 530.32 | 625.54 | 647.33 | 665.45 | 3.3 |  | 48.3 | [5 empty] | 703.33 | 16.27 | 0.7 | 0.77
242 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM027 | 1S-DL-YP-ETC-DYVR-2401-SLM027 | H BLOCK SEELAMPUR:PL | TG-SLM027A-2 | 19505146 | 400 | 120 | 229 | 0.97 | 209 | 77 | 354 | 67 | 304 | 65 | 297 | 53 | 2019-06-21 12:30 | 95.8 | 10.2 | 354 | R | 105 | 114 | 81 | 33 | 0.1 |  | 6.7 | 93.3 | 15.3 | 25.3 | 188.24 | 24.3 | 675.19 | 594.37 | 594.37 | 674.18 | 12.57 | 83.39 | 1 | 4.58 | [8 empty] | 703.46 | 16.14 | 0.53 | 0.52
243 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM033 | 1S-DL-YP-ETC-DYVR-2401-SLM033 | ZERO PUSTA USMANPUR:PL | TG-SLM033A-1 | 19503721 | 400 | 120 | 246 | 0.98 | 124 | 60 | 253 | 51 | 216 | 13 | 54 | 183 | 2019-06-29 23:00 | 20.7 | 4.7 | 274 | R | 139 | 122 | 39 | 100 |  |  | 23 | 77 | 112.58 | 206.24 | 717.19 | 472 | 588.33 | 510.55 | 510.55 | 245.19 | 15.48 | [11 empty] | 717.19 | 2.41 | 0.61 | 0.31
244 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM034 | 1S-DL-YP-ETC-DYVR-2401-SLM034 | RAJU WALA SHASTRI PARK:PL | TG-SLM034A-1 | 19505879 | 990 | 320 | 245 | 0.98 | 803 | 260 | 1123 | 304 | 1294 | 239 | 1033 | 230 | 2019-06-29 23:30 | 177.3 | 48 | 1294 | Y | 96 | 106 | 99 | 10 | 0.1 | 6.8 | 48.5 | 44.6 |  |  |  |  | 40.3 | 20.3 | 20.3 | 16.3 | 671.28 | 665.12 | 700.28 | 697.58 | 3.3 | 29.46 |  | 1 |  |  |  |  | 715.28 | 4.32 | 0.69 | 0.81
245 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM035 | 1S-DL-YP-ETC-DYVR-2401-SLM035 | E-BLOCK SHASTRI PARK | TG-SLM035A-1 | 19505651 | 990 | 320 | 250 | 0.97 | 709 | 218 | 892 | 239 | 985 | 252 | 1044 | 132 | 2019-06-11 | 201 | 65 | 1088 | Y | 89 | 107 | 104 | 18 | 0.1 | 0.7 | 62.2 | 37 |  |  |  |  | 182.47 | 20.26 | 20.26 | 44.56 | 516.44 | 679.05 | 651.36 | 654.35 | [8 empty] | 699.31 | 20.29 | 0.72 | 0.72
246 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM035 | 1S-DL-YP-ETC-DYVR-2401-SLM035 | E-BLOCK SHASTRI PARK | TG-SLM035A-2 | 19505776 | 990 | 320 | 239 | 0.98 | 745 | 281 | 1235 | 216 | 942 | 247 | 1085 | 254 | 2019-06-29 23:30 | 151.4 | 43.5 | 1235 | R | 101 | 94 | 105 | 11 | 0.1 | 0.4 | 27 | 72.5 |  |  |  |  | 173.25 | 232.24 | 232.24 | 140.51 | 523.37 | 467.08 | 597.08 | 558.41 | 2.3 | [7 empty] | 699.32 | 20.28 | 0.61 | 0.75
247 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM038 | 1S-DL-YP-ETC-DYVR-2401-SLM038 | DDA FLATS SHASTRI PARK:ID | TG-SLM038A-1 | 19504127 | 630 | 200 | 238 | 0.97 | 319 | 69 | 290 | 131 | 559 | 120 | 505 | 246 | 2019-06-01 23:30 | 72.2 | 24.8 | 560 | Y | 63 | 120 | 116 | 57 |  | 0.1 | 47.3 | 52.6 | 416.08 | 1.3 | 0.3 | 8 | 301.17 | 478.21 | 478.21 | 623.58 |  | 237.34 | 195.13 | 85.27 | [8 empty] | 717.25 | 2.35 | 0.61 | 0.51
248 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM039 | 1S-DL-YP-ETC-DYVR-2401-SLM039 | BULAND MASJID SHASTRI PARK:ID | TG-SLM039A-1 | 19500937 | 990 | 320 | 244 | 0.96 | 572 | 182 | 738 | 182 | 757 | 208 | 854 | 107 | 2019-06-01 23:30 | 138.4 | 40.5 | 879 | R | 106 | 96 | 98 | 10 |  | 5.1 | 86.1 | 8.8 | 0.3 | 2 | 3 | 1 | 345.25 | 503.43 | 503.43 | 440.43 | 369.28 | 209.4 | 247.45 | 273.4 | [8 empty] | 715.23 | 4.37 | 0.66 | 0.58
249 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM039 | 1S-DL-YP-ETC-DYVR-2401-SLM039 | BULAND MASJID SHASTRI PARK:ID | TG-SLM039A-2 | 19505771 | 630 | 200 | 244 | 0.97 | 408 | 143 | 595 | 132 | 543 | 133 | 547 | 50 | 2019-06-01 21:00 | 115.4 | 16.8 | 629 | R | 86 | 104 | 110 | 24 | 0.1 |  | 44.4 | 55.4 | 138.27 | 3.3 | 1.3 | 7 | 456.3 | 592.27 | 592.27 | 587.27 | 103.59 | 102.59 | 136.28 | 104.29 | [8 empty] | 698.56 | 21.04 | 0.48 | 0.65
250 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM041 | 1S-DL-YP-ETC-DYVR-2401-SLM041 | DSIDC SEELAMPUR:PL | TG-SLM041A-1 | 19502313 | 990 | 320 | 242 | 0.98 | 629 | 224 | 952 | 194 | 818 | 211 | 898 | 117 | 2019-06-01 14:30 | 125.9 | 4.4 | 952 | R | 101 | 102 | 97 | 5 |  |  | 8.5 | 91.5 | 21.47 |  | 1.3 |  | 165.5 | 167.09 | 167.09 | 204.47 | 528.24 | 548.52 | 478.16 | 511.14 | [8 empty] | 716.01 | 3.59 | 0.7 | 0.63
251 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM042 | 1S-DL-YP-ETC-DYVR-2401-SLM042 | CPJ BLOCK SEELAMPUR:PL | TG-SLM042A-1 | 19503141 | 990 | 320 | 257 | 0.95 | 491 | 158 | 612 | 156 | 599 | 177 | 682 | 78 | 2019-06-08 06:30 | 169.3 | 61.8 | 739 | B | 96 | 96 | 108 | 12 |  |  | 34.3 | 65.7 | 0.3 | 5 |  |  | 662.58 | 591.58 | 591.58 | 574.58 | 53.43 | 120.13 | 293.56 | 142.13 | [8 empty] | 717.11 | 2.49 | 0.71 | 0.5
252 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM047 | 1S-DL-YP-ETC-DYVR-2401-SLM047 | PRIMARY SCHOOL GAUTAM PURI | TG-SLM047A-1 | 19505461 | 990 | 320 | 239 | 0.98 | 816 | 203 | 876 | 183 | 785 | 430 | 1895 | 1067 | 2019-06-02 14:30 | 179.2 | 29.1 | 1895 | B | 99 | 105 | 96 | 9 | 0.2 | 0.4 | 62.5 | 36.9 |  |  |  |  | 267.55 | 111.57 | 111.57 | 167.25 | 431.35 | 588.33 | 487.41 | 532.35 | 1 |  |  | 0.3 |  |  | 0.3 |  | 700.3 | 19.3 | 0.54 | 0.82
253 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM049 | 1S-DL-YP-ETC-DYVR-2401-SLM049 | KUNDAN LAL PETROL PUMP:PM | TG-SLM049A-1 | 19505852 | 400 | 120 | 252 | 0.96 | 183 | 58 | 224 | 64 | 245 | 61 | 237 | 19 | 2019-06-26 01:00 | 56 | 1.3 | 494 | Y | 98 | 81 | 121 | 40 | 4.8 | 4.6 | 24.2 | 66.5 | 270.16 | 311.58 | 191.51 | 273.28 | 266.19 | 221.47 | 221.47 | 260.17 | 14.3 | 16.2 | 61.5 | 17.2 |  | 1 | [6 empty] | 694.35 | 25.25 | 0.48 | 0.46
254 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM050 | 1S-DL-YP-ETC-DYVR-2401-SLM050 | JANTA COLONY SHASTRI PARK:PM | TG-SLM050A-1 | 19503553 | 400 | 120 | 246 | 0.97 | 205 | 66 | 269 | 79 | 316 | 60 | 241 | 65 | 2019-06-28 01:00 | 56.9 | 13.8 | 333 | Y | 92 | 123 | 86 | 37 |  |  | 0.9 | 99.1 | 6 |  | 27.1 | 1.3 | 626.32 | 252.05 | 252.05 | 544.31 | 79.46 | 460.13 | 37.16 | 166.17 | [8 empty] | 712.18 | 7.42 | 0.69 | 0.51
255 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM064 | 1S-DL-YP-ETC-DYVR-2401-SLM064 | SHASTRI PARK RED LIGHT | TG-SLM064A-1 | 19506731 | 630 | 200 | 246 | 0.97 | 325 | 125 | 509 | 95 | 380 | 104 | 419 | 115 | 2019-06-28 01:00 | 91.6 | 24 | 525 | R | 113 | 83 | 104 | 30 |  | 0.3 | 11.5 | 88.2 | 0.3 | 40.43 | 5.23 | 2 | 440.28 | 645.54 | 645.54 | 609.59 | 247.3 | 1.51 | 184.56 | 76.29 | [8 empty] | 688.28 | 31.32 | 0.64 | 0.52
256 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM064 | 1S-DL-YP-ETC-DYVR-2401-SLM064 | SHASTRI PARK RED LIGHT | TG-SLM064A-2 | 19504174 | 630 | 200 | 246 | 0.97 | 284 | 81 | 327 | 94 | 379 | 109 | 442 | 100 | 2019-06-02 | 76.4 | 27.6 | 443 | B | 95 | 96 | 109 | 14 |  | 0.3 | 18.9 | 80.8 | 0.3 |  |  |  | 711.36 | 701.19 | 701.19 | 693.19 |  | 10.47 | 111.21 | 18.47 | [8 empty] | 712.06 | 7.54 | 0.72 | 0.45
257 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM065 | 1S-DL-YP-ETC-DYVR-2401-SLM065 | DDA COMPLEX NO 6 | TG-SLM065A-1 | 19506350 | 400 | 120 | 246 | 0.98 | 15 | 4 | 19 | 2 | 8 | 9 | 36 | 24 | 2019-06-01 12:30 | 2.3 | -8.5 | 44 | R | 196 | 95 | 9 | 187 |  |  | 12.5 | 87.5 | 702.45 | 702.45 | 702.45 | 702.45 | [16 empty] | 702.45 | 17.15 | 0.19 | 0.04
258 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM071 | 1S-DL-YP-ETC-DYVR-2401-SLM071 | CISF SHASTRI PARK | TG-SLM071A-1 | 19506249 | 100 | 40 | 246 | 0.54 | 77 | 33 | 131 | 29 | 117 | 15 | 60 | 65 | 2019-06-18 10:30 | 72 | -53.5 | 154 | Y | 91 | 136 | 73 | 63 | 0.2 | 2.5 | 50.6 | 46.7 | 530.19 | 433.49 | 584.13 | 557.49 | 68.43 | 143 | 143 | 35.24 | 91.43 | 57.3 | 86.43 | 98.32 | 1 | 54.56 | 1.3 |  |  | 2.3 |  |  | 691.45 | 28.15 | 0.22 | 0.77
259 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM083 | 1S-DL-YP-ETC-DYVR-2401-SLM083 | HP PETROL PUMP SHASTRI PARK:PM | TG-SLM083A-1 | 19506117 | 100 | 40 | 247 | 0.93 | 34 | 13 | 53 | 12 | 48 | 9 | 38 | 13 | 2019-06-24 15:30 | 15.2 | -0.1 | 56 | Y | 89 | 127 | 84 | 43 | 0.1 |  | 3.1 | 96.9 | 608.49 | 417.43 | 684.36 | 619.2 | 85.46 | 275.52 | 275.52 | 75.15 |  | 1 | [10 empty] | 694.35 | 25.25 | 0.44 | 0.34
260 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM084 | 1S-DL-YP-ETC-DYVR-2401-SLM084 | SHASTRI PARK LADY HOSTEL METRO | TG-SLM084A-1 | 19502255 | 400 | 120 | 253 | 0.97 | 128 | 61 | 197 | 19 | 79 | 48 | 199 | 119 | 2019-06-16 09:00 | 36.7 | -0.6 | 736 | R | 137 | 73 | 91 | 64 | 100 |  |  |  | 154.35 | 685.2 | 622.22 | 571.22 | 546.45 | 31.3 | 31.3 | 145.28 | 15.3 | [11 empty] | 716.5 | 3.1 | 0.5 | 0.32
261 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM085 | 1S-DL-YP-ETC-DYVR-2401-SLM085 | BELA FARM SHASTRI PARK:PM | TG-SLM085A-1 | 19506603 | 100 | 40 | 247 | 0.8 | 9 | 3 | 13 | 0 | 0 | 6 | 24 | 21 | 2019-06-08 09:00 | 3.7 | -0.4 | 34 | B | 9 | 0 | 291 | 291 |  | 0.3 | 47 | 52.7 | 696.08 | 696.08 | 695.38 | 696.08 | [16 empty] | 696.08 | 23.52 | 0.25 | 0.09
262 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM086 | 1S-DL-YP-ETC-DYVR-2401-SLM086 | ENGG COLL GAUTAM PUR NO-3:PL | TG-SLM086A-1 | 19503150 | 630 | 200 | 248 | 0.97 | 418 | 108 | 448 | 136 | 568 | 175 | 726 | 242 | 2019-06-30 23:00 | 111.8 | 30.4 | 754 | B | 85 | 98 | 117 | 32 |  | 0.3 | 46.3 | 53.4 |  |  |  |  | 307.53 | 110.27 | 110.27 | 72.26 | 411.51 | 609.17 | 694.44 | 647.18 |  |  | 9.3 | [5 empty] | 719.44 | 0.16 | 0.73 | 0.66
263 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM086 | 1S-DL-YP-ETC-DYVR-2401-SLM086 | ENGG COLL GAUTAM PUR NO-3:PL | TG-SLM086A-2 | 19505880 | 630 | 200 | 242 | 0.97 | 487 | 165 | 713 | 160 | 689 | 162 | 693 | 22 | 2019-06-29 23:30 | 151 | 43.2 | 813 | R | 108 | 94 | 99 | 14 | 0.1 | 3.7 | 91.9 | 4.2 |  |  |  |  | 12.3 | 51.28 | 51.28 | 16.3 | 694.5 | 667.52 | 690.2 | 702.5 | 12 |  | 1.3 | [5 empty] | 719.2 | 0.4 | 0.71 | 0.77
264 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM087 | 1S-DL-YP-ETC-DYVR-2401-SLM087 | DMRC NO 1 | TG-SLM087A-1 | 19503219 | 630 | 200 | 243 | 0.97 | 139 | 49 | 204 | 37 | 155 | 52 | 217 | 57 | 2019-06-30 | 23.9 | 2.8 | 235 | B | 102 | 88 | 110 | 22 |  |  | 3.1 | 96.9 | 701.29 | 719.59 | 667.59 | 713.29 | 18.3 |  |  | 6.3 | [12 empty] | 719.59 | 0.01 | 0.44 | 0.22
265 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM087 | 1S-DL-YP-ETC-DYVR-2401-SLM087 | DMRC NO 1 | TG-SLM087A-2 | 19500640 | 630 | 200 | 236.42 | 0.92529 | 155.9394 | 51.6615 | 216.3923 | 51.8904 | 218.8267 | 52.3875 | 219.2222 | 2.6543 | 2019-06-30 23:00 | [15 empty] | 626 |  |  |  | 94 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 720 |  | 0.59792 | 0.24752
266 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM088 | 1S-DL-YP-ETC-DYVR-2401-SLM088 | DMRC NO.2 | TG-SLM088A-1 | 19503226 | 990 | 320 | 246 | 0.97 | 143 | 47 | 193 | 50 | 207 | 45 | 186 | 19 | 2019-06-30 23:30 | 22.1 | 2.9 | 207 | Y | 92 | 107 | 101 | 15 | 0.1 |  | 40.3 | 59.5 | 333.29 | 333.29 | 333.29 | 333.29 | [16 empty] | 719.5 | 0.1 | 0.38 | 0.14
267 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM094 | 1S-DL-YP-ETC-DYVR-2401-SLM094 | JANTA COLONY SEELAMPUR NO.9 | TG-SLM094A-1 | 19504854 | 400 | 120 | 245 | 0.93 | 101 | 42 | 169 | 26 | 102 | 33 | 133 | 58 | 2019-06-03 02:00 | 38.6 | 12.1 | 169 | R | 127 | 75 | 98 | 52 |  |  | 44.4 | 55.6 | 163.56 | 717.31 | 471.37 | 594.07 | 553.35 |  |  | 123.24 | [12 empty] | 717.31 | 2.29 | 0.69 | 0.25
268 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM095 | 1S-DL-YP-ETC-DYVR-2401-SLM095 | JANTA COLONY SEELAMPUR NO.8 | TG-SLM095A-1 | 19504995 | 400 | 120 | 239 | 0.96 | 91 | 36 | 150 | 31 | 132 | 24 | 101 | 43 | 2019-06-03 02:00 | 30.4 | 8.8 | 155 | R | 114 | 107 | 80 | 34 |  |  | 7.4 | 92.6 | 693.02 | 716.31 | 717.01 | 716.31 | 24.29 | 1 | 1 | 1 | [12 empty] | 717.31 | 2.29 | 0.63 | 0.23
269 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM095 | 1S-DL-YP-ETC-DYVR-2401-SLM095 | JANTA COLONY SEELAMPUR NO.8 | TG-SLM095A-2 | 19503182 | 400 | 120 | 245 | 0.95 | 86 | 29 | 119 | 31 | 123 | 26 | 106 | 16 | 2019-06-03 00:30 | 29.3 | 9.4 | 125 | Y | 100 | 107 | 93 | 14 | 0.1 |  | 13.4 | 86.5 | 703.3 | 682.56 | 716.58 | 714.59 | 13.58 | 34.32 | 34.32 | 2.29 | [12 empty] | 717.28 | 2.32 | 0.74 | 0.22
270 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM096 | 1S-DL-YP-ETC-DYVR-2401-SLM096 | JANTA COLONY SEELAMPUR NO.2 | TG-SLM096A-1 | 19506576 | 400 | 120 | 246 | 0.97 | 30 | 2 | 7 | 0 | 0 | 29 | 114 | 110 | 2019-06-03 02:00 | 11 | 0.8 | 114 | B | 29 | 37 | 234 | 205 |  |  | 2.4 | 97.6 | 698.45 | 698.45 | 698.15 | 698.45 | [16 empty] | 698.45 | 21.15 | 0.43 | 0.08
271 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM097 | 1S-DL-YP-ETC-DYVR-2401-SLM097 | JANTA COLONY SEELAMPUR NO.3 | TG-SLM097A-1 | 19505802 | 400 | 120 | 245 | 0.96 | 151 | 59 | 235 | 48 | 191 | 44 | 174 | 54 | 2019-06-03 02:30 | 45.8 | 10.4 | 235 | R | 111 | 88 | 101 | 23 |  |  | 14.3 | 85.7 | 264.18 | 631.23 | 396.15 | 431.17 | 434.1 | 67.54 | 67.54 | 268 | 0.49 | [11 empty] | 699.17 | 20.43 | 0.5 | 0.38
272 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM098 | 1S-DL-YP-ETC-DYVR-2401-SLM098 | JANTA COLONY SEELAMPUR NO.4 | TG-SLM098A-1 | 19503160 | 400 | 120 | 233 | 0.96 | 99 | 24 | 103 | 32 | 139 | 43 | 186 | 72 | 2019-06-02 23:30 | 25.4 | 4.7 | 202 | R | 131 | 61 | 108 | 70 |  | 0.1 | 81.2 | 18.7 | 97.55 | 500.57 | 286.2 | 377.57 | 428.02 | 25 | 25 | 148 | [12 empty] | 525.57 | 2.03 | 0.74 | 0.25
273 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM099 | 1S-DL-YP-ETC-DYVR-2401-SLM099 | JANTA COLONY SEELAMPUR NO.1(THANA SIDE) | TG-SLM099A-1 | 19505132 | 400 | 120 | 239 | 0.96 | 200 | 53 | 215 | 57 | 232 | 90 | 368 | 145 | 2019-06-03 02:30 | 61.1 | 14.6 | 368 | B | 90 | 83 | 128 | 45 |  |  | 11.3 | 88.7 | 288.17 | 277.44 | 4.3 | 87.11 | 405.03 | 415.06 | 415.06 | 605.1 |  | 0.3 | 76.01 | 0.59 | [8 empty] | 693.2 | 26.4 | 0.5 | 0.5
274 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM100 | 1S-DL-YP-ETC-DYVR-2401-SLM100 | JANTA COLONY SEELAMPUR NO.6 | TG-SLM100A-1 | 19503181 | 630 | 200 | 250 | 0.93 | 214 | 62 | 244 | 87 | 342 | 65 | 253 | 94 | 2019-06-03 01:30 | 76.8 | 27.1 | 366 | Y | 82 | 126 | 93 | 44 |  | 2.2 | 81.4 | 16.3 | 385.29 | 27.54 | 194.11 | 138.14 | 332.04 | 674.1 | 674.1 | 579.19 |  | 15.29 | [10 empty] | 717.33 | 2.27 | 0.71 | 0.34
275 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM101 | 1S-DL-YP-ETC-DYVR-2401-SLM101 | JANTA COLONY SEELAMPUR NO-5 | TG-SLM101A-1 | 19506381 | 400 | 120 | 239 | 0.95 | 135 | 30 | 121 | 46 | 189 | 58 | 239 | 103 | 2019-06-03 02:00 | 46.1 | 9.5 | 242 | B | 62 | 119 | 118 | 57 |  | 0.1 | 63 | 36.9 | 697.44 | 403.57 | 383.59 | 674.15 | 1.3 | 295.17 | 295.17 | 24.59 |  |  | 0.59 | [9 empty] | 699.14 | 20.46 | 0.49 | 0.34
276 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM103 | 1S-DL-YP-ETC-DYVR-2401-SLM103 | JANTA COLONY SEELAMPUR NO.7 | TG-SLM103A-1 | 19505811 | 400 | 120 | 239 | 0.95 | 123 | 32 | 129 | 59 | 239 | 33 | 134 | 108 | 2019-06-03 02:30 | 42.7 | 8 | 239 | Y | 84 | 130 | 86 | 46 |  |  | 6.9 | 93.1 | 698.45 | 669.24 | 697.21 | 695.22 | 0.3 | 29.21 | 29.21 | 3.53 |  | 0.3 | [10 empty] | 699.15 | 20.45 | 0.4 | 0.31
277 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM105 | 1S-DL-YP-ETC-DYVR-2401-SLM105 | DMRC-No-3 | TG-SLM105A-1 | 19503216 | 990 | 320 | 244 | 0.97 | 95 | 28 | 117 | 34 | 140 | 33 | 138 | 22 | 2019-06-29 23:00 | 16.2 | 1.5 | 145 | Y | 85 | 119 | 96 | 34 |  |  | 7.2 | 92.8 | 719.59 | 719.59 | 719.59 | 719.59 | [16 empty] | 719.59 | 0.01 | 0.42 | 0.1
278 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM108 | 1S-DL-YP-ETC-DYVR-2401-SLM108 | DDA S/STN No-1 SHASTRI PARK | TG-SLM108A-1 | 19505518 | 400 | 120 | 256 | 0.97 | 388 | 129 | 517 | 128 | 516 | 131 | 522 | 5 | 2019-06-14 | 110.9 | 21.1 | 659 | B | 104 | 95 | 101 | 9 | 0.1 | 0.8 | 49.7 | 49.4 | 0.3 | 0.3 | 0.3 | 0.3 | 52.56 | 84.21 | 84.21 | 47.26 | 503.5 | 531.17 | 521.12 | 542.12 | 93.22 | 38 | 63.59 | 64 | 3.3 |  | 17.3 |  | 654.08 | 41.52 | 0.63 | 0.97
279 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM113 | 1S-DL-YP-ETC-DYVR-2401-SLM113 | DMRC NO.4 | TG-SLM113A-1 | 19506750 | 990 | 320 | 245 | 0.96 | 97 | 30 | 125 | 34 | 139 | 32 | 132 | 12 | 2019-06-30 23:30 | 23 | 2.9 | 162 | B | 89 | 108 | 103 | 19 | 0.1 |  | 49.6 | 50.4 | 702.59 | 702.59 | 702.59 | 702.59 | [16 empty] | 702.59 | 17.01 | 0.45 | 0.1
280 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM114 | 1S-DL-YP-ETC-DYVR-2401-SLM114 | POLICE BOOTH MARGINAL BANDH :PL | TG-SLM114A-1 | 19505102 | 400 | 120 | 239 | 0.96 | 175 | 58 | 242 | 63 | 258 | 54 | 223 | 31 | 2019-06-24 08:30 | 103.1 | -3.8 | 258 | Y | 114 | 90 | 96 | 24 |  | 0.2 | 22 | 77.8 | 294.2 | 509.33 | 500.32 | 446.33 | 400.12 | 185.29 | 185.29 | 248.59 | 1.3 | 1 | 0.3 | 0.3 | [8 empty] | 696.02 | 23.58 | 0.43 | 0.44
281 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM118 | 1S-DL-YP-ETC-DYVR-2401-SLM118 | BULAND MASJID SCHOOL WALA SHASTRI PARK :PL | TG-SLM118A-1 | 19505101 | 990 | 320 | 234 | 0.97 | 428 | 146 | 613 | 141 | 587 | 142 | 593 | 24 | 2019-06-27 | 89.9 | 18.6 | 689 | R | 103 | 102 | 95 | 8 |  | 0.1 | 14.4 | 85.5 | 108.12 | 102.17 | 190.08 | 127.36 | 541.03 | 569.58 | 569.58 | 542.39 | 45 | 22 | 18 | 24 | [8 empty] | 694.15 | 25.45 | 0.62 | 0.43
282 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM127 | 1S-DL-YP-ETC-DYVR-2401-SLM127 | GAUTAMPURI NALA:PL | TG-SLM127A-1 | 19505756 | 630 | 200 | 238 | 0.95 | 500 | 169 | 730 | 157 | 684 | 174 | 760 | 66 | 2019-06-11 18:30 | 184.6 | 64.8 | 765 | B | 100 | 95 | 105 | 10 | 0.2 | 0.1 | 27 | 72.7 |  |  |  |  | 88.44 | 80 | 80 | 57.3 | 612.59 | 622.43 | 650.13 | 645.13 | 1 |  | 2 | [5 empty] | 702.43 | 17.17 | 0.65 | 0.79
283 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM129 | 1S-DL-YP-ETC-DYVR-2401-SLM129 | Vijay Coat market Shastri Park:Pkg | TG-SLM129A-1 | 19506118 | 630 | 200 | 245 | 0.83 | 31 | 10 | 39 | 18 | 71 | 4 | 14 | 49 | 2019-06-25 18:30 | 23.8 | 0.2 | 90 | R | 95 | 151 | 54 | 97 |  |  | 46.3 | 53.7 | 701.58 | 701.58 | 701.58 | 701.58 | [16 empty] | 701.58 | 18.02 | 0.37 | 0.05
284 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM133 | 1S-DL-YP-ETC-DYVR-2401-SLM133 | Police Staff Qtrs Usmanpur | TG-SLM133A-1 | 19506712 | 630 | 200 | 246 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [7 empty] | 15.6 | 84.4 | 698.46 | 698.46 | 698.46 | 698.46 | [16 empty] | 698.46 | 21.14 |  | 0
285 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM137 | 1S-DL-YP-ETC-DYVR-2401-SLM137 | DMRC Staff Qtrs No.-5 S/Stn | TG-SLM137A-1 | 19506822 | 630 | 200 | 246 | 0.9 | 49 | 17 | 69 | 17 | 67 | 14 | 57 | 11 | 2019-06-25 22:30 | 12 | -10.4 | 70 | R | 111 | 94 | 94 | 17 |  |  | 5 | 95 | 701.59 | 701.59 | 701.59 | 701.59 | [16 empty] | 701.59 | 18.01 | 0.31 | 0.08