## Underload DTs
MIS Report of Distribution Transformer - Jun19
Jun19 1250 YAMUNA VIHAR (Underload DTs)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM016 | 1S-DL-YP-ETC-DYVR-2402-YAM016 | POLICE STATION., BHAJAN PURA:ID | TG-YAM016A-2 | 19506051 | 400 | 120 | 243 | 0.98 | 64 | 16 | 63 | 19 | 76 | 29 | 116 | 48 | 2019-06-11 07:00 | 26 | -0.8 | 156 | B | 79 | 79 | 142 | 63 |  |  | 3.6 | 96.4 | 702.14 | 701.44 | 690.44 | 702.14 |  | 0.3 | 0.3 | [13 empty] | 702.14 | 17.46 | 0.48 | 0.16
2 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM044 | 1S-DL-YP-ETC-DYVR-2402-YAM044 | ZAMALO KA BAGH MAUJ PUR:PL | TG-YAM044A-1 | 19505148 | 990 | 200 | 253 | 0.98 | 289 | 61 | 241 | 144 | 574 | 84 | 337 | 296 | 2019-06-28 12:00 | 95 | -61 | 578 | Y | 110 | 153 | 37 | 116 |  |  | 34.8 | 65.2 | 694.4 | 501.06 | 693.4 | 690.4 |  | 191.34 | 191.34 | 4 |  | 2 | [10 empty] | 694.4 | 25.2 | 0.33 | 0.29
3 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | C-12 YAMUNA VIHAR | 1250 | YAM061 | 1S-DL-YP-ETC-DYVR-2402-YAM061 | WZB-KHAJOORI FLYOVER T-Pt.(S.B. FLYOVER) | TG-YAM061A-1 | 19506698 | 400 | 120 | 246 | 0.99 | 36 | 7 | 26 | 19 | 70 | 11 | 41 | 38 | 2019-06-18 01:30 | 24.8 | -33.6 | 85 | Y | 67 | 147 | 86 | 80 |  | 0.1 | 3.4 | 96.5 | 696.49 | 696.49 | 696.49 | 696.49 | [16 empty] | 696.49 | 23.11 | 0.3 | 0.09
4 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO030 | 1S-DL-YP-ETC-DYVR-2404-GHO030 | NANAKSAR GURUDWARA:PM | TG-GHO030A-1 | 19505142 | 100 | 40 | 229 | 0.96 | 36 | 3 | 18 | 11 | 46 | 21 | 90 | 63 | 2019-06-30 17:30 | 15.3 | 0.8 | 90 | B | 59 | 128 | 113 | 69 | 100 |  |  |  | 696.47 | 607.49 | 634.49 | 660.19 |  | 84.28 | 84.28 | 36.28 |  | 4.3 | 5.3 | [9 empty] | 697.11 | 22.49 | 0.09 | 0.36
5 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | GHONDA | 1250 | GHO059 | 1S-DL-YP-ETC-DYVR-2404-GHO059 | DJB RAINY WELL-W-II, NEAR NANAKSAR WZB. | TG-GHO059A-1 | 19506627 | 400 | 120 | 252 | 0.9 | 159 | 54 | 210 | 53 | 207 | 53 | 206 | 4 | 2019-06-14 18:30 | 116.9 | -0.1 | 210 | R | 113 | 96 | 91 | 22 |  | 0.4 | 5.2 | 94.4 | 643.35 | 645.35 | 645.35 | 644.05 | 53.16 | 51.46 | 51.46 | 53.16 | 0.3 | [11 empty] | 697.21 | 22.39 | 0.07 | 0.4
6 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM030 | 1S-DL-YP-ETC-DYVR-2401-SLM030 | E BLOCK SEELAMPUR:K | TG-SLM030A-2 | 19506349 | 990 | 320 | 254 | 0.96 | 187 | 35 | 134 | 24 | 92 | 129 | 605 | 494 | 2019-06-01 19:00 | 53.4 | 10.9 | 605 | B | 56 | 66 | 178 | 122 | 8.9 | 2.3 | 15 | 73.8 | 710.03 | 710.03 | 235.29 | 710.03 | [16 empty] | 710.03 | 9.57 | 0.64 | 0.19
7 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM045 | 1S-DL-YP-ETC-DYVR-2401-SLM045 | POLICE STATION SEELAMPUR:ID | TG-SLM045A-1 | 19504278 | 400 | 120 | 248 | 0.97 | 56 | 19 | 77 | 20 | 80 | 17 | 70 | 9 | 2019-06-01 23:00 | 16.3 | 1.1 | 128 | Y | 80 | 117 | 103 | 37 |  |  | 6.2 | 93.8 | 711.59 | 703.33 | 711.59 | 711.59 |  | 8.26 | 8.26 | [13 empty] | 711.59 | 8.01 | 0.49 | 0.14
8 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM069 | 1S-DL-YP-ETC-DYVR-2401-SLM069 | TAJ COLONY | TG-SLM069A-1 | 19506675 | 400 | 120 | 246 | 0.97 | 83 | 26 | 109 | 19 | 80 | 37 | 152 | 63 | 2019-06-02 14:00 | 22.9 | 2.2 | 192 | B | 103 | 100 | 98 | 5 | 0.1 |  | 17.3 | 82.6 | 690.12 | 697.42 | 685.12 | 698.12 | 8.3 | 1 | 1 | 0.3 | [12 empty] | 698.42 | 21.18 | 0.59 | 0.21
9 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM104 | 1S-DL-YP-ETC-DYVR-2401-SLM104 | Fire Brigade Shastri Park Shastri Park | TG-SLM104A-1 | 19502305 | 400 | 120 | 245 | 0.99 | 15 | 7 | 30 | 3 | 14 | 4 | 18 | 14 | 2019-06-28 21:30 | 6.6 | -0.8 | 30 | R | 112 | 93 | 95 | 19 | 7.7 | 0.4 | 23 | 68.9 | 719.45 | 719.45 | 719.45 | 719.45 | [16 empty] | 719.45 | 0.15 | 0.31 | 0.04
10 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | NEW SEELAMPUR | 1250 | SLM131 | 1S-DL-YP-ETC-DYVR-2401-SLM131 | EDMC Shahadara Jheel | TG-SLM131A-1 | 19506629 | 400 | 120 | 237 | 0.94 | 456 | 140 | 624 | 167 | 731 | 149 | 664 | 94 | 2019-06-17 22:30 | 4 | -347.9 | 731 | Y | 102 | 94 | 104 | 10 | 0.1 | 0.1 | 19.2 | 80.7 | 702.35 | 702.35 | 702.35 | 702.35 | [12 empty] | 0.3 | 0.3 | 0.3 | 0.3 | 703.05 | 16.55 | 0.02 | 1.14
11 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM065 | 1S-DL-YP-ETC-DYVR-2401-SLM065 | DDA COMPLEX NO 6 | TG-SLM065A-1 | 19506350 | 400 | 120 | 246 | 0.98 | 15 | 4 | 19 | 2 | 8 | 9 | 36 | 24 | 2019-06-01 12:30 | 2.3 | -8.5 | 44 | R | 196 | 95 | 9 | 187 |  |  | 12.5 | 87.5 | 702.45 | 702.45 | 702.45 | 702.45 | [16 empty] | 702.45 | 17.15 | 0.19 | 0.04
12 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM085 | 1S-DL-YP-ETC-DYVR-2401-SLM085 | BELA FARM SHASTRI PARK:PM | TG-SLM085A-1 | 19506603 | 100 | 40 | 247 | 0.8 | 9 | 3 | 13 | 0 | 0 | 6 | 24 | 21 | 2019-06-08 09:00 | 3.7 | -0.4 | 34 | B | 9 | 0 | 291 | 291 |  | 0.3 | 47 | 52.7 | 696.08 | 696.08 | 695.38 | 696.08 | [16 empty] | 696.08 | 23.52 | 0.25 | 0.09
13 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM087 | 1S-DL-YP-ETC-DYVR-2401-SLM087 | DMRC NO 1 | TG-SLM087A-1 | 19503219 | 630 | 200 | 243 | 0.97 | 139 | 49 | 204 | 37 | 155 | 52 | 217 | 57 | 2019-06-30 | 23.9 | 2.8 | 235 | B | 102 | 88 | 110 | 22 |  |  | 3.1 | 96.9 | 701.29 | 719.59 | 667.59 | 713.29 | 18.3 |  |  | 6.3 | [12 empty] | 719.59 | 0.01 | 0.44 | 0.22
14 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM088 | 1S-DL-YP-ETC-DYVR-2401-SLM088 | DMRC NO.2 | TG-SLM088A-1 | 19503226 | 990 | 320 | 246 | 0.97 | 143 | 47 | 193 | 50 | 207 | 45 | 186 | 19 | 2019-06-30 23:30 | 22.1 | 2.9 | 207 | Y | 92 | 107 | 101 | 15 | 0.1 |  | 40.3 | 59.5 | 333.29 | 333.29 | 333.29 | 333.29 | [16 empty] | 719.5 | 0.1 | 0.38 | 0.14
15 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM095 | 1S-DL-YP-ETC-DYVR-2401-SLM095 | JANTA COLONY SEELAMPUR NO.8 | TG-SLM095A-2 | 19503182 | 400 | 120 | 245 | 0.95 | 86 | 29 | 119 | 31 | 123 | 26 | 106 | 16 | 2019-06-03 00:30 | 29.3 | 9.4 | 125 | Y | 100 | 107 | 93 | 14 | 0.1 |  | 13.4 | 86.5 | 703.3 | 682.56 | 716.58 | 714.59 | 13.58 | 34.32 | 34.32 | 2.29 | [12 empty] | 717.28 | 2.32 | 0.74 | 0.22
16 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM095 | 1S-DL-YP-ETC-DYVR-2401-SLM095 | JANTA COLONY SEELAMPUR NO.8 | TG-SLM095A-1 | 19504995 | 400 | 120 | 239 | 0.96 | 91 | 36 | 150 | 31 | 132 | 24 | 101 | 43 | 2019-06-03 02:00 | 30.4 | 8.8 | 155 | R | 114 | 107 | 80 | 34 |  |  | 7.4 | 92.6 | 693.02 | 716.31 | 717.01 | 716.31 | 24.29 | 1 | 1 | 1 | [12 empty] | 717.31 | 2.29 | 0.63 | 0.23
17 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM096 | 1S-DL-YP-ETC-DYVR-2401-SLM096 | JANTA COLONY SEELAMPUR NO.2 | TG-SLM096A-1 | 19506576 | 400 | 120 | 246 | 0.97 | 30 | 2 | 7 | 0 | 0 | 29 | 114 | 110 | 2019-06-03 02:00 | 11 | 0.8 | 114 | B | 29 | 37 | 234 | 205 |  |  | 2.4 | 97.6 | 698.45 | 698.45 | 698.15 | 698.45 | [16 empty] | 698.45 | 21.15 | 0.43 | 0.08
18 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM101 | 1S-DL-YP-ETC-DYVR-2401-SLM101 | JANTA COLONY SEELAMPUR NO-5 | TG-SLM101A-1 | 19506381 | 400 | 120 | 239 | 0.95 | 135 | 30 | 121 | 46 | 189 | 58 | 239 | 103 | 2019-06-03 02:00 | 46.1 | 9.5 | 242 | B | 62 | 119 | 118 | 57 |  | 0.1 | 63 | 36.9 | 697.44 | 403.57 | 383.59 | 674.15 | 1.3 | 295.17 | 295.17 | 24.59 |  |  | 0.59 | [9 empty] | 699.14 | 20.46 | 0.49 | 0.34
19 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM103 | 1S-DL-YP-ETC-DYVR-2401-SLM103 | JANTA COLONY SEELAMPUR NO.7 | TG-SLM103A-1 | 19505811 | 400 | 120 | 239 | 0.95 | 123 | 32 | 129 | 59 | 239 | 33 | 134 | 108 | 2019-06-03 02:30 | 42.7 | 8 | 239 | Y | 84 | 130 | 86 | 46 |  |  | 6.9 | 93.1 | 698.45 | 669.24 | 697.21 | 695.22 | 0.3 | 29.21 | 29.21 | 3.53 |  | 0.3 | [10 empty] | 699.15 | 20.45 | 0.4 | 0.31
20 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM105 | 1S-DL-YP-ETC-DYVR-2401-SLM105 | DMRC-No-3 | TG-SLM105A-1 | 19503216 | 990 | 320 | 244 | 0.97 | 95 | 28 | 117 | 34 | 140 | 33 | 138 | 22 | 2019-06-29 23:00 | 16.2 | 1.5 | 145 | Y | 85 | 119 | 96 | 34 |  |  | 7.2 | 92.8 | 719.59 | 719.59 | 719.59 | 719.59 | [16 empty] | 719.59 | 0.01 | 0.42 | 0.1
21 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM113 | 1S-DL-YP-ETC-DYVR-2401-SLM113 | DMRC NO.4 | TG-SLM113A-1 | 19506750 | 990 | 320 | 245 | 0.96 | 97 | 30 | 125 | 34 | 139 | 32 | 132 | 12 | 2019-06-30 23:30 | 23 | 2.9 | 162 | B | 89 | 108 | 103 | 19 | 0.1 |  | 49.6 | 50.4 | 702.59 | 702.59 | 702.59 | 702.59 | [16 empty] | 702.59 | 17.01 | 0.45 | 0.1
22 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM129 | 1S-DL-YP-ETC-DYVR-2401-SLM129 | Vijay Coat market Shastri Park:Pkg | TG-SLM129A-1 | 19506118 | 630 | 200 | 245 | 0.83 | 31 | 10 | 39 | 18 | 71 | 4 | 14 | 49 | 2019-06-25 18:30 | 23.8 | 0.2 | 90 | R | 95 | 151 | 54 | 97 |  |  | 46.3 | 53.7 | 701.58 | 701.58 | 701.58 | 701.58 | [16 empty] | 701.58 | 18.02 | 0.37 | 0.05
23 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM133 | 1S-DL-YP-ETC-DYVR-2401-SLM133 | Police Staff Qtrs Usmanpur | TG-SLM133A-1 | 19506712 | 630 | 200 | 246 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [7 empty] | 15.6 | 84.4 | 698.46 | 698.46 | 698.46 | 698.46 | [16 empty] | 698.46 | 21.14 |  | 0
24 | 2019-06-01 | 2019-06-30 23:30 | YAMUNA VIHAR | SHASTRI PARK | 1250 | SLM137 | 1S-DL-YP-ETC-DYVR-2401-SLM137 | DMRC Staff Qtrs No.-5 S/Stn | TG-SLM137A-1 | 19506822 | 630 | 200 | 246 | 0.9 | 49 | 17 | 69 | 17 | 67 | 14 | 57 | 11 | 2019-06-25 22:30 | 12 | -10.4 | 70 | R | 111 | 94 | 94 | 17 |  |  | 5 | 95 | 701.59 | 701.59 | 701.59 | 701.59 | [16 empty] | 701.59 | 18.01 | 0.31 | 0.08