## Complete Report
MIS Report of Distribution Transformer - Jun19
Jun19 1251 KARAWAL NAGAR (Complete Report)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL001 | 1S-DL-YP-ETC-DKWL-2451-KWL001 | RAJEEV GANDHI NAGAR GALI NO.-3:ID | TG-KWL001A-1 | 19506907 | 630 | 200 | 251 | 0.96 | 664 | 206 | 824 | 234 | 963 | 224 | 916 | 122 | 2019-06-10 21:30 | 259.4 | 62 | 963 | Y | 85 | 108 | 106 | 23 | 0.1 | 1.9 | 69.3 | 28.7 |  |  |  |  | 16 | 3.3 | 3.3 | 3 | 672.33 | 626.09 | 645.31 | 674.13 | 6.02 | 60.12 | 44.17 | 16.29 | 0.3 | 5.14 | 5.17 | 1.23 | 695.05 | 24.55 | 0.59 | 1.05
2 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL001 | 1S-DL-YP-ETC-DKWL-2451-KWL001 | RAJEEV GANDHI NAGAR GALI NO.-3:ID | TG-KWL001A-2 | 19505431 | 630 | 200 | 258 | 0.96 | 495 | 232 | 933 | 175 | 703 | 88 | 343 | 515 | 2019-06-02 | 183.4 | 45.6 | 933 | R | 144 | 107 | 49 | 95 | 1.4 | 45.2 | 53.4 |  |  |  | 291.34 |  | 5.3 | 165.25 | 165.25 | 250.23 | 674.5 | 529.02 | 0.58 | 444.57 | 11.52 | 0.53 |  |  | 3.08 |  |  |  | 695.2 | 24.4 | 0.54 | 0.79
3 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL002 | 1S-DL-YP-ETC-DKWL-2451-KWL002 | RAJEEV GANDHI NAGAR GALI NO.-8:ID | TG-KWL002A-1 | 19502976 | 990 | 200 | 255 | 0.96 | 567 | 271 | 1080 | 135 | 540 | 161 | 637 | 499 | 2019-06-02 14:30 | 169.3 | 67.2 | 1080 | R | 140 | 74 | 86 | 66 |  | 0.1 | 96.4 | 3.5 |  | 7.3 |  |  | 7.3 | 687.34 | 687.34 | 238.23 | 705.53 | 20.19 | 200.4 | 477 | 2 | [7 empty] | 715.23 | 4.37 | 0.74 | 0.57
4 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL003 | 1S-DL-YP-ETC-DKWL-2451-KWL003 | RAJEEV GANDHI NAGAR GALI NO.-15:ID | TG-KWL003A-1 | 19505388 | 990 | 320 | 240 | 0.97 | 833 | 278 | 1269 | 284 | 1343 | 271 | 1252 | 84 | 2019-06-03 14:30 | 280.6 | 56.3 | 1354 | Y | 101 | 107 | 93 | 14 | 0.4 | 91.7 | 7.8 | 0.1 |  |  |  |  | 9.3 | 20 | 20 | 19 | 696.43 | 685.43 | 668.35 | 687.43 | 1.52 | 2.22 | 0.3 | 1.22 |  |  |  |  | 708.05 | 11.55 | 0.64 | 0.84
5 | 2019-06-01 | 2019-06-06 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL003 | 1S-DL-YP-ETC-DKWL-2451-KWL003 | RAJEEV GANDHI NAGAR GALI NO.-15:ID | TG-KWL003A-2 | 19504934 | 990 | 320 | 248.3143 | 0.96797 | 882.7997 | 329.2282 | 1360.672 | 235.1079 | 956.2287 | 318.4636 | 1317.435 | 384.6517 | 2019-06-01 23:30 | [15 empty] | 0 |  |  |  | 0 |  |  |  | 110 |  |  |  | 34 |  |  |  | 0 | 144 |  | 0.83873 | 0.89172
6 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL004 | 1S-DL-YP-ETC-DKWL-2451-KWL004 | RAJEEV GANDHI NAGAR GALI NO.-21:ID | TG-KWL004A-1 | 19504064 | 990 | 320 | 251 | 0.96 | 784 | 243 | 969 | 240 | 956 | 300 | 1208 | 245 | 2019-06-30 | 197.2 | 52.3 | 1209 | B | 96 | 92 | 113 | 21 |  |  | 5.1 | 94.9 |  |  |  |  | 16 | 21 | 21 | 9.3 | 702.43 | 697.43 | 678.53 | 709.13 |  |  | 38.5 | [5 empty] | 718.43 | 1.17 | 0.75 | 0.79
7 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL004 | 1S-DL-YP-ETC-DKWL-2451-KWL004 | RAJEEV GANDHI NAGAR GALI NO.-21:ID | TG-KWL004A-2 | 19506671 | 630 | 200 | 264 | 0.97 | 443 | 145 | 590 | 136 | 552 | 163 | 667 | 102 | 2019-06-13 14:00 | 149.6 | 37 | 731 | B | 96 | 88 | 116 | 28 | 0.4 | 1 | 80.8 | 17.9 |  |  |  |  | 158 | 247.3 | 247.3 | 93.3 | 553.2 | 463.5 | 668.2 | 617.5 |  |  | 3 | [5 empty] | 711.2 | 8.4 | 0.68 | 0.7
8 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL005 | 1S-DL-YP-ETC-DKWL-2451-KWL005 | D BLOCK BHAGRATHI VIHAR:PL | TG-KWL005A-1 | 19500546 | 630 | 200 | 237 | 0.96 | 545 | 154 | 628 | 203 | 823 | 188 | 768 | 174 | 2019-06-02 08:00 | 144.4 | 53.4 | 844 | Y | 84 | 113 | 103 | 29 |  |  | 16.6 | 83.4 |  |  |  |  | 52 |  |  |  | 665.25 | 645.48 | 699.39 | 712.29 |  | 71.37 | 17.16 | 4.56 |  |  |  |  | 717.25 | 2.35 | 0.71 | 0.87
9 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL005 | 1S-DL-YP-ETC-DKWL-2451-KWL005 | D BLOCK BHAGRATHI VIHAR:PL | TG-KWL005A-2 | 19505241 | 630 | 200 | 252 | 0.95 | 300 | 99 | 429 | 107 | 471 | 94 | 412 | 53 | 2019-06-03 14:30 | 107.4 | 26.4 | 471 | Y | 104 | 95 | 101 | 9 | 0.1 | 0.3 | 15.4 | 84.2 | 3.3 | 27 | 3 | 2 | 696.54 | 678.43 | 678.43 | 712.13 | 17.48 | 12.29 | 2.29 | 3.59 | [8 empty] | 718.12 | 1.48 | 0.63 | 0.48
10 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL008 | 1S-DL-YP-ETC-DKWL-2451-KWL008 | JOH. EXT & MATA WALI GALI NALAWALA:PL | TG-KWL008A-1 | 19505229 | 630 | 200 | 236 | 0.97 | 202 | 78 | 339 | 81 | 355 | 42 | 184 | 163 | 2019-06-16 00:30 | 71.8 | 12.2 | 429 | R | 119 | 127 | 54 | 73 |  |  | 20.3 | 79.7 | 97.3 | 35.3 | 692 | 234.13 | 594.3 | 656 | 656 | 458.17 | 0.3 | 1 | [10 empty] | 692.3 | 27.3 | 0.67 | 0.32
11 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL014 | 1S-DL-YP-ETC-DKWL-2451-KWL014 | D BL BRIJPURI GALI NO. 10:ID | TG-KWL014A-1 | 19500566 | 630 | 200 | 252 | 0.96 | 529 | 211 | 852 | 188 | 738 | 131 | 525 | 288 | 2019-06-29 23:00 | 127.9 | 56.1 | 887 | R | 113 | 115 | 71 | 44 | 4.6 | 95.4 | 0 | [5 empty] | 1.3 |  |  | 25.05 | 667.21 | 674.06 | 263.27 | 688.46 | 48 | 44.15 | 1 | 4.3 | 1.3 |  |  |  | 718.21 | 1.39 | 0.64 | 0.84
12 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL019 | 1S-DL-YP-ETC-DKWL-2451-KWL019 | A BLK G N 2 BHAGIRATHI VIHAR NO-II :ID | TG-KWL019A-1 | 19506448 | 630 | 200 | 252 | 0.95 | 515 | 184 | 720 | 177 | 684 | 154 | 592 | 115 | 2019-06-30 | 176.8 | 65.2 | 784 | R | 112 | 97 | 91 | 21 | 0.1 | 0.3 | 89.8 | 9.8 |  |  |  |  | 2.3 | 26.37 | 26.37 | 14 | 691.29 | 679.01 | 657.14 | 693.38 | 15.09 | 3.3 |  | 1.3 |  |  |  |  | 709.08 | 10.52 | 0.7 | 0.82
13 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL019 | 1S-DL-YP-ETC-DKWL-2451-KWL019 | A BLK G N 2 BHAGIRATHI VIHAR NO-II :ID | TG-KWL019A-2 | 19505765 | 630 | 200 | 245 | 0.96 | 558 | 184 | 738 | 228 | 925 | 146 | 580 | 299 | 2019-06-29 23:30 | 193 | 55.8 | 1096 | Y | 97 | 123 | 79 | 44 | 0.1 | 4.8 | 93.3 | 1.7 |  |  |  |  | 6 | 0.3 | 0.3 | 1.3 | 678.53 | 463.37 | 646.38 | 686.09 | 30.16 | 232.02 |  | 27.3 |  | 19 |  |  | 715.09 | 4.51 | 0.7 | 0.89
14 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL027 | 1S-DL-YP-ETC-DKWL-2451-KWL027 | A BLOCK BRIJ PURI:ID | TG-KWL027A-1 | 19500627 | 630 | 200 | 242 | 0.97 | 643 | 298 | 1293 | 228 | 992 | 116 | 486 | 706 | 2019-06-10 23:30 | 169.7 | 14.3 | 1355 | R | 96 | 113 | 91 | 22 | 5.8 | 31.2 | 58.1 | 4.9 | 314.23 |  |  |  | 8.36 | 47.51 | 47.51 | 141.03 | 154.14 | 550.1 | 483.49 | 509.21 | 143.11 | 104.02 | 35.36 | 63.28 | 94.18 | 12.39 |  | 0.5 | 714.42 | 5.18 | 0.55 | 1.02
15 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL027 | 1S-DL-YP-ETC-DKWL-2451-KWL027 | A BLOCK BRIJ PURI:ID | TG-KWL027A-2 | 19506307 | 630 | 200 | 245 | 0.97 | 379 | 84 | 341 | 134 | 572 | 162 | 683 | 302 | 2019-06-27 18:30 | 165 | 26.6 | 683 | B | 108 | 118 | 74 | 44 | 0.2 | 0.3 | 46.3 | 53.2 | 0.3 |  | 48 | 1 | 408.1 | 281.08 | 281.08 | 540.21 | 309.59 | 437.31 | 2 | 177.18 | [8 empty] | 718.39 | 1.21 | 0.6 | 0.6
16 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL028 | 1S-DL-YP-ETC-DKWL-2451-KWL028 | B BLOCK BRIJ PURI:ID | TG-KWL028A-1 | 19505234 | 990 | 320 | 239 | 0.97 | 925 | 259 | 1110 | 279 | 1194 | 388 | 1688 | 541 | 2019-06-10 01:00 | 317.4 | 71.7 | 1688 | B | 93 | 97 | 111 | 18 | 0.3 | 0.1 | 0.6 | 99 |  |  |  |  | 33 | 30.3 | 30.3 | 17.3 | 645.3 | 621.42 | 559.49 | 624.12 | 24 | 50.18 | 131.41 | 60.48 |  |  | 5.3 |  | 702.3 | 17.3 | 0.67 | 0.93
17 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL039 | 1S-DL-YP-ETC-DKWL-2451-KWL039 | GANGA VIHAR NO-1:ID | TG-KWL039A-1 | 19504447 | 990 | 320 | 240 | 0.98 | 739 | 216 | 892 | 257 | 1059 | 265 | 1103 | 192 | 2019-06-25 23:30 | 134.7 | 21.3 | 1145 | B | 63 | 118 | 119 | 56 |  |  | 13.3 | 86.7 | 270.31 |  |  |  | 209.24 | 183.26 | 183.26 | 350.34 | 237.56 | 533.25 | 588.12 | 367.17 |  | 1 | 1.13 | [5 empty] | 717.51 | 2.09 | 0.56 | 0.75
18 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL039 | 1S-DL-YP-ETC-DKWL-2451-KWL039 | GANGA VIHAR NO-1:ID | TG-KWL039A-2 | 19500982 | 990 | 320 | 244 | 0.97 | 956 | 412 | 1691 | 272 | 1098 | 272 | 1115 | 585 | 2019-06-25 23:30 | 238.5 | 87.6 | 1718 | R | 122 | 86 | 93 | 36 |  | 0.1 | 88.3 | 11.6 |  |  |  |  | 1 | 115 | 115 | 29 | 502.13 | 594.37 | 617.47 | 610.46 | 148.33 | 8.5 | 29.4 | 78.41 | 66.41 |  |  |  | 718.27 | 1.33 | 0.61 | 0.97
19 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL040 | 1S-DL-YP-ETC-DKWL-2451-KWL040 | GANGA VIHAR NO-2:ID | TG-KWL040A-1 | 19501736 | 990 | 320 | 251 | 0.97 | 1126 | 398 | 1520 | 377 | 1378 | 351 | 1337 | 166 | 2019-06-30 07:30 | 367.3 | 88.3 | 1621 | R | 108 | 95 | 96 | 13 | 100 | [11 empty] | 457.04 | 554.47 | 546.33 | 532.03 | 208.33 | 154.23 | 134.32 | 156.27 | 48.01 | 4.28 | 31.33 | 25.08 | 713.38 | 6.22 | 0.63 | 1.14
20 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL040 | 1S-DL-YP-ETC-DKWL-2451-KWL040 | GANGA VIHAR NO-2:ID | TG-KWL040A-2 | 19503794 | 990 | 320 | 253 | 0.97 | 1153 | 282 | 1139 | 457 | 1903 | 414 | 1699 | 685 | 2019-06-08 23:30 | 276.7 | 66.2 | 1930 | Y | 82 | 115 | 103 | 33 | 0.6 | 35.6 | 63.8 | [5 empty] | 10.01 |  |  | 0.01 | 675.27 | 334.46 | 446.47 | 488.5 | 25.34 | 237.07 | 228.35 | 196.13 |  | 139.09 | 35.39 | 25.58 | 711.02 | 8.58 | 0.63 | 1.16
21 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL044 | 1S-DL-YP-ETC-DKWL-2451-KWL044 | GALI NO.3 OLD MUSTAFABAD:ID | TG-KWL044A-1 | 19502319 | 990 | 320 | 239 | 0.98 | 866 | 334 | 1409 | 240 | 1006 | 292 | 1221 | 349 | 2019-06-02 07:00 | 159 | 58.1 | 1409 | R | 111 | 90 | 99 | 21 | 13.8 | 0.1 | 21.7 | 64.5 |  |  |  |  | 2 | 17.53 | 17.53 | 1 | 571.24 | 690.01 | 691.27 | 697.37 | 135.03 | 1 | 13.27 | 10.17 | 0.27 |  |  |  | 708.54 | 11.06 | 0.72 | 0.88
22 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL044 | 1S-DL-YP-ETC-DKWL-2451-KWL044 | GALI NO.3 OLD MUSTAFABAD:ID | TG-KWL044A-2 | 19501040 | 400 | 120 | 245 | 0.97 | 373 | 136 | 566 | 119 | 496 | 117 | 481 | 79 | 2019-06-29 23:30 | 93.6 | 40.8 | 627 | R | 119 | 93 | 88 | 31 |  | 0.1 | 7.7 | 92.3 | [8 empty] | 248.1 | 682.46 | 686.22 | 607.41 | 434.22 | 26.06 | 15.3 | 101.11 | 26.2 |  |  |  | 708.52 | 11.08 | 0.75 | 0.93
23 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL045 | 1S-DL-YP-ETC-DKWL-2451-KWL045 | OLD MUSTFABAD GALI NO 6:ID | TG-KWL045A-1 | 19506638 | 990 | 320 | 242 | 0.97 | 648 | 250 | 1049 | 129 | 533 | 269 | 1094 | 540 | 2019-06-09 00:30 | 214.4 | 61.4 | 1094 | B | 117 | 75 | 108 | 42 |  | 4.8 | 86.7 | 8.5 |  | 2 |  |  | 36.33 | 645.07 | 645.07 | 154.26 | 669.02 | 58.28 | 619.11 | 551.09 |  |  | 0.3 | [5 empty] | 705.35 | 14.25 | 0.68 | 0.65
24 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL045 | 1S-DL-YP-ETC-DKWL-2451-KWL045 | OLD MUSTFABAD GALI NO 6:ID | TG-KWL045A-2 | 19506639 | 630 | 200 | 242 | 0.97 | 350 | 100 | 421 | 169 | 718 | 81 | 350 | 338 | 2019-06-29 23:30 | 118 | 31.8 | 718 | Y | 99 | 105 | 96 | 9 | 0.1 | 0.2 | 9 | 90.7 |  | 3.28 |  |  | 498.58 | 377.18 | 377.18 | 487.49 | 206.36 | 324.18 | 139.09 | 217.45 |  | 0.3 | [6 empty] | 705.34 | 14.26 | 0.67 | 0.56
25 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL047 | 1S-DL-YP-ETC-DKWL-2451-KWL047 | GOKUL PURI COMPLAINT CENTER:ID | TG-KWL047A-1 | 19503804 | 990 | 200 | 264 | 0.95 | 419 | 188 | 710 | 175 | 659 | 57 | 215 | 472 | 2019-06-28 23:30 | 116.8 | 43.2 | 718 | R | 132 | 126 | 42 | 90 |  |  | 16.4 | 83.6 |  | 0.3 | 709.41 | 17.01 | 479.02 | 501.04 | 501.04 | 691.02 | 234.01 | 211.29 |  | 5 | [8 empty] | 713.03 | 6.57 | 0.67 | 0.42
26 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL047 | 1S-DL-YP-ETC-DKWL-2451-KWL047 | GOKUL PURI COMPLAINT CENTER:ID | TG-KWL047A-2 | 19505727 | 990 | 320 | 252 | 0.95 | 762 | 266 | 1111 | 282 | 1209 | 214 | 905 | 269 | 2019-06-30 14:00 | 266.6 | 103 | 1213 | R | 108 | 112 | 81 | 31 | 0.2 | 0.6 | 65.6 | 33.6 |  |  |  |  | 7.3 | 2 | 2 | 12.3 | 678.37 | 691.33 | 580.13 | 685.02 | 11.25 | 3.59 | [6 empty] | 697.32 | 22.28 | 0.72 | 0.77
27 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL048 | 1S-DL-YP-ETC-DKWL-2451-KWL048 | A BLOCK GOKUL PURI:ID | TG-KWL048A-1 | 19505927 | 990 | 320 | 240 | 0.97 | 679 | 298 | 1233 | 152 | 624 | 229 | 956 | 528 | 2019-06-28 23:00 | 228.5 | 73.3 | 1368 | R | 125 | 78 | 98 | 47 | 0.1 | 0.3 | 36 | 63.7 |  |  |  |  | 0.3 | 401.37 | 401.37 | 39 | 636.15 | 301.1 | 665.17 | 663.47 | 66.02 | [7 empty] | 702.47 | 17.13 | 0.74 | 0.69
28 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL050 | 1S-DL-YP-ETC-DKWL-2451-KWL050 | JOHRIPUR SCHOOL WALA S/STN.:PL | TG-KWL050A-1 | 19502256 | 400 | 120 | 238 | 0.98 | 226 | 63 | 280 | 76 | 337 | 87 | 389 | 94 | 2019-06-29 14:30 | 54.1 | 8.6 | 390 | B | 52 | 123 | 125 | 73 |  |  | 9.6 | 90.4 | 400.5 |  |  | 2.31 | 292.49 | 202.13 | 202.13 | 528.13 | 22 | 513.26 | 505 | 184.55 | [8 empty] | 715.39 | 4.21 | 0.63 | 0.57
29 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL051 | 1S-DL-YP-ETC-DKWL-2451-KWL051 | JOHRIPUR DURGA FACTORY:PL | TG-KWL051A-1 | 19502299 | 630 | 200 | 251 | 0.99 | 327 | 124 | 497 | 115 | 453 | 88 | 352 | 129 | 2019-06-01 12:30 | 54.7 | -40 | 529 | R | 118 | 104 | 79 | 39 |  | 8.4 | 91.4 | 0.2 | 19 | 6.3 | 25.53 | 11 | 417.19 | 567.15 | 567.15 | 657.15 | 279.53 | 142.27 | 1 | 47.57 | [8 empty] | 716.12 | 3.48 | 0.63 | 0.52
30 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL052 | 1S-DL-YP-ETC-DKWL-2451-KWL052 | B BLOCK GOKUL PURI:PL | TG-KWL052A-1 | 19503799 | 630 | 200 | 240 | 0.96 | 538 | 214 | 942 | 139 | 598 | 185 | 804 | 299 | 2019-06-02 23:00 | 131.1 | 63.5 | 969 | R | 116 | 77 | 107 | 39 |  | 3.2 | 83.5 | 13.3 | [5 empty] | 206.41 | 206.41 | 5 | 603.06 | 512.45 | 652.36 | 695.06 | 113.3 |  | 65.2 | 19.2 | 2.5 |  |  |  | 719.26 | 0.34 | 0.69 | 0.85
31 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL053 | 1S-DL-YP-ETC-DKWL-2451-KWL053 | JAWHAR NAGAR NO.-1:PL | TG-KWL053A-1 | 19506012 | 990 | 320 | 245 | 0.98 | 894 | 224 | 937 | 335 | 1412 | 334 | 1406 | 472 | 2019-06-24 14:30 | 341.8 | -74.9 | 1412 | Y | 75 | 112 | 113 | 38 |  | 0.1 | 26.1 | 73.8 | 405.49 | 354.54 | 351.17 | 367.47 | 189.34 | 107.39 | 107.39 | 121.45 | 106 | 226.2 | 232.5 | 210.21 |  | 12 | 5.3 | 1.3 |  | 0.3 | 0.3 |  | 701.23 | 18.37 | 0.3 | 0.9
32 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL053 | 1S-DL-YP-ETC-DKWL-2451-KWL053 | JAWHAR NAGAR NO.-1:PL | TG-KWL053A-2 | 19504953 | 990 | 320 | 239 | 0.99 | 1037 | 346 | 1461 | 338 | 1428 | 354 | 1488 | 52 | 2019-06-24 12:00 | 197.2 | -69.9 | 1488 | B | 99 | 98 | 103 | 5 | 0.3 | 0.1 | 35.6 | 64 | 145.3 | 143.01 | 111.03 | 129.01 | 230.25 | 224.54 | 224.54 | 242.24 | 214.48 | 236.18 | 199.47 | 214.18 | 121.11 | 111.41 | 141.11 | 128.41 | 4.3 | 0.3 | 9 | 2 | 716.24 | 3.36 | 0.44 | 1.05
33 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL077 | 1S-DL-YP-ETC-DKWL-2451-KWL077 | SAMPAT NAGAR 1:ID | TG-KWL077A-1 | 19505662 | 630 | 200 | 245 | 0.97 | 342 | 84 | 340 | 124 | 501 | 133 | 540 | 184 | 2019-06-30 00:30 | 105.4 | 25.4 | 556 | B | 74 | 104 | 122 | 48 |  | 0.2 | 28 | 71.8 | 44.47 | 1.3 |  |  | 663.24 | 458.29 | 458.29 | 540.1 | 1.04 | 249.16 | 500.13 | 169.05 | [8 empty] | 709.15 | 10.45 | 0.66 | 0.54
34 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL077 | 1S-DL-YP-ETC-DKWL-2451-KWL077 | SAMPAT NAGAR 1:ID | TG-KWL077A-2 | 19505301 | 400 | 120 | 237 | 0.98 | 413 | 156 | 655 | 130 | 547 | 126 | 528 | 118 | 2019-06-30 | 166.4 | 18.5 | 834 | R | 108 | 95 | 97 | 13 | 0.1 | 0.2 | 4.8 | 94.8 |  |  |  |  | 0.3 |  |  |  | 310.55 | 525.28 | 511.49 | 446.15 | 315.16 | 181.22 | 193.05 | 258.09 | 82.09 | 2 | 3.26 | 4.26 | 708.5 | 11.1 | 0.73 | 1.03
35 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL081 | 1S-DL-YP-ETC-DKWL-2451-KWL081 | H BLOCK GANGA VIHAR GALI NO. 8:ID | TG-KWL081A-1 | 19505974 | 630 | 200 | 242 | 0.99 | 289 | 64 | 267 | 110 | 461 | 115 | 485 | 207 | 2019-06-29 16:00 | 79.6 | 3.4 | 595 | Y | 61 | 118 | 121 | 60 |  |  | 9.5 | 90.5 | 318.11 |  |  | 0.3 | 377.11 | 348.18 | 348.18 | 636.5 |  | 347.04 | 384.09 | 58.02 | [8 empty] | 695.22 | 24.38 | 0.73 | 0.46
36 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL081 | 1S-DL-YP-ETC-DKWL-2451-KWL081 | H BLOCK GANGA VIHAR GALI NO. 8:ID | TG-KWL081A-2 | 19506303 | 630 | 200 | 243 | 0.94 | 83 | 13 | 55 | 33 | 139 | 37 | 154 | 93 | 2019-06-29 23:30 | 33 | 8.2 | 203 | B | 47 | 109 | 144 | 97 |  | 1.4 | 84.6 | 13.9 | 694.5 | 694.5 | 689.5 | 694.5 | [16 empty] | 694.5 | 25.1 | 0.66 | 0.13
37 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL082 | 1S-DL-YP-ETC-DKWL-2451-KWL082 | HOTAL MAYUR BRIJPURI:PM | TG-KWL082A-1 | 19506397 | 400 | 120 | 257 | 0.96 | 231 | 30 | 120 | 45 | 184 | 156 | 649 | 500 | 2019-06-02 10:30 | 58.8 | 24.4 | 649 | B | 94 | 103 | 102 | 9 | 0.2 | 0.5 | 49.8 | 49.5 | 0.3 |  | 7.3 |  | 584.38 | 497.27 | 497.27 | 586.51 | 130.36 | 218.17 | 217.47 | 128.53 | [6 empty] | 0.3 |  | 715.44 | 4.16 | 0.61 | 0.58
38 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL101 | 1S-DL-YP-ETC-DKWL-2451-KWL101 | MANSINGH NAGAR GALI NO. 16:ID | TG-KWL101A-1 | 19503017 | 630 | 200 | 249 | 0.96 | 500 | 159 | 644 | 132 | 532 | 209 | 844 | 274 | 2019-06-29 23:00 | 136.2 | 47.4 | 844 | B | 99 | 84 | 118 | 34 |  | 0.5 | 44.9 | 54.6 |  |  |  |  | 24.1 | 81.09 | 81.09 | 17.3 | 687.47 | 630.48 | 630.44 | 694.27 |  |  | 80.43 | [5 empty] | 711.57 | 8.03 | 0.72 | 0.79
39 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL101 | 1S-DL-YP-ETC-DKWL-2451-KWL101 | MANSINGH NAGAR GALI NO. 16:ID | TG-KWL101A-2 | 19506035 | 990 | 320 | 244 | 0.97 | 804 | 345 | 1602 | 278 | 1268 | 181 | 838 | 663 | 2019-06-03 14:00 | 284.2 | 55.7 | 1602 | R | 119 | 103 | 78 | 41 | 0.1 | 1.8 | 71.1 | 27.1 |  |  |  |  | 5 | 21.2 | 21.2 | 21.2 | 682.16 | 678.11 | 420.45 | 680.11 | 14.15 | 2.3 |  | 0.3 | 0.3 |  |  |  | 702.01 | 17.59 | 0.67 | 0.81
40 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL102 | 1S-DL-YP-ETC-DKWL-2451-KWL102 | AKBARI MASZID:ID | TG-KWL102A-1 | 19504531 | 630 | 200 | 237 | 0.97 | 452 | 217 | 933 | 113 | 474 | 122 | 520 | 438 | 2019-06-29 23:30 | 106.3 | 43.7 | 953 | R | 140 | 78 | 83 | 62 | 2.1 | 39.3 | 58.6 | [5 empty] | 1.3 | 395.06 | 395.06 | 58.04 | 549.01 | 321.54 | 446.58 | 658.56 | 163.59 |  |  |  | 2.3 |  |  |  | 717 | 3 | 0.71 | 0.72
41 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL102 | 1S-DL-YP-ETC-DKWL-2451-KWL102 | AKBARI MASZID:ID | TG-KWL102A-2 | 19504910 | 630 | 120 | 238 | 0.97 | 462 | 133 | 565 | 193 | 828 | 136 | 582 | 255 | 2019-06-29 23:00 | 110.7 | 47.5 | 828 | Y | 92 | 123 | 85 | 38 |  |  | 83.5 | 16.5 |  |  |  |  | 52.51 | 0.3 | 0.3 | 22.51 | 665.41 | 687.4 | 572.41 | 695.41 |  | 30.22 | [6 empty] | 718.32 | 1.28 | 0.72 | 0.73
42 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL103 | 1S-DL-YP-ETC-DKWL-2451-KWL103 | MAJOR MALHOTRA FARM HOUSE:PM | TG-KWL103A-1 | 19506634 | 100 | 40 | 250 | 0.84 | 85 | 11 | 44 | 30 | 122 | 44 | 182 | 120 | 2019-06-28 12:00 | 10 | -36.1 | 207 | B | 70 | 103 | 126 | 56 | 3.2 | 14.6 | 50.9 | 31.3 | 1.3 |  |  |  | 539.06 | 270.16 | 270.16 | 233.19 | 162.53 | 364.43 | 471.44 | 464.4 |  | 65 | 110.57 | 5.3 |  | 3.3 | 55 |  | 703.29 | 16.31 | 0.6 | 0.85
43 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL107 | 1S-DL-YP-ETC-DKWL-2451-KWL107 | JOHRIPUR GUJARMAL MOHALLA:PL | TG-KWL107A-1 | 19506817 | 990 | 320 | 235 | 0.99 | 934 | 325 | 1503 | 305 | 1368 | 304 | 1391 | 125 | 2019-06-27 15:30 | 277.1 | -72.6 | 1503 | R | 102 | 101 | 97 | 5 | 5.9 | 87.9 | 6.2 |  | 29.3 | 8 | 18 | 11 | 344.41 | 367.41 | 367.41 | 371.41 | 319.48 | 321.48 | 314.13 | 317.13 | 12.54 | 9.24 | 4.29 | 6.59 |  |  |  |  | 706.53 | 13.07 | 0.45 | 0.94
44 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL109 | 1S-DL-YP-ETC-DKWL-2451-KWL109 | E BL BHAGIRATHI VIHAR(NALE WALA):PLM | TG-KWL109A-1 | 19505762 | 630 | 200 | 236 | 0.96 | 123 | 30 | 129 | 44 | 189 | 49 | 212 | 74 | 2019-06-26 02:00 | 46.4 | 9.8 | 224 | Y | 72 | 114 | 114 | 42 |  | 0.1 | 29.3 | 70.6 | 715.55 | 678.2 | 706.03 | 715.55 |  | 37.35 | 37.35 | [13 empty] | 715.55 | 4.05 | 0.62 | 0.2
45 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL162 | 1S-DL-YP-ETC-DKWL-2451-KWL162 | JAIN COMPLEX JOHIRIPUR:PM | TG-KWL162A-1 | 19506636 | 100 | 40 | 237 | 0.96 | 87 | 33 | 135 | 26 | 105 | 28 | 111 | 28 | 2019-06-12 03:30 | 33.4 | 5.8 | 171 | R | 127 | 75 | 97 | 52 | 0.1 | 7 | 54 | 39 |  | 1.23 |  |  | 31.11 | 377.46 | 377.46 | 74.07 | 489.54 | 305.42 | 573.05 | 609.44 | 137.46 |  | 2.36 | 1 | 26 |  |  |  | 684.51 | 35.09 | 0.6 | 0.87
46 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL237 | 1S-DL-YP-ETC-DKWL-2451-KWL237 | SHANI BAZAR ROAD JOHRI PUR :PM | TG-KWL237A-1 | 19505924 | 630 | 200 | 237 | 0.98 | 905 | 289 | 1325 | 292 | 1356 | 324 | 1488 | 150 | 2019-06-29 12:00 | 253.4 | -74.2 | 1488 | B | 91 | 93 | 117 | 26 |  |  | 2.1 | 97.9 | 37.3 | 31 | 6.3 | 20.3 | 197.15 | 178.45 | 178.45 | 133.44 | 435.59 | 461.29 | 475.54 | 478.31 | 36.28 | 35.28 | 145.2 | 73.27 | 0.25 | 0.55 | 19.53 | 1.25 | 707.37 | 12.23 | 0.38 | 1.44
47 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL241 | 1S-DL-YP-ETC-DKWL-2451-KWL241 | JOHRI PUR TUNDA NAGAR:PL | TG-KWL241A-1 | 19504974 | 400 | 120 | 235 | 0.76 | 36 | 9 | 39 | 6 | 26 | 21 | 91 | 60 | 2019-06-08 12:00 | 13 | -12.4 | 91 | B | 119 | 48 | 132 | 84 |  |  | 16.9 | 83.1 | 713.37 | 713.37 | 713.37 | 713.37 | [16 empty] | 713.37 | 6.23 | 0.17 | 0.09
48 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL243 | 1S-DL-YP-ETC-DKWL-2451-KWL243 | G & H BLK MUSTAFABAD GALI NO. 18:ID | TG-KWL243A-1 | 19505960 | 990 | 320 | 241 | 0.97 | 1101 | 392 | 1669 | 396 | 1692 | 314 | 1323 | 359 | 2019-06-02 05:30 | 397.8 | 75.5 | 1717 | Y | 112 | 107 | 81 | 31 | 0.3 | 1 | 44.9 | 53.8 | [8 empty] | 323.03 | 429.45 | 701.13 | 547.38 | 358.14 | 252.07 | 3.56 | 159.05 | 27.22 | 26.47 |  | 1.56 | 708.39 | 11.21 | 0.65 | 1.11
49 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL243 | 1S-DL-YP-ETC-DKWL-2451-KWL243 | G & H BLK MUSTAFABAD GALI NO. 18:ID | TG-KWL243A-2 | 19505215 | 990 | 320 | 236 | 0.97 | 889 | 280 | 1209 | 249 | 1075 | 361 | 1569 | 442 | 2019-06-02 06:00 | 319.7 | 66.6 | 1570 | B | 98 | 77 | 125 | 48 |  | 0.2 | 6.6 | 93.2 |  |  |  |  | 14 | 316.48 | 316.48 | 19.3 | 693.07 | 391.48 | 654.5 | 686.45 | 1.29 |  | 51.25 | 2.21 |  |  | 2.21 |  | 708.36 | 11.24 | 0.6 | 0.9
50 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL245 | 1S-DL-YP-ETC-DKWL-2451-KWL245 | CHAMAN PARK:PM | TG-KWL245A-1 | 19506572 | 100 | 40 | 242 | 0.83 | 49 | 2 | 8 | 24 | 99 | 23 | 99 | 91 | 2019-06-28 21:00 | 27.1 | -0.4 | 99 | Y | 114 | 101 | 85 | 29 | 0.9 | 6.3 | 78.2 | 14.7 | 553.28 | 568.46 | 629.04 | 596.55 | 126.09 | 119.4 | 119.4 | 93.31 | 11.49 | 3 | 1.3 | 1 | [8 empty] | 691.26 | 28.34 | 0.19 | 0.49
51 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL246 | 1S-DL-YP-ETC-DKWL-2451-KWL246 | C BLOCK BRIJ PURI:ID | TG-KWL246A-1 | 19505514 | 990 | 320 | 237 | 0.96 | 985 | 326 | 1578 | 344 | 1617 | 315 | 1491 | 111 | 2019-06-03 14:00 | 386.2 | 109.8 | 1617 | Y | 101 | 105 | 94 | 11 | 0.3 | 0.4 | 42.6 | 56.8 |  |  |  |  | 1 | 0.3 | 0.3 | 0.3 | 592.54 | 536.54 | 671.24 | 598.24 | 109.19 | 144.49 | 28.49 | 104.19 |  | 21 |  |  | 703.13 | 16.47 | 0.68 | 0.99
52 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL252 | 1S-DL-YP-ETC-DKWL-2451-KWL252 | E BLK BHAGIRATHI VIHAR :PL | TG-KWL252A-1 | 19500684 | 630 | 200 | 239.3038 | 0.96296 | 417.3813 | 153.2822 | 651.4607 | 122.6096 | 519.0705 | 141.4894 | 598.4159 | 115.405 | 2019-06-29 22:30 | [15 empty] | 0 |  |  |  | 154 |  |  |  | 565 |  |  |  | 0 |  |  |  | 0 | 719 |  | 0.67665 | 0.66251
53 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL253 | 1S-DL-YP-ETC-DKWL-2451-KWL253 | RAJU FLOUR MILL:PM | TG-KWL253A-1 | 19500243 | 990 | 320 | 260 | 0.94 | 411 | 126 | 483 | 129 | 495 | 156 | 601 | 112 | 2019-06-01 13:00 | 114.1 | -80.2 | 626 | B | 91 | 104 | 105 | 14 |  |  | 0.1 | 99.9 | 428.48 | 391.48 | 394.18 | 402.48 | 285.46 | 321.46 | 321.46 | 307.16 |  | 1 | 42.24 | 4.3 | [8 empty] | 714.34 | 5.26 | 0.46 | 0.41
54 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL254 | 1S-DL-YP-ETC-DKWL-2451-KWL254 | CHAMPI CHOWK:PM | TG-KWL254A-1 | 19506585 | 400 | 120 | 234 | 0.96 | 176 | 58 | 270 | 71 | 337 | 47 | 218 | 103 | 2019-06-29 15:00 | 89.6 | -35.5 | 337 | Y | 77 | 144 | 79 | 67 | 0.1 | 19 | 65.7 | 15.2 | 577.49 | 309.52 | 563.1 | 510.12 | 120.3 | 347 | 347 | 189.07 | 4 | 45.27 |  | 3 | [8 empty] | 702.19 | 17.41 | 0.36 | 0.44
55 | 2019-06-01 | 2019-06-03 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL257 | 1S-DL-YP-ETC-DKWL-2451-KWL257 | Opposite Durga Factory (BARELIA) :PM | TG-KWL257A-1 | 19502935 | 400 | 120 | 239.0043 | 0.99081 | 377.2042 | 117.3701 | 510.8157 | 140.1159 | 611.0326 | 119.7182 | 519.9938 | 95.9576 | 2019-06-02 12:00 | [15 empty] | 35 |  |  |  | 4 |  |  |  | 23.5 |  |  |  | 9 |  |  |  | 0 | 71.5 |  | 0.42923 | 0.94301
56 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL331 | 1S-DL-YP-ETC-DKWL-2451-KWL331 | GALI NO.5 JAWAHAR NAGAR P/M | TG-KWL331A-1 | 19504775 | 990 | 320 | 247 | 0.99 | 935 | 310 | 1350 | 309 | 1332 | 315 | 1363 | 27 | 2019-06-22 16:00 | 114.1 | -116.3 | 1363 | B | 103 | 99 | 98 | 5 |  |  | 47.1 | 52.9 | 10.51 | 12.21 | 43.21 | 16.21 | 324.06 | 335.4 | 335.4 | 330.52 | 310.43 | 322.25 | 299.19 | 310.27 | 61.47 | 37.01 | 51 | 49.47 |  |  |  |  | 707.27 | 12.33 | 0.5 | 0.94
57 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL344 | 1S-DL-YP-ETC-DKWL-2451-KWL344 | MAIN ROAD MCD SCHOOL JOHRI PUR | TG-KWL344A-1 | 19505304 | 990 | 320 | 245 | 0.98 | 1164 | 405 | 1827 | 384 | 1720 | 375 | 1689 | 125 | 2019-06-29 15:00 | 441.6 | -59.8 | 1827 | R | 112 | 94 | 95 | 18 | 0.1 |  | 35.6 | 64.2 | 1 | 73.05 | 47.35 | 22.3 | 260.21 | 293.32 | 293.32 | 322 | 270.45 | 229.09 | 249.27 | 239.58 | 140.58 | 95.17 | 83.46 | 104.35 | 32.15 | 14.16 | 9.16 | 16.16 | 705.19 | 14.41 | 0.44 | 1.18
58 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL349 | 1S-DL-YP-ETC-DKWL-2451-KWL349 | G BLK GANGA VIHAR(SHAMSHAAN GHAT) | TG-KWL349A-1 | 19506686 | 630 | 200 | 245 | 0.97 | 566 | 191 | 795 | 181 | 750 | 194 | 803 | 50 | 2019-06-11 23:00 | 176.8 | 35.6 | 862 | R | 106 | 90 | 104 | 16 |  | 0.1 | 1.7 | 98.2 |  |  |  |  | 43.3 | 161.3 | 161.3 | 54 | 602.23 | 537.13 | 628.23 | 620.23 | 58.5 | 6 | 40.2 | 30.2 |  |  |  |  | 704.43 | 15.17 | 0.62 | 0.9
59 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL349 | 1S-DL-YP-ETC-DKWL-2451-KWL349 | G BLK GANGA VIHAR(SHAMSHAAN GHAT) | TG-KWL349A-2 | 19506762 | 630 | 200 | 241 | 0.97 | 231 | 64 | 268 | 78 | 321 | 89 | 369 | 88 | 2019-06-11 23:00 | 66.8 | 12.8 | 411 | B | 80 | 100 | 120 | 40 |  | 0.1 | 35.6 | 64.3 | 514.23 | 310.55 | 137.57 | 351.55 | 181.5 | 385.18 | 385.18 | 344.18 |  |  | 11 | [9 empty] | 696.13 | 23.47 | 0.58 | 0.37
60 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL010 | 1S-DL-YP-ETC-DKWL-2451-KWL010 | MUKUND VIHAR "A" BLK:ID | TG-KWL010A-1 | 19500537 | 630 | 200 | 231 | 0.98 | 598 | 194 | 868 | 207 | 923 | 198 | 884 | 49 | 2019-06-12 17:00 | 130.6 | 18.4 | 949 | B | 95 | 98 | 107 | 12 |  | 0.5 | 26.7 | 72.8 |  |  |  |  | 62.18 | 21.59 | 21.59 | 19.29 | 593.38 | 630.33 | 595.18 | 630.26 | 48.5 | 52.14 | 95.58 | 54.51 |  |  |  |  | 704.46 | 15.14 | 0.65 | 0.95
61 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL012 | 1S-DL-YP-ETC-DKWL-2451-KWL012 | B BLK MUKUND VIHAR :-ID | TG-KWL012A-1 | 19500661 | 990 | 320 | 235.8856 | 0.97399 | 617.6171 | 203.2919 | 891.006 | 224.597 | 986.3724 | 189.7282 | 831.5576 | 135.271 | 2019-06-28 22:30 | [15 empty] | 5.5 |  |  |  | 335.5 |  |  |  | 376.5 |  |  |  | 0 |  |  |  | 0 | 717.5 |  | 0.65368 | 0.62386
62 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL013 | 1S-DL-YP-ETC-DKWL-2451-KWL013 | C BLK MUKUND VIHAR GALI NO. 9:ID | TG-KWL013A-1 | 19505641 | 1600 | 500 | 244 | 0.97 | 1944 | 665 | 2676 | 591 | 2390 | 689 | 2810 | 371 | 2019-06-02 05:30 | 761 | 102.5 | 2810 | B | 104 | 96 | 100 | 8 | 0.1 |  | 12.6 | 87.3 |  |  |  |  | 54.36 | 126 | 126 | 81.3 | 527.59 | 488.25 | 469.25 | 512 | 109.59 | 84.52 | 124.17 | 104.17 | 6.54 | 0.11 | 3.11 | 1.41 | 699.28 | 20.32 | 0.48 | 1.22
63 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL015 | 1S-DL-YP-ETC-DKWL-2451-KWL015 | E & F BLOCK KARWAL NAGAR:ID | TG-KWL015A-1 | 19500644 | 630 | 200 | 245 | 0.97 | 272 | 88 | 377 | 69 | 294 | 115 | 493 | 173 | 2019-06-29 23:00 | 98 | 7.8 | 516 | B | 94 | 86 | 120 | 34 |  |  | 28.8 | 71.2 | 69.18 | 163.47 | 3 | 24.24 | 639.4 | 545.41 | 545.41 | 682.08 | 0.3 |  | 98.49 | 2.56 | [8 empty] | 709.28 | 10.32 | 0.62 | 0.43
64 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL031 | 1S-DL-YP-ETC-DKWL-2451-KWL031 | PREM NAGAR S/STN :ID | TG-KWL031A-1 | 19505231 | 630 | 200 | 233 | 0.97 | 637 | 219 | 959 | 208 | 915 | 211 | 912 | 46 | 2019-06-12 00:30 | 211.4 | 51.8 | 959 | R | 101 | 103 | 96 | 7 | 0.5 | 26.5 | 58.6 | 14.4 |  |  |  |  | 28 | 16.44 | 16.44 | 30.14 | 633.02 | 660.33 | 586.28 | 645.37 | 28.18 | 12.26 | 14.03 | 13.29 | 0.23 |  | 0.23 | 0.23 | 689.43 | 30.17 | 0.55 | 1.01
65 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL031 | 1S-DL-YP-ETC-DKWL-2451-KWL031 | PREM NAGAR S/STN :ID | TG-KWL031A-2 | 19505925 | 630 | 200 | 235 | 0.98 | 332 | 97 | 432 | 84 | 374 | 150 | 673 | 275 | 2019-06-22 18:30 | 84.4 | 12.6 | 780 | B | 62 | 73 | 165 | 103 | 0.1 | 0.1 | 3.5 | 96.3 | 611.45 | 372.38 |  | 23.28 | 76.57 | 316.04 | 316.04 | 663.34 | 0.3 | 0.3 | 432.53 | 2.1 |  |  | 1.3 | [5 empty] | 689.12 | 30.48 | 0.52 | 0.53
66 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL033 | 1S-DL-YP-ETC-DKWL-2451-KWL033 | MAHALAXMI ENCLAVE:ID | TG-KWL033A-1 | 19506283 | 990 | 320 | 240 | 0.98 | 880 | 330 | 1431 | 272 | 1190 | 279 | 1219 | 227 | 2019-06-11 22:00 | 253.1 | 67.2 | 1431 | R | 111 | 92 | 97 | 19 | 0.1 | 0.1 | 10.2 | 89.6 | [5 empty] | 7 | 7 | 2 | 655.37 | 702.47 | 701.27 | 706.29 | 54.1 | 0.3 | 2 | 1.48 | 0.3 |  |  |  | 710.17 | 9.43 | 0.67 | 0.89
67 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL033 | 1S-DL-YP-ETC-DKWL-2451-KWL033 | MAHALAXMI ENCLAVE:ID | TG-KWL033A-2 | 19500685 | 630 | 200 | 237.8519 | 0.97201 | 567.545 | 192.0934 | 822.8459 | 196.3834 | 835.4606 | 179.0683 | 765.5434 | 64.5412 | 2019-06-12 | [15 empty] | 0 |  |  |  | 6 |  |  |  | 710 |  |  |  | 2.5 |  |  |  | 0 | 718.5 |  | 0.64162 | 0.90087
68 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL042 | 1S-DL-YP-ETC-DKWL-2451-KWL042 | BABU NGR S/STN NO 1 GALI NO. 4:ID | TG-KWL042A-1 | 19501717 | 990 | 320 | 241 | 0.98 | 697 | 232 | 970 | 232 | 980 | 232 | 968 | 12 | 2019-06-02 06:30 | 156 | 47.8 | 1044 | Y | 101 | 104 | 95 | 9 | 0.1 | 7.7 | 49.2 | 43 |  |  |  |  | 21.23 | 8.59 | 8.59 | 18.23 | 693.01 | 705.25 | 668.31 | 696.01 | [8 empty] | 714.24 | 5.36 | 0.75 | 0.7
69 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL043 | 1S-DL-YP-ETC-DKWL-2451-KWL043 | TELEPHONE EXCHANGE KWR:PM | TG-KWL043A-1 | 19505053 | 400 | 120 | 244 | 0.97 | 223 | 67 | 271 | 74 | 303 | 82 | 336 | 56 | 2019-06-28 10:30 | 95.5 | -19.3 | 391 | B | 86 | 89 | 125 | 39 |  |  | 8.3 | 91.7 | 358.13 | 348.47 | 83.17 | 253.42 | 290.21 | 271.32 | 271.32 | 330.49 | 60.41 | 88.56 | 258.07 | 124.44 | [8 empty] | 709.15 | 10.45 | 0.49 | 0.56
70 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL046 | 1S-DL-YP-ETC-DKWL-2451-KWL046 | C C KARAWAL NAGAR S/STN. NO. 2:I/D | TG-KWL046A-1 | 19500592 | 990 | 320 | 240 | 0.98 | 933 | 334 | 1431 | 304 | 1317 | 295 | 1269 | 143 | 2019-06-26 15:30 | 214.9 | -14 | 1446 | R | 108 | 96 | 96 | 12 | 0.1 | 0.2 | 40.4 | 59.3 | 11.23 | 27.25 | 32.35 | 16.23 | 332.05 | 373.43 | 373.43 | 372.16 | 284.37 | 301.41 | 297.26 | 301.21 | 83.14 | 9.3 | 12.51 | 22.19 | 1 |  |  |  | 712.19 | 7.41 | 0.47 | 0.94
71 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL046 | 1S-DL-YP-ETC-DKWL-2451-KWL046 | C C KARAWAL NAGAR S/STN. NO. 2:I/D | TG-KWL046A-2 | 19500664 | 990 | 320 | 236 | 0.99 | 769 | 230 | 1004 | 281 | 1240 | 258 | 1138 | 206 | 2019-06-03 14:30 | 143.5 | -64.8 | 1240 | Y | 82 | 117 | 101 | 35 |  |  | 10 | 90 | 155.25 | 4.3 | 42.03 | 35.11 | 337.3 | 316.06 | 316.06 | 367.19 | 215.56 | 380 | 305.51 | 306.21 |  | 8.15 | [6 empty] | 708.51 | 11.09 | 0.51 | 0.78
72 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL056 | 1S-DL-YP-ETC-DKWL-2451-KWL056 | KARWAL NAGAR NO.-1 DAL MILL:PL | TG-KWL056A-1 | 19505998 | 990 | 320 | 233 | 0.98 | 867 | 291 | 1329 | 275 | 1250 | 300 | 1364 | 102 | 2019-06-28 16:00 | 351.4 | -82.2 | 1364 | B | 106 | 97 | 97 | 9 |  |  | 11.8 | 88.2 | 135.53 | 122.53 | 167.43 | 148.43 | 239.57 | 307.26 | 307.26 | 268.04 | 313.48 | 271.18 | 270.49 | 280.5 | 12.29 | 0.3 | 5.59 | 4.3 |  |  |  |  | 702.07 | 17.53 | 0.44 | 0.88
73 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL056 | 1S-DL-YP-ETC-DKWL-2451-KWL056 | KARWAL NAGAR NO.-1 DAL MILL:PL | TG-KWL056A-2 | 19506728 | 990 | 320 | 233.3456 | 0.97001 | 929.3679 | 293.9679 | 1276.2345 | 296.9879 | 1298.7053 | 338.4121 | 1485.3058 | 198.7907 | 2019-06-01 12:00 | [15 empty] | 0 |  |  |  | 222 |  |  |  | 465 |  |  |  | 32.5 |  |  |  | 0 | 719.5 |  | 0.55078 | 0.93876
74 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL057 | 1S-DL-YP-ETC-DKWL-2451-KWL057 | KARWAL NAGAR NO.-3:PM | TG-KWL057A-1 | 19506846 | 630 | 200 | 236 | 0.99 | 482 | 156 | 692 | 160 | 706 | 166 | 740 | 43 | 2019-06-10 15:00 | 151.2 | -75.2 | 758 | B | 96 | 104 | 100 | 8 |  | 0.5 | 32.3 | 67.2 |  |  |  |  | 176.09 | 126.06 | 126.06 | 139.46 | 512.4 | 562.43 | 549.25 | 549.03 |  |  | 0.3 | [5 empty] | 688.49 | 31.11 | 0.64 | 0.77
75 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL058 | 1S-DL-YP-ETC-DKWL-2451-KWL058 | KARWAL NAGAR NO.-4:PL | TG-KWL058A-1 | 19504901 | 990 | 320 | 244 | 0.97 | 775 | 264 | 1127 | 266 | 1137 | 245 | 1042 | 91 | 2019-06-27 15:00 | 113.3 | -112.6 | 1137 | Y | 102 | 101 | 97 | 5 |  |  | 7.1 | 92.9 | 217.43 | 259.21 | 245.1 | 246.21 | 174.28 | 126.2 | 126.2 | 144.5 | 319.02 | 325.32 | 312.32 | 320.32 | 0.3 | 0.3 | [6 empty] | 711.43 | 8.17 | 0.48 | 0.78
76 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL058 | 1S-DL-YP-ETC-DKWL-2451-KWL058 | KARWAL NAGAR NO.-4:PL | TG-KWL058A-2 | 19503507 | 990 | 320 | 243 | 0.99 | 850 | 278 | 1180 | 272 | 1151 | 300 | 1277 | 114 | 2019-06-28 16:00 | 170.8 | -95.7 | 1354 | B | 95 | 97 | 108 | 13 |  |  | 1.8 | 98.2 | 146.36 | 129.27 | 53.08 | 96.08 | 245.34 | 262.12 | 262.12 | 290.33 | 315.29 | 314 | 284.54 | 309.01 | 3 | 5 | 52.21 | 14.57 |  |  |  |  | 710.39 | 9.21 | 0.49 | 0.86
77 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL059 | 1S-DL-YP-ETC-DKWL-2451-KWL059 | KARWAL NAGAR NO.-5 SBI KWR:PL | TG-KWL059A-1 | 19500596 | 990 | 320 | 239.6012 | 0.9886 | 1087.1146 | 431.2797 | 1884.5518 | 337.7799 | 1492.4881 | 318.0551 | 1387.0091 | 454.0861 | 2019-06-27 16:30 | [15 empty] | 86.5 |  |  |  | 298.5 |  |  |  | 260.5 |  |  |  | 70.5 |  |  |  | 2 | 718 |  | 0.40357 | 1.0981
78 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL059 | 1S-DL-YP-ETC-DKWL-2451-KWL059 | KARWAL NAGAR NO.-5 SBI KWR:PL | TG-KWL059A-2 | 19502963 | 990 | 320 | 233 | 0.99 | 823 | 262 | 1162 | 269 | 1202 | 292 | 1310 | 133 | 2019-06-03 14:30 | 158.2 | -85.4 | 1310 | B | 98 | 100 | 101 | 3 |  |  | 9.9 | 90.1 |  |  |  |  | 83.48 | 84.28 | 84.28 | 88.18 | 631.33 | 625.53 | 579.37 | 622.33 |  | 5 | 24.27 | 4.3 |  |  |  |  | 715.21 | 4.39 | 0.63 | 0.83
79 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL059 | 1S-DL-YP-ETC-DKWL-2451-KWL059 | KARWAL NAGAR NO.-5 SBI KWR:PL | TG-KWL059A-3 | 19505348 | 990 | 320 | 240 | 0.99 | 823 | 285 | 1232 | 275 | 1183 | 262 | 1132 | 87 | 2019-06-29 11:00 | 250.2 | -57.9 | 1333 | R | 106 | 103 | 91 | 15 | 0.1 |  | 4.9 | 95 | 44.5 | 51.2 | 141.29 | 67.1 | 327.05 | 339.01 | 339.01 | 323.41 | 315.58 | 299.56 | 275.56 | 300.26 | 4.24 | 2 |  | 1 |  |  |  |  | 692.17 | 27.43 | 0.48 | 0.83
80 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL067 | 1S-DL-YP-ETC-DKWL-2451-KWL067 | SADATPUR VILLAGE PANCHYAT GHAR:PL | TG-KWL067A-1 | 19506582 | 990 | 320 | 241 | 0.96 | 715 | 261 | 1130 | 166 | 719 | 288 | 1244 | 478 | 2019-06-28 22:00 | 226.6 | 73.9 | 1244 | B | 104 | 74 | 122 | 48 | 0.1 | 0.3 | 34.9 | 64.8 |  | 5.13 |  |  | 191.47 | 565.39 | 565.39 | 222.55 | 507 | 128.55 | 643.58 | 476.52 | 1 |  | 7.26 | [5 empty] | 699.47 | 20.13 | 0.62 | 0.72
81 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL100 | 1S-DL-YP-ETC-DKWL-2451-KWL100 | SAHID BHAGAT SINGH CLY GALI NO 16:ID | TG-KWL100A-1 | 19506759 | 630 | 200 | 235 | 0.97 | 616 | 194 | 840 | 187 | 811 | 236 | 1022 | 198 | 2019-06-02 07:00 | 227.6 | 62.4 | 1022 | B | 101 | 92 | 107 | 15 |  |  | 6.5 | 93.5 |  |  |  |  | 3.3 | 21.34 | 21.34 | 5 | 642.26 | 657.28 | 609.38 | 647.32 | 67.39 | 34.33 | 101.44 | 61.03 |  |  | 1.43 |  | 713.35 | 6.25 | 0.64 | 0.98
82 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL114 | 1S-DL-YP-ETC-DKWL-2451-KWL114 | KAMAL VIHAR S/STN | TG-KWL114A-1 | 19500667 | 400 | 120 | 232 | 0.98 | 237 | 80 | 352 | 87 | 386 | 70 | 307 | 69 | 2019-06-30 23:30 | 63.5 | 16.3 | 386 | Y | 101 | 99 | 100 | 2 |  | 1.8 | 50.6 | 47.6 |  |  |  |  | 325.57 | 322.2 | 322.2 | 325.13 | 385.12 | 388.49 | 397.34 | 385.56 | [8 empty] | 711.09 | 8.51 | 0.7 | 0.59
83 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL118 | 1S-DL-YP-ETC-DKWL-2451-KWL118 | SHAKTI VIHAR GALI NO. 8:ID | TG-KWL118A-1 | 19500581 | 630 | 200 | 232.9188 | 0.98105 | 480.6253 | 138.0222 | 611.7193 | 162.7055 | 733.833 | 179.8976 | 792.4657 | 159.7166 | 2019-06-29 23:30 | [15 empty] | 0 |  |  |  | 33.5 |  |  |  | 681 |  |  |  | 0 |  |  |  | 0 | 714.5 |  | 0.67596 | 0.7629
84 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL118 | 1S-DL-YP-ETC-DKWL-2451-KWL118 | SHAKTI VIHAR GALI NO. 8:ID | TG-KWL118A-2 | 19505643 | 630 | 200 | 240 | 0.96 | 356 | 138 | 630 | 112 | 514 | 106 | 484 | 134 | 2019-06-28 23:00 | 128.4 | 33.2 | 630 | R | 115 | 93 | 92 | 23 | 0.1 | 0.2 | 6 | 93.7 |  | 2 | 6 |  | 518.07 | 686.39 | 686.39 | 687.39 | 176 | 5.28 | 16.21 | 6.28 | [8 empty] | 694.07 | 25.53 | 0.56 | 0.57
85 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL123 | 1S-DL-YP-ETC-DKWL-2451-KWL123 | SAHID BHAGAT SINGH P/M | TG-KWL123A-1 | 19506631 | 400 | 120 | 247 | 0.97 | 262 | 92 | 363 | 76 | 300 | 94 | 371 | 68 | 2019-06-16 11:00 | 93.6 | 11.8 | 371 | B | 104 | 92 | 104 | 12 |  | 0.1 | 21.4 | 78.6 | 0.3 | 0.3 |  |  | 394.31 | 492.28 | 492.28 | 428.31 | 299.59 | 202.02 | 360.22 | 266.29 | [8 empty] | 695 | 25 | 0.6 | 0.65
86 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL238 | 1S-DL-YP-ETC-DKWL-2451-KWL238 | SAHID BHAGAT SINGH GALI NO 12:ID | TG-KWL238A-1 | 19500544 | 630 | 200 | 249.9929 | 0.96402 | 476.4775 | 147.8862 | 612.9492 | 186.1182 | 767.0232 | 142.4731 | 594.48 | 164.0901 | 2019-06-01 | [15 empty] | 0 |  |  |  | 101 |  |  |  | 618 |  |  |  | 0 |  |  |  | 0 | 719 |  | 0.65425 | 0.75631
87 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL264 | 1S-DL-YP-ETC-DKWL-2451-KWL264 | WEST KAMAL VIHAR (HVDS) INDUT. AREA:PM | TG-KWL264A-1 | 19505888 | 400 | 120 | 235 | 0.97 | 393 | 148 | 669 | 112 | 508 | 134 | 605 | 140 | 2019-06-30 14:30 | 277.3 | -32.6 | 669 | R | 104 | 105 | 91 | 14 | 1.2 | 0.1 | 37.3 | 61.4 | 94.45 | 92.15 | 118.5 | 97.45 | 276.1 | 283.1 | 283.1 | 286.1 | 291.02 | 292.38 | 264.31 | 295.02 | 32.28 | 27.22 | 4.29 | 16.28 | 1 |  | 0.3 |  | 695.25 | 24.35 | 0.41 | 0.98
88 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL284 | 1S-DL-YP-ETC-DKWL-2451-KWL284 | WEST KAMAL VIHAR B BLK GALI NO 1 IND AREA:PM | TG-KWL284A-1 | 19506281 | 400 | 120 | 240 | 0.92 | 168 | 56 | 238 | 57 | 240 | 55 | 236 | 3 | 2019-06-19 20:00 | 120.4 | -38.6 | 247 | R | 97 | 103 | 101 | 6 | 1.1 |  | 6.3 | 92.6 | 543.25 | 538.53 | 545.04 | 542.03 | 150.17 | 154.49 | 154.49 | 151.39 | 1 | 1 | 0.3 | 1 | [8 empty] | 694.42 | 25.18 | 0.25 | 0.42
89 | 2019-06-12 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL285 | 1S-DL-YP-ETC-DKWL-2451-KWL285 | Village New Sabha Pur(Boys Sr.School):PM | TG-KWL285A-1 | 19505115 | 400 | 120 | 247 | 0.99 | 20 | 13 | 53 | 4 | 14 | 3 | 13 | 40 | 2019-06-14 12:30 | 10 | -1.1 | 53 | R | 98 | 115 | 87 | 28 |  | 0.1 | 1.9 | 98 | 425.12 | 425.12 | 425.12 | 425.12 | [16 empty] | 425.12 | 30.48 | 0.23 | 0.05
90 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL287 | 1S-DL-YP-ETC-DKWL-2451-KWL287 | BABU NAGAR 1 GALI NO. 5:ID | TG-KWL287A-1 | 19506284 | 630 | 200 | 235 | 0.97 | 575 | 181 | 795 | 200 | 878 | 194 | 849 | 73 | 2019-06-14 11:00 | 192.2 | 52.8 | 941 | Y | 93 | 107 | 99 | 14 | 0.1 | 0.7 | 27.3 | 72 |  |  |  |  | 11 | 3 | 3 | 2 | 685.54 | 648.39 | 693.03 | 693.33 | 1.18 | 45.33 | 3.39 | 2.39 |  | 1 |  |  | 698.12 | 21.48 | 0.67 | 0.91
91 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL293 | 1S-DL-YP-ETC-DKWL-2451-KWL293 | D Blk Mukund Vihar:ID | TG-KWL293A-1 | 19505642 | 990 | 320 | 245 | 0.97 | 765 | 255 | 1044 | 239 | 979 | 272 | 1113 | 116 | 2019-06-02 05:30 | 296.6 | 54.7 | 1118 | B | 97 | 91 | 112 | 21 |  |  | 6.2 | 93.8 |  |  |  |  | 431.15 | 519.47 | 519.47 | 384.53 | 277.33 | 189.01 | 526.33 | 323.55 |  |  | 0.34 | [5 empty] | 708.48 | 11.12 | 0.52 | 0.77
92 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL296 | 1S-DL-YP-ETC-DKWL-2451-KWL296 | SAHID BHAGAT SINGH CLY GALI NO 6:ID | TG-KWL296A-1 | 19500671 | 990 | 320 | 237.805 | 0.98067 | 863.5283 | 291.338 | 1285.9764 | 295.9745 | 1301.1584 | 276.2158 | 1219.2267 | 75.4945 | 2019-06-30 23:30 | [15 empty] | 0 |  |  |  | 5.5 |  |  |  | 705 |  |  |  | 8 |  |  |  | 0 | 718.5 |  | 0.68636 | 0.87225
93 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL299 | 1S-DL-YP-ETC-DKWL-2451-KWL299 | G& H BLK WEST KARAWAL NAGAR:ID | TG-KWL299A-1 | 19500673 | 630 | 200 | 249 | 0.96 | 358 | 90 | 368 | 143 | 589 | 125 | 513 | 194 | 2019-06-11 23:00 | 116.4 | 42.8 | 589 | Y | 84 | 114 | 102 | 30 | 0 |  | 48.5 | 51.5 |  |  |  |  | 631.46 | 298.55 | 298.55 | 475.33 | 79.54 | 412.45 | 258.41 | 236.07 | [8 empty] | 711.4 | 8.2 | 0.66 | 0.57
94 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL329 | 1S-DL-YP-ETC-DKWL-2451-KWL329 | ROSHAN VIHAR GALI NO. 5:ID | TG-KWL329A-1 | 19506282 | 400 | 120 | 249 | 0.95 | 58 | 8 | 34 | 41 | 166 | 8 | 34 | 132 | 2019-06-12 | 24.1 | 3.6 | 169 | Y | 56 | 198 | 46 | 152 | 0.1 | 0.1 | 36.2 | 63.6 | 708.06 | 642.58 | 708.06 | 708.06 |  | 65.08 | 65.08 | [13 empty] | 708.06 | 11.54 | 0.55 | 0.14
95 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL330 | 1S-DL-YP-ETC-DKWL-2451-KWL330 | RAMA GARDEN:ID | TG-KWL330A-1 | 19500665 | 630 | 200 | 236.1921 | 0.9782 | 329.2854 | 118.3622 | 519.2919 | 115.4114 | 509.4303 | 95.5118 | 419.4632 | 95.2814 | 2019-06-21 14:00 | [15 empty] | 0 |  |  |  | 376.5 |  |  |  | 339 |  |  |  | 0 |  |  |  | 0 | 715.5 |  | 0.75898 | 0.52268
96 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL343 | 1S-DL-YP-ETC-DKWL-2451-KWL343 | KAMAL VIHAR MAIN RD OPP POL. CHOWKI P/M | TG-KWL343A-1 | 19506497 | 400 | 120 | 241 | 0.88 | 274 | 90 | 367 | 92 | 375 | 92 | 375 | 8 | 2019-06-08 10:30 | 191.5 | -1.7 | 375 | B | 99 | 98 | 103 | 5 | 35.7 | 6.3 | 4.4 | 53.6 | 378.49 | 367.16 | 365.16 | 367.16 | 160.28 | 137.41 | 137.41 | 153.11 | 123.18 | 157.38 | 167.52 | 142.08 | [8 empty] | 694.47 | 25.13 | 0.29 | 0.68
97 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | HVD008 | 1S-DL-YP-ETC-DKWL-2451-HVD008 | D2 MAIN RD 3-1/2 PUSTA SONIA VIHAR:PM | TG-HVD008A-1 | 19504896 | 100 | 40 | 248 | 0.99 | 12 | 2 | 6 | 4 | 18 | 6 | 25 | 16 | 2019-06-06 18:00 | 0.6 | -1.4 | 29 | B | 38 | 109 | 153 | 115 |  |  | 4.2 | 95.8 | 709.04 | 709.04 | 707.34 | 709.04 | [16 empty] | 709.04 | 10.56 | 0.53 | 0.12
98 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL006 | 1S-DL-YP-ETC-DKWL-2451-KWL006 | ZERO PUSTA STREET LIGHT SONIA VIHAR PM | TG-KWL006A-1 | 19504895 | 100 | 40 | 242 | 0.95 | 36 | 12 | 51 | 12 | 51 | 12 | 53 | 2 | 2019-06-13 15:30 | 21.8 | -1.1 | 85 | R | 89 | 98 | 113 | 24 | 0.1 | 4.2 | 74.3 | 21.3 | 640.19 | 607.56 | 595.17 | 624.19 | 61.57 | 93.22 | 93.22 | 79.57 | 2 | 2.58 | [10 empty] | 704.16 | 15.44 | 0.34 | 0.36
99 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL016 | 1S-DL-YP-ETC-DKWL-2451-KWL016 | CHANDU NAGAR:ID | TG-KWL016A-1 | 19500597 | 990 | 320 | 239 | 0.97 | 596 | 232 | 993 | 189 | 794 | 176 | 749 | 225 | 2019-06-11 00:30 | 118.5 | 44.2 | 993 | R | 111 | 102 | 87 | 24 |  | 0.2 | 56.1 | 43.7 |  |  | 3 |  | 282.29 | 356.23 | 356.23 | 418.39 | 427.2 | 353.26 | 118.44 | 291.1 | [8 empty] | 709.49 | 10.11 | 0.65 | 0.6
100 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL016 | 1S-DL-YP-ETC-DKWL-2451-KWL016 | CHANDU NAGAR:ID | TG-KWL016A-2 | 19505302 | 400 | 120 | 250 | 0.97 | 422 | 143 | 580 | 131 | 538 | 148 | 615 | 67 | 2019-06-10 22:00 | 150.7 | 26 | 615 | B | 105 | 87 | 107 | 20 |  | 1.4 | 49.2 | 49.3 |  |  |  |  | 3.07 | 24.3 | 24.3 | 2.3 | 647.35 | 685.13 | 605.13 | 685.11 | 56.31 | 1.39 | 99.52 | 23.24 | 4.39 | 0.3 | 2.17 | 0.47 | 711.52 | 8.08 | 0.58 | 1.06
101 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL017 | 1S-DL-YP-ETC-DKWL-2451-KWL017 | E BLOCK KHAJOORI GALI NO. 3:ID | TG-KWL017A-1 | 19506119 | 630 | 200 | 247 | 0.96 | 465 | 94 | 380 | 165 | 674 | 206 | 830 | 396 | 2019-06-18 00:30 | 144.8 | 38.4 | 830 | B | 105 | 78 | 117 | 39 | 0.1 | 2.9 | 57.3 | 39.7 | 0.3 | 0.3 |  |  | 275.42 | 582.41 | 582.41 | 314.45 | 442.27 | 135.28 | 523.5 | 403.54 |  |  | 14.26 | [5 empty] | 718.39 | 1.21 | 0.59 | 0.74
102 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL017 | 1S-DL-YP-ETC-DKWL-2451-KWL017 | E BLOCK KHAJOORI GALI NO. 3:ID | TG-KWL017A-2 | 19505644 | 990 | 320 | 240 | 0.97 | 892 | 305 | 1346 | 282 | 1226 | 304 | 1342 | 118 | 2019-06-30 23:00 | 273.9 | 81.3 | 1397 | B | 96 | 96 | 109 | 13 | 0.1 | 0.3 | 68.6 | 30.9 |  |  |  |  | 44.58 | 94.58 | 94.58 | 36.28 | 673.04 | 611.34 | 654.19 | 672.34 | 0.47 | 12.17 | 48.3 | 9.47 |  |  |  |  | 718.49 | 1.11 | 0.61 | 0.9
103 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL018 | 1S-DL-YP-ETC-DKWL-2451-KWL018 | F BLOCK KHAJOORI GALI NO. 11&13:ID | TG-KWL018A-1 | 19504694 | 990 | 320 | 247 | 0.97 | 973 | 319 | 1353 | 341 | 1463 | 313 | 1317 | 131 | 2019-06-02 22:30 | 218.6 | 100.1 | 1470 | Y | 100 | 104 | 96 | 8 | 0.1 | 1.6 | 81.3 | 16.9 | [8 empty] | 597.24 | 500.37 | 629.25 | 585.44 | 94.39 | 185.56 | 62.08 | 106.19 |  | 5.3 |  |  | 715.19 | 4.41 | 0.71 | 0.98
104 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL018 | 1S-DL-YP-ETC-DKWL-2451-KWL018 | F BLOCK KHAJOORI GALI NO. 11&13:ID | TG-KWL018A-2 | 19502248 | 630 | 200 | 240 | 0.97 | 544 | 155 | 677 | 224 | 988 | 166 | 724 | 290 | 2019-06-03 15:30 | 153.2 | 56.6 | 1006 | Y | 88 | 119 | 93 | 31 |  | 0.1 | 59.7 | 40.1 |  |  |  |  | 17.2 | 2.57 | 2.57 | 7.22 | 696.52 | 456.47 | 698.2 | 694.3 |  | 246.08 | 5.3 | 12.2 |  | 8.2 |  |  | 714.12 | 5.48 | 0.73 | 0.86
105 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL021 | 1S-DL-YP-ETC-DKWL-2451-KWL021 | A BLOCK NEHRU VIHAR GALI NO. 2:ID | TG-KWL021A-1 | 19500600 | 630 | 200 | 244.6037 | 0.97309 | 414.0984 | 129.6131 | 534.1567 | 160.5479 | 664.1621 | 123.9374 | 513.6874 | 141.356 | 2019-06-01 12:00 | [15 empty] | 0 |  |  |  | 154.5 |  |  |  | 564.5 |  |  |  | 0 |  |  |  | 0 | 719 |  | 0.70641 | 0.6573
106 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL022 | 1S-DL-YP-ETC-DKWL-2451-KWL022 | B-II BLOCK NEHRU VIHAR GALI NO. 6:ID | TG-KWL022A-1 | 19506820 | 630 | 200 | 249 | 0.96 | 933 | 336 | 1412 | 305 | 1272 | 292 | 1217 | 174 | 2019-06-28 14:30 | 319.4 | 106.4 | 1412 | R | 109 | 101 | 90 | 19 |  | 0.1 | 1.9 | 98 | [8 empty] | 33.3 | 122 | 323.3 | 112.3 | 354.09 | 389.54 | 330.31 | 430.09 | 316.52 | 192.37 | 50.3 | 161.52 | 704.31 | 15.29 | 0.62 | 1.48
107 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL025 | 1S-DL-YP-ETC-DKWL-2451-KWL025 | E-2, NEHRU VIHAR:ID | TG-KWL025A-1 | 19506446 | 1600 | 500 | 241 | 0.97 | 1347 | 449 | 1976 | 473 | 2085 | 425 | 1850 | 204 | 2019-06-26 10:00 | 452 | 115 | 2085 | Y | 94 | 104 | 101 | 10 | 0.1 | 0.1 | 5.7 | 94.1 |  |  |  |  | 38.3 | 16.3 | 16.3 | 25 | 668.58 | 688.58 | 686.33 | 681.58 | 0.41 | 2.41 |  | 1.11 |  |  |  |  | 708.09 | 11.51 | 0.63 | 0.84
108 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL026 | 1S-DL-YP-ETC-DKWL-2451-KWL026 | E-1, NEHRU VIHAR:ID | TG-KWL026A-1 | 19505257 | 990 | 320 | 235 | 0.96 | 891 | 270 | 1221 | 308 | 1399 | 312 | 1414 | 186 | 2019-06-11 22:30 | 376.3 | 78.1 | 1414 | B | 99 | 103 | 98 | 5 | 0.1 | 0.4 | 7.3 | 92.3 |  |  |  |  | 34.52 | 28.3 | 28.3 | 32.3 | 651.54 | 639.19 | 626.39 | 649.25 | 4.49 | 23.46 | 16.49 | 9.4 |  |  |  |  | 691.35 | 28.25 | 0.61 | 0.9
109 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL037 | 1S-DL-YP-ETC-DKWL-2451-KWL037 | MOONGA NAGAR:ID | TG-KWL037A-1 | 19500666 | 990 | 320 | 244.0058 | 0.96289 | 685.7208 | 214.6358 | 897.307 | 265.6236 | 1103.0423 | 205.4614 | 863.9364 | 224.2903 | 2019-06-10 22:30 | [15 empty] | 3 |  |  |  | 546 |  |  |  | 169 |  |  |  | 0 |  |  |  | 0 | 718 |  | 0.50122 | 0.69265
110 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL060 | 1S-DL-YP-ETC-DKWL-2451-KWL060 | C BLOCK KHAJORI MAIN MARKET | TG-KWL060A-1 | 19506447 | 990 | 320 | 246.9138 | 0.96703 | 869.5479 | 236.4072 | 974.5939 | 367.6768 | 1527.8487 | 265.4639 | 1115.7695 | 497.911 | 2019-06-13 23:00 | [15 empty] | 0 |  |  |  | 194 |  |  |  | 509.5 |  |  |  | 14 |  |  |  | 0 | 717.5 |  | 0.56357 | 0.87833
111 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL060 | 1S-DL-YP-ETC-DKWL-2451-KWL060 | C BLOCK KHAJORI MAIN MARKET | TG-KWL060A-2 | 19502298 | 990 | 320 | 246 | 0.96 | 786 | 252 | 1009 | 234 | 936 | 301 | 1210 | 246 | 2019-06-27 01:00 | 190.6 | 21.3 | 1289 | B | 101 | 90 | 109 | 19 |  |  | 3.8 | 96.2 | 1.3 | 1.3 | 1.3 | 1.3 | 290.36 | 426.38 | 426.38 | 327.52 | 421.18 | 285.16 | 446.3 | 384.02 |  |  | 21.37 | [5 empty] | 713.24 | 6.36 | 0.55 | 0.79
112 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL060 | 1S-DL-YP-ETC-DKWL-2451-KWL060 | C BLOCK KHAJORI MAIN MARKET | TG-KWL060A-3 | 19506413 | 630 | 200 | 245 | 0.97 | 647 | 199 | 825 | 261 | 1079 | 187 | 769 | 286 | 2019-06-12 | 215.6 | 36.4 | 1271 | Y | 95 | 112 | 94 | 18 | 0.3 |  | 5.4 | 94.3 |  | 0.56 | 0.56 |  | 18.13 | 7.43 | 7.43 | 11.09 | 600.48 | 479.12 | 614.5 | 559.4 | 77.51 | 131.32 | 62.59 | 124.53 |  | 77.29 |  | 1.1 | 696.52 | 23.08 | 0.62 | 1.03
113 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL061 | 1S-DL-YP-ETC-DKWL-2451-KWL061 | FATMA NURSARY CHAND BAGH MRD WZB ROAD:PL | TG-KWL061A-1 | 19502590 | 990 | 320 | 245 | 0.97 | 875 | 299 | 1223 | 282 | 1151 | 294 | 1203 | 64 | 2019-06-30 23:30 | 200.9 | 84.6 | 1337 | R | 99 | 92 | 109 | 17 | 0 |  | 13.4 | 86.6 |  |  | 0.21 |  | 2.21 | 1.51 | 1.51 | 0.21 | 636.21 | 703.5 | 588.07 | 678.33 | 74.21 | 7.22 | 124.35 | 34.09 |  |  |  |  | 715.33 | 4.27 | 0.74 | 0.88
114 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL063 | 1S-DL-YP-ETC-DKWL-2451-KWL063 | VILLAGE SABHAPUR:PM | TG-KWL063A-1 | 19502302 | 630 | 200 | 230 | 0.98 | 758 | 293 | 1297 | 211 | 918 | 255 | 1125 | 329 | 2019-06-09 23:00 | 156.9 | 26.2 | 1297 | R | 112 | 89 | 99 | 23 |  | 4.7 | 41.4 | 54 |  |  |  |  | 0.31 | 8.53 | 8.53 | 1.23 | 318.29 | 550.08 | 442.56 | 428.44 | 207.48 | 136.2 | 229.14 | 222.01 | 171.33 | 3 | 25.19 | 46.13 | 698.21 | 21.39 | 0.62 | 1.2
115 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL064 | 1S-DL-YP-ETC-DKWL-2451-KWL064 | SHERPUR CHOWK:PL | TG-KWL064A-1 | 19505767 | 990 | 320 | 240 | 0.97 | 784 | 254 | 1111 | 268 | 1167 | 262 | 1143 | 48 | 2019-06-26 12:00 | 327.4 | -27.8 | 1167 | Y | 101 | 101 | 98 | 3 |  |  | 13 | 87 | 53.01 | 68.31 | 78.31 | 64.31 | 336.46 | 319.15 | 319.15 | 328.46 | 326.31 | 328.32 | 320.01 | 323.31 | 0.3 | 0.3 | [6 empty] | 716.48 | 3.12 | 0.5 | 0.79
116 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL064 | 1S-DL-YP-ETC-DKWL-2451-KWL064 | SHERPUR CHOWK:PL | TG-KWL064A-2 | 19506395 | 630 | 200 | 246 | 0.97 | 624 | 200 | 841 | 223 | 946 | 201 | 852 | 100 | 2019-06-24 15:30 | 312 | -1.2 | 990 | Y | 88 | 109 | 102 | 21 | 0.1 |  | 36.9 | 63 | 41 |  |  |  | 303.36 | 199.15 | 199.15 | 261.36 | 315.43 | 403.19 | 419.52 | 371.13 | 41.49 | 87.15 | 68.4 | 69.19 |  | 12.19 |  |  | 702.08 | 17.52 | 0.52 | 0.99
117 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL069 | 1S-DL-YP-ETC-DKWL-2451-KWL069 | DAYAL PUR 1 TANKI MAIN ROAD DAYAL PUR:PL | TG-KWL069A-1 | 19506842 | 630 | 200 | 234 | 0.97 | 435 | 131 | 562 | 156 | 675 | 148 | 634 | 99 | 2019-06-15 20:00 | 167.8 | 34 | 859 | Y | 90 | 118 | 91 | 28 | 0.1 | 0.9 | 50 | 49 | 2.3 | 1 | 1.3 | 1 | 292.1 | 88.14 | 88.14 | 173.37 | 407.35 | 610.01 | 451.36 | 527.38 |  | 3 | [6 empty] | 702.15 | 17.45 | 0.67 | 0.69
118 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL069 | 1S-DL-YP-ETC-DKWL-2451-KWL069 | DAYAL PUR 1 TANKI MAIN ROAD DAYAL PUR:PL | TG-KWL069A-2 | 19506601 | 630 | 200 | 240 | 0.97 | 564 | 154 | 651 | 165 | 695 | 246 | 1089 | 418 | 2019-06-11 22:30 | 152.4 | 36.6 | 1089 | B | 102 | 92 | 106 | 14 | 0.6 | 2.1 | 55.8 | 41.6 |  |  |  |  | 13 | 19.49 | 19.49 | 9 | 673.45 | 680.26 | 648.16 | 691.15 | 15.3 | 1.3 | 39 | 2 |  | 0.3 | 1.3 |  | 702.15 | 17.45 | 0.66 | 0.9
119 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL069 | 1S-DL-YP-ETC-DKWL-2451-KWL069 | DAYAL PUR 1 TANKI MAIN ROAD DAYAL PUR:PL | TG-KWL069A-3 | 19506880 | 630 | 200 | 242 | 0.99 | 384 | 93 | 406 | 151 | 652 | 140 | 614 | 230 | 2019-06-01 15:00 | 83 | -66.2 | 652 | Y | 70 | 122 | 108 | 52 | 0.1 | 0.1 | 14.7 | 85.1 | 24.24 | 0.3 | 0.3 | 0.3 | 662.22 | 115.13 | 115.13 | 345.48 | 15.3 | 586.33 | 392.28 | 355.58 | [8 empty] | 702.16 | 17.44 | 0.67 | 0.61
120 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL070 | 1S-DL-YP-ETC-DKWL-2451-KWL070 | B BLK GALI NO. 9, CHAND BAGH:ID | TG-KWL070A-1 | 19500570 | 630 | 200 | 236 | 0.97 | 584 | 196 | 859 | 225 | 994 | 164 | 715 | 242 | 2019-06-02 23:30 | 154.6 | 63 | 1075 | Y | 93 | 125 | 82 | 43 | 39.5 | 11.4 | 16.1 | 33 |  |  |  |  | 4 |  |  |  | 673.43 | 316.08 | 630.24 | 647.45 | 37.32 | 361.3 | 13.26 | 67.3 |  | 37.37 |  |  | 715.15 | 4.45 | 0.72 | 0.93
121 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL070 | 1S-DL-YP-ETC-DKWL-2451-KWL070 | B BLK GALI NO. 9, CHAND BAGH:ID | TG-KWL070A-2 | 19505139 | 990 | 320 | 235 | 0.96 | 884 | 307 | 1390 | 302 | 1372 | 276 | 1239 | 142 | 2019-06-02 15:00 | 325.4 | 88.6 | 1404 | Y | 95 | 107 | 99 | 12 | 0.1 | 0.2 | 59 | 40.7 |  |  |  |  | 45.38 | 6 | 6 | 16.11 | 652.27 | 688.07 | 658.26 | 680.56 | 2.3 | 6.28 | 3.58 | 3.28 |  |  |  |  | 700.35 | 19.25 | 0.6 | 0.89
122 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL071 | 1S-DL-YP-ETC-DKWL-2451-KWL071 | CHAND BAGH "F" BLK:ID | TG-KWL071A-1 | 19505573 | 990 | 320 | 235 | 0.97 | 865 | 229 | 1029 | 304 | 1371 | 332 | 1507 | 426 | 2019-06-02 14:30 | 296.6 | 46.4 | 1507 | B | 84 | 107 | 108 | 24 | 0.4 | 0.2 | 2.1 | 97.3 | 0.3 | 0.3 |  |  | 92.47 | 3 | 3 | 11.3 | 607.46 | 689.43 | 686.46 | 686.11 |  | 7.5 | 7.23 | 3.22 |  |  | 0.26 |  | 701.03 | 18.57 | 0.63 | 0.87
123 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL072 | 1S-DL-YP-ETC-DKWL-2451-KWL072 | VILLAGE KHAJOORI NR.SCHOOL:PL | TG-KWL072A-1 | 19504805 | 630 | 200 | 244 | 0.99 | 601 | 253 | 1061 | 174 | 721 | 174 | 720 | 340 | 2019-06-12 15:00 | 118.7 | -10.6 | 1085 | R | 116 | 92 | 91 | 25 |  | 2.2 | 39.9 | 58 |  |  |  |  | 3 | 30.3 | 30.3 | 5.3 | 481.58 | 645.16 | 697.46 | 647.47 | 143.19 | 41 | 8.3 | 63.29 | 88.29 |  |  |  | 716.46 | 3.14 | 0.68 | 0.95
124 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL076 | 1S-DL-YP-ETC-DKWL-2451-KWL076 | A BL MAIN ROAD DAYALPUR:PL | TG-KWL076A-1 | 19506896 | 990 | 320 | 243 | 0.97 | 988 | 353 | 1486 | 286 | 1185 | 349 | 1457 | 287 | 2019-06-16 02:00 | 351.4 | 89.9 | 1486 | R | 107 | 92 | 100 | 15 |  |  | 8.7 | 91.3 | [5 empty] | 20.18 | 20.18 |  | 575.58 | 652.58 | 630.42 | 640.01 | 115.49 | 20.15 | 61.19 | 53.3 | 1.44 |  | 0.3 |  | 693.31 | 26.29 | 0.63 | 1
125 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL079 | 1S-DL-YP-ETC-DKWL-2451-KWL079 | B BLK SADAT PUR GALI NO. 8:ID | TG-KWL079A-1 | 19504409 | 400 | 120 | 239 | 0.97 | 369 | 141 | 631 | 112 | 491 | 115 | 508 | 132 | 2019-06-29 23:00 | 69.3 | 28.2 | 670 | R | 114 | 96 | 90 | 24 | 1.3 | 28.9 | 69.1 | 0.7 |  |  |  |  | 30 | 66 | 66 | 59.3 | 525.41 | 642.31 | 528.31 | 602.31 | 137.2 | 11 | 15 | 57.3 | 26.3 |  |  |  | 719.31 | 0.29 | 0.61 | 0.92
126 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL080 | 1S-DL-YP-ETC-DKWL-2451-KWL080 | BIHARI PUR VILLNR. NLA KHJURI PUST RD:PL | TG-KWL080A-1 | 19506903 | 990 | 320 | 240 | 0.97 | 842 | 309 | 1384 | 257 | 1170 | 276 | 1266 | 186 | 2019-06-30 14:30 | 256.6 | 50.9 | 1559 | R | 117 | 96 | 87 | 30 | 0.1 | 0.5 | 47.8 | 51.5 |  |  |  |  | 1 | 13.3 | 13.3 | 6.3 | 593.2 | 687.03 | 642.31 | 693.33 | 101.43 |  | 0.3 | 0.3 | 4.3 |  |  |  | 700.33 | 19.27 | 0.68 | 0.85
127 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL083 | 1S-DL-YP-ETC-DKWL-2451-KWL083 | L BLK SADAT PUR:ID | TG-KWL083A-1 | 19500560 | 990 | 320 | 233.991 | 0.96903 | 893.8565 | 286.146 | 1304.1016 | 295.6431 | 1344.5655 | 312.0675 | 1416.2997 | 98.4163 | 2019-06-30 | [15 empty] | 0 |  |  |  | 180.5 |  |  |  | 525.5 |  |  |  | 14 |  |  |  | 0 | 720 |  | 0.5541 | 0.90289
128 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL085 | 1S-DL-YP-ETC-DKWL-2451-KWL085 | B BLK PUSTA 1 SONIA VIHAR GALI NO 1 | TG-KWL085A-1 | 19506042 | 630 | 200 | 234 | 0.97 | 589 | 176 | 745 | 202 | 854 | 210 | 883 | 126 | 2019-06-08 09:30 | 174.6 | 50.2 | 988 | Y | 99 | 99 | 103 | 4 |  | 10.1 | 75.9 | 14 |  |  |  |  | 7.3 | 46.49 | 46.49 | 8 | 659.02 | 591.13 | 658.29 | 654.56 | 6.39 | 31.58 | 14.03 | 10.15 |  | 3.11 | 0.39 |  | 673.11 | 46.49 | 0.63 | 0.93
129 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL088 | 1S-DL-YP-ETC-DKWL-2451-KWL088 | BALAJI TEMPLE SABHAPUR:PL | TG-KWL088A-1 | 19504363 | 630 | 200 | 233 | 0.96 | 316 | 104 | 448 | 81 | 353 | 130 | 570 | 188 | 2019-06-12 | 106.7 | 18.9 | 589 | B | 104 | 76 | 120 | 44 |  |  | 27.3 | 72.7 |  | 96.58 |  |  | 522.33 | 601.3 | 601.3 | 599.41 | 179.25 | 3.3 | 418.36 | 102.17 | [8 empty] | 701.58 | 18.02 | 0.69 | 0.5
130 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL089 | 1S-DL-YP-ETC-DKWL-2451-KWL089 | WAZIRA BAD RAW WATER ST LT :PM | TG-KWL089A-1 | 19504407 | 400 | 120 | 245 | 0.95 | 58 | 15 | 59 | 5 | 18 | 38 | 155 | 121 | 2019-06-12 19:00 | 23.5 | 0.3 | 155 | B | 78 | 36 | 186 | 150 |  | 0.1 | 52.6 | 47.4 | 720 | 720 | 505 | 720 | [16 empty] | 720 | 0 | 0.37 | 0.14
131 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL090 | 1S-DL-YP-ETC-DKWL-2451-KWL090 | LAL FARM HOUSE SABHAPUR:PM | TG-KWL090A-1 | 19506390 | 400 | 120 | 244 | 0.96 | 93 | 12 | 50 | 66 | 265 | 15 | 59 | 211 | 2019-06-04 10:30 | 43.9 | 4.1 | 265 | Y | 94 | 119 | 87 | 32 |  | 0.1 | 17 | 82.9 | 528.02 | 533.44 | 549.02 | 549.02 | 21.3 | 15.18 | 15.18 | 0.3 |  | 0.3 | [10 empty] | 549.32 | 50.28 | 0.47 | 0.23
132 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL093 | 1S-DL-YP-ETC-DKWL-2451-KWL093 | CHAUHAN PATTI PUSTA VILL SONIA VIHAR:PL | TG-KWL093A-1 | 19506301 | 630 | 200 | 238 | 0.96 | 714 | 218 | 952 | 262 | 1154 | 234 | 1025 | 177 | 2019-06-29 22:30 | 243.6 | 70.8 | 1216 | Y | 96 | 109 | 95 | 14 |  | 2.6 | 25.7 | 71.8 |  |  |  |  | 0.57 |  |  |  | 603.09 | 408.36 | 543.13 | 518.53 | 79.32 | 247.25 | 139.48 | 164.05 | 2.34 | 30.11 | 1.44 | 3.14 | 686.12 | 33.48 | 0.63 | 1.13
133 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL094 | 1S-DL-YP-ETC-DKWL-2451-KWL094 | CHAWLA FARM CHAUHAN PATI:PM | TG-KWL094A-1 | 19504335 | 400 | 120 | 245 | 0.96 | 269 | 90 | 379 | 94 | 398 | 85 | 362 | 31 | 2019-06-29 23:00 | 97.7 | 28.7 | 414 | R | 103 | 102 | 95 | 8 |  |  | 24.5 | 75.5 |  |  |  |  | 95.02 | 136.59 | 136.59 | 129.34 | 607.13 | 565.16 | 454.04 | 572.41 | [8 empty] | 702.15 | 17.45 | 0.67 | 0.67
134 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL096 | 1S-DL-YP-ETC-DKWL-2451-KWL096 | B-I, NEHRU VIHAR:ID | TG-KWL096A-1 | 19500614 | 990 | 320 | 254 | 0.96 | 1166 | 389 | 1610 | 380 | 1576 | 397 | 1648 | 62 | 2019-06-29 23:00 | 249.5 | 128.8 | 1658 | B | 106 | 103 | 91 | 15 |  | 0.1 | 22 | 77.8 | [8 empty] | 423.1 | 435.23 | 546.23 | 481.53 | 201.43 | 217 | 143 | 177 | 94 | 66.3 | 29.3 | 60 | 718.53 | 1.07 | 0.64 | 1.18
135 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL111 | 1S-DL-YP-ETC-DKWL-2451-KWL111 | B BL SONIA VIHAR GALI 17:ID | TG-KWL111A-1 | 19506403 | 990 | 320 | 246 | 0.96 | 832 | 245 | 991 | 294 | 1204 | 293 | 1194 | 208 | 2019-06-10 05:00 | 307.5 | 86.4 | 1204 | Y | 92 | 102 | 106 | 14 | 0.1 | 0.1 | 16.3 | 83.6 |  |  |  |  | 23.19 | 9 | 9 | 7.19 | 666.11 | 679.4 | 686.03 | 681.44 |  | 0.5 | 0.27 | 0.27 |  |  |  |  | 689.3 | 30.3 | 0.65 | 0.84
136 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL113 | 1S-DL-YP-ETC-DKWL-2451-KWL113 | SONIA VIHAR "B" BLK GALI NO-27 | TG-KWL113A-1 | 19506291 | 400 | 200 | 243 | 0.96 | 524 | 193 | 808 | 181 | 756 | 150 | 616 | 172 | 2019-06-10 05:00 | 192.4 | 56.6 | 808 | R | 103 | 106 | 91 | 15 |  | 0.1 | 20.4 | 79.5 | [8 empty] | 394.32 | 305.16 | 586.25 | 464.17 | 263.15 | 360.29 | 99.08 | 218.16 | 29.13 | 21.15 | 1.27 | 4.27 | 687 | 33 | 0.59 | 1.31
137 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL115 | 1S-DL-YP-ETC-DKWL-2451-KWL115 | C 1 KHAJOORI GALI NO. 24:PM | TG-KWL115A-1 | 19502314 | 400 | 120 | 251 | 0.98 | 439 | 152 | 636 | 89 | 365 | 198 | 832 | 406 | 2019-06-02 23:00 | 86.4 | 20.7 | 879 | B | 100 | 58 | 142 | 84 | 0.2 | 40.5 | 57.9 | 1.3 |  | 1 |  |  |  | 274.4 | 274.4 |  | 471.39 | 443.58 | 38.29 | 492.39 | 201.29 |  | 261.49 | 197.59 | 46.3 |  | 419.2 | 29 | 719.38 | 0.22 | 0.68 | 1.1
138 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL116 | 1S-DL-YP-ETC-DKWL-2451-KWL116 | E BLK DAYAL PUR 33 FEETA ROAD | TG-KWL116A-1 | 19506001 | 630 | 120 | 239 | 0.97 | 380 | 92 | 392 | 111 | 471 | 177 | 793 | 368 | 2019-06-11 23:00 | 129.2 | 34.4 | 793 | B | 86 | 97 | 116 | 30 | 0.1 | 1.8 | 47.1 | 51 |  |  |  |  | 629.49 | 423.45 | 423.45 | 392.51 | 87.55 | 293.59 | 528.51 | 324.53 |  |  | 0.3 | [5 empty] | 717.44 | 2.16 | 0.66 | 0.6
139 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL119 | 1S-DL-YP-ETC-DKWL-2451-KWL119 | F BLK DAYAL PUR : ID | TG-KWL119A-1 | 19503341 | 630 | 200 | 234 | 0.97 | 500 | 213 | 952 | 139 | 614 | 148 | 664 | 316 | 2019-06-29 23:30 | 110.9 | 45.5 | 1035 | R | 128 | 90 | 82 | 46 |  |  | 2.9 | 97.1 |  |  |  |  | 1 | 125.02 | 125.02 | 41 | 548.5 | 592.21 | 464.15 | 676.23 | 139.33 |  |  |  | 28 |  |  |  | 717.23 | 2.37 | 0.67 | 0.79
140 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL121 | 1S-DL-YP-ETC-DKWL-2451-KWL121 | JEEVAN JYOTI SCHOOL SADAT PUR : ID | TG-KWL121A-1 | 19506411 | 630 | 200 | 236 | 0.96 | 276 | 114 | 512 | 81 | 368 | 81 | 361 | 148 | 2019-06-11 23:00 | 71 | 14 | 609 | R | 118 | 99 | 83 | 35 | 0.2 | 19.6 | 69.5 | 10.7 | 131.28 | 287.49 | 374.26 | 262.26 | 458.21 | 399.3 | 399.3 | 424.23 | 112.3 | 15 |  | 15.3 | [8 empty] | 702.19 | 17.41 | 0.55 | 0.44
141 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL121 | 1S-DL-YP-ETC-DKWL-2451-KWL121 | JEEVAN JYOTI SCHOOL SADAT PUR : ID | TG-KWL121A-2 | 19500551 | 990 | 320 | 238.1585 | 0.97477 | 1161.4047 | 414.5778 | 1811.5699 | 392.1803 | 1725.8417 | 354.6466 | 1563.8355 | 217.9078 | 2019-06-27 | [15 empty] | 0 |  |  |  | 8.5 |  |  |  | 485.5 |  |  |  | 146.5 |  |  |  | 79.5 | 720 |  | 0.60838 | 1.1731
142 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL124 | 1S-DL-YP-ETC-DKWL-2451-KWL124 | JELE SINGH KOTHI TUKMEERPUR VILLAGE:PM | TG-KWL124A-1 | 19506720 | 400 | 120 | 248 | 0.84 | 350 | 108 | 466 | 126 | 548 | 116 | 500 | 71 | 2019-06-26 12:00 | 185.5 | -159 | 548 | Y | 102 | 100 | 97 | 5 |  | 0.1 | 12.8 | 87.1 |  |  |  |  | 305.51 | 336.06 | 336.06 | 329.36 | 387.57 | 354.12 | 335.15 | 363.12 | 1 | 4.3 | 1.3 | 2 |  |  |  |  | 694.48 | 25.12 | 0.48 | 0.88
143 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL127 | 1S-DL-YP-ETC-DKWL-2451-KWL127 | NIKKA PLASTIC TUKMEERPUR VILLAGE:PM | TG-KWL127A-1 | 19505123 | 400 | 120 | 245 | 0.99 | 501 | 165 | 662 | 166 | 674 | 169 | 683 | 18 | 2019-06-17 20:00 | 89.6 | -27.4 | 717 | Y | 96 | 102 | 102 | 6 | 25.1 | 6.4 | 39.8 | 28.6 | 61.3 | 57.3 | 46 | 58 | 91.52 | 93.52 | 93.52 | 93.52 | 112.47 | 113.47 | 108.55 | 111.17 | 62.18 | 52.48 | 40.3 | 52.48 | 49.16 | 59.46 | 80.36 | 61.46 | 696.41 | 23.19 | 0.46 | 1.25
144 | 2019-06-03 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL138 | 1S-DL-YP-ETC-DKWL-2451-KWL138 | TRANSFORMER WORKSHOP KHAJOORI:PLM | TG-KWL138A-1 | 19503679 | 400 | 120 | 251.7764 | 0.96178 | 45.9583 | 15.18 | 60.8295 | 15.5983 | 62.5633 | 15.18 | 60.1641 | 2.1453 | 2019-06-03 12:00 | [15 empty] | 671.5 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 671.5 |  | 0.38816 | 0.1149
145 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL139 | 1S-DL-YP-ETC-DKWL-2451-KWL139 | E BLK RAMLILLA GROUND SHRI RAM CLY:PLM | TG-KWL139A-1 | 19506410 | 630 | 200 | 252 | 0.97 | 429 | 178 | 744 | 138 | 569 | 113 | 472 | 239 | 2019-06-29 22:30 | 123 | 46.8 | 762 | R | 126 | 89 | 85 | 41 | 0.3 |  | 19.1 | 80.6 |  |  |  |  | 0.3 | 76 | 76 | 10 | 684.06 | 625.36 | 548.23 | 691.36 | 17 | [7 empty] | 701.36 | 18.24 | 0.76 | 0.68
146 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL139 | 1S-DL-YP-ETC-DKWL-2451-KWL139 | E BLK RAMLILLA GROUND SHRI RAM CLY:PLM | TG-KWL139A-2 | 19506871 | 630 | 200 | 252 | 0.96 | 340 | 136 | 544 | 95 | 377 | 109 | 433 | 147 | 2019-06-22 11:00 | 116.4 | 36.6 | 544 | R | 122 | 83 | 95 | 39 |  |  | 12 | 88 |  | 18 | 1 |  | 375.47 | 684.3 | 684.3 | 701 | 327.23 | 0.4 | 3.1 | 2.1 | [8 empty] | 703.1 | 16.5 | 0.61 | 0.54
147 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL142 | 1S-DL-YP-ETC-DKWL-2451-KWL142 | SHRI RAM COLONY A BLK NALA:PLM | TG-KWL142A-1 | 19505474 | 990 | 320 | 254 | 0.97 | 951 | 341 | 1346 | 352 | 1376 | 258 | 1011 | 351 | 2019-06-23 05:00 | 253.1 | 41 | 1376 | Y | 101 | 123 | 76 | 47 |  |  | 4.2 | 95.8 |  |  | 2.3 |  | 227.09 | 22.24 | 22.24 | 202.52 | 481.44 | 686.29 | 3.2 | 506.01 |  |  |  | 0.3 | 0.3 | 0.3 |  |  | 709.23 | 10.37 | 0.45 | 0.96
148 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL145 | 1S-DL-YP-ETC-DKWL-2451-KWL145 | SHRI RAM COLONY B BLK RAMLILA GROUND | TG-KWL145A-1 | 19506532 | 400 | 120 | 241.4765 | 0.97368 | 487.9528 | 196.3645 | 800.2791 | 110.7378 | 443.377 | 180.8505 | 734.5673 | 329.0053 | 2019-06-30 14:30 | [15 empty] | 0.5 |  |  |  | 1.5 |  |  |  | 642.5 |  |  |  | 71 |  |  |  | 2.5 | 718 |  | 0.55697 | 1.2199
149 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL146 | 1S-DL-YP-ETC-DKWL-2451-KWL146 | C BLK SHRI RAM COLONY :PLM | TG-KWL146A-1 | 19506504 | 630 | 200 | 236.2604 | 0.98007 | 697.4431 | 155.4979 | 636.4779 | 299.0081 | 1262.3832 | 242.9371 | 1014.5206 | 545.944 | 2019-06-14 06:00 | [15 empty] | 0 |  |  |  | 0 |  |  |  | 592.5 |  |  |  | 123 |  |  |  | 1.5 | 717 |  | 0.65412 | 1.1071
150 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL147 | 1S-DL-YP-ETC-DKWL-2451-KWL147 | SHRI RAM COLONY D BLK:PLM | TG-KWL147A-1 | 19506716 | 630 | 200 | 243 | 0.97 | 788 | 259 | 1094 | 301 | 1302 | 228 | 968 | 292 | 2019-06-30 01:30 | 279.8 | 62 | 1302 | Y | 96 | 114 | 90 | 24 | 0.1 | 1.6 | 72.4 | 26 |  |  |  |  | 1 |  |  |  | 687.22 | 571.52 | 686.4 | 680.28 | 3.41 | 119.42 | 2.21 | 11.35 | 1.12 | 1.41 | 0.44 | 1.12 | 693.15 | 26.45 | 0.51 | 1.25
151 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL151 | 1S-DL-YP-ETC-DKWL-2451-KWL151 | ANNPURNA MANDIR | TG-KWL151A-1 | 19502316 | 400 | 120 | 242 | 0.96 | 202 | 78 | 336 | 68 | 291 | 57 | 245 | 79 | 2019-06-29 11:30 | 63.5 | 11.9 | 341 | R | 114 | 102 | 84 | 30 |  | 20.1 | 67.7 | 12.3 | 6.3 | 6 | 19.3 | 5 | 347.54 | 500.1 | 500.1 | 566.22 | 344.59 | 193.13 | 42.36 | 128.01 | [8 empty] | 699.23 | 20.37 | 0.69 | 0.51
152 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL154 | 1S-DL-YP-ETC-DKWL-2451-KWL154 | SHRI RAM CLY E BLK GN 3 NR MASJID :PM | TG-KWL154A-1 | 19504596 | 400 | 120 | 239 | 0.98 | 388 | 124 | 530 | 122 | 519 | 143 | 614 | 89 | 2019-06-02 15:00 | 84.5 | 29 | 694 | B | 91 | 95 | 114 | 23 |  | 2.1 | 44.6 | 53.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1.3 | 0.3 | 0.3 |  | 655.59 | 619.34 | 311.46 | 551.21 | 56.59 | 93.54 | 314.05 | 163.07 |  | 0.3 | 88.37 |  | 714.58 | 5.02 | 0.75 | 0.97
153 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL155 | 1S-DL-YP-ETC-DKWL-2451-KWL155 | SONIA VIHAR B BL GALI NO-10:PLM | TG-KWL155A-1 | 19500680 | 630 | 120 | 241 | 0.97 | 500 | 171 | 726 | 197 | 849 | 133 | 566 | 246 | 2019-06-29 | 144.9 | 44.7 | 849 | Y | 97 | 116 | 86 | 30 | 38.6 | 43 | 18.4 | [5 empty] | 119.27 | 19.55 | 19.55 | 78.37 | 583.02 | 674.23 | 424.12 | 624.22 | 0.3 | 8.41 | [6 empty] | 702.59 | 17.01 | 0.62 | 0.79
154 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL157 | 1S-DL-YP-ETC-DKWL-2451-KWL157 | D BLOCK GALI NO 2 DAYAL PUR | TG-KWL157A-1 | 19504362 | 990 | 320 | 241 | 0.97 | 972 | 292 | 1180 | 341 | 1386 | 339 | 1374 | 200 | 2019-06-28 23:00 | 224.5 | 85.4 | 1543 | B | 92 | 100 | 108 | 16 |  |  | 9 | 91 |  |  |  |  | 2 |  |  |  | 693.23 | 636.5 | 580.09 | 647.59 | 20.05 | 76.08 | 128.14 | 67.29 |  | 2.3 | 7.05 |  | 715.28 | 4.32 | 0.65 | 0.98
155 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL157 | 1S-DL-YP-ETC-DKWL-2451-KWL157 | D BLOCK GALI NO 2 DAYAL PUR | TG-KWL157A-2 | 19505019 | 630 | 200 | 233 | 0.97 | 639 | 191 | 819 | 214 | 917 | 235 | 1004 | 160 | 2019-06-11 23:00 | 138.5 | 31.3 | 1004 | B | 88 | 107 | 105 | 19 |  | 0.1 | 11.6 | 88.3 | 1.3 |  |  |  | 273.25 | 135.53 | 135.53 | 182.56 | 426.18 | 498.34 | 474.17 | 486.06 | 10.02 | 76.06 | 62.39 | 42.01 |  | 0.42 | 1.32 | 0.12 | 711.15 | 8.45 | 0.51 | 1.01
156 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL158 | 1S-DL-YP-ETC-DKWL-2451-KWL158 | D-3 NEHRU VIHAR : ID | TG-KWL158A-1 | 19500584 | 990 | 320 | 248 | 0.96 | 874 | 250 | 1056 | 339 | 1438 | 285 | 1192 | 336 | 2019-06-10 23:00 | 227.4 | 111.1 | 1445 | Y | 87 | 113 | 100 | 26 |  |  | 26 | 74 |  |  |  |  | 4 |  |  |  | 713.3 | 510.55 | 672.5 | 668.4 | 0.3 | 199.14 | 44.1 | 49.2 |  | 7.51 |  |  | 718 | 2 | 0.74 | 0.88
157 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL158 | 1S-DL-YP-ETC-DKWL-2451-KWL158 | D-3 NEHRU VIHAR : ID | TG-KWL158A-2 | 19505769 | 990 | 320 | 256 | 0.96 | 813 | 335 | 1490 | 199 | 881 | 279 | 1248 | 531 | 2019-06-28 23:00 | 288.6 | 78.7 | 1490 | R | 131 | 71 | 98 | 60 |  |  | 6.6 | 93.4 |  |  |  |  | 0.3 | 485.47 | 485.47 | 34 | 571.46 | 223.29 | 665.46 | 674.46 | 133 |  | 1 | 0.3 | 4 |  |  |  | 709.16 | 10.44 | 0.64 | 0.82
158 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL160 | 1S-DL-YP-ETC-DKWL-2451-KWL160 | C-1 NEHRU VIHAR : ID | TG-KWL160A-1 | 19504970 | 990 | 320 | 244 | 0.96 | 684 | 215 | 907 | 229 | 966 | 241 | 1021 | 99 | 2019-06-30 | 162.7 | 68.4 | 1086 | B | 94 | 101 | 105 | 11 |  |  | 2.8 | 97.2 |  |  |  |  | 219.3 | 94 | 94 | 100 | 499.41 | 625.11 | 667.41 | 619.11 | [8 empty] | 719.11 | 0.49 | 0.69 | 0.69
159 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL160 | 1S-DL-YP-ETC-DKWL-2451-KWL160 | C-1 NEHRU VIHAR : ID | TG-KWL160A-2 | 19505368 | 630 | 120 | 251 | 0.96 | 573 | 212 | 873 | 195 | 796 | 166 | 679 | 169 | 2019-06-28 14:30 | 198.6 | 54.5 | 873 | R | 108 | 101 | 91 | 17 | 0.1 | 0.1 | 5.4 | 94.5 |  |  |  |  | 5.3 | 9 | 9 | 12.3 | 685.11 | 694.41 | 627.11 | 691.11 | 13 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 704.11 | 15.49 | 0.61 | 0.91
160 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL234 | 1S-DL-YP-ETC-DKWL-2451-KWL234 | B BLK SHRI RAM COLONY :PL | TG-KWL234A-1 | 19506536 | 990 | 320 | 244 | 0.97 | 1156 | 424 | 1808 | 445 | 1885 | 287 | 1202 | 648 | 2019-06-30 01:30 | 400.3 | 77.8 | 1891 | Y | 103 | 119 | 78 | 41 | 0.1 | 1.5 | 52 | 46.4 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | 665.5 | 452.23 | 681.12 | 666.2 | 42.24 | 237.05 | 0.43 | 42.22 | 1.11 | 19.57 |  | 0.43 | 709.55 | 10.05 | 0.56 | 1.17
161 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL235 | 1S-DL-YP-ETC-DKWL-2451-KWL235 | A BLK SHRI RAM CLY NEAR GALI 26:PL | TG-KWL235A-1 | 19505324 | 630 | 200 | 243 | 0.96 | 755 | 277 | 1189 | 210 | 887 | 268 | 1146 | 283 | 2019-06-30 01:30 | 286.6 | 58.6 | 1189 | R | 102 | 84 | 114 | 30 |  | 0.6 | 27.4 | 72.1 |  |  |  |  | 4.3 | 20.18 | 20.18 |  | 691.13 | 686.06 | 597.38 | 701.04 | 11.11 | 1.28 | 108.16 | 5.5 | 1.01 | 0.03 | 2.01 | 1.01 | 707.55 | 12.05 | 0.5 | 1.2
162 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL236 | 1S-DL-YP-ETC-DKWL-2451-KWL236 | MILAN GARDEN:PLM | TG-KWL236A-1 | 19504268 | 630 | 200 | 238 | 0.96 | 460 | 173 | 774 | 146 | 650 | 141 | 621 | 141 | 2019-06-29 23:30 | 153.2 | 12.9 | 774 | R | 119 | 89 | 92 | 30 |  | 3.2 | 64.1 | 32.7 | 0.3 | 0.3 | 0.3 | 0.3 | 4.47 | 143.52 | 143.52 | 29.11 | 695.12 | 557.55 | 583.44 | 672.36 | 1.48 | [7 empty] | 702.17 | 17.43 | 0.68 | 0.73
163 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL240 | 1S-DL-YP-ETC-DKWL-2451-KWL240 | MAMTA COOKER FACTORY TUKMEERPUR:PM | TG-KWL240A-1 | 19504915 | 100 | 40 | 247 | 0.9 | 44 | 15 | 59 | 18 | 73 | 12 | 47 | 23 | 2019-06-15 15:30 | 13.9 | -18.8 | 73 | Y | 96 | 120 | 84 | 36 | 0 |  | 4.4 | 95.6 | 445.47 | 359.23 | 500.3 | 446.5 | 255.21 | 322.3 | 322.3 | 260.18 | 11.3 | 30.45 |  | 5.3 | [8 empty] | 712.38 | 7.22 | 0.4 | 0.44
164 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL244 | 1S-DL-YP-ETC-DKWL-2451-KWL244 | E BLOCK DAYAL PUR 33 FEETA ROAD:PL | TG-KWL244A-1 | 19504401 | 990 | 320 | 242 | 0.96 | 687 | 230 | 937 | 250 | 1011 | 206 | 837 | 151 | 2019-06-12 | 160.4 | 55.9 | 1058 | Y | 103 | 111 | 85 | 26 |  |  | 3.6 | 96.4 |  |  | 5 |  | 343.14 | 260.35 | 260.35 | 375.03 | 372.43 | 455.22 | 203.32 | 340.54 | [8 empty] | 715.57 | 4.03 | 0.6 | 0.69
165 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL248 | 1S-DL-YP-ETC-DKWL-2451-KWL248 | AMBEY COLONY SONIA VIHAR:PM | TG-KWL248A-1 | 19506388 | 400 | 120 | 238 | 0.96 | 262 | 106 | 456 | 73 | 308 | 83 | 354 | 131 | 2019-06-09 02:00 | 107.4 | 13 | 456 | R | 130 | 79 | 91 | 51 | 0.4 | 0.1 | 25.2 | 74.2 |  | 32.05 | 15.29 | 3.28 | 225.08 | 654.07 | 654.07 | 621.42 | 463.34 | 2.3 | 27.31 | 63.32 | [8 empty] | 688.42 | 31.18 | 0.51 | 0.66
166 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL249 | 1S-DL-YP-ETC-DKWL-2451-KWL249 | A BLOCK SHRI RAM CLY. NEAR SERVICE RD:PL | TG-KWL249A-1 | 19506533 | 630 | 200 | 243 | 0.97 | 739 | 207 | 870 | 304 | 1307 | 228 | 964 | 398 | 2019-06-30 | 238.4 | 49.8 | 1307 | Y | 78 | 137 | 85 | 59 | 0.1 | 0.2 | 26.2 | 73.6 |  |  |  |  | 17 |  |  |  | 698.54 | 122.11 | 706.24 | 676.5 | 0.56 | 407.09 | 0.27 | 39.31 |  | 187.3 | 0.29 | 0.29 | 716.5 | 3.1 | 0.57 | 1.17
167 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL250 | 1S-DL-YP-ETC-DKWL-2451-KWL250 | A BLOCK POCKET 6 SONIA VIHAR:PM | TG-KWL250A-1 | 19506041 | 400 | 120 | 246 | 0.95 | 61 | 24 | 95 | 21 | 82 | 17 | 69 | 23 | 2019-06-04 21:30 | 25.3 | 3.7 | 156 | Y | 103 | 137 | 60 | 77 | 46.9 | 0.1 | 24.3 | 28.6 | 691.24 | 690.05 | 691.24 | 691.24 |  | 1.19 | 1.19 | [13 empty] | 691.24 | 28.36 | 0.54 | 0.15
168 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL251 | 1S-DL-YP-ETC-DKWL-2451-KWL251 | A BLK KHAJOORI:PL | TG-KWL251A-1 | 19505294 | 630 | 200 | 246 | 0.97 | 747 | 227 | 923 | 284 | 1159 | 236 | 968 | 217 | 2019-06-01 05:00 | 226.6 | 40.2 | 1159 | Y | 94 | 108 | 98 | 14 |  | 0.1 | 5 | 94.9 |  |  |  |  | 43 | 12.3 | 12.3 | 18 | 654.55 | 634.58 | 663.55 | 678.55 | 0.3 | 50.57 | 1 | 1.3 | 0.3 | 0.3 | 0.3 | 0.3 | 698.55 | 21.05 | 0.46 | 1.19
169 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL255 | 1S-DL-YP-ETC-DKWL-2451-KWL255 | GAS GODAM E-2 SONIA VIHAR:PM | TG-KWL255A-1 | 19504328 | 400 | 120 | 238 | 0.96 | 107 | 24 | 105 | 35 | 157 | 48 | 215 | 95 | 2019-06-30 00:30 | 32.3 | 6.6 | 215 | B | 70 | 121 | 109 | 51 | 0.1 | 3.8 | 89.7 | 6.4 | 691.49 | 171.28 | 370.04 | 536.24 | 8.53 | 529.14 | 529.14 | 164.18 | [12 empty] | 700.42 | 19.18 | 0.68 | 0.27
170 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL286 | 1S-DL-YP-ETC-DKWL-2451-KWL286 | CRPF CAMP SONIA VIHAR:PM | TG-KWL286A-1 | 19504269 | 400 | 120 | 253 | 0.96 | 245 | 69 | 274 | 86 | 343 | 90 | 357 | 77 | 2019-06-03 11:00 | 70.4 | 16 | 370 | B | 95 | 112 | 93 | 19 |  |  | 2 | 98 | 19.52 | 6.3 | 8.3 | 5 | 404.21 | 208.44 | 208.44 | 401.17 | 290.48 | 499.47 | 241 | 308.44 | [8 empty] | 715.01 | 4.59 | 0.64 | 0.61
171 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL292 | 1S-DL-YP-ETC-DKWL-2451-KWL292 | E BLOCK CHAND BAGH:PL | TG-KWL292A-1 | 19506537 | 630 | 200 | 238 | 0.96 | 810 | 242 | 1030 | 280 | 1194 | 289 | 1244 | 194 | 2019-06-30 01:30 | 291.2 | 85 | 1298 | B | 87 | 108 | 105 | 21 | 0.2 | 0.6 | 57.5 | 41.7 | [8 empty] | 521.56 | 215.49 | 244.45 | 320.45 | 169.44 | 291.07 | 336.41 | 293.3 | 8.59 | 193.43 | 119.13 | 86.24 | 700.39 | 19.21 | 0.65 | 1.29
172 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL294 | 1S-DL-YP-ETC-DKWL-2451-KWL294 | C 1 KHAJOORI NEAR GALI NO 21:ID | TG-KWL294A-1 | 19502304 | 990 | 320 | 241 | 0.97 | 551 | 185 | 811 | 214 | 935 | 152 | 655 | 243 | 2019-06-29 23:30 | 113.3 | 35.3 | 966 | Y | 93 | 115 | 92 | 23 |  |  | 65.7 | 34.3 | 12 | 2 | 32.3 | 8 | 567.19 | 412.55 | 412.55 | 512.53 | 139.16 | 303.4 | 159.16 | 197.42 | [8 empty] | 718.35 | 1.25 | 0.63 | 0.56
173 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL294 | 1S-DL-YP-ETC-DKWL-2451-KWL294 | C 1 KHAJOORI NEAR GALI NO 21:ID | TG-KWL294A-2 | 19506306 | 630 | 200 | 248 | 0.97 | 342 | 132 | 563 | 132 | 570 | 77 | 328 | 238 | 2019-06-29 23:00 | 111.6 | 27.2 | 570 | Y | 125 | 100 | 75 | 50 | 0.1 |  | 2.1 | 97.8 | 2 | 9.3 | 40.58 | 2 | 252.53 | 532.13 | 532.13 | 570.15 | 458.17 | 171.27 | 1.29 | 140.55 | [8 empty] | 713.1 | 6.5 | 0.64 | 0.54
174 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL295 | 1S-DL-YP-ETC-DKWL-2451-KWL295 | K BLK SADAT PUR EXT. GALI NO. 51:ID | TG-KWL295A-1 | 19500647 | 990 | 320 | 236 | 0.96 | 876 | 265 | 1156 | 302 | 1322 | 308 | 1366 | 192 | 2019-06-09 23:00 | 211.2 | 79.5 | 1435 | B | 91 | 102 | 108 | 17 | 27 | 33.8 | 25 | 14.1 |  |  |  |  | 41.3 | 11.3 | 11.3 | 12.3 | 668.27 | 663.07 | 627.5 | 671.07 | 9.12 | 44.32 | 81.19 | 35.32 |  |  |  |  | 719.09 | 0.51 | 0.67 | 0.88
175 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL297 | 1S-DL-YP-ETC-DKWL-2451-KWL297 | B BLK SHRI RAM COLONY SAITAN CHOWK:PL | TG-KWL297A-1 | 19506034 | 990 | 320 | 244 | 0.97 | 1222 | 493 | 2032 | 393 | 1595 | 337 | 1358 | 592 | 2019-06-15 07:30 | 443.5 | 93.4 | 2032 | R | 119 | 102 | 78 | 41 | 0.3 | 14 | 31.2 | 54.5 | [8 empty] | 107.29 | 398 | 696.14 | 423.33 | 420.27 | 268.14 | 5.48 | 270.06 | 175.35 | 37.17 | 0.29 | 9.52 | 703.31 | 16.29 | 0.63 | 1.23
176 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL298 | 1S-DL-YP-ETC-DKWL-2451-KWL298 | Delhi Police Training Center:PM | TG-KWL298A-1 | 19506396 | 400 | 120 | 251 | 0.98 | 460 | 162 | 623 | 151 | 576 | 147 | 567 | 53 | 2019-06-18 04:00 | 121.9 | 9.7 | 763 | B | 101 | 110 | 89 | 21 | 0.1 | 0.1 | 3.7 | 96.2 | 1.08 |  |  |  | 2 | 3.38 | 3.38 | 4.38 | 524.21 | 410.1 | 602.35 | 531.51 | 160 | 243.41 | 34 | 153 | 5 | 35 | 1 | 3 | 692.29 | 27.31 | 0.59 | 1.15
177 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL300 | 1S-DL-YP-ETC-DKWL-2451-KWL300 | MAIN ROAD BANK OF BARODA:PM | TG-KWL300A-1 | 19504417 | 400 | 120 | 249 | 0.98 | 172 | 72 | 292 | 38 | 153 | 62 | 252 | 124 | 2019-06-03 15:00 | 43.1 | 0.8 | 313 | R | 122 | 68 | 111 | 54 |  |  | 28.1 | 71.9 | 344 | 416.58 | 347.3 | 349.3 | 165.59 | 302.28 | 302.28 | 361.28 | 209.27 |  | 67.58 | 8.28 | [8 empty] | 719.26 | 0.34 | 0.48 | 0.43
178 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL301 | 1S-DL-YP-ETC-DKWL-2451-KWL301 | BADARPUR KHADAR VILLAGE:O/D | TG-KWL301A-1 | 19506509 | 400 | 120 | 240 | 0.95 | 132 | 64 | 269 | 33 | 139 | 35 | 147 | 126 | 2019-06-09 02:00 | 48.4 | 7 | 269 | R | 149 | 71 | 81 | 78 |  | 0.2 | 45.2 | 54.6 | 274.39 | 688.45 | 676.22 | 673.28 | 408.49 | 0.3 | 0.3 | 15.47 | 5.47 | [11 empty] | 689.15 | 30.45 | 0.47 | 0.33
179 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL327 | 1S-DL-YP-ETC-DKWL-2451-KWL327 | PWD TR. MAIN WAZIRABAD RD (STLT):PM | TG-KWL327A-1 | 19506392 | 100 | 40 | 248 | 0.98 | 15 | 5 | 19 | 5 | 21 | 5 | 19 | 2 | 2019-06-08 04:00 | 4.1 | -0.8 | 23 | Y | 98 | 101 | 101 | 3 |  |  | 4.7 | 95.3 | 698.4 | 698.4 | 698.4 | 698.4 | [16 empty] | 698.4 | 21.2 | 0.56 | 0.15
180 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL338 | 1S-DL-YP-ETC-DKWL-2451-KWL338 | KAUSHAL PURI, CHAUHAN PATTI Nr SCHOOL:PM | TG-KWL338A-1 | 19506389 | 100 | 40 | 240 | 0.97 | 46 | 19 | 77 | 17 | 72 | 9 | 38 | 36 | 2019-06-02 05:30 | 18 | 2.6 | 77 | R | 124 | 111 | 66 | 58 |  | 0.1 | 37.1 | 62.9 | 131 | 189.43 | 648.47 | 286.34 | 551.04 | 494.25 | 494.25 | 401.24 | 6.41 | 4.37 |  | 0.47 | [8 empty] | 688.45 | 31.15 | 0.46 | 0.46
181 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL341 | 1S-DL-YP-ETC-DKWL-2451-KWL341 | SABHAPUR VILLAGE DISPENSARY :PL | TG-KWL341A-1 | 19505903 | 990 | 320 | 253 | 0.97 | 755 | 267 | 1077 | 239 | 959 | 249 | 1016 | 102 | 2019-06-29 23:00 | 209.6 | 19.5 | 1290 | B | 91 | 105 | 104 | 14 | 0.1 | 2.5 | 35.4 | 62 | 8.32 | 3.55 | 2.55 | 2.55 | 329.23 | 251.04 | 251.04 | 266.19 | 345.24 | 412.2 | 418.24 | 416.05 | 2 | 18 | 16.29 | [5 empty] | 685.19 | 34.41 | 0.59 | 0.76
182 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL342 | 1S-DL-YP-ETC-DKWL-2451-KWL342 | BIHARI PUR VILLAGE EXTN.NO-2 NALA WALA | TG-KWL342A-1 | 19506302 | 630 | 200 | 239 | 0.97 | 550 | 231 | 1033 | 185 | 836 | 134 | 604 | 372 | 2019-06-30 14:30 | 175.6 | 18.4 | 1033 | R | 124 | 105 | 71 | 53 | 6.4 | 2.2 | 25.4 | 66 |  |  | 2 |  | 9.3 | 62.45 | 62.45 | 75.15 | 597.43 | 629.28 | 240.07 | 618.58 | 84.3 | 2.3 |  | 0.3 | 3 |  |  |  | 694.43 | 25.17 | 0.59 | 0.87
183 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL345 | 1S-DL-YP-ETC-DKWL-2451-KWL345 | DJB,W-I Rainywell near Yamuna Raw WTP | TG-KWL345A-1 | 19506029 | 400 | 120 | 248 | 0.98 | 125 | 40 | 161 | 42 | 166 | 43 | 171 | 9 | 2019-06-24 17:00 | 38.9 | -0.4 | 174 | B | 100 | 59 | 141 | 82 |  | 0.1 | 21.1 | 78.9 | 701.3 | 701.3 | 701.3 | 701.3 | 1.3 | 1.3 | 1.3 | 1.3 | [12 empty] | 703 | 17 | 0.03 | 0.31