## Loading Condition > 80%
MIS Report of Distribution Transformer - Jun19
Jun19 1251 KARAWAL NAGAR (Loading Condition > 80% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL001 | 1S-DL-YP-ETC-DKWL-2451-KWL001 | RAJEEV GANDHI NAGAR GALI NO.-3:ID | TG-KWL001A-1 | 19506907 | 630 | 200 | 251 | 0.96 | 664 | 206 | 824 | 234 | 963 | 224 | 916 | 122 | 2019-06-10 21:30 | 259.4 | 62 | 963 | Y | 85 | 108 | 106 | 23 | 0.1 | 1.9 | 69.3 | 28.7 |  |  |  |  | 16 | 3.3 | 3.3 | 3 | 672.33 | 626.09 | 645.31 | 674.13 | 6.02 | 60.12 | 44.17 | 16.29 | 0.3 | 5.14 | 5.17 | 1.23 | 695.05 | 24.55 | 0.59 | 1.05
2 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL004 | 1S-DL-YP-ETC-DKWL-2451-KWL004 | RAJEEV GANDHI NAGAR GALI NO.-21:ID | TG-KWL004A-1 | 19504064 | 990 | 320 | 251 | 0.96 | 784 | 243 | 969 | 240 | 956 | 300 | 1208 | 245 | 2019-06-30 | 197.2 | 52.3 | 1209 | B | 96 | 92 | 113 | 21 |  |  | 5.1 | 94.9 |  |  |  |  | 16 | 21 | 21 | 9.3 | 702.43 | 697.43 | 678.53 | 709.13 |  |  | 38.5 | [5 empty] | 718.43 | 1.17 | 0.75 | 0.79
3 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL005 | 1S-DL-YP-ETC-DKWL-2451-KWL005 | D BLOCK BHAGRATHI VIHAR:PL | TG-KWL005A-1 | 19500546 | 630 | 200 | 237 | 0.96 | 545 | 154 | 628 | 203 | 823 | 188 | 768 | 174 | 2019-06-02 08:00 | 144.4 | 53.4 | 844 | Y | 84 | 113 | 103 | 29 |  |  | 16.6 | 83.4 |  |  |  |  | 52 |  |  |  | 665.25 | 645.48 | 699.39 | 712.29 |  | 71.37 | 17.16 | 4.56 |  |  |  |  | 717.25 | 2.35 | 0.71 | 0.87
4 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL014 | 1S-DL-YP-ETC-DKWL-2451-KWL014 | D BL BRIJPURI GALI NO. 10:ID | TG-KWL014A-1 | 19500566 | 630 | 200 | 252 | 0.96 | 529 | 211 | 852 | 188 | 738 | 131 | 525 | 288 | 2019-06-29 23:00 | 127.9 | 56.1 | 887 | R | 113 | 115 | 71 | 44 | 4.6 | 95.4 | 0 | [5 empty] | 1.3 |  |  | 25.05 | 667.21 | 674.06 | 263.27 | 688.46 | 48 | 44.15 | 1 | 4.3 | 1.3 |  |  |  | 718.21 | 1.39 | 0.64 | 0.84
5 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL019 | 1S-DL-YP-ETC-DKWL-2451-KWL019 | A BLK G N 2 BHAGIRATHI VIHAR NO-II :ID | TG-KWL019A-2 | 19505765 | 630 | 200 | 245 | 0.96 | 558 | 184 | 738 | 228 | 925 | 146 | 580 | 299 | 2019-06-29 23:30 | 193 | 55.8 | 1096 | Y | 97 | 123 | 79 | 44 | 0.1 | 4.8 | 93.3 | 1.7 |  |  |  |  | 6 | 0.3 | 0.3 | 1.3 | 678.53 | 463.37 | 646.38 | 686.09 | 30.16 | 232.02 |  | 27.3 |  | 19 |  |  | 715.09 | 4.51 | 0.7 | 0.89
6 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL028 | 1S-DL-YP-ETC-DKWL-2451-KWL028 | B BLOCK BRIJ PURI:ID | TG-KWL028A-1 | 19505234 | 990 | 320 | 239 | 0.97 | 925 | 259 | 1110 | 279 | 1194 | 388 | 1688 | 541 | 2019-06-10 01:00 | 317.4 | 71.7 | 1688 | B | 93 | 97 | 111 | 18 | 0.3 | 0.1 | 0.6 | 99 |  |  |  |  | 33 | 30.3 | 30.3 | 17.3 | 645.3 | 621.42 | 559.49 | 624.12 | 24 | 50.18 | 131.41 | 60.48 |  |  | 5.3 |  | 702.3 | 17.3 | 0.67 | 0.93
7 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL044 | 1S-DL-YP-ETC-DKWL-2451-KWL044 | GALI NO.3 OLD MUSTAFABAD:ID | TG-KWL044A-1 | 19502319 | 990 | 320 | 239 | 0.98 | 866 | 334 | 1409 | 240 | 1006 | 292 | 1221 | 349 | 2019-06-02 07:00 | 159 | 58.1 | 1409 | R | 111 | 90 | 99 | 21 | 13.8 | 0.1 | 21.7 | 64.5 |  |  |  |  | 2 | 17.53 | 17.53 | 1 | 571.24 | 690.01 | 691.27 | 697.37 | 135.03 | 1 | 13.27 | 10.17 | 0.27 |  |  |  | 708.54 | 11.06 | 0.72 | 0.88
8 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL044 | 1S-DL-YP-ETC-DKWL-2451-KWL044 | GALI NO.3 OLD MUSTAFABAD:ID | TG-KWL044A-2 | 19501040 | 400 | 120 | 245 | 0.97 | 373 | 136 | 566 | 119 | 496 | 117 | 481 | 79 | 2019-06-29 23:30 | 93.6 | 40.8 | 627 | R | 119 | 93 | 88 | 31 |  | 0.1 | 7.7 | 92.3 | [8 empty] | 248.1 | 682.46 | 686.22 | 607.41 | 434.22 | 26.06 | 15.3 | 101.11 | 26.2 |  |  |  | 708.52 | 11.08 | 0.75 | 0.93
9 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL048 | 1S-DL-YP-ETC-DKWL-2451-KWL048 | A BLOCK GOKUL PURI:ID | TG-KWL048A-1 | 19505927 | 990 | 320 | 240 | 0.97 | 679 | 298 | 1233 | 152 | 624 | 229 | 956 | 528 | 2019-06-28 23:00 | 228.5 | 73.3 | 1368 | R | 125 | 78 | 98 | 47 | 0.1 | 0.3 | 36 | 63.7 |  |  |  |  | 0.3 | 401.37 | 401.37 | 39 | 636.15 | 301.1 | 665.17 | 663.47 | 66.02 | [7 empty] | 702.47 | 17.13 | 0.74 | 0.69
10 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL052 | 1S-DL-YP-ETC-DKWL-2451-KWL052 | B BLOCK GOKUL PURI:PL | TG-KWL052A-1 | 19503799 | 630 | 200 | 240 | 0.96 | 538 | 214 | 942 | 139 | 598 | 185 | 804 | 299 | 2019-06-02 23:00 | 131.1 | 63.5 | 969 | R | 116 | 77 | 107 | 39 |  | 3.2 | 83.5 | 13.3 | [5 empty] | 206.41 | 206.41 | 5 | 603.06 | 512.45 | 652.36 | 695.06 | 113.3 |  | 65.2 | 19.2 | 2.5 |  |  |  | 719.26 | 0.34 | 0.69 | 0.85
11 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL053 | 1S-DL-YP-ETC-DKWL-2451-KWL053 | JAWHAR NAGAR NO.-1:PL | TG-KWL053A-2 | 19504953 | 990 | 320 | 239 | 0.99 | 1037 | 346 | 1461 | 338 | 1428 | 354 | 1488 | 52 | 2019-06-24 12:00 | 197.2 | -69.9 | 1488 | B | 99 | 98 | 103 | 5 | 0.3 | 0.1 | 35.6 | 64 | 145.3 | 143.01 | 111.03 | 129.01 | 230.25 | 224.54 | 224.54 | 242.24 | 214.48 | 236.18 | 199.47 | 214.18 | 121.11 | 111.41 | 141.11 | 128.41 | 4.3 | 0.3 | 9 | 2 | 716.24 | 3.36 | 0.44 | 1.05
12 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL101 | 1S-DL-YP-ETC-DKWL-2451-KWL101 | MANSINGH NAGAR GALI NO. 16:ID | TG-KWL101A-1 | 19503017 | 630 | 200 | 249 | 0.96 | 500 | 159 | 644 | 132 | 532 | 209 | 844 | 274 | 2019-06-29 23:00 | 136.2 | 47.4 | 844 | B | 99 | 84 | 118 | 34 |  | 0.5 | 44.9 | 54.6 |  |  |  |  | 24.1 | 81.09 | 81.09 | 17.3 | 687.47 | 630.48 | 630.44 | 694.27 |  |  | 80.43 | [5 empty] | 711.57 | 8.03 | 0.72 | 0.79
13 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL102 | 1S-DL-YP-ETC-DKWL-2451-KWL102 | AKBARI MASZID:ID | TG-KWL102A-2 | 19504910 | 630 | 120 | 238 | 0.97 | 462 | 133 | 565 | 193 | 828 | 136 | 582 | 255 | 2019-06-29 23:00 | 110.7 | 47.5 | 828 | Y | 92 | 123 | 85 | 38 |  |  | 83.5 | 16.5 |  |  |  |  | 52.51 | 0.3 | 0.3 | 22.51 | 665.41 | 687.4 | 572.41 | 695.41 |  | 30.22 | [6 empty] | 718.32 | 1.28 | 0.72 | 0.73
14 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL102 | 1S-DL-YP-ETC-DKWL-2451-KWL102 | AKBARI MASZID:ID | TG-KWL102A-1 | 19504531 | 630 | 200 | 237 | 0.97 | 452 | 217 | 933 | 113 | 474 | 122 | 520 | 438 | 2019-06-29 23:30 | 106.3 | 43.7 | 953 | R | 140 | 78 | 83 | 62 | 2.1 | 39.3 | 58.6 | [5 empty] | 1.3 | 395.06 | 395.06 | 58.04 | 549.01 | 321.54 | 446.58 | 658.56 | 163.59 |  |  |  | 2.3 |  |  |  | 717 | 3 | 0.71 | 0.72
15 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL162 | 1S-DL-YP-ETC-DKWL-2451-KWL162 | JAIN COMPLEX JOHIRIPUR:PM | TG-KWL162A-1 | 19506636 | 100 | 40 | 237 | 0.96 | 87 | 33 | 135 | 26 | 105 | 28 | 111 | 28 | 2019-06-12 03:30 | 33.4 | 5.8 | 171 | R | 127 | 75 | 97 | 52 | 0.1 | 7 | 54 | 39 |  | 1.23 |  |  | 31.11 | 377.46 | 377.46 | 74.07 | 489.54 | 305.42 | 573.05 | 609.44 | 137.46 |  | 2.36 | 1 | 26 |  |  |  | 684.51 | 35.09 | 0.6 | 0.87
16 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL237 | 1S-DL-YP-ETC-DKWL-2451-KWL237 | SHANI BAZAR ROAD JOHRI PUR :PM | TG-KWL237A-1 | 19505924 | 630 | 200 | 237 | 0.98 | 905 | 289 | 1325 | 292 | 1356 | 324 | 1488 | 150 | 2019-06-29 12:00 | 253.4 | -74.2 | 1488 | B | 91 | 93 | 117 | 26 |  |  | 2.1 | 97.9 | 37.3 | 31 | 6.3 | 20.3 | 197.15 | 178.45 | 178.45 | 133.44 | 435.59 | 461.29 | 475.54 | 478.31 | 36.28 | 35.28 | 145.2 | 73.27 | 0.25 | 0.55 | 19.53 | 1.25 | 707.37 | 12.23 | 0.38 | 1.44
17 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL243 | 1S-DL-YP-ETC-DKWL-2451-KWL243 | G & H BLK MUSTAFABAD GALI NO. 18:ID | TG-KWL243A-2 | 19505215 | 990 | 320 | 236 | 0.97 | 889 | 280 | 1209 | 249 | 1075 | 361 | 1569 | 442 | 2019-06-02 06:00 | 319.7 | 66.6 | 1570 | B | 98 | 77 | 125 | 48 |  | 0.2 | 6.6 | 93.2 |  |  |  |  | 14 | 316.48 | 316.48 | 19.3 | 693.07 | 391.48 | 654.5 | 686.45 | 1.29 |  | 51.25 | 2.21 |  |  | 2.21 |  | 708.36 | 11.24 | 0.6 | 0.9
18 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL243 | 1S-DL-YP-ETC-DKWL-2451-KWL243 | G & H BLK MUSTAFABAD GALI NO. 18:ID | TG-KWL243A-1 | 19505960 | 990 | 320 | 241 | 0.97 | 1101 | 392 | 1669 | 396 | 1692 | 314 | 1323 | 359 | 2019-06-02 05:30 | 397.8 | 75.5 | 1717 | Y | 112 | 107 | 81 | 31 | 0.3 | 1 | 44.9 | 53.8 | [8 empty] | 323.03 | 429.45 | 701.13 | 547.38 | 358.14 | 252.07 | 3.56 | 159.05 | 27.22 | 26.47 |  | 1.56 | 708.39 | 11.21 | 0.65 | 1.11
19 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL246 | 1S-DL-YP-ETC-DKWL-2451-KWL246 | C BLOCK BRIJ PURI:ID | TG-KWL246A-1 | 19505514 | 990 | 320 | 237 | 0.96 | 985 | 326 | 1578 | 344 | 1617 | 315 | 1491 | 111 | 2019-06-03 14:00 | 386.2 | 109.8 | 1617 | Y | 101 | 105 | 94 | 11 | 0.3 | 0.4 | 42.6 | 56.8 |  |  |  |  | 1 | 0.3 | 0.3 | 0.3 | 592.54 | 536.54 | 671.24 | 598.24 | 109.19 | 144.49 | 28.49 | 104.19 |  | 21 |  |  | 703.13 | 16.47 | 0.68 | 0.99
20 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL331 | 1S-DL-YP-ETC-DKWL-2451-KWL331 | GALI NO.5 JAWAHAR NAGAR P/M | TG-KWL331A-1 | 19504775 | 990 | 320 | 247 | 0.99 | 935 | 310 | 1350 | 309 | 1332 | 315 | 1363 | 27 | 2019-06-22 16:00 | 114.1 | -116.3 | 1363 | B | 103 | 99 | 98 | 5 |  |  | 47.1 | 52.9 | 10.51 | 12.21 | 43.21 | 16.21 | 324.06 | 335.4 | 335.4 | 330.52 | 310.43 | 322.25 | 299.19 | 310.27 | 61.47 | 37.01 | 51 | 49.47 |  |  |  |  | 707.27 | 12.33 | 0.5 | 0.94
21 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL349 | 1S-DL-YP-ETC-DKWL-2451-KWL349 | G BLK GANGA VIHAR(SHAMSHAAN GHAT) | TG-KWL349A-1 | 19506686 | 630 | 200 | 245 | 0.97 | 566 | 191 | 795 | 181 | 750 | 194 | 803 | 50 | 2019-06-11 23:00 | 176.8 | 35.6 | 862 | R | 106 | 90 | 104 | 16 |  | 0.1 | 1.7 | 98.2 |  |  |  |  | 43.3 | 161.3 | 161.3 | 54 | 602.23 | 537.13 | 628.23 | 620.23 | 58.5 | 6 | 40.2 | 30.2 |  |  |  |  | 704.43 | 15.17 | 0.62 | 0.9
22 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL010 | 1S-DL-YP-ETC-DKWL-2451-KWL010 | MUKUND VIHAR "A" BLK:ID | TG-KWL010A-1 | 19500537 | 630 | 200 | 231 | 0.98 | 598 | 194 | 868 | 207 | 923 | 198 | 884 | 49 | 2019-06-12 17:00 | 130.6 | 18.4 | 949 | B | 95 | 98 | 107 | 12 |  | 0.5 | 26.7 | 72.8 |  |  |  |  | 62.18 | 21.59 | 21.59 | 19.29 | 593.38 | 630.33 | 595.18 | 630.26 | 48.5 | 52.14 | 95.58 | 54.51 |  |  |  |  | 704.46 | 15.14 | 0.65 | 0.95
23 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL013 | 1S-DL-YP-ETC-DKWL-2451-KWL013 | C BLK MUKUND VIHAR GALI NO. 9:ID | TG-KWL013A-1 | 19505641 | 1600 | 500 | 244 | 0.97 | 1944 | 665 | 2676 | 591 | 2390 | 689 | 2810 | 371 | 2019-06-02 05:30 | 761 | 102.5 | 2810 | B | 104 | 96 | 100 | 8 | 0.1 |  | 12.6 | 87.3 |  |  |  |  | 54.36 | 126 | 126 | 81.3 | 527.59 | 488.25 | 469.25 | 512 | 109.59 | 84.52 | 124.17 | 104.17 | 6.54 | 0.11 | 3.11 | 1.41 | 699.28 | 20.32 | 0.48 | 1.22
24 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL033 | 1S-DL-YP-ETC-DKWL-2451-KWL033 | MAHALAXMI ENCLAVE:ID | TG-KWL033A-1 | 19506283 | 990 | 320 | 240 | 0.98 | 880 | 330 | 1431 | 272 | 1190 | 279 | 1219 | 227 | 2019-06-11 22:00 | 253.1 | 67.2 | 1431 | R | 111 | 92 | 97 | 19 | 0.1 | 0.1 | 10.2 | 89.6 | [5 empty] | 7 | 7 | 2 | 655.37 | 702.47 | 701.27 | 706.29 | 54.1 | 0.3 | 2 | 1.48 | 0.3 |  |  |  | 710.17 | 9.43 | 0.67 | 0.89
25 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL046 | 1S-DL-YP-ETC-DKWL-2451-KWL046 | C C KARAWAL NAGAR S/STN. NO. 2:I/D | TG-KWL046A-1 | 19500592 | 990 | 320 | 240 | 0.98 | 933 | 334 | 1431 | 304 | 1317 | 295 | 1269 | 143 | 2019-06-26 15:30 | 214.9 | -14 | 1446 | R | 108 | 96 | 96 | 12 | 0.1 | 0.2 | 40.4 | 59.3 | 11.23 | 27.25 | 32.35 | 16.23 | 332.05 | 373.43 | 373.43 | 372.16 | 284.37 | 301.41 | 297.26 | 301.21 | 83.14 | 9.3 | 12.51 | 22.19 | 1 |  |  |  | 712.19 | 7.41 | 0.47 | 0.94
26 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL058 | 1S-DL-YP-ETC-DKWL-2451-KWL058 | KARWAL NAGAR NO.-4:PL | TG-KWL058A-2 | 19503507 | 990 | 320 | 243 | 0.99 | 850 | 278 | 1180 | 272 | 1151 | 300 | 1277 | 114 | 2019-06-28 16:00 | 170.8 | -95.7 | 1354 | B | 95 | 97 | 108 | 13 |  |  | 1.8 | 98.2 | 146.36 | 129.27 | 53.08 | 96.08 | 245.34 | 262.12 | 262.12 | 290.33 | 315.29 | 314 | 284.54 | 309.01 | 3 | 5 | 52.21 | 14.57 |  |  |  |  | 710.39 | 9.21 | 0.49 | 0.86
27 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL100 | 1S-DL-YP-ETC-DKWL-2451-KWL100 | SAHID BHAGAT SINGH CLY GALI NO 16:ID | TG-KWL100A-1 | 19506759 | 630 | 200 | 235 | 0.97 | 616 | 194 | 840 | 187 | 811 | 236 | 1022 | 198 | 2019-06-02 07:00 | 227.6 | 62.4 | 1022 | B | 101 | 92 | 107 | 15 |  |  | 6.5 | 93.5 |  |  |  |  | 3.3 | 21.34 | 21.34 | 5 | 642.26 | 657.28 | 609.38 | 647.32 | 67.39 | 34.33 | 101.44 | 61.03 |  |  | 1.43 |  | 713.35 | 6.25 | 0.64 | 0.98
28 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL264 | 1S-DL-YP-ETC-DKWL-2451-KWL264 | WEST KAMAL VIHAR (HVDS) INDUT. AREA:PM | TG-KWL264A-1 | 19505888 | 400 | 120 | 235 | 0.97 | 393 | 148 | 669 | 112 | 508 | 134 | 605 | 140 | 2019-06-30 14:30 | 277.3 | -32.6 | 669 | R | 104 | 105 | 91 | 14 | 1.2 | 0.1 | 37.3 | 61.4 | 94.45 | 92.15 | 118.5 | 97.45 | 276.1 | 283.1 | 283.1 | 286.1 | 291.02 | 292.38 | 264.31 | 295.02 | 32.28 | 27.22 | 4.29 | 16.28 | 1 |  | 0.3 |  | 695.25 | 24.35 | 0.41 | 0.98
29 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | KARAWAL NAGAR | 1251 | KWL287 | 1S-DL-YP-ETC-DKWL-2451-KWL287 | BABU NAGAR 1 GALI NO. 5:ID | TG-KWL287A-1 | 19506284 | 630 | 200 | 235 | 0.97 | 575 | 181 | 795 | 200 | 878 | 194 | 849 | 73 | 2019-06-14 11:00 | 192.2 | 52.8 | 941 | Y | 93 | 107 | 99 | 14 | 0.1 | 0.7 | 27.3 | 72 |  |  |  |  | 11 | 3 | 3 | 2 | 685.54 | 648.39 | 693.03 | 693.33 | 1.18 | 45.33 | 3.39 | 2.39 |  | 1 |  |  | 698.12 | 21.48 | 0.67 | 0.91
30 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL016 | 1S-DL-YP-ETC-DKWL-2451-KWL016 | CHANDU NAGAR:ID | TG-KWL016A-2 | 19505302 | 400 | 120 | 250 | 0.97 | 422 | 143 | 580 | 131 | 538 | 148 | 615 | 67 | 2019-06-10 22:00 | 150.7 | 26 | 615 | B | 105 | 87 | 107 | 20 |  | 1.4 | 49.2 | 49.3 |  |  |  |  | 3.07 | 24.3 | 24.3 | 2.3 | 647.35 | 685.13 | 605.13 | 685.11 | 56.31 | 1.39 | 99.52 | 23.24 | 4.39 | 0.3 | 2.17 | 0.47 | 711.52 | 8.08 | 0.58 | 1.06
31 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL017 | 1S-DL-YP-ETC-DKWL-2451-KWL017 | E BLOCK KHAJOORI GALI NO. 3:ID | TG-KWL017A-2 | 19505644 | 990 | 320 | 240 | 0.97 | 892 | 305 | 1346 | 282 | 1226 | 304 | 1342 | 118 | 2019-06-30 23:00 | 273.9 | 81.3 | 1397 | B | 96 | 96 | 109 | 13 | 0.1 | 0.3 | 68.6 | 30.9 |  |  |  |  | 44.58 | 94.58 | 94.58 | 36.28 | 673.04 | 611.34 | 654.19 | 672.34 | 0.47 | 12.17 | 48.3 | 9.47 |  |  |  |  | 718.49 | 1.11 | 0.61 | 0.9
32 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL018 | 1S-DL-YP-ETC-DKWL-2451-KWL018 | F BLOCK KHAJOORI GALI NO. 11&13:ID | TG-KWL018A-2 | 19502248 | 630 | 200 | 240 | 0.97 | 544 | 155 | 677 | 224 | 988 | 166 | 724 | 290 | 2019-06-03 15:30 | 153.2 | 56.6 | 1006 | Y | 88 | 119 | 93 | 31 |  | 0.1 | 59.7 | 40.1 |  |  |  |  | 17.2 | 2.57 | 2.57 | 7.22 | 696.52 | 456.47 | 698.2 | 694.3 |  | 246.08 | 5.3 | 12.2 |  | 8.2 |  |  | 714.12 | 5.48 | 0.73 | 0.86
33 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL018 | 1S-DL-YP-ETC-DKWL-2451-KWL018 | F BLOCK KHAJOORI GALI NO. 11&13:ID | TG-KWL018A-1 | 19504694 | 990 | 320 | 247 | 0.97 | 973 | 319 | 1353 | 341 | 1463 | 313 | 1317 | 131 | 2019-06-02 22:30 | 218.6 | 100.1 | 1470 | Y | 100 | 104 | 96 | 8 | 0.1 | 1.6 | 81.3 | 16.9 | [8 empty] | 597.24 | 500.37 | 629.25 | 585.44 | 94.39 | 185.56 | 62.08 | 106.19 |  | 5.3 |  |  | 715.19 | 4.41 | 0.71 | 0.98
34 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL061 | 1S-DL-YP-ETC-DKWL-2451-KWL061 | FATMA NURSARY CHAND BAGH MRD WZB ROAD:PL | TG-KWL061A-1 | 19502590 | 990 | 320 | 245 | 0.97 | 875 | 299 | 1223 | 282 | 1151 | 294 | 1203 | 64 | 2019-06-30 23:30 | 200.9 | 84.6 | 1337 | R | 99 | 92 | 109 | 17 | 0 |  | 13.4 | 86.6 |  |  | 0.21 |  | 2.21 | 1.51 | 1.51 | 0.21 | 636.21 | 703.5 | 588.07 | 678.33 | 74.21 | 7.22 | 124.35 | 34.09 |  |  |  |  | 715.33 | 4.27 | 0.74 | 0.88
35 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL064 | 1S-DL-YP-ETC-DKWL-2451-KWL064 | SHERPUR CHOWK:PL | TG-KWL064A-2 | 19506395 | 630 | 200 | 246 | 0.97 | 624 | 200 | 841 | 223 | 946 | 201 | 852 | 100 | 2019-06-24 15:30 | 312 | -1.2 | 990 | Y | 88 | 109 | 102 | 21 | 0.1 |  | 36.9 | 63 | 41 |  |  |  | 303.36 | 199.15 | 199.15 | 261.36 | 315.43 | 403.19 | 419.52 | 371.13 | 41.49 | 87.15 | 68.4 | 69.19 |  | 12.19 |  |  | 702.08 | 17.52 | 0.52 | 0.99
36 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL069 | 1S-DL-YP-ETC-DKWL-2451-KWL069 | DAYAL PUR 1 TANKI MAIN ROAD DAYAL PUR:PL | TG-KWL069A-2 | 19506601 | 630 | 200 | 240 | 0.97 | 564 | 154 | 651 | 165 | 695 | 246 | 1089 | 418 | 2019-06-11 22:30 | 152.4 | 36.6 | 1089 | B | 102 | 92 | 106 | 14 | 0.6 | 2.1 | 55.8 | 41.6 |  |  |  |  | 13 | 19.49 | 19.49 | 9 | 673.45 | 680.26 | 648.16 | 691.15 | 15.3 | 1.3 | 39 | 2 |  | 0.3 | 1.3 |  | 702.15 | 17.45 | 0.66 | 0.9
37 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL076 | 1S-DL-YP-ETC-DKWL-2451-KWL076 | A BL MAIN ROAD DAYALPUR:PL | TG-KWL076A-1 | 19506896 | 990 | 320 | 243 | 0.97 | 988 | 353 | 1486 | 286 | 1185 | 349 | 1457 | 287 | 2019-06-16 02:00 | 351.4 | 89.9 | 1486 | R | 107 | 92 | 100 | 15 |  |  | 8.7 | 91.3 | [5 empty] | 20.18 | 20.18 |  | 575.58 | 652.58 | 630.42 | 640.01 | 115.49 | 20.15 | 61.19 | 53.3 | 1.44 |  | 0.3 |  | 693.31 | 26.29 | 0.63 | 1
38 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL079 | 1S-DL-YP-ETC-DKWL-2451-KWL079 | B BLK SADAT PUR GALI NO. 8:ID | TG-KWL079A-1 | 19504409 | 400 | 120 | 239 | 0.97 | 369 | 141 | 631 | 112 | 491 | 115 | 508 | 132 | 2019-06-29 23:00 | 69.3 | 28.2 | 670 | R | 114 | 96 | 90 | 24 | 1.3 | 28.9 | 69.1 | 0.7 |  |  |  |  | 30 | 66 | 66 | 59.3 | 525.41 | 642.31 | 528.31 | 602.31 | 137.2 | 11 | 15 | 57.3 | 26.3 |  |  |  | 719.31 | 0.29 | 0.61 | 0.92
39 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL080 | 1S-DL-YP-ETC-DKWL-2451-KWL080 | BIHARI PUR VILLNR. NLA KHJURI PUST RD:PL | TG-KWL080A-1 | 19506903 | 990 | 320 | 240 | 0.97 | 842 | 309 | 1384 | 257 | 1170 | 276 | 1266 | 186 | 2019-06-30 14:30 | 256.6 | 50.9 | 1559 | R | 117 | 96 | 87 | 30 | 0.1 | 0.5 | 47.8 | 51.5 |  |  |  |  | 1 | 13.3 | 13.3 | 6.3 | 593.2 | 687.03 | 642.31 | 693.33 | 101.43 |  | 0.3 | 0.3 | 4.3 |  |  |  | 700.33 | 19.27 | 0.68 | 0.85
40 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL085 | 1S-DL-YP-ETC-DKWL-2451-KWL085 | B BLK PUSTA 1 SONIA VIHAR GALI NO 1 | TG-KWL085A-1 | 19506042 | 630 | 200 | 234 | 0.97 | 589 | 176 | 745 | 202 | 854 | 210 | 883 | 126 | 2019-06-08 09:30 | 174.6 | 50.2 | 988 | Y | 99 | 99 | 103 | 4 |  | 10.1 | 75.9 | 14 |  |  |  |  | 7.3 | 46.49 | 46.49 | 8 | 659.02 | 591.13 | 658.29 | 654.56 | 6.39 | 31.58 | 14.03 | 10.15 |  | 3.11 | 0.39 |  | 673.11 | 46.49 | 0.63 | 0.93
41 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL119 | 1S-DL-YP-ETC-DKWL-2451-KWL119 | F BLK DAYAL PUR : ID | TG-KWL119A-1 | 19503341 | 630 | 200 | 234 | 0.97 | 500 | 213 | 952 | 139 | 614 | 148 | 664 | 316 | 2019-06-29 23:30 | 110.9 | 45.5 | 1035 | R | 128 | 90 | 82 | 46 |  |  | 2.9 | 97.1 |  |  |  |  | 1 | 125.02 | 125.02 | 41 | 548.5 | 592.21 | 464.15 | 676.23 | 139.33 |  |  |  | 28 |  |  |  | 717.23 | 2.37 | 0.67 | 0.79
42 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL147 | 1S-DL-YP-ETC-DKWL-2451-KWL147 | SHRI RAM COLONY D BLK:PLM | TG-KWL147A-1 | 19506716 | 630 | 200 | 243 | 0.97 | 788 | 259 | 1094 | 301 | 1302 | 228 | 968 | 292 | 2019-06-30 01:30 | 279.8 | 62 | 1302 | Y | 96 | 114 | 90 | 24 | 0.1 | 1.6 | 72.4 | 26 |  |  |  |  | 1 |  |  |  | 687.22 | 571.52 | 686.4 | 680.28 | 3.41 | 119.42 | 2.21 | 11.35 | 1.12 | 1.41 | 0.44 | 1.12 | 693.15 | 26.45 | 0.51 | 1.25
43 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL157 | 1S-DL-YP-ETC-DKWL-2451-KWL157 | D BLOCK GALI NO 2 DAYAL PUR | TG-KWL157A-1 | 19504362 | 990 | 320 | 241 | 0.97 | 972 | 292 | 1180 | 341 | 1386 | 339 | 1374 | 200 | 2019-06-28 23:00 | 224.5 | 85.4 | 1543 | B | 92 | 100 | 108 | 16 |  |  | 9 | 91 |  |  |  |  | 2 |  |  |  | 693.23 | 636.5 | 580.09 | 647.59 | 20.05 | 76.08 | 128.14 | 67.29 |  | 2.3 | 7.05 |  | 715.28 | 4.32 | 0.65 | 0.98
44 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL157 | 1S-DL-YP-ETC-DKWL-2451-KWL157 | D BLOCK GALI NO 2 DAYAL PUR | TG-KWL157A-2 | 19505019 | 630 | 200 | 233 | 0.97 | 639 | 191 | 819 | 214 | 917 | 235 | 1004 | 160 | 2019-06-11 23:00 | 138.5 | 31.3 | 1004 | B | 88 | 107 | 105 | 19 |  | 0.1 | 11.6 | 88.3 | 1.3 |  |  |  | 273.25 | 135.53 | 135.53 | 182.56 | 426.18 | 498.34 | 474.17 | 486.06 | 10.02 | 76.06 | 62.39 | 42.01 |  | 0.42 | 1.32 | 0.12 | 711.15 | 8.45 | 0.51 | 1.01
45 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL158 | 1S-DL-YP-ETC-DKWL-2451-KWL158 | D-3 NEHRU VIHAR : ID | TG-KWL158A-1 | 19500584 | 990 | 320 | 248 | 0.96 | 874 | 250 | 1056 | 339 | 1438 | 285 | 1192 | 336 | 2019-06-10 23:00 | 227.4 | 111.1 | 1445 | Y | 87 | 113 | 100 | 26 |  |  | 26 | 74 |  |  |  |  | 4 |  |  |  | 713.3 | 510.55 | 672.5 | 668.4 | 0.3 | 199.14 | 44.1 | 49.2 |  | 7.51 |  |  | 718 | 2 | 0.74 | 0.88
46 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL158 | 1S-DL-YP-ETC-DKWL-2451-KWL158 | D-3 NEHRU VIHAR : ID | TG-KWL158A-2 | 19505769 | 990 | 320 | 256 | 0.96 | 813 | 335 | 1490 | 199 | 881 | 279 | 1248 | 531 | 2019-06-28 23:00 | 288.6 | 78.7 | 1490 | R | 131 | 71 | 98 | 60 |  |  | 6.6 | 93.4 |  |  |  |  | 0.3 | 485.47 | 485.47 | 34 | 571.46 | 223.29 | 665.46 | 674.46 | 133 |  | 1 | 0.3 | 4 |  |  |  | 709.16 | 10.44 | 0.64 | 0.82
47 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL234 | 1S-DL-YP-ETC-DKWL-2451-KWL234 | B BLK SHRI RAM COLONY :PL | TG-KWL234A-1 | 19506536 | 990 | 320 | 244 | 0.97 | 1156 | 424 | 1808 | 445 | 1885 | 287 | 1202 | 648 | 2019-06-30 01:30 | 400.3 | 77.8 | 1891 | Y | 103 | 119 | 78 | 41 | 0.1 | 1.5 | 52 | 46.4 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | 665.5 | 452.23 | 681.12 | 666.2 | 42.24 | 237.05 | 0.43 | 42.22 | 1.11 | 19.57 |  | 0.43 | 709.55 | 10.05 | 0.56 | 1.17
48 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL235 | 1S-DL-YP-ETC-DKWL-2451-KWL235 | A BLK SHRI RAM CLY NEAR GALI 26:PL | TG-KWL235A-1 | 19505324 | 630 | 200 | 243 | 0.96 | 755 | 277 | 1189 | 210 | 887 | 268 | 1146 | 283 | 2019-06-30 01:30 | 286.6 | 58.6 | 1189 | R | 102 | 84 | 114 | 30 |  | 0.6 | 27.4 | 72.1 |  |  |  |  | 4.3 | 20.18 | 20.18 |  | 691.13 | 686.06 | 597.38 | 701.04 | 11.11 | 1.28 | 108.16 | 5.5 | 1.01 | 0.03 | 2.01 | 1.01 | 707.55 | 12.05 | 0.5 | 1.2
49 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL251 | 1S-DL-YP-ETC-DKWL-2451-KWL251 | A BLK KHAJOORI:PL | TG-KWL251A-1 | 19505294 | 630 | 200 | 246 | 0.97 | 747 | 227 | 923 | 284 | 1159 | 236 | 968 | 217 | 2019-06-01 05:00 | 226.6 | 40.2 | 1159 | Y | 94 | 108 | 98 | 14 |  | 0.1 | 5 | 94.9 |  |  |  |  | 43 | 12.3 | 12.3 | 18 | 654.55 | 634.58 | 663.55 | 678.55 | 0.3 | 50.57 | 1 | 1.3 | 0.3 | 0.3 | 0.3 | 0.3 | 698.55 | 21.05 | 0.46 | 1.19
50 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL295 | 1S-DL-YP-ETC-DKWL-2451-KWL295 | K BLK SADAT PUR EXT. GALI NO. 51:ID | TG-KWL295A-1 | 19500647 | 990 | 320 | 236 | 0.96 | 876 | 265 | 1156 | 302 | 1322 | 308 | 1366 | 192 | 2019-06-09 23:00 | 211.2 | 79.5 | 1435 | B | 91 | 102 | 108 | 17 | 27 | 33.8 | 25 | 14.1 |  |  |  |  | 41.3 | 11.3 | 11.3 | 12.3 | 668.27 | 663.07 | 627.5 | 671.07 | 9.12 | 44.32 | 81.19 | 35.32 |  |  |  |  | 719.09 | 0.51 | 0.67 | 0.88
51 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL342 | 1S-DL-YP-ETC-DKWL-2451-KWL342 | BIHARI PUR VILLAGE EXTN.NO-2 NALA WALA | TG-KWL342A-1 | 19506302 | 630 | 200 | 239 | 0.97 | 550 | 231 | 1033 | 185 | 836 | 134 | 604 | 372 | 2019-06-30 14:30 | 175.6 | 18.4 | 1033 | R | 124 | 105 | 71 | 53 | 6.4 | 2.2 | 25.4 | 66 |  |  | 2 |  | 9.3 | 62.45 | 62.45 | 75.15 | 597.43 | 629.28 | 240.07 | 618.58 | 84.3 | 2.3 |  | 0.3 | 3 |  |  |  | 694.43 | 25.17 | 0.59 | 0.87

## Loading Condition > 100%
MIS Report of Distribution Transformer - Jun19
Jun19 1251 KARAWAL NAGAR (Loading Condition > 100% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL027 | 1S-DL-YP-ETC-DKWL-2451-KWL027 | A BLOCK BRIJ PURI:ID | TG-KWL027A-1 | 19500627 | 630 | 200 | 242 | 0.97 | 643 | 298 | 1293 | 228 | 992 | 116 | 486 | 706 | 2019-06-10 23:30 | 169.7 | 14.3 | 1355 | R | 96 | 113 | 91 | 22 | 5.8 | 31.2 | 58.1 | 4.9 | 314.23 |  |  |  | 8.36 | 47.51 | 47.51 | 141.03 | 154.14 | 550.1 | 483.49 | 509.21 | 143.11 | 104.02 | 35.36 | 63.28 | 94.18 | 12.39 |  | 0.5 | 714.42 | 5.18 | 0.55 | 1.02
2 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL039 | 1S-DL-YP-ETC-DKWL-2451-KWL039 | GANGA VIHAR NO-1:ID | TG-KWL039A-2 | 19500982 | 990 | 320 | 244 | 0.97 | 956 | 412 | 1691 | 272 | 1098 | 272 | 1115 | 585 | 2019-06-25 23:30 | 238.5 | 87.6 | 1718 | R | 122 | 86 | 93 | 36 |  | 0.1 | 88.3 | 11.6 |  |  |  |  | 1 | 115 | 115 | 29 | 502.13 | 594.37 | 617.47 | 610.46 | 148.33 | 8.5 | 29.4 | 78.41 | 66.41 |  |  |  | 718.27 | 1.33 | 0.61 | 0.97
3 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL040 | 1S-DL-YP-ETC-DKWL-2451-KWL040 | GANGA VIHAR NO-2:ID | TG-KWL040A-2 | 19503794 | 990 | 320 | 253 | 0.97 | 1153 | 282 | 1139 | 457 | 1903 | 414 | 1699 | 685 | 2019-06-08 23:30 | 276.7 | 66.2 | 1930 | Y | 82 | 115 | 103 | 33 | 0.6 | 35.6 | 63.8 | [5 empty] | 10.01 |  |  | 0.01 | 675.27 | 334.46 | 446.47 | 488.5 | 25.34 | 237.07 | 228.35 | 196.13 |  | 139.09 | 35.39 | 25.58 | 711.02 | 8.58 | 0.63 | 1.16
4 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL040 | 1S-DL-YP-ETC-DKWL-2451-KWL040 | GANGA VIHAR NO-2:ID | TG-KWL040A-1 | 19501736 | 990 | 320 | 251 | 0.97 | 1126 | 398 | 1520 | 377 | 1378 | 351 | 1337 | 166 | 2019-06-30 07:30 | 367.3 | 88.3 | 1621 | R | 108 | 95 | 96 | 13 | 100 | [11 empty] | 457.04 | 554.47 | 546.33 | 532.03 | 208.33 | 154.23 | 134.32 | 156.27 | 48.01 | 4.28 | 31.33 | 25.08 | 713.38 | 6.22 | 0.63 | 1.14
5 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL077 | 1S-DL-YP-ETC-DKWL-2451-KWL077 | SAMPAT NAGAR 1:ID | TG-KWL077A-2 | 19505301 | 400 | 120 | 237 | 0.98 | 413 | 156 | 655 | 130 | 547 | 126 | 528 | 118 | 2019-06-30 | 166.4 | 18.5 | 834 | R | 108 | 95 | 97 | 13 | 0.1 | 0.2 | 4.8 | 94.8 |  |  |  |  | 0.3 |  |  |  | 310.55 | 525.28 | 511.49 | 446.15 | 315.16 | 181.22 | 193.05 | 258.09 | 82.09 | 2 | 3.26 | 4.26 | 708.5 | 11.1 | 0.73 | 1.03
6 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL103 | 1S-DL-YP-ETC-DKWL-2451-KWL103 | MAJOR MALHOTRA FARM HOUSE:PM | TG-KWL103A-1 | 19506634 | 100 | 40 | 250 | 0.84 | 85 | 11 | 44 | 30 | 122 | 44 | 182 | 120 | 2019-06-28 12:00 | 10 | -36.1 | 207 | B | 70 | 103 | 126 | 56 | 3.2 | 14.6 | 50.9 | 31.3 | 1.3 |  |  |  | 539.06 | 270.16 | 270.16 | 233.19 | 162.53 | 364.43 | 471.44 | 464.4 |  | 65 | 110.57 | 5.3 |  | 3.3 | 55 |  | 703.29 | 16.31 | 0.6 | 0.85
7 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | GOKUL PURI | 1251 | KWL344 | 1S-DL-YP-ETC-DKWL-2451-KWL344 | MAIN ROAD MCD SCHOOL JOHRI PUR | TG-KWL344A-1 | 19505304 | 990 | 320 | 245 | 0.98 | 1164 | 405 | 1827 | 384 | 1720 | 375 | 1689 | 125 | 2019-06-29 15:00 | 441.6 | -59.8 | 1827 | R | 112 | 94 | 95 | 18 | 0.1 |  | 35.6 | 64.2 | 1 | 73.05 | 47.35 | 22.3 | 260.21 | 293.32 | 293.32 | 322 | 270.45 | 229.09 | 249.27 | 239.58 | 140.58 | 95.17 | 83.46 | 104.35 | 32.15 | 14.16 | 9.16 | 16.16 | 705.19 | 14.41 | 0.44 | 1.18
8 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL022 | 1S-DL-YP-ETC-DKWL-2451-KWL022 | B-II BLOCK NEHRU VIHAR GALI NO. 6:ID | TG-KWL022A-1 | 19506820 | 630 | 200 | 249 | 0.96 | 933 | 336 | 1412 | 305 | 1272 | 292 | 1217 | 174 | 2019-06-28 14:30 | 319.4 | 106.4 | 1412 | R | 109 | 101 | 90 | 19 |  | 0.1 | 1.9 | 98 | [8 empty] | 33.3 | 122 | 323.3 | 112.3 | 354.09 | 389.54 | 330.31 | 430.09 | 316.52 | 192.37 | 50.3 | 161.52 | 704.31 | 15.29 | 0.62 | 1.48
9 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL060 | 1S-DL-YP-ETC-DKWL-2451-KWL060 | C BLOCK KHAJORI MAIN MARKET | TG-KWL060A-3 | 19506413 | 630 | 200 | 245 | 0.97 | 647 | 199 | 825 | 261 | 1079 | 187 | 769 | 286 | 2019-06-12 | 215.6 | 36.4 | 1271 | Y | 95 | 112 | 94 | 18 | 0.3 |  | 5.4 | 94.3 |  | 0.56 | 0.56 |  | 18.13 | 7.43 | 7.43 | 11.09 | 600.48 | 479.12 | 614.5 | 559.4 | 77.51 | 131.32 | 62.59 | 124.53 |  | 77.29 |  | 1.1 | 696.52 | 23.08 | 0.62 | 1.03
10 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL063 | 1S-DL-YP-ETC-DKWL-2451-KWL063 | VILLAGE SABHAPUR:PM | TG-KWL063A-1 | 19502302 | 630 | 200 | 230 | 0.98 | 758 | 293 | 1297 | 211 | 918 | 255 | 1125 | 329 | 2019-06-09 23:00 | 156.9 | 26.2 | 1297 | R | 112 | 89 | 99 | 23 |  | 4.7 | 41.4 | 54 |  |  |  |  | 0.31 | 8.53 | 8.53 | 1.23 | 318.29 | 550.08 | 442.56 | 428.44 | 207.48 | 136.2 | 229.14 | 222.01 | 171.33 | 3 | 25.19 | 46.13 | 698.21 | 21.39 | 0.62 | 1.2
11 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL070 | 1S-DL-YP-ETC-DKWL-2451-KWL070 | B BLK GALI NO. 9, CHAND BAGH:ID | TG-KWL070A-1 | 19500570 | 630 | 200 | 236 | 0.97 | 584 | 196 | 859 | 225 | 994 | 164 | 715 | 242 | 2019-06-02 23:30 | 154.6 | 63 | 1075 | Y | 93 | 125 | 82 | 43 | 39.5 | 11.4 | 16.1 | 33 |  |  |  |  | 4 |  |  |  | 673.43 | 316.08 | 630.24 | 647.45 | 37.32 | 361.3 | 13.26 | 67.3 |  | 37.37 |  |  | 715.15 | 4.45 | 0.72 | 0.93
12 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL072 | 1S-DL-YP-ETC-DKWL-2451-KWL072 | VILLAGE KHAJOORI NR.SCHOOL:PL | TG-KWL072A-1 | 19504805 | 630 | 200 | 244 | 0.99 | 601 | 253 | 1061 | 174 | 721 | 174 | 720 | 340 | 2019-06-12 15:00 | 118.7 | -10.6 | 1085 | R | 116 | 92 | 91 | 25 |  | 2.2 | 39.9 | 58 |  |  |  |  | 3 | 30.3 | 30.3 | 5.3 | 481.58 | 645.16 | 697.46 | 647.47 | 143.19 | 41 | 8.3 | 63.29 | 88.29 |  |  |  | 716.46 | 3.14 | 0.68 | 0.95
13 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL093 | 1S-DL-YP-ETC-DKWL-2451-KWL093 | CHAUHAN PATTI PUSTA VILL SONIA VIHAR:PL | TG-KWL093A-1 | 19506301 | 630 | 200 | 238 | 0.96 | 714 | 218 | 952 | 262 | 1154 | 234 | 1025 | 177 | 2019-06-29 22:30 | 243.6 | 70.8 | 1216 | Y | 96 | 109 | 95 | 14 |  | 2.6 | 25.7 | 71.8 |  |  |  |  | 0.57 |  |  |  | 603.09 | 408.36 | 543.13 | 518.53 | 79.32 | 247.25 | 139.48 | 164.05 | 2.34 | 30.11 | 1.44 | 3.14 | 686.12 | 33.48 | 0.63 | 1.13
14 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL096 | 1S-DL-YP-ETC-DKWL-2451-KWL096 | B-I, NEHRU VIHAR:ID | TG-KWL096A-1 | 19500614 | 990 | 320 | 254 | 0.96 | 1166 | 389 | 1610 | 380 | 1576 | 397 | 1648 | 62 | 2019-06-29 23:00 | 249.5 | 128.8 | 1658 | B | 106 | 103 | 91 | 15 |  | 0.1 | 22 | 77.8 | [8 empty] | 423.1 | 435.23 | 546.23 | 481.53 | 201.43 | 217 | 143 | 177 | 94 | 66.3 | 29.3 | 60 | 718.53 | 1.07 | 0.64 | 1.18
15 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL113 | 1S-DL-YP-ETC-DKWL-2451-KWL113 | SONIA VIHAR "B" BLK GALI NO-27 | TG-KWL113A-1 | 19506291 | 400 | 200 | 243 | 0.96 | 524 | 193 | 808 | 181 | 756 | 150 | 616 | 172 | 2019-06-10 05:00 | 192.4 | 56.6 | 808 | R | 103 | 106 | 91 | 15 |  | 0.1 | 20.4 | 79.5 | [8 empty] | 394.32 | 305.16 | 586.25 | 464.17 | 263.15 | 360.29 | 99.08 | 218.16 | 29.13 | 21.15 | 1.27 | 4.27 | 687 | 33 | 0.59 | 1.31
16 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL115 | 1S-DL-YP-ETC-DKWL-2451-KWL115 | C 1 KHAJOORI GALI NO. 24:PM | TG-KWL115A-1 | 19502314 | 400 | 120 | 251 | 0.98 | 439 | 152 | 636 | 89 | 365 | 198 | 832 | 406 | 2019-06-02 23:00 | 86.4 | 20.7 | 879 | B | 100 | 58 | 142 | 84 | 0.2 | 40.5 | 57.9 | 1.3 |  | 1 |  |  |  | 274.4 | 274.4 |  | 471.39 | 443.58 | 38.29 | 492.39 | 201.29 |  | 261.49 | 197.59 | 46.3 |  | 419.2 | 29 | 719.38 | 0.22 | 0.68 | 1.1
17 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL127 | 1S-DL-YP-ETC-DKWL-2451-KWL127 | NIKKA PLASTIC TUKMEERPUR VILLAGE:PM | TG-KWL127A-1 | 19505123 | 400 | 120 | 245 | 0.99 | 501 | 165 | 662 | 166 | 674 | 169 | 683 | 18 | 2019-06-17 20:00 | 89.6 | -27.4 | 717 | Y | 96 | 102 | 102 | 6 | 25.1 | 6.4 | 39.8 | 28.6 | 61.3 | 57.3 | 46 | 58 | 91.52 | 93.52 | 93.52 | 93.52 | 112.47 | 113.47 | 108.55 | 111.17 | 62.18 | 52.48 | 40.3 | 52.48 | 49.16 | 59.46 | 80.36 | 61.46 | 696.41 | 23.19 | 0.46 | 1.25
18 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL154 | 1S-DL-YP-ETC-DKWL-2451-KWL154 | SHRI RAM CLY E BLK GN 3 NR MASJID :PM | TG-KWL154A-1 | 19504596 | 400 | 120 | 239 | 0.98 | 388 | 124 | 530 | 122 | 519 | 143 | 614 | 89 | 2019-06-02 15:00 | 84.5 | 29 | 694 | B | 91 | 95 | 114 | 23 |  | 2.1 | 44.6 | 53.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1.3 | 0.3 | 0.3 |  | 655.59 | 619.34 | 311.46 | 551.21 | 56.59 | 93.54 | 314.05 | 163.07 |  | 0.3 | 88.37 |  | 714.58 | 5.02 | 0.75 | 0.97
19 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL249 | 1S-DL-YP-ETC-DKWL-2451-KWL249 | A BLOCK SHRI RAM CLY. NEAR SERVICE RD:PL | TG-KWL249A-1 | 19506533 | 630 | 200 | 243 | 0.97 | 739 | 207 | 870 | 304 | 1307 | 228 | 964 | 398 | 2019-06-30 | 238.4 | 49.8 | 1307 | Y | 78 | 137 | 85 | 59 | 0.1 | 0.2 | 26.2 | 73.6 |  |  |  |  | 17 |  |  |  | 698.54 | 122.11 | 706.24 | 676.5 | 0.56 | 407.09 | 0.27 | 39.31 |  | 187.3 | 0.29 | 0.29 | 716.5 | 3.1 | 0.57 | 1.17
20 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL292 | 1S-DL-YP-ETC-DKWL-2451-KWL292 | E BLOCK CHAND BAGH:PL | TG-KWL292A-1 | 19506537 | 630 | 200 | 238 | 0.96 | 810 | 242 | 1030 | 280 | 1194 | 289 | 1244 | 194 | 2019-06-30 01:30 | 291.2 | 85 | 1298 | B | 87 | 108 | 105 | 21 | 0.2 | 0.6 | 57.5 | 41.7 | [8 empty] | 521.56 | 215.49 | 244.45 | 320.45 | 169.44 | 291.07 | 336.41 | 293.3 | 8.59 | 193.43 | 119.13 | 86.24 | 700.39 | 19.21 | 0.65 | 1.29
21 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL297 | 1S-DL-YP-ETC-DKWL-2451-KWL297 | B BLK SHRI RAM COLONY SAITAN CHOWK:PL | TG-KWL297A-1 | 19506034 | 990 | 320 | 244 | 0.97 | 1222 | 493 | 2032 | 393 | 1595 | 337 | 1358 | 592 | 2019-06-15 07:30 | 443.5 | 93.4 | 2032 | R | 119 | 102 | 78 | 41 | 0.3 | 14 | 31.2 | 54.5 | [8 empty] | 107.29 | 398 | 696.14 | 423.33 | 420.27 | 268.14 | 5.48 | 270.06 | 175.35 | 37.17 | 0.29 | 9.52 | 703.31 | 16.29 | 0.63 | 1.23
22 | 2019-06-01 | 2019-06-30 23:30 | KARAWAL NAGAR | SONIA VIHAR | 1251 | KWL298 | 1S-DL-YP-ETC-DKWL-2451-KWL298 | Delhi Police Training Center:PM | TG-KWL298A-1 | 19506396 | 400 | 120 | 251 | 0.98 | 460 | 162 | 623 | 151 | 576 | 147 | 567 | 53 | 2019-06-18 04:00 | 121.9 | 9.7 | 763 | B | 101 | 110 | 89 | 21 | 0.1 | 0.1 | 3.7 | 96.2 | 1.08 |  |  |  | 2 | 3.38 | 3.38 | 4.38 | 524.21 | 410.1 | 602.35 | 531.51 | 160 | 243.41 | 34 | 153 | 5 | 35 | 1 | 3 | 692.29 | 27.31 | 0.59 | 1.15