## Complete Report
MIS Report of Distribution Transformer - Jun19
Jun19 1260 NAND NAGARI (Complete Report)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR001 | 1S-DL-YP-ETC-DNNG-2901-NGR001 | 960 MIG ,S/STN-2 POCKET F GTB ENCLAVE:ID | TG-NGR001A-1 | 19506617 | 630 | 200 | 242 | 0.98 | 322 | 97 | 401 | 95 | 396 | 130 | 544 | 145 | 2019-06-29 23:00 | 61.8 | 11.6 | 544 | B | 92 | 98 | 111 | 19 |  |  | 21.2 | 78.8 | 246.17 | 235.24 | 175.27 | 201.54 | 419 | 377.23 | 377.23 | 410.53 | 30.3 | 83 | 136 | 83 | [8 empty] | 695.47 | 24.13 | 0.51 | 0.51
2 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR001 | 1S-DL-YP-ETC-DNNG-2901-NGR001 | 960 MIG ,S/STN-2 POCKET F GTB ENCLAVE:ID | TG-NGR001A-2 | 19502677 | 630 | 200 | 247 | 0.97 | 260 | 70 | 285 | 77 | 311 | 113 | 461 | 164 | 2019-06-03 | 61.2 | 13.3 | 494 | B | 83 | 91 | 127 | 44 |  |  | 24 | 76 | 307.54 | 219.24 | 46.27 | 125.54 | 411.52 | 500.22 | 500.22 | 591.52 |  |  | 139 | 2 | [8 empty] | 719.46 | 0.14 | 0.61 | 0.41
3 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR002 | 1S-DL-YP-ETC-DNNG-2901-NGR002 | 960 MIG S/S NO.3 PKT F GTB ENCLAVE:ID | TG-NGR002A-1 | 19502675 | 630 | 200 | 239 | 0.97 | 409 | 126 | 532 | 153 | 649 | 130 | 550 | 109 | 2019-06-08 00:30 | 80.5 | 17.9 | 742 | Y | 91 | 116 | 93 | 25 |  |  | 2.6 | 97.4 | 129.27 | 43 | 108.58 | 83.58 | 438 | 402.27 | 402.27 | 444.29 | 152.01 | 273.01 | 152.01 | 191.01 |  | 1 | [6 empty] | 719.28 | 0.32 | 0.51 | 0.65
4 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR002 | 1S-DL-YP-ETC-DNNG-2901-NGR002 | 960 MIG S/S NO.3 PKT F GTB ENCLAVE:ID | TG-NGR002A-2 | 19502681 | 630 | 200 | 238 | 0.98 | 418 | 141 | 599 | 138 | 586 | 139 | 592 | 11 | 2019-06-08 | 77.3 | 9.2 | 636 | B | 98 | 105 | 96 | 9 |  |  | 1.5 | 98.5 | 126.58 | 39.3 | 129.27 | 86.3 | 413.29 | 477.57 | 477.57 | 454.57 | 179.01 | 202.01 | 180.31 | 178.01 | [8 empty] | 719.28 | 0.32 | 0.5 | 0.66
5 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR003 | 1S-DL-YP-ETC-DNNG-2901-NGR003 | LIG,S/STN-4 POCKET E GTB ENCLAVE:ID | TG-NGR003A-1 | 19505251 | 990 | 320 | 246 | 0.97 | 646 | 254 | 1058 | 224 | 936 | 168 | 693 | 322 | 2019-06-30 | 137.3 | 33 | 1143 | R | 123 | 104 | 73 | 50 |  | 0.1 | 25.1 | 74.8 | 16.3 | 87.58 | 284.58 | 84 | 391.57 | 406.59 | 406.59 | 437.27 | 287.01 | 201.01 | 46.31 | 174.31 | 0.3 | [7 empty] | 695.58 | 24.02 | 0.5 | 0.65
6 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR003 | 1S-DL-YP-ETC-DNNG-2901-NGR003 | LIG,S/STN-4 POCKET E GTB ENCLAVE:ID | TG-NGR003A-2 | 19505183 | 630 | 200 | 239 | 0.97 | 443 | 128 | 546 | 152 | 651 | 162 | 691 | 130 | 2019-06-29 23:30 | 115.4 | 22.6 | 720 | B | 81 | 101 | 118 | 37 |  |  | 33.8 | 66.2 | 142.28 | 44 | 7 | 31 | 438.29 | 418.57 | 418.57 | 441.57 | 115 | 233 | 366.47 | 223 |  |  | 0.43 | [5 empty] | 695.57 | 24.03 | 0.51 | 0.7
7 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR004 | 1S-DL-YP-ETC-DNNG-2901-NGR004 | LIG,S/STN NO-5 POCKET-E GTB ENCLAVE:ID | TG-NGR004A-1 | 19506219 | 630 | 200 | 240 | 0.97 | 1096 | 370 | 1626 | 351 | 1548 | 375 | 1657 | 97 | 2019-06-26 18:30 | 262.4 | 16 | 1657 | B | 127 | 79 | 94 | 48 |  | 0.1 | 8.6 | 91.3 | 55.3 | 279.11 | 159 | 126 | 400.44 | 406.33 | 406.33 | 456.14 | 238.01 | 9.01 | 126.31 | 112.01 | 0.3 |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 695.15 | 24.45 | 0.17 | 1.74
8 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR004 | 1S-DL-YP-ETC-DNNG-2901-NGR004 | LIG,S/STN NO-5 POCKET-E GTB ENCLAVE:ID | TG-NGR004A-2 | 19506218 | 630 | 200 | 246 | 0.97 | 474 | 157 | 647 | 153 | 630 | 164 | 676 | 40 | 2019-06-08 | 95.6 | 20.8 | 679 | Y | 99 | 100 | 100 | 1 |  |  | 4.7 | 95.3 | 30 | 21 | 33.3 | 21.3 | 407.57 | 400.13 | 400.13 | 409.43 | 257.17 | 274.01 | 273.31 | 264.01 | [8 empty] | 695.14 | 24.46 | 0.51 | 0.75
9 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR005 | 1S-DL-YP-ETC-DNNG-2901-NGR005 | 240 MIG PKT A S/STN:ID | TG-NGR005A-1 | 19504985 | 630 | 200 | 236 | 0.97 | 405 | 137 | 589 | 166 | 721 | 102 | 442 | 242 | 2019-06-11 23:00 | 79.6 | 19.8 | 735 | Y | 110 | 115 | 75 | 40 |  |  | 23.9 | 76.1 | 12.3 | 29.3 | 188.34 | 36 | 431.53 | 392.23 | 392.23 | 468.53 | 275 | 297.3 | 26.3 | 214.3 | [8 empty] | 719.23 | 0.37 | 0.54 | 0.64
10 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR005 | 1S-DL-YP-ETC-DNNG-2901-NGR005 | 240 MIG PKT A S/STN:ID | TG-NGR005A-2 | 19505498 | 630 | 200 | 238 | 0.97 | 214 | 61 | 261 | 95 | 405 | 58 | 249 | 150 | 2019-06-30 23:30 | 77 | 8.2 | 442 | Y | 84 | 140 | 76 | 64 |  | 2.3 | 91.1 | 6.6 | 558.01 | 196.01 | 571.01 | 451.01 | 138.3 | 440.3 | 440.3 | 245.3 |  | 60 | [10 empty] | 696.31 | 23.29 | 0.54 | 0.34
11 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR006 | 1S-DL-YP-ETC-DNNG-2901-NGR006 | JANTA FLAT S/S NO.1 GTB ENCLAVE:ID | TG-NGR006A-1 | 19505505 | 990 | 320 | 241.8233 | 0.96683 | 956.1592 | 314.798 | 1386.409 | 276.0916 | 1206.6412 | 365.2696 | 1618.9593 | 358.0519 | 2019-06-30 23:30 | [15 empty] | 0 |  |  |  | 171 |  |  |  | 504 |  |  |  | 43.5 |  |  |  | 0 | 718.5 |  | 0.53175 | 0.96582
12 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR006 | 1S-DL-YP-ETC-DNNG-2901-NGR006 | JANTA FLAT S/S NO.1 GTB ENCLAVE:ID | TG-NGR006A-2 | 19506194 | 630 | 200 | 250 | 0.98 | 734 | 318 | 1273 | 285 | 1172 | 130 | 509 | 720 | 2019-06-18 02:00 | 245.4 | 15.2 | 1273 | R | 96 | 128 | 76 | 52 | 0.1 | 0.1 | 48.7 | 51.1 | 86.22 | 16.08 | 269.28 | 77.14 | 500.31 | 395.15 | 395.15 | 474.09 | 129.31 | 302.01 | 36.14 | 165.01 |  | 3 |  |  | 0.3 | 0.3 |  | 0.3 | 716.54 | 3.06 | 0.27 | 1.16
13 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR006 | 1S-DL-YP-ETC-DNNG-2901-NGR006 | JANTA FLAT S/S NO.1 GTB ENCLAVE:ID | TG-NGR006A-3 | 19506507 | 630 | 200 | 243 | 0.97 | 385 | 114 | 466 | 96 | 391 | 175 | 716 | 295 | 2019-06-29 23:30 | 83.4 | 23.2 | 779 | B | 91 | 85 | 124 | 39 |  |  | 4.5 | 95.5 | 58.36 | 85 | 3.3 | 20.06 | 541.56 | 561.32 | 561.32 | 517.26 | 116.31 | 70.31 | 353.24 | 179.31 |  |  | 1.3 | [5 empty] | 717.03 | 2.57 | 0.56 | 0.61
14 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR007 | 1S-DL-YP-ETC-DNNG-2901-NGR007 | JANTA FLAT S/S NO.2 GTB ENCLAVE:ID | TG-NGR007A-1 | 19505795 | 630 | 200 | 248 | 0.96 | 525 | 174 | 736 | 217 | 939 | 134 | 570 | 321 | 2019-06-30 23:30 | 145.2 | 44.2 | 939 | Y | 99 | 120 | 82 | 38 |  | 1.7 | 57.8 | 40.5 | 0.3 |  | 5.24 |  | 291.26 | 152.14 | 152.14 | 269.03 | 422.21 | 481.4 | 241.21 | 442.44 | 4.3 | 78.53 |  | 7 |  | 6 |  |  | 718.47 | 1.13 | 0.56 | 0.83
15 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR007 | 1S-DL-YP-ETC-DNNG-2901-NGR007 | JANTA FLAT S/S NO.2 GTB ENCLAVE:ID | TG-NGR007A-2 | 19505794 | 630 | 200 | 232 | 0.97 | 593 | 164 | 687 | 186 | 786 | 244 | 1049 | 324 | 2019-06-03 | 148.8 | 34.8 | 1073 | B | 92 | 106 | 102 | 14 | 0.1 | 2.9 | 38.6 | 58.5 |  |  |  |  | 255.31 | 182.42 | 182.42 | 209.01 | 460.36 | 473.02 | 451.42 | 473.43 | 2.3 | 56.23 | 41.23 | 35.53 |  | 6.3 | 12.3 |  | 718.37 | 1.23 | 0.54 | 0.94
16 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR007 | 1S-DL-YP-ETC-DNNG-2901-NGR007 | JANTA FLAT S/S NO.2 GTB ENCLAVE:ID | TG-NGR007A-3 | 19505801 | 630 | 200 | 239 | 0.97 | 518 | 218 | 944 | 114 | 480 | 186 | 788 | 409 | 2019-06-12 00:30 | 122 | 28.2 | 984 | B | 91 | 89 | 120 | 31 |  | 0.9 | 39.5 | 59.6 | 20.55 | 8.25 | 0.3 | 2.26 | 398.29 | 450.29 | 450.29 | 363.58 | 298.53 | 250.23 | 438.23 | 349.53 |  | 9.3 | 63.23 | 2.3 | 0.3 |  | 1 |  | 718.47 | 1.13 | 0.52 | 0.82
17 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR008 | 1S-DL-YP-ETC-DNNG-2901-NGR008 | JANTA FLAT S/S NO.3 GTB ENCLAVE:ID | TG-NGR008A-1 | 19505360 | 990 | 320 | 243 | 0.97 | 752 | 202 | 849 | 267 | 1140 | 283 | 1193 | 321 | 2019-06-30 23:30 | 233.9 | 49 | 1207 | B | 87 | 98 | 115 | 28 |  | 0.2 | 51 | 48.8 | 10.23 | 6.53 |  | 1.23 | 454.49 | 398.36 | 398.36 | 356.25 | 229.05 | 285.48 | 483.54 | 336.29 |  | 3 | 11 | [5 empty] | 694.17 | 25.43 | 0.56 | 0.76
18 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR008 | 1S-DL-YP-ETC-DNNG-2901-NGR008 | JANTA FLAT S/S NO.3 GTB ENCLAVE:ID | TG-NGR008A-2 | 19505177 | 990 | 320 | 242 | 0.97 | 926 | 222 | 910 | 303 | 1264 | 401 | 1678 | 666 | 2019-06-30 00:30 | 247 | 59.5 | 1678 | B | 86 | 109 | 105 | 23 |  | 1.5 | 43.7 | 54.8 | 1.45 | 1.45 | 1.45 | 1.45 | 328.47 | 180.47 | 180.47 | 215.47 | 363.46 | 444.46 | 446.16 | 455.46 |  | 62 | 49.3 | 21 |  | 5 | 3.3 |  | 694.18 | 25.42 | 0.52 | 0.94
19 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR009 | 1S-DL-YP-ETC-DNNG-2901-NGR009 | GTB HOSPITAL:ID | TG-NGR009A-1 | 19502673 | 630 | 200 | 242 | 0.98 | 360 | 121 | 505 | 156 | 649 | 83 | 343 | 266 | 2019-06-11 23:30 | 60.7 | 14.3 | 694 | Y | 107 | 115 | 78 | 37 |  |  | 0.2 | 99.8 | 38.24 | 78.24 | 248.12 | 71.24 | 458.09 | 382.09 | 382.09 | 474.39 | 221.54 | 257.54 | 38.3 | 172.24 | [8 empty] | 718.27 | 1.33 | 0.56 | 0.57
20 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR010 | 1S-DL-YP-ETC-DNNG-2901-NGR010 | WEAVER,S COMPLEX SDM OFFICE NNG:ID | TG-NGR010A-1 | 19503192 | 400 | 120 | 238 | 0.98 | 112 | 42 | 176 | 31 | 130 | 39 | 166 | 42 | 2019-06-03 12:00 | 31.7 | 0.6 | 185 | B | 99 | 82 | 119 | 37 |  | 3.1 | 53.3 | 43.6 | 584.58 | 693.01 | 572.47 | 609.31 | 134.33 | 26.3 | 26.3 | 110 | [12 empty] | 719.31 | 0.29 | 0.3 | 0.28
21 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR010 | 1S-DL-YP-ETC-DNNG-2901-NGR010 | WEAVER,S COMPLEX SDM OFFICE NNG:ID | TG-NGR010A-2 | 19504116 | 990 | 320 | 238 | 0.96 | 606 | 184 | 769 | 209 | 878 | 213 | 894 | 118 | 2019-06-29 23:00 | 169.3 | 78.8 | 952 | B | 89 | 100 | 111 | 22 |  |  | 17.7 | 82.3 |  |  |  |  | 190.28 | 90 | 90 | 56.3 | 529.26 | 629.54 | 708.54 | 663.24 | [8 empty] | 719.54 | 0.06 | 0.79 | 0.61
22 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR010 | 1S-DL-YP-ETC-DNNG-2901-NGR010 | WEAVERS COMPLEX SDM Office NNG:ID | TG-NGR010A-3 | 19505262 | 630 | 200 | 239 | 0.96 | 298 | 97 | 432 | 99 | 436 | 103 | 455 | 22 | 2019-06-27 13:00 | 104.6 | 36.8 | 455 | B | 100 | 94 | 106 | 12 |  | 0.4 | 46.2 | 53.4 |  | 0.3 | 0.3 |  | 657.28 | 691.57 | 691.57 | 673.58 | 38.56 | 3.57 | 131.56 | 22.26 | [8 empty] | 696.24 | 23.36 | 0.71 | 0.47
23 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR011 | 1S-DL-YP-ETC-DNNG-2901-NGR011 | H-BLOCK SUNDER NAGRI:PL | TG-NGR011A-1 | 19502704 | 990 | 320 | 244 | 0.94 | 384 | 166 | 689 | 98 | 406 | 121 | 504 | 248 | 2019-06-30 23:30 | 128.1 | 55.2 | 698 | R | 123 | 78 | 99 | 45 |  |  | 17.6 | 82.4 | 2.3 | 227.13 | 13 | 14 | 538.12 | 491.29 | 491.29 | 704.42 | 178 | [11 empty] | 718.42 | 1.18 | 0.73 | 0.39
24 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR011 | 1S-DL-YP-ETC-DNNG-2901-NGR011 | H-BLOCK SUNDER NAGRI:PL | TG-NGR011A-2 | 19506464 | 990 | 320 | 240 | 0.96 | 402 | 157 | 648 | 110 | 457 | 135 | 558 | 166 | 2019-06-02 | 144 | 45.8 | 748 | R | 119 | 93 | 87 | 32 |  |  | 7.8 | 92.2 |  | 26.3 | 68.4 | 8 | 562.47 | 668.43 | 668.43 | 684.43 | 132.26 |  | 0.3 | 2.3 | [8 empty] | 695.13 | 24.47 | 0.71 | 0.41
25 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR011 | 1S-DL-YP-ETC-DNNG-2901-NGR011 | H-BLOCK SUNDER NAGRI:PL | TG-NGR011A-3 | 19502703 | 400 | 120 | 246 | 0.86 | 179 | 59 | 255 | 61 | 260 | 59 | 254 | 6 | 2019-06-14 09:30 | 79.2 | 0.3 | 260 | Y | 99 | 100 | 102 | 3 |  |  | 1 | 99 | 634.52 | 635.22 | 632.52 | 634.22 | 81.53 | 82.23 | 82.23 | 82.53 | 1.58 | 0.58 | 1.28 | 1.28 | [8 empty] | 718.43 | 1.17 | 0.15 | 0.45
26 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR012 | 1S-DL-YP-ETC-DNNG-2901-NGR012 | O-BLOCK SUNDER NAGARI:PL | TG-NGR012A-1 | 19506234 | 990 | 200 | 239 | 0.96 | 498 | 198 | 836 | 157 | 656 | 144 | 602 | 213 | 2019-06-11 00:30 | 165 | 55.2 | 923 | R | 123 | 91 | 85 | 38 |  | 0.2 | 40.1 | 59.7 |  | 2.3 | 12.3 | 0.3 | 225.28 | 593 | 593 | 487.01 | 470.28 | 100.26 | 40.56 | 208.25 | [8 empty] | 695.56 | 24.04 | 0.72 | 0.5
27 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR012 | 1S-DL-YP-ETC-DNNG-2901-NGR012 | O-BLOCK SUNDER NAGARI:PL | TG-NGR012A-2 | 19503508 | 630 | 200 | 244 | 0.96 | 349 | 97 | 404 | 163 | 689 | 90 | 370 | 303 | 2019-06-10 22:30 | 92 | 38.2 | 700 | Y | 78 | 136 | 86 | 58 | 10 | 87.4 | 2.6 |  | 21.26 |  | 1 |  | 643.45 | 49 | 49 | 326.31 | 53.3 | 669.41 | 130.15 | 392.1 | [8 empty] | 718.41 | 1.19 | 0.73 | 0.55
28 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR013 | 1S-DL-YP-ETC-DNNG-2901-NGR013 | F-1 SUNDER NAGARI:ID | TG-NGR013A-1 | 19502685 | 990 | 320 | 237 | 0.97 | 627 | 196 | 820 | 227 | 950 | 203 | 859 | 115 | 2019-06-01 23:30 | 162.7 | 63.3 | 950 | Y | 97 | 103 | 100 | 6 |  |  | 12.6 | 87.4 |  |  |  |  | 202.24 | 84.05 | 84.05 | 131.37 | 514 | 632.19 | 564.17 | 584.47 | [8 empty] | 716.24 | 3.36 | 0.73 | 0.63
29 | 2019-06-28 12:00 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR013 | 1S-DL-YP-ETC-DNNG-2901-NGR013 | F-1 SUNDER NAGARI:ID | TG-NGR013A-2 | 19506932 | 990 | 320 | 240.6189 | 0.96961 | 688.2421 | 216.657 | 909.3302 | 193.065 | 813.0424 | 278.5201 | 1169.81 | 319.6906 | 2019-06-29 23:00 | [15 empty] | 0 |  |  |  | 0 |  |  |  | 60 |  |  |  | 0 |  |  |  | 0 | 60 |  | 0.8195 | 0.69519
30 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR014 | 1S-DL-YP-ETC-DNNG-2901-NGR014 | I.J K BLOCK SUNDER NAGARI:K | TG-NGR014A-1 | 19502680 | 990 | 320 | 235 | 0.96 | 876 | 267 | 1129 | 303 | 1289 | 306 | 1293 | 162 | 2019-06-11 23:00 | 243.6 | 106 | 1604 | B | 89 | 100 | 112 | 23 |  |  | 19.7 | 80.3 |  |  |  |  | 10.3 |  |  | 1.3 | 700.51 | 667.51 | 503.31 | 660.3 | 5.3 | 49 | 195.2 | 54.51 |  |  | 16.3 |  | 716.51 | 3.09 | 0.72 | 0.88
31 | 2019-06-18 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR014 | 1S-DL-YP-ETC-DNNG-2901-NGR014 | I.J K BLOCK SUNDER NAGARI:K | TG-NGR014A-2 | 19505808 | 990 | 320 | 237 | 0.96 | 719 | 227 | 956 | 213 | 906 | 279 | 1187 | 259 | 2019-06-28 23:30 | 224 | 90.6 | 1245 | B | 95 | 88 | 117 | 29 |  | 0.2 | 30.2 | 69.7 |  |  |  |  | 24 | 70 | 70 | 9.3 | 263.16 | 217.16 | 271.46 | 277.46 |  |  | 15 | [5 empty] | 287.16 | 24.44 | 0.72 | 0.73
32 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR015 | 1S-DL-YP-ETC-DNNG-2901-NGR015 | MN BLOCK SUNDER NAGARI:K | TG-NGR015A-1 | 19502676 | 630 | 200 | 244 | 0.96 | 287 | 68 | 281 | 121 | 503 | 99 | 413 | 194 | 2019-06-11 | 81 | 36.8 | 505 | Y | 78 | 116 | 106 | 38 |  |  |  | 100 | 48.3 |  |  | 1 | 669.34 | 432.17 | 432.17 | 652.39 |  | 285.47 | 127.55 | 64.25 | [8 empty] | 718.04 | 1.56 | 0.71 | 0.46
33 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR015 | 1S-DL-YP-ETC-DNNG-2901-NGR015 | MN BLOCK SUNDER NAGARI:K | TG-NGR015A-2 | 19506466 | 630 | 200 | 242 | 0.96 | 555 | 176 | 740 | 169 | 708 | 209 | 880 | 158 | 2019-06-11 | 173.2 | 61.2 | 908 | B | 99 | 90 | 111 | 21 | 1.5 | 0.6 | 19.8 | 78.1 |  |  |  |  | 2 | 28.3 | 28.3 | 3.3 | 688.34 | 660.39 | 537.1 | 663.09 | 4 | 5.25 | 154.24 | 27.55 |  |  | 1.3 |  | 694.34 | 25.26 | 0.71 | 0.88
34 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR015 | 1S-DL-YP-ETC-DNNG-2901-NGR015 | MN BLOCK SUNDER NAGARI:K | TG-NGR015A-3 | 19502650 | 630 | 200 | 238 | 0.96 | 332 | 106 | 453 | 87 | 376 | 139 | 605 | 202 | 2019-06-10 22:30 | 100.3 | 35 | 605 | B | 98 | 84 | 118 | 34 |  |  | 18.8 | 81.2 | 0.3 | 6 |  |  | 492.23 | 608.07 | 608.07 | 449.06 | 225.11 | 103.57 | 478.22 | 268.58 | [8 empty] | 718.04 | 1.56 | 0.72 | 0.53
35 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR016 | 1S-DL-YP-ETC-DNNG-2901-NGR016 | E-1 NAND NAGARI PK WALA GAGAN CINEMA:PL | TG-NGR016A-1 | 19505497 | 630 | 200 | 254 | 0.94 | 553 | 142 | 595 | 199 | 849 | 211 | 913 | 291 | 2019-06-14 16:00 | 211.6 | 28.6 | 913 | B | 78 | 107 | 115 | 37 | 0.1 | 12.2 | 72.5 | 15.2 | 134.17 |  |  |  | 9.3 | 14.3 | 14.3 | 13.3 | 552.27 | 642.22 | 599.22 | 675.52 |  | 39.22 | 92.52 | 6.52 |  |  | 1 |  | 696.14 | 23.46 | 0.66 | 0.88
36 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR017 | 1S-DL-YP-ETC-DNNG-2901-NGR017 | D-1 NAND NAGARI:PL | TG-NGR017A-1 | 19502692 | 630 | 200 | 234 | 0.96 | 444 | 161 | 700 | 153 | 670 | 130 | 564 | 123 | 2019-06-30 23:30 | 124.7 | 52 | 724 | R | 109 | 102 | 90 | 19 |  |  | 21.4 | 78.6 |  |  |  |  | 25.54 | 26.24 | 26.24 | 42.54 | 693.27 | 692.57 | 572.13 | 676.27 | [8 empty] | 719.21 | 0.39 | 0.73 | 0.7
37 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR017 | 1S-DL-YP-ETC-DNNG-2901-NGR017 | D-1 NAND NAGARI:PL | TG-NGR017A-2 | 19504693 | 630 | 200 | 241 | 0.95 | 367 | 126 | 529 | 89 | 368 | 153 | 647 | 243 | 2019-06-29 23:30 | 108.6 | 51.1 | 649 | B | 99 | 79 | 122 | 43 |  | 2 | 92.4 | 5.5 | 0.3 | 6 |  |  | 262.35 | 571.35 | 571.35 | 215.35 | 456.27 | 141.57 | 673.14 | 503.57 | [8 empty] | 719.32 | 0.28 | 0.74 | 0.58
38 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR018 | 1S-DL-YP-ETC-DNNG-2901-NGR018 | E-4 NAND NAGARI:ID | TG-NGR018A-1 | 19506221 | 630 | 200 | 243 | 0.96 | 635 | 234 | 1020 | 226 | 980 | 175 | 748 | 254 | 2019-06-08 00:30 | 228.8 | 58.8 | 1020 | R | 103 | 106 | 92 | 14 | 0.1 | 0.2 | 7.7 | 92 |  |  |  |  | 12.3 | 7.3 | 7.3 | 9 | 538.04 | 556.23 | 647.28 | 576.3 | 131.54 | 125.35 | 27.18 | 106.28 | 9.48 | 2.48 |  | 0.18 | 692.16 | 27.44 | 0.64 | 1.01
39 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR018 | 1S-DL-YP-ETC-DNNG-2901-NGR018 | E-4 NAND NAGARI:ID | TG-NGR018A-2 | 19506220 | 630 | 200 | 244 | 0.95 | 631 | 206 | 865 | 250 | 1067 | 175 | 740 | 285 | 2019-06-29 23:00 | 330.6 | 55.4 | 1067 | Y | 97 | 108 | 95 | 13 | 0.1 | 0.1 | 7.8 | 92 |  |  |  |  | 124.53 | 61.23 | 61.23 | 121.16 | 590.25 | 648.07 | 515.41 | 592.32 | 0.3 | 5.18 | 1 | 1.3 |  | 1 |  | 0.3 | 715.48 | 4.12 | 0.51 | 1
40 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR018 | 1S-DL-YP-ETC-DNNG-2901-NGR018 | E-4 NAND NAGARI:ID | TG-NGR018A-3 | 19506699 | 630 | 200 | 238 | 0.96 | 631 | 193 | 846 | 223 | 985 | 215 | 938 | 122 | 2019-06-08 21:00 | 233.6 | 59.6 | 985 | Y | 94 | 108 | 99 | 14 |  |  | 2.1 | 97.9 |  |  |  |  | 23.3 | 2 | 2 | 3.3 | 640.57 | 584.49 | 663.42 | 645.23 | 38.49 | 115.57 | 34.34 | 53.53 |  | 0.3 | 0.3 | 0.3 | 703.16 | 16.44 | 0.63 | 1
41 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR019 | 1S-DL-YP-ETC-DNNG-2901-NGR019 | JAGAT PURI EXT.NO.1:ID | TG-NGR019A-1 | 19505917 | 990 | 320 | 244 | 0.97 | 883 | 293 | 1205 | 340 | 1390 | 250 | 1017 | 323 | 2019-06-11 23:30 | 241 | 81.9 | 1450 | Y | 94 | 111 | 95 | 17 |  | 0.1 | 15.8 | 84.2 |  |  |  |  | 62.3 | 9.3 | 9.3 | 10 | 626.08 | 605.25 | 649.38 | 664.38 | 30.3 | 99.43 | 35.3 | 44.3 |  | 4.3 |  |  | 719.08 | 0.52 | 0.66 | 0.89
42 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR020 | 1S-DL-YP-ETC-DNNG-2901-NGR020 | JAGAT PURI EXT.NO.2:ID | TG-NGR020A-1 | 19502686 | 990 | 320 | 244 | 0.96 | 755 | 313 | 1292 | 265 | 1085 | 176 | 723 | 498 | 2019-06-11 23:00 | 181.8 | 68.4 | 1296 | R | 112 | 105 | 83 | 29 |  |  | 6.3 | 93.7 |  |  |  |  | 74.3 | 115.53 | 115.53 | 146.53 | 615.36 | 596.12 | 360.04 | 572.02 | 28.49 | 6.5 | [6 empty] | 718.55 | 1.05 | 0.65 | 0.76
43 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR021 | 1S-DL-YP-ETC-DNNG-2901-NGR021 | A-4 NAND NAGARI:ID | TG-NGR021A-1 | 19504975 | 630 | 200 | 240 | 0.96 | 460 | 204 | 858 | 127 | 543 | 129 | 565 | 304 | 2019-06-30 23:00 | 110.4 | 48.3 | 863 | R | 125 | 79 | 97 | 46 | 94.1 | 5.9 | [6 empty] | 9 | 413.06 | 413.06 | 82.09 | 635.39 | 303.03 | 581.41 | 634 | 71.3 | [7 empty] | 716.09 | 3.51 | 0.69 | 0.73
44 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR021 | 1S-DL-YP-ETC-DNNG-2901-NGR021 | A-4 NAND NAGARI:ID | TG-NGR021A-2 | 19505803 | 990 | 320 | 240 | 0.96 | 789 | 315 | 1331 | 214 | 890 | 259 | 1077 | 384 | 2019-06-30 00:30 | 300.2 | 85.8 | 1385 | R | 117 | 87 | 96 | 30 |  | 0.5 | 68.1 | 31.4 |  |  |  |  | 11 | 98.23 | 98.23 | 28.59 | 604.49 | 617.47 | 655.47 | 687.11 | 100.21 |  | 1 | [5 empty] | 716.1 | 3.5 | 0.7 | 0.8
45 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR021 | 1S-DL-YP-ETC-DNNG-2901-NGR021 | A-4 NAND NAGARI:ID | TG-NGR021A-3 | 19505342 | 990 | 320 | 229 | 0.97 | 805 | 313 | 1442 | 167 | 758 | 325 | 1463 | 695 | 2019-06-14 15:00 | 264 | 79.4 | 1467 | B | 103 | 94 | 103 | 9 |  | 0.4 | 53.4 | 46.2 |  |  |  |  | 20 | 47.3 | 47.3 | 17 | 669.46 | 645.16 | 678.46 | 674.46 | 3 |  | 1.3 | 1 |  |  |  |  | 692.46 | 27.14 | 0.69 | 0.81
46 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR022 | 1S-DL-YP-ETC-DNNG-2901-NGR022 | B-4 NAND NAGARI AKHADA WALA :ID | TG-NGR022A-1 | 19502143 | 990 | 320 | 240 | 0.96 | 592 | 216 | 911 | 209 | 872 | 166 | 687 | 207 | 2019-06-29 23:30 | 187.7 | 64.8 | 936 | Y | 108 | 107 | 85 | 23 |  | 7.1 | 87.8 | 5.1 |  |  | 1.3 |  | 234.53 | 236.53 | 236.53 | 333.53 | 483.52 | 481.52 | 172.29 | 384.52 | [8 empty] | 718.45 | 1.15 | 0.69 | 0.6
47 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR022 | 1S-DL-YP-ETC-DNNG-2901-NGR022 | B-4 NAND NAGARI AKHADA WALA :ID | TG-NGR022A-2 | 19503369 | 990 | 200 | 248 | 0.95 | 683 | 203 | 837 | 218 | 895 | 262 | 1081 | 221 | 2019-06-30 23:30 | 245.6 | 82.3 | 1087 | B | 92 | 97 | 111 | 19 |  | 0.1 | 5.7 | 94.2 |  |  |  |  | 196.45 | 141.51 | 141.51 | 112.21 | 522.03 | 576.57 | 666.25 | 606.27 | [8 empty] | 718.48 | 1.12 | 0.71 | 0.69
48 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR022 | 1S-DL-YP-ETC-DNNG-2901-NGR022 | B-4 NAND NAGARI AKHADA WALA :ID | TG-NGR022A-3 | 19505435 | 630 | 200 | 246 | 0.95 | 526 | 168 | 704 | 216 | 913 | 142 | 586 | 287 | 2019-06-01 23:00 | 192.6 | 57.2 | 913 | Y | 94 | 120 | 86 | 34 | 0.3 | 24.1 | 72.5 | 3.1 |  |  |  |  | 173.26 | 26.3 | 26.3 | 106.56 | 545.19 | 629.33 | 500.33 | 611.2 |  | 62.13 |  | 0.29 |  | 0.29 |  |  | 718.45 | 1.15 | 0.61 | 0.84
49 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR022 | 1S-DL-YP-ETC-DNNG-2901-NGR022 | B-4 NAND NAGARI AKHADA WALA :ID | TG-NGR022A-4 | 19506004 | 630 | 200 | 234 | 0.96 | 501 | 170 | 725 | 194 | 839 | 137 | 598 | 209 | 2019-06-29 23:30 | 168 | 50.8 | 839 | Y | 105 | 108 | 86 | 22 |  | 11.3 | 84.9 | 3.9 |  |  |  |  | 4 | 7.3 | 7.3 | 12.3 | 691.32 | 663.32 | 572.34 | 684.02 | 1 | 25.3 | [6 empty] | 696.32 | 23.28 | 0.71 | 0.8
50 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR023 | 1S-DL-YP-ETC-DNNG-2901-NGR023 | C BLOCK COMPLAINT CENTRE NNG:ID | TG-NGR023A-1 | 19502651 | 990 | 320 | 240 | 0.95 | 609 | 204 | 855 | 223 | 949 | 182 | 763 | 161 | 2019-06-29 23:30 | 190.6 | 87.6 | 982 | Y | 103 | 107 | 90 | 17 |  |  | 45 | 55 |  |  |  |  | 84.55 | 107.23 | 107.23 | 158.23 | 634.22 | 611.54 | 425.06 | 560.54 | [8 empty] | 719.17 | 0.43 | 0.75 | 0.62
51 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR023 | 1S-DL-YP-ETC-DNNG-2901-NGR023 | C BLOCK COMPLAINT CENTRE NNG:ID | TG-NGR023A-2 | 19505918 | 990 | 320 | 228 | 0.96 | 869 | 296 | 1316 | 280 | 1250 | 294 | 1294 | 59 | 2019-06-30 | 291.2 | 85.4 | 1335 | B | 97 | 98 | 104 | 7 |  |  | 39.8 | 60.2 |  |  |  |  | 59.39 | 41.04 | 41.04 | 22 | 654.52 | 674.57 | 693.39 | 693.01 | 3.3 | 2 | 13.22 | 3 |  |  |  |  | 718.01 | 1.59 | 0.64 | 0.88
52 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR023 | 1S-DL-YP-ETC-DNNG-2901-NGR023 | C BLOCK COMPLAINT CENTRE NNG:ID | TG-NGR023A-3 | 19502635 | 630 | 200 | 244 | 0.96 | 585 | 203 | 838 | 197 | 805 | 185 | 766 | 63 | 2019-06-29 23:30 | 146.3 | 62.1 | 887 | R | 108 | 100 | 92 | 16 |  | 0 | 77.9 | 22.1 |  |  |  |  | 4.3 | 28 | 28 | 19.3 | 584.11 | 596.32 | 633.06 | 617.32 | 127.5 | 93.29 | 19 | 80.59 | 1.3 |  |  |  | 718.01 | 1.59 | 0.67 | 0.93
53 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR023 | 1S-DL-YP-ETC-DNNG-2901-NGR023 | C BLOCK COMPLAINT CENTRE NNG:ID | TG-NGR023A-4 | 19505379 | 630 | 200 | 234 | 0.97 | 431 | 140 | 615 | 101 | 436 | 191 | 837 | 348 | 2019-06-11 22:30 | 150.6 | 42.6 | 844 | B | 105 | 82 | 113 | 31 |  | 0.1 | 40.8 | 59.1 |  |  |  |  | 31 | 294.23 | 294.23 | 70.25 | 664.47 | 401.24 | 647.47 | 625.22 |  |  | 10 | [5 empty] | 695.47 | 24.13 | 0.72 | 0.68
54 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR024 | 1S-DL-YP-ETC-DNNG-2901-NGR024 | SCHOOL BLOCK NATHU COL.:ID | TG-NGR024A-1 | 19503601 | 630 | 200 | 238 | 0.97 | 392 | 113 | 478 | 124 | 527 | 155 | 639 | 143 | 2019-06-11 23:00 | 91.1 | 24.4 | 707 | B | 100 | 86 | 115 | 29 | 87.3 | 12.7 | [6 empty] | 94.03 | 439.01 | 439.01 | 109.24 | 623.51 | 278.53 | 687.24 | 608.3 | [8 empty] | 717.54 | 2.06 | 0.74 | 0.62
55 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR024 | 1S-DL-YP-ETC-DNNG-2901-NGR024 | SCHOOL BLOCK NATHU COL.:ID | TG-NGR024A-2 | 19502137 | 630 | 200 | 239 | 0.98 | 219 | 100 | 422 | 58 | 244 | 61 | 256 | 173 | 2019-06-28 18:30 | 58 | -11 | 453 | R | 120 | 76 | 104 | 44 |  |  | 43.6 | 56.4 | 128.19 | 511.06 | 78.08 | 182.49 | 536.41 | 206.47 | 206.47 | 535.04 | 52.53 | [11 empty] | 717.53 | 2.07 | 0.67 | 0.35
56 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR025 | 1S-DL-YP-ETC-DNNG-2901-NGR025 | KACHHI PURA VILLAGE:PL | TG-NGR025A-1 | 19505515 | 630 | 200 | 245 | 0.97 | 298 | 70 | 291 | 58 | 237 | 170 | 710 | 448 | 2019-06-15 09:00 | 107.8 | 17.8 | 710 | B | 110 | 97 | 93 | 17 | 0.6 | 7.1 | 47.6 | 44.7 |  | 2.3 | 5.3 |  | 496.41 | 627.05 | 627.05 | 654.39 | 208.29 | 75.35 | 30.1 | 50.31 |  |  | 1 | [5 empty] | 705.1 | 14.5 | 0.72 | 0.47
57 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR027 | 1S-DL-YP-ETC-DNNG-2901-NGR027 | MANDOLI S/S-1 (KIOSK) :K | TG-NGR027A-1 | 19505677 | 630 | 200 | 239 | 0.99 | 366 | 128 | 540 | 113 | 477 | 125 | 526 | 57 | 2019-06-13 15:00 | 150.8 | -10 | 576 | R | 105 | 87 | 108 | 21 |  |  | 9.9 | 90.1 | 182.3 | 371.14 | 172.15 | 258 | 385.48 | 220.27 | 220.27 | 314.12 | 146.26 | 123.03 | 168.32 | 142.32 | [8 empty] | 714.44 | 5.16 | 0.47 | 0.58
58 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR028 | 1S-DL-YP-ETC-DNNG-2901-NGR028 | MANDOLI S/S-2 (RATAN WALA) :PL | TG-NGR028A-1 | 19505303 | 990 | 200 | 227 | 0.98 | 629 | 122 | 556 | 262 | 1204 | 245 | 1127 | 613 | 2019-06-02 16:30 | 322.2 | -3 | 1226 | Y | 31 | 137 | 132 | 106 | 13.3 | 3.7 | 23.8 | 59.2 | 463.39 | 40.3 | 1 | 20.3 | 145.38 | 113.17 | 113.17 | 385.52 |  | 452.3 | 467.2 | 202.55 |  | 3 | [6 empty] | 691.31 | 28.29 | 0.58 | 0.64
59 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR029 | 1S-DL-YP-ETC-DNNG-2901-NGR029 | MANDOLI S/S-3 (SHANTI LAL) :PL | TG-NGR029A-1 | 19506609 | 990 | 320 | 246 | 0.99 | 602 | 199 | 821 | 185 | 760 | 217 | 896 | 118 | 2019-06-28 12:00 | 208.3 | -103 | 896 | B | 105 | 87 | 108 | 21 | 0.1 |  | 8.3 | 91.6 | 303.36 | 387.04 | 334.35 | 353.35 | 262.31 | 213.52 | 213.52 | 214.19 | 125.2 | 90.31 | 148.3 | 123.33 | [8 empty] | 691.27 | 28.33 | 0.41 | 0.61
60 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR030 | 1S-DL-YP-ETC-DNNG-2901-NGR030 | MANDOLI S/S-4 (PANI KI TANKI) :PL | TG-NGR030A-1 | 19506090 | 990 | 320 | 244 | 0.97 | 838 | 282 | 1137 | 252 | 1014 | 305 | 1235 | 192 | 2019-06-12 01:00 | 209 | 73.3 | 1254 | B | 105 | 94 | 101 | 11 |  |  | 3.8 | 96.2 |  |  |  |  | 15 | 45 | 45 | 24.3 | 665.49 | 639.4 | 634.12 | 658.39 | 3.51 |  | 12.28 | 1.31 |  |  |  |  | 684.4 | 35.2 | 0.65 | 0.85
61 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR030 | 1S-DL-YP-ETC-DNNG-2901-NGR030 | MANDOLI S/S-4 (PANI KI TANKI) :PL | TG-NGR030A-2 | 19506385 | 400 | 120 | 252 | 0.97 | 235 | 84 | 337 | 88 | 352 | 63 | 251 | 94 | 2019-06-13 10:00 | 84.6 | -85.4 | 381 | Y | 94 | 125 | 82 | 43 |  | 0.3 | 20.6 | 79.1 | 354.14 | 19 | 341.15 | 186.21 | 180.46 | 476.37 | 476.37 | 387.19 | 152.31 | 191.54 | 45.2 | 113.51 | [8 empty] | 687.31 | 32.29 | 0.47 | 0.59
62 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR031 | 1S-DL-YP-ETC-DNNG-2901-NGR031 | SABOLI VILL S/S NO.1(RAILWAY PHATAK):PL | TG-NGR031A-1 | 19506091 | 990 | 200 | 241 | 0.98 | 508 | 153 | 642 | 176 | 736 | 179 | 758 | 107 | 2019-06-13 11:30 | 181.8 | 10.2 | 798 | B | 91 | 100 | 109 | 18 | 0.1 | 7.8 | 81.7 | 10.4 | 4 | 1.3 |  |  | 573.54 | 460.19 | 460.19 | 505.4 | 27.47 | 143.52 | 209.57 | 100.01 | [8 empty] | 685.14 | 34.46 | 0.69 | 0.51
63 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR032 | 1S-DL-YP-ETC-DNNG-2901-NGR032 | SABOLI VILL S/S NO.2( NATHU PRADHAN):PL | TG-NGR032A-1 | 19502968 | 630 | 200 | 240 | 0.98 | 450 | 168 | 722 | 137 | 589 | 145 | 622 | 121 | 2019-06-28 15:30 | 109.9 | 0.9 | 722 | R | 107 | 107 | 86 | 21 |  |  | 35.1 | 64.9 |  |  | 0.3 |  | 37.02 | 45.02 | 45.02 | 91.15 | 671.28 | 663.58 | 385.31 | 617.45 | 0.3 | [7 empty] | 709 | 11 | 0.69 | 0.71
64 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR035 | 1S-DL-YP-ETC-DNNG-2901-NGR035 | MANDOLI EXTN.NO.1,GALI NO.-9:ID | TG-NGR035A-1 | 19502142 | 400 | 120 | 238 | 0.97 | 388 | 155 | 702 | 116 | 521 | 117 | 524 | 179 | 2019-06-02 21:30 | 72 | 27.6 | 741 | R | 112 | 95 | 93 | 19 |  | 0.1 | 14.8 | 85.1 |  |  | 0.3 |  | 1 | 23 | 23 | 12 | 578.29 | 659.16 | 652.16 | 657.13 | 97.17 | 11.3 | 7.3 | 24.33 | 17 |  |  |  | 715.07 | 4.53 | 0.6 | 0.97
65 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR035 | 1S-DL-YP-ETC-DNNG-2901-NGR035 | MANDOLI EXTN.NO.1,GALI NO.-9:ID | TG-NGR035A-2 | 19506611 | 990 | 320 | 238 | 0.97 | 874 | 307 | 1305 | 236 | 996 | 331 | 1418 | 378 | 2019-06-10 22:00 | 263.7 | 6.4 | 1469 | B | 109 | 83 | 108 | 26 |  | 1.1 | 28.4 | 70.4 | 0.3 | 0.3 | 0.3 | 0.3 |  | 72 | 72 | 0.3 | 634.28 | 619.27 | 626.14 | 677.4 | 56.59 |  | 64.43 | 13.17 |  |  | 0.3 |  | 691.57 | 28.03 | 0.66 | 0.88
66 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR036 | 1S-DL-YP-ETC-DNNG-2901-NGR036 | MANDOLI EXT.NO1 GALI NO 12:ID | TG-NGR036A-1 | 19505214 | 990 | 320 | 256 | 0.95 | 759 | 292 | 1179 | 195 | 776 | 272 | 1098 | 368 | 2019-06-25 18:00 | 281.9 | 111 | 1179 | R | 114 | 78 | 108 | 36 |  | 0.2 | 16.2 | 83.5 |  |  |  |  | 1 | 381.17 | 381.17 | 25 | 669.25 | 307.5 | 678.37 | 664.07 | 18.42 |  | 0.3 | [5 empty] | 689.07 | 30.53 | 0.67 | 0.77
67 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR039 | 1S-DL-YP-ETC-DNNG-2901-NGR039 | ST LTG GAGAN CINEMA WAZIRABAD RD:PM | TG-NGR039A-1 | 19505418 | 400 | 120 | 247 | 0.92 | 227 | 117 | 486 | 109 | 473 | 1 | 4 | 475 | 2019-06-09 09:00 | 166.3 | -0.4 | 486 | R | 135 | 76 | 89 | 59 | 98.9 | 0.8 | 0.3 |  | 617.17 | 629.47 | 629.47 | 626.17 | 59.4 | 56.1 | 56.1 | 58.4 | 15 | 6 | 6.3 | 7.3 | 0.3 | 0.3 | [6 empty] | 692.27 | 27.33 | 0.16 | 0.57
68 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR040 | 1S-DL-YP-ETC-DNNG-2901-NGR040 | A-1NAND NAGRI:PM | TG-NGR040A-1 | 19503387 | 630 | 200 | 238 | 0.96 | 341 | 109 | 461 | 146 | 624 | 86 | 362 | 229 | 2019-06-29 23:30 | 98 | 34 | 645 | Y | 96 | 127 | 77 | 50 |  |  | 17.6 | 82.4 | 1.3 | 1 | 16 | 1 | 497.08 | 96.48 | 96.48 | 429.32 | 218.13 | 619.03 | 6 | 286.19 | [8 empty] | 716.51 | 3.09 | 0.72 | 0.54
69 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR041 | 1S-DL-YP-ETC-DNNG-2901-NGR041 | POCKET-C GTB ENCLAVE:PM | TG-NGR041A-1 | 19506690 | 400 | 120 | 237 | 0.96 | 322 | 98 | 427 | 106 | 472 | 118 | 528 | 88 | 2019-06-18 20:00 | 82.1 | 19 | 528 | B | 86 | 109 | 105 | 23 |  | 2.2 | 72.2 | 25.6 | 58.2 | 12.3 | 4.39 | 7.5 | 420.46 | 318.06 | 318.06 | 384.16 | 216.3 | 363 | 340.59 | 303 |  | 2 | 1 | 0.3 |  |  |  |  | 695.36 | 24.24 | 0.5 | 0.81
70 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR042 | 1S-DL-YP-ETC-DNNG-2901-NGR042 | MIG S/STN NO-1 GTB ENCLAVE F POCKET:ID | TG-NGR042A-1 | 19502669 | 630 | 200 | 241 | 0.96 | 285 | 69 | 305 | 113 | 503 | 102 | 453 | 179 | 2019-06-11 | 67.2 | 8.7 | 503 | Y | 85 | 105 | 110 | 25 |  |  | 2.6 | 97.4 | 366.47 | 251.54 | 223.53 | 260.24 | 352.59 | 404.22 | 404.22 | 428.22 |  | 63.3 | 90.3 | 31 | [8 empty] | 719.46 | 0.14 | 0.53 | 0.45
71 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR042 | 1S-DL-YP-ETC-DNNG-2901-NGR042 | MIG S/STN NO-1 GTB ENCLAVE F POCKET:ID | TG-NGR042A-2 | 19502663 | 630 | 200 | 241 | 0.97 | 188 | 50 | 202 | 59 | 241 | 79 | 323 | 106 | 2019-06-29 17:00 | 54.3 | 9.2 | 386 | B | 87 | 91 | 122 | 35 |  |  | 0.1 | 99.9 | 632.16 | 499.16 | 248.46 | 421.16 | 87.3 | 220.3 | 220.3 | 298.3 |  |  | 3 | [9 empty] | 719.46 | 0.14 | 0.63 | 0.3
72 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR043 | 1S-DL-YP-ETC-DNNG-2901-NGR043 | SAFAI KARA. SUNDER NAGRI-L BLOCK: ID | TG-NGR043A-1 | 19505971 | 400 | 120 | 246 | 0.94 | 113 | 52 | 209 | 22 | 87 | 39 | 159 | 106 | 2019-06-12 | 39.2 | 11.8 | 223 | R | 138 | 56 | 107 | 82 |  | 0.1 | 22.7 | 77.2 | 143 | 718.26 | 383.34 | 467.04 | 576.26 | 1 | 1 | 252.22 | [12 empty] | 719.26 | 0.34 | 0.66 | 0.28
73 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR044 | 1S-DL-YP-ETC-DNNG-2901-NGR044 | SAFAI KARAMCHARI NAND NAGARI-E BLK:ID | TG-NGR044A-1 | 19503383 | 400 | 120 | 235 | 0.97 | 336 | 112 | 500 | 124 | 549 | 100 | 445 | 90 | 2019-06-09 23:00 | 70.7 | 21 | 559 | R | 107 | 109 | 84 | 25 | 0.1 |  | 2.4 | 97.5 |  |  | 8.3 | 1 | 115.28 | 143.28 | 143.28 | 168.58 | 556 | 470.3 | 371.3 | 521 | 48.3 | 106 |  | 29 |  |  |  |  | 719.58 | 0.02 | 0.62 | 0.84
74 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR050 | 1S-DL-YP-ETC-DNNG-2901-NGR050 | JAIL ROAD PWD(WAZIRABAD ROAD):PM | TG-NGR050A-1 | 19506235 | 400 | 120 | 246 | 0.86 | 401 | 140 | 581 | 136 | 583 | 124 | 564 | 17 | 2019-06-18 18:30 | 343.3 | -21.4 | 583 | Y | 101 | 96 | 102 | 6 | 100 |  |  |  | 408.04 | 441.26 | 441.04 | 438.04 | 165.18 | 163.3 | 163.3 | 155.59 | 111.55 | 81.21 | 79.05 | 92.14 | 1 |  | 1 |  | 0.3 | 0.3 |  | 0.3 | 686.47 | 33.13 | 0.21 | 1
75 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR051 | 1S-DL-YP-ETC-DNNG-2901-NGR051 | K BLOCK SAFAI KARAMCHARI SUNDERI NAGARI | TG-NGR051A-1 | 19504767 | 630 | 200 | 239 | 0.96 | 183 | 59 | 241 | 66 | 274 | 58 | 240 | 34 | 2019-06-11 22:00 | 49.7 | 16.6 | 292 | Y | 101 | 109 | 90 | 19 |  |  | 5.1 | 94.9 | 406.23 | 327.41 | 485.4 | 420.4 | 313.03 | 391.45 | 391.45 | 298.46 | [12 empty] | 719.26 | 0.34 | 0.66 | 0.29
76 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR052 | 1S-DL-YP-ETC-DNNG-2901-NGR052 | D1 SAFAI KARMCHARI NNG-1:ID | TG-NGR052A-1 | 19502691 | 400 | 120 | 243 | 0.97 | 49 | 23 | 94 | 17 | 73 | 9 | 39 | 48 | 2019-06-11 23:00 | 11.6 | 1.1 | 96 | R | 124 | 99 | 76 | 48 |  |  | 36.1 | 63.9 | 719.44 | 719.44 | 719.44 | 719.44 | [16 empty] | 719.44 | 0.16 | 0.6 | 0.12
77 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR052 | 1S-DL-YP-ETC-DNNG-2901-NGR052 | D1 SAFAI KARMCHARI NNG-1:ID | TG-NGR052A-2 | 19504785 | 400 | 120 | 243 | 0.98 | 109 | 51 | 209 | 52 | 217 | 6 | 25 | 189 | 2019-06-29 23:30 | 27.6 | 5 | 228 | Y | 136 | 148 | 15 | 133 |  | 15.2 | 83.3 | 1.5 | 322.13 | 219.58 | 719.43 | 530.13 | 397.3 | 498.45 | 498.45 | 189.3 |  | 1 | [10 empty] | 719.43 | 0.17 | 0.6 | 0.27
78 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR053 | 1S-DL-YP-ETC-DNNG-2901-NGR053 | D1 SAFAI KARMCHARI NNG-2:ID | TG-NGR053A-1 | 19504504 | 400 | 120 | 244 | 0.27 | 8 | 0 | 0 | 8 | 31 | 0 | 0 | 31 | 2019-06-27 21:30 | -0.3 | -7.7 | 31 | Y | 0 | 300 | 0 | 300 |  |  | 62.7 | 37.3 | 719.43 | 719.43 | 719.43 | 719.43 | [16 empty] | 719.43 | 0.17 | 0.21 | 0.02
79 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR054 | 1S-DL-YP-ETC-DNNG-2901-NGR054 | BANK OF BARODA | TG-NGR054A-1 | 19502442 | 990 | 320 | 245 | 0.97 | 559 | 202 | 830 | 152 | 619 | 205 | 844 | 218 | 2019-06-13 16:30 | 158.2 | 16.9 | 880 | R | 113 | 79 | 108 | 34 |  |  | 4.6 | 95.4 | 1 | 37 | 4 | 6 | 279.11 | 627.39 | 627.39 | 463.57 | 419.1 | 34.42 | 346.46 | 229.24 | [8 empty] | 699.21 | 20.39 | 0.65 | 0.56
80 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR094 | 1S-DL-YP-ETC-DNNG-2901-NGR094 | Police Housing Complex S/Stn No.1 | TG-NGR094A-1 | 19506086 | 630 | 200 | 248 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [5 empty] | 1.2 | 9.4 | 47.9 | 41.6 | 693.53 | 693.53 | 693.53 | 693.53 | [16 empty] | 693.53 | 26.07 |  | 0
81 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR094 | 1S-DL-YP-ETC-DNNG-2901-NGR094 | Police Housing Complex S/Stn No.1 | TG-NGR094A-2 | 19506087 | 630 | 200 | 247 | 0.96 | 33 | 27 | 108 | 3 | 11 | 3 | 13 | 96 | 2019-06-02 | 10.6 | 0.6 | 111 | R | 265 | 18 | 17 | 248 |  |  | 2.2 | 97.8 | 693.53 | 693.53 | 693.53 | 693.53 | [16 empty] | 693.53 | 26.07 | 0.46 | 0.05
82 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR095 | 1S-DL-YP-ETC-DNNG-2901-NGR095 | Police Housing Complex S/Stn No.2 | TG-NGR095A-1 | 19506088 | 630 | 200 | 248 | 0.95 | 17 | 4 | 16 | 4 | 15 | 9 | 38 | 23 | 2019-06-30 23:00 | 6.4 | 0.2 | 39 | Y | 102 | 110 | 88 | 22 |  |  | 0.6 | 99.4 | 694.39 | 694.39 | 694.39 | 694.39 | [16 empty] | 694.39 | 25.21 | 0.53 | 0.03
83 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR095 | 1S-DL-YP-ETC-DNNG-2901-NGR095 | Police Housing Complex S/Stn No.2 | TG-NGR095A-2 | 19506089 | 630 | 200 | 248 | 0.96 | 29 | 18 | 72 | 1 | 3 | 10 | 41 | 59 | 2019-06-21 22:30 | 9 | -0.6 | 72 | R | 153 | 13 | 134 | 140 |  |  | 1.1 | 98.9 | 694.39 | 694.39 | 694.39 | 694.39 | [16 empty] | 694.39 | 25.21 | 0.43 | 0.05
84 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1001 | 1S-DL-YP-ETC-DNNG-2902-LO1001 | A-BLOCK MEET NAGAR:ID | TG-LO1001A-1 | 19502169 | 990 | 320 | 234 | 0.97 | 736 | 178 | 795 | 267 | 1189 | 290 | 1311 | 467 | 2019-06-11 22:30 | 181.1 | 44.2 | 1311 | B | 82 | 87 | 130 | 48 |  | 0.6 | 76.8 | 22.5 | 6 | 18.38 |  |  | 512.33 | 434.34 | 434.34 | 278.22 | 186.18 | 249.14 | 637.02 | 426.29 |  | 2.25 | 7.19 | [5 empty] | 704.51 | 15.09 | 0.58 | 0.74
85 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1001 | 1S-DL-YP-ETC-DNNG-2902-LO1001 | A-BLOCK MEET NAGAR:ID | TG-LO1001A-2 | 19505752 | 630 | 200 | 235 | 0.97 | 467 | 121 | 544 | 135 | 601 | 212 | 971 | 402 | 2019-06-10 23:00 | 169.2 | 21.8 | 971 | B | 87 | 97 | 116 | 29 | 0.8 | 7.7 | 77.3 | 14.2 | 8.3 | 4.39 |  |  | 497.2 | 368.47 | 368.47 | 352.59 | 199.38 | 332.02 | 476.33 | 352.29 |  |  | 5.2 |  |  |  | 0.3 |  | 705.28 | 14.32 | 0.56 | 0.74
86 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1002 | 1S-DL-YP-ETC-DNNG-2902-LO1002 | B-BLOCK MEET NAGAR:ID | TG-LO1002A-1 | 19505636 | 990 | 320 | 244.1688 | 0.95936 | 968.3635 | 239.9317 | 1005.9609 | 421.3517 | 1775.2335 | 307.0801 | 1288.0338 | 674.0583 | 2019-06-11 01:00 | [15 empty] | 0 |  |  |  | 29.5 |  |  |  | 661 |  |  |  | 15 |  |  |  | 0 | 705.5 |  | 0.58121 | 0.97814
87 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1002 | 1S-DL-YP-ETC-DNNG-2902-LO1002 | B-BLOCK MEET NAGAR:ID | TG-LO1002A-2 | 19502162 | 990 | 320 | 245 | 0.96 | 754 | 223 | 923 | 282 | 1169 | 249 | 1024 | 214 | 2019-06-29 23:30 | 220.8 | 55.9 | 1173 | Y | 85 | 112 | 102 | 27 |  |  | 12.5 | 87.5 | 13.3 | 0.3 | 1 | 3 | 517.34 | 249.24 | 249.24 | 380.21 | 167.01 | 443.13 | 349.24 | 314.44 |  | 4.58 | [6 empty] | 698.05 | 21.55 | 0.53 | 0.76
88 | 2019-06-12 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1003 | 1S-DL-YP-ETC-DNNG-2902-LO1003 | HARIJAN BASTI AMAR CLY BHUSA WALA:PL | TG-LO1003A-1 | 19502170 | 630 | 200 | 246 | 0.96 | 110 | 34 | 138 | 42 | 169 | 33 | 135 | 33 | 2019-06-26 18:30 | 36.3 | 8.7 | 185 | Y | 98 | 120 | 82 | 38 | 0.1 | 2.6 | 76.1 | 21.2 | 441.4 | 440.15 | 442.1 | 442.1 | 0.3 | 1.55 | 1.55 | [13 empty] | 442.1 | 13.5 | 0.61 | 0.17
89 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1004 | 1S-DL-YP-ETC-DNNG-2902-LO1004 | HARIJAN BASTI BURFKHANA:K | TG-LO1004A-1 | 19503452 | 630 | 200 | 236 | 0.98 | 367 | 114 | 499 | 159 | 699 | 94 | 412 | 255 | 2019-06-29 15:30 | 88.3 | 6.4 | 699 | Y | 96 | 132 | 72 | 60 |  |  | 5.8 | 94.2 | 20.3 |  | 137.3 | 8 | 492.22 | 148 | 148 | 479.02 | 205.44 | 570.36 | 32.47 | 231.34 | [8 empty] | 718.36 | 1.24 | 0.63 | 0.58
90 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1004 | 1S-DL-YP-ETC-DNNG-2902-LO1004 | HARIJAN BASTI BURFKHANA:K | TG-LO1004A-2 | 19505666 | 630 | 200 | 243 | 0.99 | 342 | 120 | 497 | 140 | 578 | 82 | 340 | 210 | 2019-06-14 15:30 | 110.2 | -15.2 | 579 | Y | 105 | 122 | 73 | 49 | 0.1 | 0.1 | 0.2 | 99.6 | 332.45 | 71 | 424.21 | 325.16 | 160.3 | 398.15 | 398.15 | 231.53 | 202.17 | 226.17 | 9.3 | 138.23 | [8 empty] | 695.32 | 24.28 | 0.5 | 0.54
91 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1005 | 1S-DL-YP-ETC-DNNG-2902-LO1005 | HARIJAN BASTI G PUR(BHAWANI WALA):PL | TG-LO1005A-1 | 19506879 | 630 | 200 | 246 | 0.97 | 111 | 33 | 141 | 59 | 255 | 19 | 78 | 155 | 2019-06-11 01:00 | 33.2 | 0.2 | 260 | Y | 96 | 132 | 72 | 60 | 0.1 | 4.6 | 80.5 | 14.8 | 677.42 | 644 | 677.42 | 677.42 |  | 33.42 | 33.42 | [13 empty] | 677.42 | 42.18 | 0.6 | 0.18
92 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1008 | 1S-DL-YP-ETC-DNNG-2902-LO1008 | GOKUL PUR VILLAGE NO.2(NEHAR WALA):K | TG-LO1008A-1 | 19505757 | 990 | 320 | 243 | 0.97 | 707 | 258 | 1102 | 224 | 953 | 226 | 958 | 146 | 2019-06-22 17:00 | 250.9 | -24 | 1141 | R | 121 | 84 | 95 | 37 | 0.1 |  | 25 | 75 | 9.3 | 284.3 | 185 | 86.3 | 396.3 | 256.18 | 256.18 | 383.06 | 311.37 | 177.19 | 248.27 | 248.31 | 0.3 | [7 empty] | 718.07 | 1.53 | 0.48 | 0.71
93 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1008 | 1S-DL-YP-ETC-DNNG-2902-LO1008 | GOKUL PUR VILLAGE NO.2(NEHAR WALA):K | TG-LO1008A-2 | 19506231 | 990 | 320 | 242 | 0.97 | 621 | 197 | 852 | 237 | 1022 | 187 | 801 | 200 | 2019-06-29 11:00 | 223.7 | -20.8 | 1022 | Y | 98 | 110 | 92 | 18 | 1 |  | 13.5 | 85.5 | 282.28 | 259.18 | 322.18 | 287.18 | 220.42 | 192.52 | 192.52 | 198.52 | 191.44 | 242.44 | 148.49 | 208.44 | [8 empty] | 694.54 | 25.06 | 0.47 | 0.63
94 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1008 | 1S-DL-YP-ETC-DNNG-2902-LO1008 | GOKUL PUR VILLAGE NO.2(NEHAR WALA):K | TG-LO1008A-3 | 19506232 | 630 | 200 | 248 | 0.97 | 546 | 173 | 723 | 177 | 736 | 195 | 808 | 80 | 2019-06-07 15:30 | 139.8 | -4 | 808 | B | 96 | 96 | 108 | 12 |  | 0.1 | 11.7 | 88.2 | 45.3 | 23.3 | 32.3 | 32 | 367.42 | 399.1 | 399.1 | 368.12 | 277.29 | 268.01 | 317.53 | 290.29 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | 691.11 | 28.49 | 0.45 | 0.87
95 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1009 | 1S-DL-YP-ETC-DNNG-2902-LO1009 | GOKUL PUR VILL NO.KAPOOR WALA PETROL:PL | TG-LO1009A-1 | 19506309 | 990 | 320 | 240 | 0.98 | 770 | 234 | 1015 | 265 | 1151 | 271 | 1170 | 146 | 2019-06-26 15:30 | 251.5 | -113.9 | 1206 | B | 96 | 102 | 102 | 6 | 0.1 | 0.4 | 32.3 | 67.3 | 3.3 | 4 | 5 | 3.3 | 387.54 | 371.54 | 371.54 | 387.54 | 302.1 | 315.1 | 295.4 | 302.1 |  | 2.3 | 5 | [5 empty] | 693.34 | 26.26 | 0.55 | 0.78
96 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1009 | 1S-DL-YP-ETC-DNNG-2902-LO1009 | GOKUL PUR VILL NO.KAPOOR WALA PETROL:PL | TG-LO1009A-2 | 19500607 | 630 | 200 | 243.115 | 0.97981 | 307.7469 | 80.2314 | 342.3281 | 137.0345 | 586.4193 | 90.481 | 387.2003 | 225.0358 | 2019-06-29 14:00 | [15 empty] | 241 |  |  |  | 399 |  |  |  | 78 |  |  |  | 0 |  |  |  | 0 | 718 |  | 0.54242 | 0.48849
97 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1009 | 1S-DL-YP-ETC-DNNG-2902-LO1009 | GOKUL PUR VILL NO.KAPOOR WALA PETROL:PL | TG-LO1009A-3 | 19506226 | 630 | 200 | 245 | 0.97 | 235 | 64 | 254 | 93 | 366 | 78 | 306 | 97 | 2019-06-12 18:00 | 62 | 11.8 | 402 | Y | 93 | 102 | 105 | 12 |  |  | 13.9 | 86.1 | 33.53 | 33.28 | 28.28 | 33.28 | 659.41 | 644.07 | 644.07 | 660.06 |  | 15.59 | 38.3 | [9 empty] | 693.34 | 26.26 | 0.8 | 0.37
98 | 2019-06-04 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1017 | 1S-DL-YP-ETC-DNNG-2902-LO1017 | E JYOTI NAGAR BEHAIND JOYATI NURSING:ID | TG-LO1017A-1 | 19502178 | 630 | 200 | 237 | 0.98 | 578 | 143 | 624 | 209 | 923 | 226 | 1002 | 345 | 2019-06-30 01:30 | 127.9 | 19.8 | 1002 | B | 72 | 120 | 109 | 48 |  | 1.6 | 76.6 | 21.8 | 39.38 |  | 1 | 0.3 | 445.28 | 174.11 | 174.11 | 291.25 | 137.36 | 381.35 | 320.2 | 326.12 |  | 64.58 | 43.05 | 4.35 |  | 1.58 | 0.2 |  | 622.42 | 25.18 | 0.49 | 0.92
99 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1017 | 1S-DL-YP-ETC-DNNG-2902-LO1017 | E JYOTI NAGAR BEHAIND JOYATI NURSING:ID | TG-LO1017A-2 | 19504503 | 990 | 320 | 238 | 0.98 | 1223 | 299 | 1281 | 407 | 1753 | 517 | 2254 | 843 | 2019-06-11 23:30 | 219.3 | 44.9 | 2254 | B | 79 | 82 | 139 | 60 |  | 0.9 | 35 | 64.1 | 2.14 | 82.05 |  |  | 186.2 | 138.26 | 138.26 | 98.47 | 374.17 | 265.04 | 270.34 | 371.35 | 2.14 | 45.46 | 102.34 | 65.59 |  | 33.44 | 167.41 | 28.44 | 565.05 | 34.55 | 0.48 | 1.24
100 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1017 | 1S-DL-YP-ETC-DNNG-2902-LO1017 | E JYOTI NAGAR BEHAIND JOYATI NURSING:ID | TG-LO1017A-3 | 19502206 | 990 | 320 | 243 | 0.97 | 1003 | 394 | 1696 | 354 | 1507 | 255 | 1076 | 551 | 2019-06-30 01:30 | 205.3 | 53 | 1696 | R | 107 | 92 | 102 | 15 |  | 0.3 | 25 | 74.7 |  | 0.3 |  |  | 150.4 | 271.34 | 271.34 | 188.57 | 461.18 | 397.55 | 444.16 | 457.28 | 80.42 | 27.33 | 65.11 | 52.07 | 6.22 | 1.3 | 2.54 | 0.3 | 699.02 | 20.58 | 0.51 | 1.01
101 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1017 | 1S-DL-YP-ETC-DNNG-2902-LO1017 | E JYOTI NAGAR BEHAIND JOYATI NURSING:ID | TG-LO1017A-4 | 19506358 | 630 | 200 | 247 | 0.97 | 587 | 166 | 690 | 219 | 922 | 202 | 850 | 206 | 2019-06-30 01:00 | 191 | 30.4 | 1029 | Y | 80 | 117 | 103 | 37 | 0.3 | 0.7 | 81.9 | 17.1 | 20.24 |  |  |  | 421.16 | 168.06 | 168.06 | 253.17 | 243.46 | 447.21 | 461.24 | 426.49 |  | 60.26 | 6.43 | 5.2 |  | 9.33 |  |  | 685.26 | 34.34 | 0.5 | 0.93
102 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1018 | 1S-DL-YP-ETC-DNNG-2902-LO1018 | EAST OF LONI ROAD,MIG,S/STN-1:ID | TG-LO1018A-1 | 19506833 | 630 | 200 | 247 | 0.96 | 347 | 78 | 319 | 110 | 449 | 158 | 651 | 290 | 2019-06-29 23:30 | 81.6 | 24.8 | 824 | B | 66 | 97 | 136 | 70 | 0.2 | 0.2 | 12 | 87.5 | 112.24 | 31.59 |  | 15.29 | 92 | 126.25 | 126.25 | 143.25 |  | 46 | 93.3 | 45.3 |  |  | 0.3 | [5 empty] | 205.25 | 58.35 | 0.56 | 0.55
103 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1018 | 1S-DL-YP-ETC-DNNG-2902-LO1018 | EAST OF LONI ROAD,MIG,S/STN-1:ID | TG-LO1018A-2 | 19506831 | 630 | 200 | 242 | 0.98 | 380 | 181 | 749 | 89 | 370 | 109 | 453 | 345 | 2019-06-02 02:30 | 70.2 | 14.8 | 749 | R | 140 | 71 | 90 | 69 | 0.1 |  | 1.8 | 98.1 | 1.3 | 351.52 | 190.35 | 87.14 | 364.45 | 335.38 | 335.38 | 476.01 | 324.12 | 4.18 | 87.08 | 128.33 | 1.21 | [7 empty] | 691.48 | 28.12 | 0.5 | 0.6
104 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1019 | 1S-DL-YP-ETC-DNNG-2902-LO1019 | EAST OF LONI ROAD,MIG,S/STN-2:ID | TG-LO1019A-1 | 19502213 | 630 | 200 | 241 | 0.97 | 462 | 148 | 641 | 157 | 687 | 157 | 686 | 45 | 2019-06-02 23:30 | 91.1 | 18.9 | 731 | B | 89 | 102 | 109 | 20 |  |  | 44.9 | 55.1 | 85 | 48.3 | 13 | 30.3 | 464.35 | 422.35 | 422.35 | 461.05 | 169.19 | 247.49 | 279.19 | 227.19 |  |  | 1 | [5 empty] | 718.54 | 1.06 | 0.49 | 0.73
105 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1019 | 1S-DL-YP-ETC-DNNG-2902-LO1019 | EAST OF LONI ROAD,MIG,S/STN-2:ID | TG-LO1019A-2 | 19506398 | 630 | 200 | 241 | 0.96 | 283 | 99 | 417 | 106 | 445 | 79 | 331 | 102 | 2019-06-29 23:30 | 62.2 | 21.6 | 461 | R | 112 | 101 | 87 | 25 | 0.1 |  | 14.7 | 85.2 | 85.3 | 173 | 294.18 | 146 | 537.05 | 487.35 | 487.35 | 529.22 | 72.49 | 34.49 |  | 20.02 | [8 empty] | 695.24 | 24.36 | 0.57 | 0.45
106 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1020 | 1S-DL-YP-ETC-DNNG-2902-LO1020 | EAST OF LONI ROAD,MIG,S/STN-3:ID | TG-LO1020A-1 | 19505480 | 400 | 120 | 242.7014 | 0.95845 | 581.9066 | 92.8664 | 386.5405 | 248.1852 | 1067.8765 | 240.8551 | 1083.0302 | 689.0379 | 2019-06-29 17:30 | [15 empty] | 268 |  |  |  | 418.5 |  |  |  | 16 |  |  |  | 0 |  |  |  | 5.5 | 708 |  | 0.16463 | 1.4548
107 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1020 | 1S-DL-YP-ETC-DNNG-2902-LO1020 | EAST OF LONI ROAD,MIG,S/STN-3:ID | TG-LO1020A-2 | 19505380 | 630 | 200 | 243 | 0.97 | 236 | 102 | 426 | 74 | 312 | 59 | 247 | 157 | 2019-06-29 23:30 | 40.4 | 4.6 | 454 | R | 122 | 101 | 77 | 45 | 0.1 |  | 0.7 | 99.2 | 492.57 | 610.09 | 656.54 | 616.11 | 185.57 | 84.45 | 84.45 | 78.43 | 16 | [11 empty] | 694.54 | 25.06 | 0.36 | 0.37
108 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1021 | 1S-DL-YP-ETC-DNNG-2902-LO1021 | EAST OF LONI ROAD,MIG,S/STN-4:ID | TG-LO1021A-1 | 19502172 | 400 | 120 | 237 | 0.99 | 109 | 23 | 98 | 50 | 213 | 36 | 152 | 99 | 2019-06-29 22:30 | 12.1 | -1.4 | 220 | Y | 82 | 124 | 94 | 42 |  |  | 20.7 | 79.3 | 695.12 | 524.47 | 666.52 | 635.17 | 23.31 | 193.56 | 193.56 | 83.26 | [12 empty] | 718.43 | 1.17 | 0.47 | 0.27
109 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1021 | 1S-DL-YP-ETC-DNNG-2902-LO1021 | EAST OF LONI ROAD,MIG,S/STN-4:ID | TG-LO1021A-2 | 19502173 | 400 | 120 | 243 | 0.98 | 171 | 75 | 311 | 39 | 161 | 56 | 233 | 130 | 2019-06-12 01:00 | 28.2 | 6.3 | 319 | R | 134 | 76 | 90 | 58 |  |  | 0.8 | 99.2 | 266 | 564.18 | 482.48 | 433.48 | 334.48 | 154.05 | 154.05 | 281.42 | 117.35 |  | 3.3 | 2.53 | [8 empty] | 718.23 | 1.37 | 0.46 | 0.43
110 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1022 | 1S-DL-YP-ETC-DNNG-2902-LO1022 | EAST OF LONI ROAD,MIG,S/STN-5:ID | TG-LO1022A-1 | 19505942 | 400 | 120 | 242 | 0.97 | 221 | 65 | 272 | 43 | 181 | 114 | 490 | 275 | 2019-06-11 | 51.5 | 12.8 | 491 | B | 87 | 66 | 147 | 81 | 0.1 | 0.3 | 71.8 | 27.9 | 140.4 | 368.56 | 1.3 | 58.01 | 510.01 | 346.42 | 346.42 | 523.4 | 66.27 | 1.3 | 419.29 | 135.27 |  |  | 5.3 | [5 empty] | 717.08 | 2.52 | 0.56 | 0.55
111 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1022 | 1S-DL-YP-ETC-DNNG-2902-LO1022 | EAST OF LONI ROAD,MIG,S/STN-5:ID | TG-LO1022A-2 | 19502897 | 400 | 120 | 241 | 0.97 | 249 | 71 | 300 | 85 | 360 | 92 | 387 | 77 | 2019-06-29 23:30 | 48.9 | 16.8 | 478 | B | 88 | 88 | 124 | 36 |  |  | 2.1 | 97.9 | 71.04 | 101 | 0.3 | 19 | 474.25 | 432.15 | 432.15 | 461.15 | 168.27 | 180.41 | 417.01 | 233.41 |  |  | 1.25 | [5 empty] | 713.56 | 6.04 | 0.58 | 0.62
112 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1023 | 1S-DL-YP-ETC-DNNG-2902-LO1023 | EAST OF LONI ROAD,MIG,S/STN-6:ID | TG-LO1023A-1 | 19505768 | 400 | 120 | 236 | 0.97 | 217 | 32 | 146 | 64 | 286 | 120 | 548 | 354 | 2019-06-30 23:00 | 46.7 | 10.2 | 585 | B | 55 | 70 | 174 | 119 | 0.1 | 30.8 | 68.7 | 0.4 | 543.07 | 429.17 | 0.3 | 160 | 175.26 | 282.16 | 282.16 | 453.36 |  | 7 | 421.02 | 104.57 |  |  | 26.02 | [5 empty] | 718.33 | 1.27 | 0.52 | 0.54
113 | 2019-06-01 | 2019-06-20 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1023 | 1S-DL-YP-ETC-DNNG-2902-LO1023 | EAST OF LONI ROAD,MIG,S/STN-6:ID | TG-LO1023A-2 | 19501770 | 400 | 120 | 237 | 0.98 | 92 | 27 | 122 | 28 | 126 | 37 | 164 | 40 | 2019-06-02 22:30 | 12.4 | 2.8 | 167 | B | 77 | 90 | 133 | 56 |  |  | 7.1 | 92.9 | 477.05 | 478.05 | 375.08 | 473.35 | 1.3 | 0.3 | 0.3 | 5 | [12 empty] | 478.35 | 1.25 | 0.47 | 0.23
114 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1024 | 1S-DL-YP-ETC-DNNG-2902-LO1024 | EAST OF LONI ROAD,MIG,S/STN-7:ID | TG-LO1024A-1 | 19502176 | 400 | 120 | 234 | 0.99 | 365 | 112 | 481 | 114 | 485 | 139 | 598 | 115 | 2019-06-03 02:30 | 56.3 | -11 | 648 | B | 101 | 77 | 122 | 45 |  | 0.6 | 51.9 | 47.6 | 6 | 59.3 | 52 | 17.3 | 361.15 | 463.38 | 463.38 | 342.57 | 328.02 | 194.03 | 384.11 | 342.29 | 23.18 | 1.24 | 122.03 | 15.39 |  |  | 5.54 |  | 718.35 | 1.25 | 0.48 | 0.91
115 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1024 | 1S-DL-YP-ETC-DNNG-2902-LO1024 | EAST OF LONI ROAD,MIG,S/STN-7:ID | TG-LO1024A-2 | 19502202 | 400 | 120 | 241 | 0.98 | 335 | 146 | 617 | 95 | 404 | 93 | 401 | 215 | 2019-06-11 23:30 | 62.9 | 10.5 | 617 | R | 126 | 86 | 89 | 40 | 12.8 | 85.2 | 1.9 |  |  | 16.3 | 28 |  | 120 | 413.07 | 413.07 | 327.11 | 478.37 | 288.58 | 317.28 | 383 | 109.04 |  |  | 8.24 | 10.54 |  |  |  | 718.35 | 1.25 | 0.55 | 0.84
116 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1025 | 1S-DL-YP-ETC-DNNG-2902-LO1025 | BAGICHI NARULA LONI RD:PL | TG-LO1025A-1 | 19502902 | 630 | 200 | 245 | 0.97 | 454 | 165 | 675 | 156 | 632 | 133 | 543 | 116 | 2019-06-11 12:30 | 122.8 | 21.6 | 695 | R | 110 | 94 | 96 | 16 |  |  | 44.6 | 55.4 | 5.3 | 69 | 24 | 17 | 352 | 389 | 389 | 425.3 | 362.02 | 261.32 | 267.32 | 277.02 | [8 empty] | 719.32 | 0.28 | 0.55 | 0.72
117 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1026 | 1S-DL-YP-ETC-DNNG-2902-LO1026 | MTNL S/S,EAST OF LONI ROAD:PL | TG-LO1026A-1 | 19502165 | 400 | 120 | 238 | 0.98 | 38 | 13 | 58 | 13 | 57 | 11 | 49 | 9 | 2019-06-01 15:00 | 11.9 | 1.4 | 62 | Y | 109 | 82 | 109 | 27 |  |  | 21.8 | 78.2 | 719.48 | 719.48 | 719.48 | 719.48 | [16 empty] | 719.48 | 0.12 | 0.71 | 0.09
118 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1027 | 1S-DL-YP-ETC-DNNG-2902-LO1027 | D-BLOCK ASHOK NAGAR GALI NO-13:ID | TG-LO1027A-1 | 19502133 | 990 | 320 | 242 | 0.99 | 452 | 135 | 568 | 215 | 915 | 103 | 432 | 431 | 2019-06-29 23:00 | 83.9 | -15.5 | 952 | Y | 91 | 130 | 79 | 51 |  |  | 45.8 | 54.2 | 14 |  | 63 | 5.3 | 696.24 | 310.3 | 310.3 | 649.39 | 6.3 | 406.24 |  | 61.45 | [8 empty] | 716.54 | 3.06 | 0.72 | 0.46
119 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1027 | 1S-DL-YP-ETC-DNNG-2902-LO1027 | D-BLOCK ASHOK NAGAR GALI NO-13:ID | TG-LO1027A-2 | 19506250 | 630 | 200 | 235 | 0.97 | 438 | 157 | 661 | 203 | 865 | 78 | 326 | 471 | 2019-06-10 02:00 | 134 | 29.8 | 918 | Y | 108 | 113 | 79 | 34 | 0.2 | 1.9 | 21 | 76.9 |  | 3.3 | 6 |  | 314 | 317 | 317 | 384 | 380.17 | 340.17 | 79 | 310.17 |  | 33.3 | [6 empty] | 694.17 | 25.43 | 0.58 | 0.7
120 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1028 | 1S-DL-YP-ETC-DNNG-2902-LO1028 | D-BLOCK ASHOK NAGAR GALI NO-3:ID | TG-LO1028A-1 | 19503018 | 990 | 320 | 235 | 0.97 | 950 | 381 | 1641 | 319 | 1392 | 250 | 1096 | 472 | 2019-06-30 | 186.9 | 43.4 | 1690 | R | 130 | 99 | 71 | 59 | 2.4 | 22.4 | 72.2 | 3 | 0.27 | 0.27 | 143.49 | 2.27 | 160.53 | 385.32 | 385.32 | 350.3 | 458.17 | 301.02 | 116.39 | 338.04 | 76.03 | 23.53 |  | 19.53 | 15.14 |  |  |  | 710.54 | 9.06 | 0.45 | 0.96
121 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1028 | 1S-DL-YP-ETC-DNNG-2902-LO1028 | D-BLOCK ASHOK NAGAR GALI NO-3:ID | TG-LO1028A-2 | 19503472 | 630 | 200 | 234 | 0.97 | 549 | 170 | 759 | 178 | 800 | 201 | 892 | 118 | 2019-06-10 23:30 | 126.5 | 39.6 | 1046 | B | 97 | 98 | 105 | 8 |  | 3.1 | 28.8 | 68.1 |  | 0.09 | 48.24 |  | 109 | 134.12 | 134.12 | 112.4 | 596.52 | 545.37 | 514 | 577.06 | 5 | 30.54 | 92.25 | 21.06 |  |  | 6.24 |  | 710.52 | 9.08 | 0.61 | 0.87
122 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1028 | 1S-DL-YP-ETC-DNNG-2902-LO1028 | D-BLOCK ASHOK NAGAR GALI NO-3:ID | TG-LO1028A-3 | 19504095 | 990 | 200 | 235 | 0.97 | 941 | 334 | 1502 | 324 | 1446 | 283 | 1246 | 233 | 2019-06-10 23:30 | 195 | 49.2 | 1584 | B | 102 | 101 | 98 | 4 | 0.1 | 3.3 | 78.5 | 18.2 |  |  |  |  | 132.45 | 177.19 | 177.19 | 166.46 | 522.25 | 453.39 | 406.53 | 478.42 | 30.3 | 56.12 | 43.04 | 41.42 | 1.3 |  | 8.42 |  | 710.54 | 9.06 | 0.54 | 0.95
123 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1029 | 1S-DL-YP-ETC-DNNG-2902-LO1029 | B-BLOCK ASHOK NAGAR SCHOOL WALA:K | TG-LO1029A-1 | 19506195 | 990 | 320 | 243.6799 | 0.97557 | 1128.7818 | 384.6673 | 1712.1435 | 386.7725 | 1691.1785 | 357.342 | 1571.0103 | 131.9062 | 2019-06-01 01:30 | [15 empty] | 0 |  |  |  | 70 |  |  |  | 566 |  |  |  | 74.5 |  |  |  | 3.5 | 714 |  | 0.50894 | 1.1402
124 | 2019-06-10 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1029 | 1S-DL-YP-ETC-DNNG-2902-LO1029 | B-BLOCK ASHOK NAGAR SCHOOL WALA:K | TG-LO1029A-2 | 19502179 | 630 | 200 | 245 | 0.96 | 595 | 144 | 616 | 245 | 1057 | 207 | 890 | 386 | 2019-06-30 02:00 | 148.1 | 42.3 | 1087 | Y | 80 | 116 | 104 | 36 |  |  | 13.5 | 86.5 | 2 |  |  |  | 274.21 | 113.16 | 113.16 | 162.15 | 216.32 | 301.35 | 323.49 | 308.15 |  | 59.25 | 36.02 | 22.23 |  | 18.37 |  |  | 492.53 | 11.07 | 0.52 | 0.94
125 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1029 | 1S-DL-YP-ETC-DNNG-2902-LO1029 | B-BLOCK ASHOK NAGAR SCHOOL WALA:K | TG-LO1029A-3 | 19502205 | 990 | 320 | 242 | 0.97 | 1145 | 408 | 1689 | 281 | 1157 | 455 | 1898 | 662 | 2019-06-12 00:30 | 241.4 | 70.7 | 1916 | B | 107 | 77 | 116 | 39 |  |  | 3.8 | 96.2 |  |  |  |  | 53.32 | 266.43 | 266.43 | 74.02 | 495.15 | 404.35 | 490.14 | 509.13 | 98.39 | 7.3 | 98.31 | 83.13 | 31.22 |  | 73.03 | 12.2 | 700.56 | 19.04 | 0.51 | 1.16
126 | 2019-06-02 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1031 | 1S-DL-YP-ETC-DNNG-2902-LO1031 | HARDEV PURI NO.1:ID | TG-LO1031A-1 | 19502158 | 990 | 320 | 241 | 0.97 | 805 | 198 | 857 | 356 | 1584 | 251 | 1124 | 637 | 2019-06-11 | 171.5 | 75.8 | 1584 | Y | 75 | 124 | 101 | 49 | 0.4 | 21.9 | 73.5 | 4.3 |  |  |  |  | 357.59 | 10.3 | 10.3 | 86.23 | 332.48 | 558.47 | 591.54 | 603.24 |  | 110 |  | 1 |  | 11.3 |  |  | 690.47 | 5.13 | 0.65 | 0.81
127 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1032 | 1S-DL-YP-ETC-DNNG-2902-LO1032 | HARDEVPURI NO.2 ( JOSHI WALA):PL | TG-LO1032A-1 | 19506310 | 990 | 320 | 234 | 0.98 | 1146 | 375 | 1697 | 464 | 2148 | 306 | 1378 | 670 | 2019-06-29 23:00 | 305.9 | 66.9 | 2259 | Y | 99 | 118 | 83 | 35 | 3.1 | 14.9 | 60.4 | 21.5 |  |  | 83.41 |  | 49.51 | 7 | 7 | 40.51 | 473.33 | 431.22 | 466.18 | 490.44 | 105.27 | 115.29 | 69.42 | 93.42 | 28.56 | 103.56 | 11 | 32.3 | 662.12 | 57.48 | 0.55 | 1.16
128 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1033 | 1S-DL-YP-ETC-DNNG-2902-LO1033 | E-1 BLK ASHOK NAGAR.KANCH WALA NR S BHAWAN:K | TG-LO1033A-1 | 19504098 | 630 | 200 | 250 | 0.97 | 587 | 223 | 879 | 235 | 948 | 130 | 515 | 403 | 2019-06-03 01:30 | 135.7 | 47.4 | 992 | Y | 113 | 120 | 67 | 53 | 0.3 | 13.5 | 85 | 1.2 | 1 | 1 | 10.3 | 1 | 22.3 | 13 | 13 | 81.37 | 595.4 | 561.05 | 232.35 | 595.44 | 89.41 | 121.46 |  | 37.28 | 6.58 | 18.58 |  |  | 715.49 | 4.11 | 0.59 | 0.93
129 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1033 | 1S-DL-YP-ETC-DNNG-2902-LO1033 | E-1 BLK ASHOK NAGAR.KANCH WALA NR S BHAWAN:K | TG-LO1033A-2 | 19505663 | 630 | 200 | 245 | 0.97 | 490 | 160 | 676 | 175 | 736 | 155 | 640 | 84 | 2019-06-02 23:00 | 172.8 | 39.2 | 829 | Y | 101 | 114 | 85 | 29 | 0.3 | 10.1 | 88.7 | 0.9 | 1 | 1 | 2 | 1 | 191.18 | 95.58 | 95.58 | 195.18 | 495.44 | 568.06 | 306.06 | 496.14 | 4.3 | 27.28 | [6 empty] | 692.32 | 27.28 | 0.61 | 0.78
130 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1034 | 1S-DL-YP-ETC-DNNG-2902-LO1034 | ASHOK NAGAR NO EXTN NO 1 KACHCHI CLY:PL | TG-LO1034A-1 | 19503619 | 630 | 200 | 239 | 0.97 | 437 | 178 | 796 | 117 | 522 | 142 | 625 | 240 | 2019-06-29 23:30 | 81.9 | 16.1 | 796 | R | 117 | 87 | 96 | 30 |  | 1.8 | 89.2 | 9.1 | 126.11 | 492.17 | 398.24 | 373.45 | 467 | 126.32 | 126.32 | 232.59 | 116.44 | 91.36 | 100.11 | 103.41 | 0.3 | [7 empty] | 710.25 | 9.35 | 0.36 | 0.69
131 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1034 | 1S-DL-YP-ETC-DNNG-2902-LO1034 | ASHOK NAGAR NO EXTN NO 1 KACHCHI CLY:PL | TG-LO1034A-2 | 19505269 | 630 | 200 | 237 | 0.97 | 711 | 186 | 850 | 201 | 900 | 324 | 1534 | 660 | 2019-06-10 23:30 | 245.6 | 42.8 | 1534 | B | 86 | 84 | 131 | 47 | 11.1 | 36.8 | 18.1 | 34 |  |  |  |  | 60.23 | 126.47 | 126.47 | 37.3 | 603.45 | 531.42 | 316.55 | 545.24 | 24.07 | 29.46 | 212.29 | 87.32 |  |  | 147.51 | 17.49 | 688.15 | 31.45 | 0.56 | 1.13
132 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1035 | 1S-DL-YP-ETC-DNNG-2902-LO1035 | NATHU COLONY:K | TG-LO1035A-1 | 19506177 | 990 | 320 | 235 | 0.97 | 912 | 248 | 1090 | 324 | 1443 | 340 | 1541 | 411 | 2019-06-11 23:30 | 265 | 64.3 | 1778 | B | 91 | 108 | 101 | 17 | 5.9 | 16 | 72.4 | 5.7 | 0.3 | 0.3 | 0.3 | 0.3 | 102.51 | 30 | 30 | 45.21 | 584.54 | 577.45 | 594.55 | 625.54 | 1 | 80.3 | 39.3 | 17.3 |  | 0.3 | 2.3 |  | 689.15 | 30.45 | 0.61 | 0.92
133 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1035 | 1S-DL-YP-ETC-DNNG-2902-LO1035 | NATHU COLONY:K | TG-LO1035A-2 | 19504782 | 990 | 320 | 236 | 0.97 | 690 | 233 | 1036 | 255 | 1145 | 202 | 880 | 231 | 2019-06-11 23:30 | 139.1 | 46.4 | 1183 | Y | 113 | 107 | 80 | 33 | 1.5 | 69.4 | 29.1 |  |  |  | 7 |  | 156.11 | 226.42 | 226.42 | 279.41 | 559.56 | 489.25 | 195.41 | 436.26 | [8 empty] | 716.07 | 3.53 | 0.63 | 0.7
134 | 2019-06-04 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1040 | 1S-DL-YP-ETC-DNNG-2902-LO1040 | DURGAPURI EXT. OPP KALA NIKETAN SCHOOL:K | TG-LO1040A-1 | 19502154 | 990 | 320 | 245 | 0.96 | 765 | 332 | 1458 | 173 | 749 | 259 | 1107 | 615 | 2019-06-30 23:30 | 170 | 83.9 | 1458 | R | 124 | 71 | 104 | 53 | 2.6 | 56.2 | 41.2 | [5 empty] | 29.56 | 506.31 | 506.31 | 132.43 | 531.33 | 140.12 | 543.1 | 514 | 82.19 |  |  |  | 2.55 |  |  |  | 646.43 | 1.17 | 0.64 | 0.77
135 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1043 | 1S-DL-YP-ETC-DNNG-2902-LO1043 | LALITA MANDIR ASHOK NAGAR D BLK:PL | TG-LO1043A-1 | 19502640 | 990 | 320 | 244 | 0.96 | 907 | 319 | 1378 | 324 | 1408 | 264 | 1144 | 250 | 2019-06-26 23:30 | 214.2 | 84.6 | 1568 | R | 108 | 102 | 90 | 18 |  |  | 14.6 | 85.4 |  |  |  |  | 17 | 47.27 | 47.27 | 46.46 | 591.16 | 600.43 | 591.52 | 618.24 | 97.43 | 62.19 | 3.21 | 45.19 | 4.3 |  |  |  | 710.29 | 9.31 | 0.62 | 0.92
136 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1045 | 1S-DL-YP-ETC-DNNG-2902-LO1045 | HARIJAN BASTI, AKHADA EAST GOKAL PUR:PL | TG-LO1045A-1 | 19505674 | 990 | 320 | 236 | 0.99 | 879 | 297 | 1284 | 292 | 1257 | 290 | 1252 | 30 | 2019-06-01 10:30 | 302.7 | -31.7 | 1313 | R | 107 | 92 | 101 | 15 |  | 0.1 | 13.6 | 86.3 | 40.3 | 127.18 | 59.33 | 74.33 | 310.45 | 301.27 | 301.27 | 315.12 | 340.46 | 279.05 | 328.26 | 315.35 | 23.49 | 8 | 7.49 | 10.3 |  |  |  |  | 715.5 | 4.1 | 0.47 | 0.89
137 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1045 | 1S-DL-YP-ETC-DNNG-2902-LO1045 | HARIJAN BASTI, AKHADA EAST GOKAL PUR:PL | TG-LO1045A-2 | 19505673 | 630 | 200 | 248 | 0.97 | 478 | 152 | 624 | 158 | 654 | 168 | 688 | 55 | 2019-06-20 16:30 | 364.4 | -89 | 688 | B | 95 | 99 | 107 | 12 |  |  | 7.5 | 92.5 | 37.24 | 30.24 | 16.24 | 25.54 | 387.28 | 354.58 | 354.58 | 347.58 | 293.01 | 332.31 | 426.52 | 344.01 | [8 empty] | 717.53 | 2.07 | 0.53 | 0.76
138 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1047 | 1S-DL-YP-ETC-DNNG-2902-LO1047 | D-1 ASHOK NAGAR WAZIRA BAD ROAD:PL | TG-LO1047A-1 | 19505923 | 630 | 200 | 244 | 0.96 | 725 | 206 | 895 | 283 | 1219 | 237 | 1051 | 281 | 2019-06-02 18:30 | 270 | 31.8 | 1310 | B | 93 | 113 | 95 | 20 | 0.2 | 14.7 | 84.3 | 0.8 | 5.3 | 0.45 | 1.3 | 0.3 | 180.42 | 147.13 | 147.13 | 185 | 454.26 | 308.17 | 413.05 | 409.43 | 51.14 | 168.36 | 68.14 | 87.44 | 8.55 | 75.56 | 4.13 | 17.5 | 700.47 | 19.13 | 0.5 | 1.15
139 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1053 | 1S-DL-YP-ETC-DNNG-2902-LO1053 | D 1/1 BLK ASHOK NAGAR DP :PL | TG-LO1053A-1 | 19505926 | 990 | 320 | 242 | 0.97 | 928 | 394 | 1684 | 302 | 1281 | 232 | 981 | 611 | 2019-06-29 23:30 | 275.5 | 53.8 | 1684 | R | 111 | 104 | 85 | 26 |  | 0.4 | 14.2 | 85.4 |  | 1.02 | 1.02 | 0.32 | 132.36 | 105.04 | 105.04 | 157.34 | 516.47 | 582.17 | 376.15 | 540.03 | 54.16 | 24.4 |  | 14.54 | 9.24 |  |  |  | 713.03 | 6.57 | 0.53 | 0.94
140 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1054 | 1S-DL-YP-ETC-DNNG-2902-LO1054 | HARNAM PALACE MEET NAGAR | TG-LO1054A-1 | 19503627 | 630 | 200 | 243 | 0.98 | 246 | 81 | 337 | 79 | 327 | 86 | 359 | 29 | 2019-06-26 18:00 | 60.3 | -3.2 | 385 | Y | 100 | 106 | 95 | 11 |  |  | 4.3 | 95.7 | 422.3 | 418.3 | 437 | 426.3 | 296.47 | 298.47 | 298.47 | 293.17 | 0.3 | 2.3 | 1.3 | [9 empty] | 719.47 | 0.13 | 0.4 | 0.39
141 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1055 | 1S-DL-YP-ETC-DNNG-2902-LO1055 | LONI BORDER S/S NO-1 | TG-LO1055A-1 | 19505051 | 630 | 200 | 247 | 0.97 | 653 | 272 | 1185 | 206 | 871 | 175 | 755 | 385 | 2019-06-10 22:30 | 153.6 | 54.3 | 1185 | R | 124 | 84 | 92 | 40 | 0.3 | 22.7 | 64.9 | 12 | [5 empty] | 24.42 | 24.42 |  | 382.16 | 665.02 | 680.09 | 662.21 | 276.3 | 2.55 | 10.29 | 30.07 | 33.53 |  |  | 0.11 | 692.39 | 27.21 | 0.62 | 1.04
142 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1056 | 1S-DL-YP-ETC-DNNG-2902-LO1056 | LONI BORDER S/S NO-2 | TG-LO1056A-1 | 19503678 | 630 | 200 | 244 | 0.96 | 875 | 357 | 1543 | 240 | 1023 | 279 | 1166 | 466 | 2019-06-18 17:30 | 213 | 14.3 | 1543 | R | 122 | 82 | 96 | 40 | 10.4 | 25 | 57 | 7.7 | 0.05 | 3.19 | 3 | 3.05 | 3.31 | 109.56 | 109.56 | 1.57 | 99.2 | 454.38 | 482.28 | 430.07 | 391.41 | 94.34 | 134.35 | 220.18 | 173.06 | 5.16 | 43.57 | 12.16 | 667.43 | 52.17 | 0.55 | 1.39
143 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1059 | 1S-DL-YP-ETC-DNNG-2902-LO1059 | D.P Kundan Lal Petrol Pump East Gokalpur | TG-LO1059A-1 | 19505021 | 400 | 200 | 246 | 0.99 | 54 | 20 | 81 | 18 | 72 | 16 | 63 | 16 | 2019-06-15 11:30 | 13.8 | 0.5 | 88 | B | 93 | 103 | 103 | 10 |  | 2 | 83.9 | 14.1 | 698.19 | 698.19 | 698.19 | 698.19 | [16 empty] | 698.19 | 21.41 | 0.59 | 0.13
144 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1060 | 1S-DL-YP-ETC-DNNG-2902-LO1060 | DURGA PURI MAIN GALI - 10:ID | TG-LO1060A-1 | 19505223 | 630 | 200 | 233.6663 | 0.97315 | 897.5917 | 336.1458 | 1603.2901 | 265.3966 | 1236.1852 | 296.0493 | 1392.649 | 319.0741 | 2019-06-08 02:00 | [15 empty] | 1.5 |  |  |  | 31 |  |  |  | 495.5 |  |  |  | 98.5 |  |  |  | 42.5 | 669 |  | 0.45567 | 1.4247
145 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1060 | 1S-DL-YP-ETC-DNNG-2902-LO1060 | DURGA PURI MAIN GALI - 10:ID | TG-LO1060A-2 | 19506308 | 990 | 320 | 239 | 0.98 | 1286 | 307 | 1392 | 465 | 2154 | 514 | 2263 | 822 | 2019-06-08 01:30 | 446.7 | 70.1 | 2263 | B | 88 | 98 | 114 | 26 | 96.7 | 2.3 | 1 | [5 empty] | 62.28 | 7 | 7 | 3.3 | 518.27 | 529.32 | 297.12 | 479.24 | 97.27 | 128.23 | 239.58 | 162.07 | 0.5 | 14.17 | 141.32 | 34.11 | 679.12 | 40.48 | 0.55 | 1.3
146 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1060 | 1S-DL-YP-ETC-DNNG-2902-LO1060 | DURGA PURI MAIN GALI - 10:ID | TG-LO1060A-3 | 19502695 | 630 | 200 | 235 | 0.98 | 491 | 142 | 612 | 176 | 768 | 173 | 755 | 150 | 2019-06-30 00:30 | 85.6 | 12.4 | 786 | B | 78 | 96 | 126 | 48 |  | 14.9 | 82.6 | 2.5 | 183.14 | 69.53 | 7 | 46.02 | 438.3 | 482.39 | 482.39 | 481.54 | 81.18 | 149.5 | 357.56 | 175.06 |  | 0.4 | 2.1 | [5 empty] | 703.02 | 16.58 | 0.43 | 0.78
147 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1061 | 1S-DL-YP-ETC-DNNG-2902-LO1061 | JAGAT PURI MAIN:PL | TG-LO1061A-1 | 19503373 | 630 | 200 | 237 | 0.97 | 603 | 174 | 741 | 225 | 964 | 204 | 873 | 194 | 2019-06-11 23:00 | 109.9 | 15.6 | 1035 | R | 98 | 102 | 100 | 4 |  | 2.9 | 38.7 | 58.3 | 33.1 |  |  |  | 49.52 | 73.26 | 73.26 | 56.09 | 551.12 | 549.03 | 548.03 | 589.35 | 48.23 | 59.08 | 49 | 41.53 | 5 | 6 | 0.3 |  | 711.05 | 8.55 | 0.58 | 0.96
148 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1061 | 1S-DL-YP-ETC-DNNG-2902-LO1061 | JAGAT PURI MAIN:PL | TG-LO1061A-2 | 19506558 | 630 | 200 | 243.0412 | 0.96852 | 936.9566 | 336.9131 | 1386.8161 | 248.7815 | 1032.8027 | 351.262 | 1486.6975 | 413.1115 | 2019-06-11 19:30 | [15 empty] | 0 |  |  |  | 5 |  |  |  | 665 |  |  |  | 43.5 |  |  |  | 1 | 714.5 |  | 0.41517 | 1.4872
149 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1063 | 1S-DL-YP-ETC-DNNG-2902-LO1063 | JAG JIVAN NAGAR:PL | TG-LO1063A-1 | 19506222 | 990 | 320 | 230 | 0.97 | 1078 | 322 | 1419 | 418 | 1857 | 338 | 1510 | 400 | 2019-06-06 00:30 | 275.2 | 54.4 | 1928 | Y | 90 | 121 | 89 | 32 | 0.3 | 1.5 | 60.5 | 37.8 |  |  |  |  | 163.16 | 3 | 3 | 60.49 | 511.49 | 548.05 | 512.34 | 586.02 | 32.59 | 132.32 | 24.03 | 60.34 | 0.59 | 25.26 | 2.19 | 1.38 | 709.03 | 10.57 | 0.53 | 1.09
150 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1064 | 1S-DL-YP-ETC-DNNG-2902-LO1064 | PRIMARY SCHOOL WALA MEET NAGAR | TG-LO1064A-1 | 19506670 | 990 | 320 | 243 | 0.99 | 114 | 75 | 296 | 16 | 64 | 23 | 93 | 219 | 2019-06-17 10:30 | 24 | 0.3 | 296 | R | 78 | 123 | 99 | 45 | 0.1 | 0.1 | 72.9 | 26.9 | 704.23 | 704.53 | 704.53 | 704.53 | 0.3 | [15 empty] | 704.53 | 15.07 | 0.47 | 0.12
151 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1066 | 1S-DL-YP-ETC-DNNG-2902-LO1066 | CHANDER LOK:PL | TG-LO1066A-1 | 19505936 | 990 | 320 | 234.2582 | 0.9779 | 1182.4515 | 360.6617 | 1579.0102 | 475.0448 | 2102.8987 | 346.7449 | 1504.8386 | 564.6399 | 2019-06-30 01:00 | [15 empty] | 0 |  |  |  | 16 |  |  |  | 544 |  |  |  | 113 |  |  |  | 44.5 | 717.5 |  | 0.56737 | 1.1944
152 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1073 | 1S-DL-YP-ETC-DNNG-2902-LO1073 | POLICE STATION GOKULPURI | TG-LO1073A-1 | 19506028 | 990 | 300 | 244 | 0.99 | 115 | 11 | 48 | 8 | 33 | 96 | 405 | 365 | 2019-06-29 15:30 | 16.5 | -0.6 | 405 | B | 83 | 68 | 149 | 81 |  |  | 8.4 | 91.6 | 719.11 | 719.11 | 718.41 | 719.11 | [16 empty] | 719.11 | 0.49 | 0.27 | 0.12
153 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO1070 | 1S-DL-YP-ETC-DNNG-2902-LO1070 | EDMC DISPENSARY NEAR AMBEDKAR COLLEGE | TG-LO1070A-1 | 19506359 | 100 | 40 | 247 | 0.94 | 6 | 6 | 23 | 0 | 0 | 1 | 3 | 22 | 2019-06-28 12:30 | 1.6 | 0 | 23 | R | 189 | 0 | 111 | 189 |  | 0.1 | 4.7 | 95.3 | 718.21 | 718.21 | 718.21 | 718.21 | [16 empty] | 718.21 | 1.39 | 0.29 | 0.06
154 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2004 | 1S-DL-YP-ETC-DNNG-2903-LO2004 | JYOTI COLONY NO.1:K | TG-LO2004A-1 | 19506079 | 630 | 200 | 240 | 0.97 | 874 | 295 | 1306 | 249 | 1085 | 330 | 1457 | 324 | 2019-06-11 00:30 | 227.2 | 68.2 | 1643 | B | 93 | 89 | 118 | 29 | 36.9 | 9.2 | 25.7 | 28.2 |  |  |  |  | 7.3 |  |  |  | 266.57 | 291.31 | 121.12 | 227.13 | 91.55 | 122.3 | 144.27 | 118.56 | 61.12 | 13.33 | 161.55 | 81.25 | 689.16 | 30.44 | 0.59 | 1.39
155 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2004 | 1S-DL-YP-ETC-DNNG-2903-LO2004 | JYOTI COLONY NO.1:K | TG-LO2004A-2 | 19505874 | 400 | 120 | 249 | 0.97 | 402 | 186 | 802 | 94 | 395 | 122 | 515 | 362 | 2019-06-11 01:00 | 107 | 24.6 | 883 | R | 119 | 87 | 94 | 32 | 1.3 | 0.7 | 11.7 | 86.4 | 1 | 3.3 |  |  | 96.31 | 328.33 | 328.33 | 189.15 | 487.14 | 358.22 | 493.12 | 487.07 | 83.07 | 21.41 | 5.38 | 35.44 | 44.44 | 0.3 |  | 0.3 | 712.36 | 7.24 | 0.51 | 1
156 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2006 | 1S-DL-YP-ETC-DNNG-2903-LO2006 | JYOTI COLONY NO.3:K | TG-LO2006A-1 | 19504914 | 990 | 320 | 244 | 0.97 | 644 | 258 | 1091 | 164 | 689 | 222 | 931 | 351 | 2019-06-29 23:30 | 118.5 | 28.7 | 1165 | R | 120 | 74 | 105 | 46 |  |  | 4 | 96 | 19.3 | 178.51 | 37.1 | 53.55 | 306.19 | 407.46 | 407.46 | 405.42 | 300.24 | 41.06 | 200.15 | 168.06 | 1.3 | [7 empty] | 627.43 | 68.17 | 0.52 | 0.65
157 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2006 | 1S-DL-YP-ETC-DNNG-2903-LO2006 | JYOTI COLONY NO.3:K | TG-LO2006A-2 | 19506078 | 630 | 200 | 242 | 0.96 | 689 | 283 | 1176 | 199 | 814 | 207 | 854 | 344 | 2019-06-12 00:30 | 203.6 | 25.2 | 1177 | R | 106 | 97 | 97 | 9 | 0.2 | 2.3 | 7.1 | 90.4 | 1 | 1 | 1 | 1 | 83.32 | 104.54 | 104.54 | 83.02 | 529.29 | 554.24 | 584.39 | 563.46 | 47.56 | 27.47 | 19.13 | 37.39 | 26.08 |  |  | 2.38 | 688.05 | 31.55 | 0.49 | 1.09
158 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2007 | 1S-DL-YP-ETC-DNNG-2903-LO2007 | AMBEDKAR PARK:PL | TG-LO2007A-1 | 19506615 | 990 | 320 | 245 | 0.97 | 974 | 344 | 1494 | 437 | 1859 | 193 | 819 | 914 | 2019-06-10 23:00 | 238.7 | 73.9 | 1859 | Y | 119 | 115 | 66 | 53 | 8.7 | 51.5 | 39.3 | 0.6 |  |  | 7 |  | 23 | 32.3 | 32.3 | 86.03 | 537.01 | 519.01 | 219.3 | 546.26 | 111.02 | 102.22 |  | 58.33 | 19.59 | 37.09 |  |  | 691.02 | 28.58 | 0.56 | 0.98
159 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2007 | 1S-DL-YP-ETC-DNNG-2903-LO2007 | AMBEDKAR PARK:PL | TG-LO2007A-2 | 19506514 | 630 | 200 | 243 | 0.97 | 774 | 262 | 1120 | 293 | 1233 | 218 | 916 | 279 | 2019-06-11 01:00 | 158 | 33.4 | 1254 | R | 111 | 104 | 85 | 26 | 0.4 | 4.2 | 82.7 | 12.7 |  |  |  |  | 22.3 | 24.3 | 24.3 | 40.3 | 462.43 | 504 | 498.11 | 505.27 | 122.09 | 96.16 | 69.38 | 104.14 | 82.49 | 65.25 | 0.47 | 40 | 690.11 | 29.49 | 0.52 | 1.23
160 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2008 | 1S-DL-YP-ETC-DNNG-2903-LO2008 | CHANAKYA MARG CHAJJUPUR:PKG | TG-LO2008A-1 | 19504959 | 990 | 320 | 237 | 0.94 | 325 | 129 | 556 | 120 | 531 | 76 | 334 | 210 | 2019-06-01 23:30 | 71.4 | -143.5 | 580 | Y | 119 | 104 | 77 | 42 | 2.9 | 23.7 | 44.3 | 29.2 | 60.56 | 217.53 | 595.09 | 190.33 | 657.45 | 500.48 | 500.48 | 528.08 | [12 empty] | 718.41 | 1.19 | 0.68 | 0.33
161 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2009 | 1S-DL-YP-ETC-DNNG-2903-LO2009 | SHIV MANDIR 100 FT. RD:PL | TG-LO2009A-1 | 19506076 | 990 | 320 | 236 | 0.97 | 746 | 227 | 985 | 299 | 1402 | 220 | 953 | 434 | 2019-06-01 | 235.8 | 51.5 | 1717 | B | 88 | 105 | 107 | 19 | 100 | [7 empty] | 222.2 | 159.58 | 159.58 | 156.28 | 329.05 | 387.57 | 398.13 | 394.57 |  | 3.3 | 17.3 |  |  |  | 2 |  | 689.02 | 30.58 | 0.61 | 0.75
162 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2009 | 1S-DL-YP-ETC-DNNG-2903-LO2009 | SHIV MANDIR 100 FT. RD:PL | TG-LO2009A-2 | 19506549 | 400 | 120 | 247 | 0.97 | 405 | 167 | 721 | 123 | 519 | 116 | 496 | 215 | 2019-06-10 23:00 | 118.9 | 26.5 | 896 | R | 119 | 96 | 84 | 35 | 1.2 | 15.4 | 57.5 | 25.9 |  |  |  |  | 17.1 | 40.38 | 40.38 | 13.5 | 465.56 | 613.52 | 578.22 | 608.18 | 133.32 | 34.3 | 7.3 | 66.22 | 72.22 |  |  | 0.3 | 689 | 31 | 0.6 | 1.01
163 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2010 | 1S-DL-YP-ETC-DNNG-2903-LO2010 | KABRISTAN BABAR PUR MAIN ROAD:PL | TG-LO2010A-1 | 19502725 | 990 | 320 | 245 | 0.98 | 564 | 158 | 645 | 190 | 807 | 217 | 916 | 236 | 2019-06-29 15:30 | 160.4 | 19.9 | 926 | B | 76 | 108 | 116 | 40 | 89.1 | 9.3 | 1 | 0.6 | 23.59 |  |  |  | 616.03 | 299 | 299 | 407.28 | 77.04 | 418.06 | 507.36 | 309.38 | [8 empty] | 717.06 | 2.54 | 0.68 | 0.57
164 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2011 | 1S-DL-YP-ETC-DNNG-2903-LO2011 | CHAJJUPUR MAIN:K | TG-LO2011A-1 | 19505876 | 990 | 320 | 248 | 0.95 | 647 | 252 | 1008 | 228 | 901 | 167 | 663 | 305 | 2019-06-08 10:30 | 176.3 | 41.3 | 1008 | R | 103 | 87 | 109 | 22 | 0.1 | 0.8 | 73.6 | 25.5 | 0.3 | 12 | 5 |  | 487.24 | 640.5 | 640.5 | 574.47 | 230.48 | 65.52 | 313.24 | 143.55 | [8 empty] | 718.42 | 1.18 | 0.55 | 0.65
165 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2011 | 1S-DL-YP-ETC-DNNG-2903-LO2011 | CHAJJUPUR MAIN:K | TG-LO2011A-2 | 19505270 | 630 | 200 | 242 | 0.99 | 324 | 57 | 251 | 92 | 411 | 176 | 801 | 490 | 2019-06-30 23:30 | 72.8 | -18 | 801 | B | 69 | 101 | 130 | 61 | 0.1 | 0.4 | 22.5 | 77 | 244.35 | 22.3 | 3.3 | 17.3 | 451.04 | 581.09 | 581.09 | 607.09 |  | 92 | 347.24 | 71 |  |  | 0.3 | [5 empty] | 695.39 | 24.21 | 0.61 | 0.51
166 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2012 | 1S-DL-YP-ETC-DNNG-2903-LO2012 | BABAR PUR VILLAGE:PL | TG-LO2012A-1 | 19502729 | 630 | 200 | 238 | 0.97 | 525 | 140 | 589 | 181 | 772 | 203 | 869 | 246 | 2019-06-11 23:30 | 128.8 | 36.8 | 1038 | B | 84 | 89 | 127 | 43 |  | 21.1 | 71 | 7.9 |  |  |  |  | 126.19 | 159.19 | 159.19 | 23.24 | 586.41 | 540.41 | 547.17 | 685.06 |  | 13 | 150.43 | 4.3 |  |  | 14 |  | 713 | 7 | 0.68 | 0.83
167 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2012 | 1S-DL-YP-ETC-DNNG-2903-LO2012 | BABAR PUR VILLAGE:PL | TG-LO2012A-2 | 19504911 | 990 | 320 | 233 | 0.98 | 655 | 256 | 1131 | 217 | 959 | 182 | 786 | 299 | 2019-06-10 23:30 | 110.4 | 21.3 | 1143 | R | 113 | 108 | 79 | 34 | 0.1 | 16.3 | 61.1 | 22.4 | 0.02 |  | 20.05 | 0.02 | 221.59 | 249.5 | 249.5 | 340.48 | 490.56 | 463.07 | 154.15 | 372.07 | [8 empty] | 712.57 | 7.03 | 0.63 | 0.66
168 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2013 | 1S-DL-YP-ETC-DNNG-2903-LO2013 | MAHA DEVI SCHOOL:PL | TG-LO2013A-1 | 19502715 | 630 | 200 | 240 | 0.96 | 716 | 263 | 1160 | 217 | 961 | 236 | 1053 | 172 | 2019-06-03 | 160.1 | 56.6 | 1160 | R | 106 | 101 | 93 | 13 | 0.2 | 0.8 | 79.2 | 19.7 |  |  |  |  | 41.3 | 50.24 | 50.24 | 52.53 | 528.59 | 561.21 | 550.22 | 556.21 | 100.57 | 88.36 | 60.1 | 92.23 | 40.54 | 11.59 | 2.3 | 10.43 | 712.2 | 7.4 | 0.53 | 1.14
169 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2013 | 1S-DL-YP-ETC-DNNG-2903-LO2013 | MAHA DEVI SCHOOL:PL | TG-LO2013A-2 | 19502722 | 630 | 200 | 241 | 0.97 | 550 | 131 | 562 | 207 | 905 | 212 | 928 | 355 | 2019-06-29 00:30 | 113.6 | 31.3 | 928 | B | 75 | 104 | 121 | 46 | 0.4 | 40.9 | 58.7 | 0.1 | 5.3 |  |  |  | 386.53 | 97.3 | 97.3 | 89.2 | 319.13 | 594.58 | 633.38 | 618.46 |  | 19.08 | 60.27 | 3.3 |  |  | 0.3 |  | 711.36 | 8.24 | 0.59 | 0.87
170 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2014 | 1S-DL-YP-ETC-DNNG-2903-LO2014 | SUDAMAPURI NO.1:PL | TG-LO2014A-1 | 19506223 | 990 | 320 | 243 | 0.98 | 583 | 187 | 829 | 198 | 872 | 198 | 870 | 42 | 2019-06-08 01:30 | 221.8 | 16.6 | 872 | Y | 72 | 124 | 103 | 52 | 0.3 | 0.1 | 63.3 | 36.2 | 503.34 | 56.3 | 212.3 | 208 | 208.39 | 535.36 | 535.36 | 500.13 | 0.3 | 120.37 | 26.23 | 4.3 | [8 empty] | 712.43 | 7.17 | 0.42 | 0.59
171 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2015 | 1S-DL-YP-ETC-DNNG-2903-LO2015 | SUDAMA PURI NO.2:PL | TG-LO2015A-1 | 19506010 | 630 | 200 | 237 | 0.99 | 454 | 204 | 908 | 28 | 121 | 222 | 968 | 819 | 2019-06-07 01:30 | 176.6 | -0.2 | 968 | B | 122 | 93 | 85 | 37 | 0.1 | 0.4 | 70.5 | 29 | 682.03 | 709.03 | 705.33 | 708.33 | 26.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 1 | 0.3 | [5 empty] | 0.3 |  | 709.33 | 10.27 | 0.14 | 0.72
172 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2016 | 1S-DL-YP-ETC-DNNG-2903-LO2016 | SUDAMA PURI NO.3:PL | TG-LO2016A-1 | 19506468 | 990 | 320 | 240.0754 | 0.96321 | 992.4833 | 275.2841 | 1161.2912 | 279.1033 | 1187.7747 | 438.0959 | 1848.194 | 674.0513 | 2019-06-27 00:30 | [15 empty] | 2 |  |  |  | 29 |  |  |  | 589.5 |  |  |  | 97 |  |  |  | 0.5 | 718 |  | 0.6145 | 1.0025
173 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2018 | 1S-DL-YP-ETC-DNNG-2903-LO2018 | SUDAMAPURI NO. 4:PL | TG-LO2018A-1 | 19506829 | 400 | 120 | 242 | 0.96 | 481 | 178 | 755 | 130 | 552 | 174 | 735 | 194 | 2019-06-09 23:30 | 133.1 | 41.3 | 850 | R | 110 | 84 | 106 | 26 | 0.4 | 0.6 | 36.8 | 62.2 |  |  |  |  | 1 | 32.3 | 32.3 | 4.3 | 402.45 | 553.37 | 436.1 | 486.41 | 156.52 | 117.51 | 161.27 | 133.2 | 146.21 | 3 | 106.21 | 82.27 | 706.58 | 13.02 | 0.61 | 1.2
174 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2020 | 1S-DL-YP-ETC-DNNG-2903-LO2020 | JYOTI COLONY/ BALBIR NGR NO.2:PL | TG-LO2020A-1 | 19504551 | 990 | 320 | 247 | 0.97 | 1475 | 451 | 1824 | 478 | 1967 | 546 | 2289 | 412 | 2019-06-11 00:30 | 325.3 | 86.1 | 2289 | B | 95 | 102 | 103 | 8 | 0.2 | 2.7 | 22.2 | 74.9 |  |  |  |  | 6 | 2 | 2 |  | 386 | 338.36 | 325.53 | 355.54 | 179.14 | 176.23 | 205.22 | 187.41 | 133.33 | 187.48 | 173.32 | 161.12 | 704.47 | 15.13 | 0.56 | 1.49
175 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2020 | 1S-DL-YP-ETC-DNNG-2903-LO2020 | JYOTI COLONY/ BALBIR NGR NO.2:PL | TG-LO2020A-2 | 19506261 | 630 | 200 | 256 | 0.95 | 473 | 131 | 515 | 220 | 879 | 122 | 481 | 382 | 2019-06-12 | 142 | 37.8 | 905 | Y | 93 | 132 | 75 | 57 | 0.1 | 0.3 | 55.4 | 44.2 | 11 |  | 88.55 |  | 443.26 | 158.06 | 158.06 | 399.02 | 226.55 | 483.3 | 120.54 | 282.19 |  | 38.27 |  |  |  | 1.18 |  |  | 681.21 | 38.39 | 0.53 | 0.75
176 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2021 | 1S-DL-YP-ETC-DNNG-2903-LO2021 | D BLOCK KABIR NAGAR(SHAMSHAN GHAT) | TG-LO2021A-1 | 19505805 | 990 | 320 | 249 | 0.97 | 972 | 368 | 1557 | 310 | 1294 | 294 | 1235 | 296 | 2019-06-01 23:30 | 257 | 87 | 1596 | R | 99 | 102 | 99 | 3 | 12.6 | 1.3 | 25.6 | 60.5 |  |  |  |  | 31.01 | 6 | 6 | 8.3 | 633.22 | 678.53 | 669.11 | 675.53 | 40.51 | 29.51 | 19.2 | 30.21 | 9.3 |  |  |  | 714.44 | 5.16 | 0.6 | 0.98
177 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2021 | 1S-DL-YP-ETC-DNNG-2903-LO2021 | D BLOCK KABIR NAGAR(SHAMSHAN GHAT) | TG-LO2021A-2 | 19505296 | 630 | 200 | 245 | 0.96 | 513 | 174 | 715 | 150 | 617 | 189 | 777 | 139 | 2019-06-26 13:00 | 175.8 | 38.4 | 827 | R | 116 | 83 | 101 | 33 |  |  | 24.4 | 75.6 |  | 1.3 |  |  | 127.09 | 401.5 | 401.5 | 254.39 | 528.01 | 288.13 | 444.25 | 435.54 | 36.23 |  | 0.59 | 1 |  |  |  |  | 691.34 | 28.26 | 0.57 | 0.81
178 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2021 | 1S-DL-YP-ETC-DNNG-2903-LO2021 | D BLOCK KABIR NAGAR(SHAMSHAN GHAT) | TG-LO2021A-3 | 19506074 | 630 | 200 | 240 | 0.97 | 270 | 96 | 400 | 109 | 457 | 65 | 271 | 166 | 2019-06-29 23:30 | 89.6 | 24.6 | 466 | Y | 98 | 122 | 80 | 42 | 0.1 | 0.1 | 8.2 | 91.7 | 69.07 | 2.3 | 224.23 | 23.58 | 609.21 | 581.41 | 581.41 | 661 | 13.09 | 107.26 |  | 6.39 | [8 empty] | 691.37 | 28.23 | 0.65 | 0.43
179 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2022 | 1S-DL-YP-ETC-DNNG-2903-LO2022 | FIRE STATION EAST OF LONI ROAD:-PL | TG-LO2022A-1 | 19504695 | 100 | 40 | 243 | 0.98 | 65 | 27 | 118 | 20 | 87 | 18 | 76 | 37 | 2019-06-01 15:30 | 26.7 | -0.3 | 125 | R | 153 | 91 | 56 | 97 | 1 | 29.8 | 67.4 | 1.8 | 32.3 | 402 | 539.22 | 218 | 403.52 | 231.21 | 231.21 | 463.51 | 282.29 | 86.3 | 8 | 38 | 1 | [7 empty] | 719.51 | 0.09 | 0.38 | 0.65
180 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2023 | 1S-DL-YP-ETC-DNNG-2903-LO2023 | A BLOCK KABIR NAGAR:ID | TG-LO2023A-1 | 19502671 | 990 | 320 | 256 | 0.96 | 975 | 331 | 1301 | 356 | 1417 | 288 | 1144 | 237 | 2019-06-01 | 226.7 | 93.5 | 1517 | Y | 100 | 112 | 88 | 24 |  | 0.7 | 40.2 | 59.1 |  |  |  |  | 1 |  |  |  | 626.41 | 502.04 | 682.02 | 629.41 | 64.21 | 171.36 | 6 | 62.51 | 0.3 | 18.52 |  |  | 715.23 | 4.37 | 0.65 | 0.98
181 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2023 | 1S-DL-YP-ETC-DNNG-2903-LO2023 | A BLOCK KABIR NAGAR:ID | TG-LO2023A-2 | 19503249 | 990 | 320 | 239 | 0.98 | 554 | 196 | 835 | 189 | 805 | 169 | 722 | 101 | 2019-06-01 17:00 | 108.2 | 24.3 | 841 | R | 106 | 95 | 100 | 11 |  |  | 14.9 | 85.1 | 1.3 | 16 | 6.3 | 2 | 511.04 | 621.44 | 621.44 | 601.13 | 203.09 | 77.59 | 106.52 | 112.3 | [8 empty] | 715.43 | 4.17 | 0.6 | 0.56
182 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2023 | 1S-DL-YP-ETC-DNNG-2903-LO2023 | A BLOCK KABIR NAGAR:ID | TG-LO2023A-3 | 19505875 | 630 | 200 | 244 | 0.95 | 325 | 98 | 407 | 104 | 429 | 123 | 510 | 94 | 2019-06-29 11:00 | 137.6 | -13 | 527 | B | 82 | 92 | 126 | 44 |  | 0.4 | 39.9 | 59.7 | 438.17 | 427.47 | 348.26 | 404.47 | 265.59 | 272.59 | 272.59 | 273.59 | 11 | 14.3 | 110.33 | 36.3 | [8 empty] | 715.16 | 4.44 | 0.39 | 0.52
183 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2025 | 1S-DL-YP-ETC-DNNG-2903-LO2025 | B-BLOCK KABIR NAGAR:ID | TG-LO2025A-1 | 19506075 | 990 | 320 | 244 | 0.97 | 816 | 300 | 1291 | 242 | 1037 | 274 | 1174 | 220 | 2019-06-01 | 230.1 | 82.6 | 1291 | R | 109 | 91 | 101 | 18 |  | 3.5 | 54.6 | 42 |  |  |  |  | 15.31 | 153.17 | 153.17 | 42.31 | 664.01 | 538.17 | 629.34 | 648.33 | 12.02 |  | 1.3 | 0.3 |  |  |  |  | 691.34 | 28.26 | 0.62 | 0.82
184 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2025 | 1S-DL-YP-ETC-DNNG-2903-LO2025 | B-BLOCK KABIR NAGAR:ID | TG-LO2025A-2 | 19502720 | 990 | 320 | 243 | 0.97 | 761 | 305 | 1328 | 204 | 891 | 252 | 1075 | 380 | 2019-06-01 22:00 | 167.8 | 55.9 | 1328 | R | 124 | 86 | 90 | 38 | 0.9 | 11.8 | 37.9 | 49.5 |  |  |  |  | 44.3 | 477.13 | 477.13 | 265.55 | 652.12 | 237.26 | 316.29 | 448.44 | 17.57 | [7 empty] | 714.39 | 5.21 | 0.57 | 0.77
185 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2026 | 1S-DL-YP-ETC-DNNG-2903-LO2026 | C BLOCK KABIR NAGAR | TG-LO2026A-1 | 19502709 | 990 | 320 | 237 | 0.96 | 960 | 351 | 1503 | 292 | 1308 | 317 | 1355 | 176 | 2019-06-01 01:00 | 253.9 | 84.6 | 1503 | R | 107 | 95 | 98 | 12 | 53.6 | 5.3 | 11.9 | 29.2 | [5 empty] | 46.39 | 46.39 | 3.3 | 597.34 | 641.25 | 664.5 | 665.04 | 110.07 | 24.2 | 47.04 | 43.5 | 4.43 |  | 0.3 |  | 712.24 | 7.36 | 0.64 | 0.97
186 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2026 | 1S-DL-YP-ETC-DNNG-2903-LO2026 | C BLOCK KABIR NAGAR | TG-LO2026A-2 | 19502707 | 990 | 320 | 243 | 0.98 | 683 | 183 | 745 | 260 | 1062 | 240 | 973 | 283 | 2019-06-01 17:30 | 149.4 | 37.5 | 1162 | Y | 84 | 121 | 95 | 37 | 1.4 | 2.8 | 70.6 | 25.2 |  |  |  |  | 478.57 | 27.18 | 27.18 | 176.53 | 233.48 | 684.27 | 403.2 | 535.52 |  | 1 | [6 empty] | 712.45 | 7.15 | 0.65 | 0.69
187 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2028 | 1S-DL-YP-ETC-DNNG-2903-LO2028 | HARIJAN BASTI WEST JYOTI NARAR:ID | TG-LO2028A-1 | 19502724 | 630 | 200 | 243 | 0.97 | 622 | 234 | 985 | 190 | 795 | 197 | 822 | 178 | 2019-06-29 23:30 | 113.6 | 40.5 | 985 | R | 111 | 87 | 102 | 24 |  |  | 2.8 | 97.2 |  |  |  |  | 16.3 | 155 | 155 | 36 | 535.56 | 534.26 | 605.26 | 586.26 | 136 | 30 | 88.3 | 97 | 31 |  |  |  | 719.26 | 0.34 | 0.61 | 0.99
188 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2028 | 1S-DL-YP-ETC-DNNG-2903-LO2028 | HARIJAN BASTI WEST JYOTI NARAR:ID | TG-LO2028A-2 | 19502719 | 400 | 120 | 237 | 0.98 | 467 | 95 | 398 | 187 | 817 | 186 | 807 | 414 | 2019-06-11 00:30 | 74.5 | 18.2 | 925 | B | 65 | 114 | 121 | 56 | 7.4 | 48.6 | 43.7 | 0.2 | 10.3 |  |  |  | 288.57 | 17 | 17 | 28.3 | 420 | 450.57 | 419.57 | 515.27 |  | 117.3 | 117.3 | 112 |  | 134 | 174 | 63.3 | 719.27 | 0.33 | 0.57 | 1.17
189 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2029 | 1S-DL-YP-ETC-DNNG-2903-LO2029 | KARDAM MARG KHET WALA:-PL | TG-LO2029A-1 | 19506176 | 630 | 200 | 241 | 0.98 | 441 | 171 | 765 | 146 | 641 | 124 | 550 | 187 | 2019-06-08 01:30 | 169.2 | 19 | 786 | Y | 99 | 95 | 106 | 11 | 0.1 | 0.4 | 80.1 | 19.3 | 62.28 | 134.23 | 29.22 | 53 | 471.47 | 409.45 | 409.45 | 476 | 152.43 | 142.04 | 184.19 | 158.12 | 0.14 | 1 | 0.3 | [5 empty] | 687.12 | 32.48 | 0.46 | 0.7
190 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2029 | 1S-DL-YP-ETC-DNNG-2903-LO2029 | KARDAM MARG KHET WALA:-PL | TG-LO2029A-2 | 19506895 | 990 | 320 | 241 | 0.97 | 1018 | 291 | 1264 | 425 | 1883 | 302 | 1302 | 601 | 2019-06-11 23:00 | 302.7 | 65.9 | 1883 | Y | 92 | 107 | 101 | 15 | 0.7 | 0.3 | 57.3 | 41.7 |  |  |  |  | 231.53 | 88.09 | 88.09 | 142.01 | 414.01 | 498.54 | 482.46 | 468.23 | 41.44 | 86.05 | 79.14 | 77.14 | 1 | 15.3 | 1 | 1 | 688.38 | 31.22 | 0.53 | 1.03
191 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2030 | 1S-DL-YP-ETC-DNNG-2903-LO2030 | KARDAM PURI AZAD CHOWK:-ID | TG-LO2030A-1 | 19506684 | 990 | 320 | 243 | 0.96 | 892 | 253 | 1062 | 343 | 1453 | 296 | 1236 | 339 | 2019-06-01 | 268.8 | 95.4 | 1482 | Y | 87 | 118 | 95 | 31 | 0.3 | 16.3 | 33.7 | 49.7 |  |  |  |  | 35.4 |  |  | 1.47 | 657.03 | 560.31 | 675.16 | 676.16 |  | 124.52 | 5.4 | 14.4 |  | 7.2 |  |  | 692.43 | 27.17 | 0.65 | 0.9
192 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2030 | 1S-DL-YP-ETC-DNNG-2903-LO2030 | KARDAM PURI AZAD CHOWK:-ID | TG-LO2030A-2 | 19506490 | 990 | 320 | 251 | 0.96 | 696 | 226 | 911 | 242 | 972 | 228 | 906 | 64 | 2019-06-02 02:00 | 205.4 | 89 | 1025 | Y | 95 | 112 | 92 | 20 | 0.1 | 1.2 | 95.4 | 3.3 |  |  |  |  | 169 | 19.3 | 19.3 | 125.02 | 298.46 | 448.16 | 248.53 | 342.44 | [8 empty] | 692.43 | 27.17 | 0.64 | 0.7
193 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2031 | 1S-DL-YP-ETC-DNNG-2903-LO2031 | NEW KARDAMPURI NO 1 GALI NO -4:PL | TG-LO2031A-1 | 19506465 | 630 | 200 | 238 | 0.97 | 603 | 176 | 784 | 259 | 1183 | 168 | 699 | 448 | 2019-06-29 23:30 | 195.6 | 0.2 | 1183 | Y | 127 | 103 | 70 | 57 | 17.4 | 20.3 | 55.4 | 6.9 | 2.43 | 2.43 | 2.43 | 2.43 | 1.25 | 1.25 | 1.25 | 1.25 | 182.58 | 378.18 | 350.35 | 397.18 | 181.51 | 71.3 | 7.3 | 75 | 107.29 | 22.3 |  |  | 681.18 | 38.42 | 0.71 | 0.96
194 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2032 | 1S-DL-YP-ETC-DNNG-2903-LO2032 | NORTH CHAJJUPUR:ID | TG-LO2032A-1 | 19502700 | 990 | 320 | 246 | 0.97 | 1029 | 337 | 1402 | 310 | 1286 | 382 | 1599 | 275 | 2019-06-11 02:00 | 204.6 | 61.8 | 1604 | B | 96 | 93 | 111 | 18 | 0 | 1.1 | 30.9 | 68.1 |  |  | 0.01 |  | 119.23 | 190.11 | 190.11 | 113.58 | 514 | 445.42 | 514.33 | 494.55 | 62.1 | 62.54 | 104.04 | 87.39 | 3.14 |  | 23.09 | 2.15 | 708.54 | 11.06 | 0.54 | 1.04
195 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2032 | 1S-DL-YP-ETC-DNNG-2903-LO2032 | NORTH CHAJJUPUR:ID | TG-LO2032A-2 | 19505766 | 990 | 320 | 235 | 0.97 | 757 | 255 | 1156 | 257 | 1175 | 246 | 1113 | 55 | 2019-06-08 01:30 | 293.1 | 55.7 | 1176 | R | 104 | 92 | 104 | 12 | 0.2 | 0.2 | 56 | 43.6 |  | 1 |  |  | 167.55 | 254.06 | 254.06 | 191.58 | 543.35 | 456.54 | 566.02 | 520.02 | 0.3 | [7 empty] | 712 | 8 | 0.62 | 0.77
196 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2033 | 1S-DL-YP-ETC-DNNG-2903-LO2033 | RAGHUBIR SINGH GARDEN KARDAM PURI RD:-PL | TG-LO2033A-1 | 19505095 | 990 | 320 | 243 | 0.97 | 649 | 223 | 961 | 225 | 972 | 201 | 853 | 113 | 2019-06-27 09:30 | 204.8 | 63.4 | 1056 | R | 105 | 98 | 97 | 8 | 0.1 | 2.2 | 79.8 | 17.9 |  |  |  |  | 103.39 | 185.5 | 185.5 | 146.27 | 591.59 | 509.48 | 517.11 | 549.11 | [8 empty] | 695.38 | 24.22 | 0.71 | 0.66
197 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2038 | 1S-DL-YP-ETC-DNNG-2903-LO2038 | WEST JYOTI NAGAR NO.1(THAKUR WALA):K | TG-LO2038A-1 | 19505191 | 630 | 200 | 241 | 0.97 | 507 | 107 | 466 | 208 | 931 | 193 | 858 | 434 | 2019-06-08 02:00 | 190.2 | 35.6 | 931 | Y | 98 | 99 | 103 | 5 | 0.1 | 0.4 | 53.5 | 46 |  |  |  |  | 179 | 173 | 173 | 170.3 | 515.47 | 520.47 | 550.17 | 524.47 | 1 | 2 | 4.3 | 0.3 |  |  |  |  | 695.47 | 24.13 | 0.62 | 0.8
198 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2039 | 1S-DL-YP-ETC-DNNG-2903-LO2039 | NEW KARDAMPURI NO 2 GALI NO-8:PL | TG-LO2039A-1 | 19504913 | 990 | 320 | 243 | 0.96 | 692 | 188 | 800 | 183 | 765 | 321 | 1369 | 587 | 2019-06-30 | 156.8 | 75.1 | 1405 | B | 84 | 79 | 136 | 57 |  | 9.6 | 89.2 | 1.2 |  |  |  |  | 383.11 | 503.3 | 503.3 | 159.37 | 330.28 | 210.09 | 645.39 | 554.02 |  |  | 64.3 | [5 empty] | 713.39 | 6.21 | 0.67 | 0.7
199 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2039 | 1S-DL-YP-ETC-DNNG-2903-LO2039 | NEW KARDAMPURI NO 2 GALI NO-8:PL | TG-LO2039A-2 | 19506009 | 630 | 200 | 255.5376 | 0.96332 | 443.7338 | 154.8245 | 623.4378 | 165.9429 | 672.596 | 122.9663 | 487.6714 | 165.9008 | 2019-06-01 | [15 empty] | 0 |  |  |  | 120.5 |  |  |  | 596.5 |  |  |  | 0 |  |  |  | 0 | 717 |  | 0.66941 | 0.70434
200 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2040 | 1S-DL-YP-ETC-DNNG-2903-LO2040 | STORM WATER PUMPING STN ( NAHAR ROAD):PL | TG-LO2040A-1 | 19504771 | 400 | 120 | 240 | 0.86 | 22 | 6 | 24 | 12 | 49 | 4 | 16 | 30 | 2019-06-11 19:30 | 13.8 | 0.6 | 62 | Y | 62 | 164 | 74 | 102 |  |  | 12.3 | 87.7 | 718.45 | 718.45 | 718.45 | 718.45 | [16 empty] | 718.45 | 1.15 | 0.57 | 0.05
201 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2041 | 1S-DL-YP-ETC-DNNG-2903-LO2041 | West Jyoti Ngr(Beh. Gopal Nur Home):-PL | TG-LO2041A-1 | 19506073 | 990 | 320 | 245 | 0.98 | 900 | 354 | 1474 | 295 | 1232 | 251 | 1046 | 372 | 2019-06-11 00:30 | 228.8 | 39.4 | 1499 | R | 118 | 101 | 81 | 37 | 0.2 | 0.1 | 0.9 | 98.8 |  |  |  |  | 63 | 142.26 | 142.26 | 161.19 | 550.2 | 557.23 | 338.3 | 543.29 | 91.29 | 15.48 | 0.3 | 10.49 | 10.48 |  |  |  | 715.37 | 4.23 | 0.56 | 0.91
202 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2041 | 1S-DL-YP-ETC-DNNG-2903-LO2041 | West Jyoti Ngr(Beh. Gopal Nur Home):-PL | TG-LO2041A-2 | 19506072 | 990 | 320 | 245 | 0.97 | 667 | 259 | 1086 | 181 | 746 | 227 | 949 | 296 | 2019-06-11 00:30 | 161.9 | 32 | 1147 | R | 120 | 81 | 99 | 39 | 0.3 | 0.1 | 39.5 | 60.1 | 1.3 | 108.02 | 17.3 | 17.3 | 336.22 | 499.17 | 499.17 | 481.41 | 355.14 | 85.47 | 180.11 | 193.55 | [8 empty] | 693.06 | 26.54 | 0.52 | 0.67
203 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2044 | 1S-DL-YP-ETC-DNNG-2903-LO2044 | CNG STATION LONI ROAD:PM | TG-LO2044A-1 | 19503385 | 400 | 120 | 242 | 0.84 | 16 | 6 | 25 | 3 | 11 | 7 | 29 | 17 | 2019-06-14 03:30 | 5.8 | -9.1 | 31 | B | 91 | 85 | 124 | 39 |  | 0.1 | 50.7 | 49.2 | 719.4 | 719.4 | 719.4 | 719.4 | [16 empty] | 719.4 | 0.2 | 0.74 | 0.04
204 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2044 | 1S-DL-YP-ETC-DNNG-2903-LO2044 | CNG STATION LONI ROAD:PM | TG-LO2044A-2 | 19506633 | 400 | 120 | 241 | 0.67 | 355 | 118 | 481 | 118 | 482 | 119 | 489 | 8 | 2019-06-04 06:00 | 334.2 | -121.2 | 518 | B | 99 | 100 | 102 | 3 |  |  | 0.9 | 99.1 | 16 | 15.3 | 15.3 | 15.3 | 456 | 455 | 455 | 455.3 | 194.56 | 195.26 | 187.56 | 193.56 | 27 | 28 | 36.3 | 29 |  |  |  |  | 693.56 | 26.04 | 0.44 | 0.89
205 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2046 | 1S-DL-YP-ETC-DNNG-2903-LO2046 | SUDAMAPURI S/S- 5 Nr. BABARPUR BUS TERM. | TG-LO2046A-1 | 19505667 | 630 | 200 | 252 | 0.97 | 886 | 312 | 1364 | 250 | 1077 | 324 | 1419 | 319 | 2019-06-08 01:30 | 291.4 | 38 | 1579 | B | 99 | 81 | 120 | 39 | 0.4 | 0.3 | 5.5 | 93.8 |  |  |  |  | 33.3 | 102 | 102 | 11 | 499.57 | 567.15 | 347.26 | 533 | 140.25 | 41.1 | 266.22 | 152.37 | 37.03 | 0.3 | 97.07 | 14.18 | 710.55 | 9.05 | 0.48 | 1.41
206 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2048 | 1S-DL-YP-ETC-DNNG-2903-LO2048 | WEST JYOTI NAGAR THANA | TG-LO2048A-1 | 19506233 | 400 | 120 | 251 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [7 empty] | 81.8 | 18.2 | 707.51 | 707.51 | 707.51 | 707.51 | [16 empty] | 707.51 | 12.09 |  | 0
207 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2048 | 1S-DL-YP-ETC-DNNG-2903-LO2048 | WEST JYOTI NAGAR THANA | TG-LO2048A-2 | 19506257 | 400 | 120 | 251 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [6 empty] | 0.1 | 75 | 24.9 | 719.51 | 719.51 | 719.51 | 719.51 | [16 empty] | 719.51 | 0.09 |  | 0
208 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2050 | 1S-DL-YP-ETC-DNNG-2903-LO2050 | C BLOCK KABIR NAGAR S/STN No.2(NALEWALA) | TG-LO2050A-1 | 19506550 | 630 | 200 | 244 | 0.97 | 304 | 120 | 490 | 123 | 503 | 62 | 251 | 246 | 2019-06-04 16:30 | 105.8 | 21.2 | 555 | R | 105 | 110 | 84 | 26 | 0.1 | 0.1 | 0.5 | 99.3 | 3.57 | 1.27 | 61.53 | 3.27 | 582.31 | 508.32 | 508.32 | 634.4 | 103.19 | 179.48 | 11 | 51.4 | [8 empty] | 689.47 | 30.13 | 0.67 | 0.48
209 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2051 | 1S-DL-YP-ETC-DNNG-2903-LO2051 | B BLOCK KABIR NAGAR S/STN (NALEWALA) | TG-LO2051A-1 | 19506668 | 630 | 200 | 232 | 0.98 | 247 | 151 | 682 | 41 | 180 | 56 | 248 | 472 | 2019-06-01 | 65.8 | 6.2 | 691 | R | 186 | 61 | 52 | 134 | 0.1 | 2.1 | 46.5 | 51.2 | 2.41 | 680.18 | 674.34 | 194.07 | 282.25 | 11.19 | 11.19 | 497.3 | 406.31 | [11 empty] | 691.37 | 28.23 | 0.58 | 0.39