## Loading Condition > 80%
MIS Report of Distribution Transformer - Jun19
Jun19 1260 NAND NAGARI (Loading Condition > 80% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR007 | 1S-DL-YP-ETC-DNNG-2901-NGR007 | JANTA FLAT S/S NO.2 GTB ENCLAVE:ID | TG-NGR007A-2 | 19505794 | 630 | 200 | 232 | 0.97 | 593 | 164 | 687 | 186 | 786 | 244 | 1049 | 324 | 2019-06-03 | 148.8 | 34.8 | 1073 | B | 92 | 106 | 102 | 14 | 0.1 | 2.9 | 38.6 | 58.5 |  |  |  |  | 255.31 | 182.42 | 182.42 | 209.01 | 460.36 | 473.02 | 451.42 | 473.43 | 2.3 | 56.23 | 41.23 | 35.53 |  | 6.3 | 12.3 |  | 718.37 | 1.23 | 0.54 | 0.94
2 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR007 | 1S-DL-YP-ETC-DNNG-2901-NGR007 | JANTA FLAT S/S NO.2 GTB ENCLAVE:ID | TG-NGR007A-1 | 19505795 | 630 | 200 | 248 | 0.96 | 525 | 174 | 736 | 217 | 939 | 134 | 570 | 321 | 2019-06-30 23:30 | 145.2 | 44.2 | 939 | Y | 99 | 120 | 82 | 38 |  | 1.7 | 57.8 | 40.5 | 0.3 |  | 5.24 |  | 291.26 | 152.14 | 152.14 | 269.03 | 422.21 | 481.4 | 241.21 | 442.44 | 4.3 | 78.53 |  | 7 |  | 6 |  |  | 718.47 | 1.13 | 0.56 | 0.83
3 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR007 | 1S-DL-YP-ETC-DNNG-2901-NGR007 | JANTA FLAT S/S NO.2 GTB ENCLAVE:ID | TG-NGR007A-3 | 19505801 | 630 | 200 | 239 | 0.97 | 518 | 218 | 944 | 114 | 480 | 186 | 788 | 409 | 2019-06-12 00:30 | 122 | 28.2 | 984 | B | 91 | 89 | 120 | 31 |  | 0.9 | 39.5 | 59.6 | 20.55 | 8.25 | 0.3 | 2.26 | 398.29 | 450.29 | 450.29 | 363.58 | 298.53 | 250.23 | 438.23 | 349.53 |  | 9.3 | 63.23 | 2.3 | 0.3 |  | 1 |  | 718.47 | 1.13 | 0.52 | 0.82
4 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR008 | 1S-DL-YP-ETC-DNNG-2901-NGR008 | JANTA FLAT S/S NO.3 GTB ENCLAVE:ID | TG-NGR008A-2 | 19505177 | 990 | 320 | 242 | 0.97 | 926 | 222 | 910 | 303 | 1264 | 401 | 1678 | 666 | 2019-06-30 00:30 | 247 | 59.5 | 1678 | B | 86 | 109 | 105 | 23 |  | 1.5 | 43.7 | 54.8 | 1.45 | 1.45 | 1.45 | 1.45 | 328.47 | 180.47 | 180.47 | 215.47 | 363.46 | 444.46 | 446.16 | 455.46 |  | 62 | 49.3 | 21 |  | 5 | 3.3 |  | 694.18 | 25.42 | 0.52 | 0.94
5 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR014 | 1S-DL-YP-ETC-DNNG-2901-NGR014 | I.J K BLOCK SUNDER NAGARI:K | TG-NGR014A-1 | 19502680 | 990 | 320 | 235 | 0.96 | 876 | 267 | 1129 | 303 | 1289 | 306 | 1293 | 162 | 2019-06-11 23:00 | 243.6 | 106 | 1604 | B | 89 | 100 | 112 | 23 |  |  | 19.7 | 80.3 |  |  |  |  | 10.3 |  |  | 1.3 | 700.51 | 667.51 | 503.31 | 660.3 | 5.3 | 49 | 195.2 | 54.51 |  |  | 16.3 |  | 716.51 | 3.09 | 0.72 | 0.88
6 | 2019-06-18 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR014 | 1S-DL-YP-ETC-DNNG-2901-NGR014 | I.J K BLOCK SUNDER NAGARI:K | TG-NGR014A-2 | 19505808 | 990 | 320 | 237 | 0.96 | 719 | 227 | 956 | 213 | 906 | 279 | 1187 | 259 | 2019-06-28 23:30 | 224 | 90.6 | 1245 | B | 95 | 88 | 117 | 29 |  | 0.2 | 30.2 | 69.7 |  |  |  |  | 24 | 70 | 70 | 9.3 | 263.16 | 217.16 | 271.46 | 277.46 |  |  | 15 | [5 empty] | 287.16 | 24.44 | 0.72 | 0.73
7 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR015 | 1S-DL-YP-ETC-DNNG-2901-NGR015 | MN BLOCK SUNDER NAGARI:K | TG-NGR015A-2 | 19506466 | 630 | 200 | 242 | 0.96 | 555 | 176 | 740 | 169 | 708 | 209 | 880 | 158 | 2019-06-11 | 173.2 | 61.2 | 908 | B | 99 | 90 | 111 | 21 | 1.5 | 0.6 | 19.8 | 78.1 |  |  |  |  | 2 | 28.3 | 28.3 | 3.3 | 688.34 | 660.39 | 537.1 | 663.09 | 4 | 5.25 | 154.24 | 27.55 |  |  | 1.3 |  | 694.34 | 25.26 | 0.71 | 0.88
8 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR016 | 1S-DL-YP-ETC-DNNG-2901-NGR016 | E-1 NAND NAGARI PK WALA GAGAN CINEMA:PL | TG-NGR016A-1 | 19505497 | 630 | 200 | 254 | 0.94 | 553 | 142 | 595 | 199 | 849 | 211 | 913 | 291 | 2019-06-14 16:00 | 211.6 | 28.6 | 913 | B | 78 | 107 | 115 | 37 | 0.1 | 12.2 | 72.5 | 15.2 | 134.17 |  |  |  | 9.3 | 14.3 | 14.3 | 13.3 | 552.27 | 642.22 | 599.22 | 675.52 |  | 39.22 | 92.52 | 6.52 |  |  | 1 |  | 696.14 | 23.46 | 0.66 | 0.88
9 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR018 | 1S-DL-YP-ETC-DNNG-2901-NGR018 | E-4 NAND NAGARI:ID | TG-NGR018A-1 | 19506221 | 630 | 200 | 243 | 0.96 | 635 | 234 | 1020 | 226 | 980 | 175 | 748 | 254 | 2019-06-08 00:30 | 228.8 | 58.8 | 1020 | R | 103 | 106 | 92 | 14 | 0.1 | 0.2 | 7.7 | 92 |  |  |  |  | 12.3 | 7.3 | 7.3 | 9 | 538.04 | 556.23 | 647.28 | 576.3 | 131.54 | 125.35 | 27.18 | 106.28 | 9.48 | 2.48 |  | 0.18 | 692.16 | 27.44 | 0.64 | 1.01
10 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR018 | 1S-DL-YP-ETC-DNNG-2901-NGR018 | E-4 NAND NAGARI:ID | TG-NGR018A-3 | 19506699 | 630 | 200 | 238 | 0.96 | 631 | 193 | 846 | 223 | 985 | 215 | 938 | 122 | 2019-06-08 21:00 | 233.6 | 59.6 | 985 | Y | 94 | 108 | 99 | 14 |  |  | 2.1 | 97.9 |  |  |  |  | 23.3 | 2 | 2 | 3.3 | 640.57 | 584.49 | 663.42 | 645.23 | 38.49 | 115.57 | 34.34 | 53.53 |  | 0.3 | 0.3 | 0.3 | 703.16 | 16.44 | 0.63 | 1
11 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR019 | 1S-DL-YP-ETC-DNNG-2901-NGR019 | JAGAT PURI EXT.NO.1:ID | TG-NGR019A-1 | 19505917 | 990 | 320 | 244 | 0.97 | 883 | 293 | 1205 | 340 | 1390 | 250 | 1017 | 323 | 2019-06-11 23:30 | 241 | 81.9 | 1450 | Y | 94 | 111 | 95 | 17 |  | 0.1 | 15.8 | 84.2 |  |  |  |  | 62.3 | 9.3 | 9.3 | 10 | 626.08 | 605.25 | 649.38 | 664.38 | 30.3 | 99.43 | 35.3 | 44.3 |  | 4.3 |  |  | 719.08 | 0.52 | 0.66 | 0.89
12 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR021 | 1S-DL-YP-ETC-DNNG-2901-NGR021 | A-4 NAND NAGARI:ID | TG-NGR021A-1 | 19504975 | 630 | 200 | 240 | 0.96 | 460 | 204 | 858 | 127 | 543 | 129 | 565 | 304 | 2019-06-30 23:00 | 110.4 | 48.3 | 863 | R | 125 | 79 | 97 | 46 | 94.1 | 5.9 | [6 empty] | 9 | 413.06 | 413.06 | 82.09 | 635.39 | 303.03 | 581.41 | 634 | 71.3 | [7 empty] | 716.09 | 3.51 | 0.69 | 0.73
13 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR021 | 1S-DL-YP-ETC-DNNG-2901-NGR021 | A-4 NAND NAGARI:ID | TG-NGR021A-2 | 19505803 | 990 | 320 | 240 | 0.96 | 789 | 315 | 1331 | 214 | 890 | 259 | 1077 | 384 | 2019-06-30 00:30 | 300.2 | 85.8 | 1385 | R | 117 | 87 | 96 | 30 |  | 0.5 | 68.1 | 31.4 |  |  |  |  | 11 | 98.23 | 98.23 | 28.59 | 604.49 | 617.47 | 655.47 | 687.11 | 100.21 |  | 1 | [5 empty] | 716.1 | 3.5 | 0.7 | 0.8
14 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR022 | 1S-DL-YP-ETC-DNNG-2901-NGR022 | B-4 NAND NAGARI AKHADA WALA :ID | TG-NGR022A-3 | 19505435 | 630 | 200 | 246 | 0.95 | 526 | 168 | 704 | 216 | 913 | 142 | 586 | 287 | 2019-06-01 23:00 | 192.6 | 57.2 | 913 | Y | 94 | 120 | 86 | 34 | 0.3 | 24.1 | 72.5 | 3.1 |  |  |  |  | 173.26 | 26.3 | 26.3 | 106.56 | 545.19 | 629.33 | 500.33 | 611.2 |  | 62.13 |  | 0.29 |  | 0.29 |  |  | 718.45 | 1.15 | 0.61 | 0.84
15 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR023 | 1S-DL-YP-ETC-DNNG-2901-NGR023 | C BLOCK COMPLAINT CENTRE NNG:ID | TG-NGR023A-3 | 19502635 | 630 | 200 | 244 | 0.96 | 585 | 203 | 838 | 197 | 805 | 185 | 766 | 63 | 2019-06-29 23:30 | 146.3 | 62.1 | 887 | R | 108 | 100 | 92 | 16 |  | 0 | 77.9 | 22.1 |  |  |  |  | 4.3 | 28 | 28 | 19.3 | 584.11 | 596.32 | 633.06 | 617.32 | 127.5 | 93.29 | 19 | 80.59 | 1.3 |  |  |  | 718.01 | 1.59 | 0.67 | 0.93
16 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR035 | 1S-DL-YP-ETC-DNNG-2901-NGR035 | MANDOLI EXTN.NO.1,GALI NO.-9:ID | TG-NGR035A-1 | 19502142 | 400 | 120 | 238 | 0.97 | 388 | 155 | 702 | 116 | 521 | 117 | 524 | 179 | 2019-06-02 21:30 | 72 | 27.6 | 741 | R | 112 | 95 | 93 | 19 |  | 0.1 | 14.8 | 85.1 |  |  | 0.3 |  | 1 | 23 | 23 | 12 | 578.29 | 659.16 | 652.16 | 657.13 | 97.17 | 11.3 | 7.3 | 24.33 | 17 |  |  |  | 715.07 | 4.53 | 0.6 | 0.97
17 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR035 | 1S-DL-YP-ETC-DNNG-2901-NGR035 | MANDOLI EXTN.NO.1,GALI NO.-9:ID | TG-NGR035A-2 | 19506611 | 990 | 320 | 238 | 0.97 | 874 | 307 | 1305 | 236 | 996 | 331 | 1418 | 378 | 2019-06-10 22:00 | 263.7 | 6.4 | 1469 | B | 109 | 83 | 108 | 26 |  | 1.1 | 28.4 | 70.4 | 0.3 | 0.3 | 0.3 | 0.3 |  | 72 | 72 | 0.3 | 634.28 | 619.27 | 626.14 | 677.4 | 56.59 |  | 64.43 | 13.17 |  |  | 0.3 |  | 691.57 | 28.03 | 0.66 | 0.88
18 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR044 | 1S-DL-YP-ETC-DNNG-2901-NGR044 | SAFAI KARAMCHARI NAND NAGARI-E BLK:ID | TG-NGR044A-1 | 19503383 | 400 | 120 | 235 | 0.97 | 336 | 112 | 500 | 124 | 549 | 100 | 445 | 90 | 2019-06-09 23:00 | 70.7 | 21 | 559 | R | 107 | 109 | 84 | 25 | 0.1 |  | 2.4 | 97.5 |  |  | 8.3 | 1 | 115.28 | 143.28 | 143.28 | 168.58 | 556 | 470.3 | 371.3 | 521 | 48.3 | 106 |  | 29 |  |  |  |  | 719.58 | 0.02 | 0.62 | 0.84
19 | 2019-06-04 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1017 | 1S-DL-YP-ETC-DNNG-2902-LO1017 | E JYOTI NAGAR BEHAIND JOYATI NURSING:ID | TG-LO1017A-1 | 19502178 | 630 | 200 | 237 | 0.98 | 578 | 143 | 624 | 209 | 923 | 226 | 1002 | 345 | 2019-06-30 01:30 | 127.9 | 19.8 | 1002 | B | 72 | 120 | 109 | 48 |  | 1.6 | 76.6 | 21.8 | 39.38 |  | 1 | 0.3 | 445.28 | 174.11 | 174.11 | 291.25 | 137.36 | 381.35 | 320.2 | 326.12 |  | 64.58 | 43.05 | 4.35 |  | 1.58 | 0.2 |  | 622.42 | 25.18 | 0.49 | 0.92
20 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1017 | 1S-DL-YP-ETC-DNNG-2902-LO1017 | E JYOTI NAGAR BEHAIND JOYATI NURSING:ID | TG-LO1017A-3 | 19502206 | 990 | 320 | 243 | 0.97 | 1003 | 394 | 1696 | 354 | 1507 | 255 | 1076 | 551 | 2019-06-30 01:30 | 205.3 | 53 | 1696 | R | 107 | 92 | 102 | 15 |  | 0.3 | 25 | 74.7 |  | 0.3 |  |  | 150.4 | 271.34 | 271.34 | 188.57 | 461.18 | 397.55 | 444.16 | 457.28 | 80.42 | 27.33 | 65.11 | 52.07 | 6.22 | 1.3 | 2.54 | 0.3 | 699.02 | 20.58 | 0.51 | 1.01
21 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1017 | 1S-DL-YP-ETC-DNNG-2902-LO1017 | E JYOTI NAGAR BEHAIND JOYATI NURSING:ID | TG-LO1017A-4 | 19506358 | 630 | 200 | 247 | 0.97 | 587 | 166 | 690 | 219 | 922 | 202 | 850 | 206 | 2019-06-30 01:00 | 191 | 30.4 | 1029 | Y | 80 | 117 | 103 | 37 | 0.3 | 0.7 | 81.9 | 17.1 | 20.24 |  |  |  | 421.16 | 168.06 | 168.06 | 253.17 | 243.46 | 447.21 | 461.24 | 426.49 |  | 60.26 | 6.43 | 5.2 |  | 9.33 |  |  | 685.26 | 34.34 | 0.5 | 0.93
22 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1024 | 1S-DL-YP-ETC-DNNG-2902-LO1024 | EAST OF LONI ROAD,MIG,S/STN-7:ID | TG-LO1024A-1 | 19502176 | 400 | 120 | 234 | 0.99 | 365 | 112 | 481 | 114 | 485 | 139 | 598 | 115 | 2019-06-03 02:30 | 56.3 | -11 | 648 | B | 101 | 77 | 122 | 45 |  | 0.6 | 51.9 | 47.6 | 6 | 59.3 | 52 | 17.3 | 361.15 | 463.38 | 463.38 | 342.57 | 328.02 | 194.03 | 384.11 | 342.29 | 23.18 | 1.24 | 122.03 | 15.39 |  |  | 5.54 |  | 718.35 | 1.25 | 0.48 | 0.91
23 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1024 | 1S-DL-YP-ETC-DNNG-2902-LO1024 | EAST OF LONI ROAD,MIG,S/STN-7:ID | TG-LO1024A-2 | 19502202 | 400 | 120 | 241 | 0.98 | 335 | 146 | 617 | 95 | 404 | 93 | 401 | 215 | 2019-06-11 23:30 | 62.9 | 10.5 | 617 | R | 126 | 86 | 89 | 40 | 12.8 | 85.2 | 1.9 |  |  | 16.3 | 28 |  | 120 | 413.07 | 413.07 | 327.11 | 478.37 | 288.58 | 317.28 | 383 | 109.04 |  |  | 8.24 | 10.54 |  |  |  | 718.35 | 1.25 | 0.55 | 0.84
24 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1027 | 1S-DL-YP-ETC-DNNG-2902-LO1027 | D-BLOCK ASHOK NAGAR GALI NO-13:ID | TG-LO1027A-2 | 19506250 | 630 | 200 | 235 | 0.97 | 438 | 157 | 661 | 203 | 865 | 78 | 326 | 471 | 2019-06-10 02:00 | 134 | 29.8 | 918 | Y | 108 | 113 | 79 | 34 | 0.2 | 1.9 | 21 | 76.9 |  | 3.3 | 6 |  | 314 | 317 | 317 | 384 | 380.17 | 340.17 | 79 | 310.17 |  | 33.3 | [6 empty] | 694.17 | 25.43 | 0.58 | 0.7
25 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1028 | 1S-DL-YP-ETC-DNNG-2902-LO1028 | D-BLOCK ASHOK NAGAR GALI NO-3:ID | TG-LO1028A-1 | 19503018 | 990 | 320 | 235 | 0.97 | 950 | 381 | 1641 | 319 | 1392 | 250 | 1096 | 472 | 2019-06-30 | 186.9 | 43.4 | 1690 | R | 130 | 99 | 71 | 59 | 2.4 | 22.4 | 72.2 | 3 | 0.27 | 0.27 | 143.49 | 2.27 | 160.53 | 385.32 | 385.32 | 350.3 | 458.17 | 301.02 | 116.39 | 338.04 | 76.03 | 23.53 |  | 19.53 | 15.14 |  |  |  | 710.54 | 9.06 | 0.45 | 0.96
26 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1028 | 1S-DL-YP-ETC-DNNG-2902-LO1028 | D-BLOCK ASHOK NAGAR GALI NO-3:ID | TG-LO1028A-2 | 19503472 | 630 | 200 | 234 | 0.97 | 549 | 170 | 759 | 178 | 800 | 201 | 892 | 118 | 2019-06-10 23:30 | 126.5 | 39.6 | 1046 | B | 97 | 98 | 105 | 8 |  | 3.1 | 28.8 | 68.1 |  | 0.09 | 48.24 |  | 109 | 134.12 | 134.12 | 112.4 | 596.52 | 545.37 | 514 | 577.06 | 5 | 30.54 | 92.25 | 21.06 |  |  | 6.24 |  | 710.52 | 9.08 | 0.61 | 0.87
27 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1028 | 1S-DL-YP-ETC-DNNG-2902-LO1028 | D-BLOCK ASHOK NAGAR GALI NO-3:ID | TG-LO1028A-3 | 19504095 | 990 | 200 | 235 | 0.97 | 941 | 334 | 1502 | 324 | 1446 | 283 | 1246 | 233 | 2019-06-10 23:30 | 195 | 49.2 | 1584 | B | 102 | 101 | 98 | 4 | 0.1 | 3.3 | 78.5 | 18.2 |  |  |  |  | 132.45 | 177.19 | 177.19 | 166.46 | 522.25 | 453.39 | 406.53 | 478.42 | 30.3 | 56.12 | 43.04 | 41.42 | 1.3 |  | 8.42 |  | 710.54 | 9.06 | 0.54 | 0.95
28 | 2019-06-10 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1029 | 1S-DL-YP-ETC-DNNG-2902-LO1029 | B-BLOCK ASHOK NAGAR SCHOOL WALA:K | TG-LO1029A-2 | 19502179 | 630 | 200 | 245 | 0.96 | 595 | 144 | 616 | 245 | 1057 | 207 | 890 | 386 | 2019-06-30 02:00 | 148.1 | 42.3 | 1087 | Y | 80 | 116 | 104 | 36 |  |  | 13.5 | 86.5 | 2 |  |  |  | 274.21 | 113.16 | 113.16 | 162.15 | 216.32 | 301.35 | 323.49 | 308.15 |  | 59.25 | 36.02 | 22.23 |  | 18.37 |  |  | 492.53 | 11.07 | 0.52 | 0.94
29 | 2019-06-02 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1031 | 1S-DL-YP-ETC-DNNG-2902-LO1031 | HARDEV PURI NO.1:ID | TG-LO1031A-1 | 19502158 | 990 | 320 | 241 | 0.97 | 805 | 198 | 857 | 356 | 1584 | 251 | 1124 | 637 | 2019-06-11 | 171.5 | 75.8 | 1584 | Y | 75 | 124 | 101 | 49 | 0.4 | 21.9 | 73.5 | 4.3 |  |  |  |  | 357.59 | 10.3 | 10.3 | 86.23 | 332.48 | 558.47 | 591.54 | 603.24 |  | 110 |  | 1 |  | 11.3 |  |  | 690.47 | 5.13 | 0.65 | 0.81
30 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1033 | 1S-DL-YP-ETC-DNNG-2902-LO1033 | E-1 BLK ASHOK NAGAR.KANCH WALA NR S BHAWAN:K | TG-LO1033A-1 | 19504098 | 630 | 200 | 250 | 0.97 | 587 | 223 | 879 | 235 | 948 | 130 | 515 | 403 | 2019-06-03 01:30 | 135.7 | 47.4 | 992 | Y | 113 | 120 | 67 | 53 | 0.3 | 13.5 | 85 | 1.2 | 1 | 1 | 10.3 | 1 | 22.3 | 13 | 13 | 81.37 | 595.4 | 561.05 | 232.35 | 595.44 | 89.41 | 121.46 |  | 37.28 | 6.58 | 18.58 |  |  | 715.49 | 4.11 | 0.59 | 0.93
31 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1035 | 1S-DL-YP-ETC-DNNG-2902-LO1035 | NATHU COLONY:K | TG-LO1035A-1 | 19506177 | 990 | 320 | 235 | 0.97 | 912 | 248 | 1090 | 324 | 1443 | 340 | 1541 | 411 | 2019-06-11 23:30 | 265 | 64.3 | 1778 | B | 91 | 108 | 101 | 17 | 5.9 | 16 | 72.4 | 5.7 | 0.3 | 0.3 | 0.3 | 0.3 | 102.51 | 30 | 30 | 45.21 | 584.54 | 577.45 | 594.55 | 625.54 | 1 | 80.3 | 39.3 | 17.3 |  | 0.3 | 2.3 |  | 689.15 | 30.45 | 0.61 | 0.92
32 | 2019-06-04 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1040 | 1S-DL-YP-ETC-DNNG-2902-LO1040 | DURGAPURI EXT. OPP KALA NIKETAN SCHOOL:K | TG-LO1040A-1 | 19502154 | 990 | 320 | 245 | 0.96 | 765 | 332 | 1458 | 173 | 749 | 259 | 1107 | 615 | 2019-06-30 23:30 | 170 | 83.9 | 1458 | R | 124 | 71 | 104 | 53 | 2.6 | 56.2 | 41.2 | [5 empty] | 29.56 | 506.31 | 506.31 | 132.43 | 531.33 | 140.12 | 543.1 | 514 | 82.19 |  |  |  | 2.55 |  |  |  | 646.43 | 1.17 | 0.64 | 0.77
33 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1043 | 1S-DL-YP-ETC-DNNG-2902-LO1043 | LALITA MANDIR ASHOK NAGAR D BLK:PL | TG-LO1043A-1 | 19502640 | 990 | 320 | 244 | 0.96 | 907 | 319 | 1378 | 324 | 1408 | 264 | 1144 | 250 | 2019-06-26 23:30 | 214.2 | 84.6 | 1568 | R | 108 | 102 | 90 | 18 |  |  | 14.6 | 85.4 |  |  |  |  | 17 | 47.27 | 47.27 | 46.46 | 591.16 | 600.43 | 591.52 | 618.24 | 97.43 | 62.19 | 3.21 | 45.19 | 4.3 |  |  |  | 710.29 | 9.31 | 0.62 | 0.92
34 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1053 | 1S-DL-YP-ETC-DNNG-2902-LO1053 | D 1/1 BLK ASHOK NAGAR DP :PL | TG-LO1053A-1 | 19505926 | 990 | 320 | 242 | 0.97 | 928 | 394 | 1684 | 302 | 1281 | 232 | 981 | 611 | 2019-06-29 23:30 | 275.5 | 53.8 | 1684 | R | 111 | 104 | 85 | 26 |  | 0.4 | 14.2 | 85.4 |  | 1.02 | 1.02 | 0.32 | 132.36 | 105.04 | 105.04 | 157.34 | 516.47 | 582.17 | 376.15 | 540.03 | 54.16 | 24.4 |  | 14.54 | 9.24 |  |  |  | 713.03 | 6.57 | 0.53 | 0.94
35 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1061 | 1S-DL-YP-ETC-DNNG-2902-LO1061 | JAGAT PURI MAIN:PL | TG-LO1061A-1 | 19503373 | 630 | 200 | 237 | 0.97 | 603 | 174 | 741 | 225 | 964 | 204 | 873 | 194 | 2019-06-11 23:00 | 109.9 | 15.6 | 1035 | R | 98 | 102 | 100 | 4 |  | 2.9 | 38.7 | 58.3 | 33.1 |  |  |  | 49.52 | 73.26 | 73.26 | 56.09 | 551.12 | 549.03 | 548.03 | 589.35 | 48.23 | 59.08 | 49 | 41.53 | 5 | 6 | 0.3 |  | 711.05 | 8.55 | 0.58 | 0.96
36 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1063 | 1S-DL-YP-ETC-DNNG-2902-LO1063 | JAG JIVAN NAGAR:PL | TG-LO1063A-1 | 19506222 | 990 | 320 | 230 | 0.97 | 1078 | 322 | 1419 | 418 | 1857 | 338 | 1510 | 400 | 2019-06-06 00:30 | 275.2 | 54.4 | 1928 | Y | 90 | 121 | 89 | 32 | 0.3 | 1.5 | 60.5 | 37.8 |  |  |  |  | 163.16 | 3 | 3 | 60.49 | 511.49 | 548.05 | 512.34 | 586.02 | 32.59 | 132.32 | 24.03 | 60.34 | 0.59 | 25.26 | 2.19 | 1.38 | 709.03 | 10.57 | 0.53 | 1.09
37 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2006 | 1S-DL-YP-ETC-DNNG-2903-LO2006 | JYOTI COLONY NO.3:K | TG-LO2006A-2 | 19506078 | 630 | 200 | 242 | 0.96 | 689 | 283 | 1176 | 199 | 814 | 207 | 854 | 344 | 2019-06-12 00:30 | 203.6 | 25.2 | 1177 | R | 106 | 97 | 97 | 9 | 0.2 | 2.3 | 7.1 | 90.4 | 1 | 1 | 1 | 1 | 83.32 | 104.54 | 104.54 | 83.02 | 529.29 | 554.24 | 584.39 | 563.46 | 47.56 | 27.47 | 19.13 | 37.39 | 26.08 |  |  | 2.38 | 688.05 | 31.55 | 0.49 | 1.09
38 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2012 | 1S-DL-YP-ETC-DNNG-2903-LO2012 | BABAR PUR VILLAGE:PL | TG-LO2012A-1 | 19502729 | 630 | 200 | 238 | 0.97 | 525 | 140 | 589 | 181 | 772 | 203 | 869 | 246 | 2019-06-11 23:30 | 128.8 | 36.8 | 1038 | B | 84 | 89 | 127 | 43 |  | 21.1 | 71 | 7.9 |  |  |  |  | 126.19 | 159.19 | 159.19 | 23.24 | 586.41 | 540.41 | 547.17 | 685.06 |  | 13 | 150.43 | 4.3 |  |  | 14 |  | 713 | 7 | 0.68 | 0.83
39 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2013 | 1S-DL-YP-ETC-DNNG-2903-LO2013 | MAHA DEVI SCHOOL:PL | TG-LO2013A-2 | 19502722 | 630 | 200 | 241 | 0.97 | 550 | 131 | 562 | 207 | 905 | 212 | 928 | 355 | 2019-06-29 00:30 | 113.6 | 31.3 | 928 | B | 75 | 104 | 121 | 46 | 0.4 | 40.9 | 58.7 | 0.1 | 5.3 |  |  |  | 386.53 | 97.3 | 97.3 | 89.2 | 319.13 | 594.58 | 633.38 | 618.46 |  | 19.08 | 60.27 | 3.3 |  |  | 0.3 |  | 711.36 | 8.24 | 0.59 | 0.87
40 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2020 | 1S-DL-YP-ETC-DNNG-2903-LO2020 | JYOTI COLONY/ BALBIR NGR NO.2:PL | TG-LO2020A-2 | 19506261 | 630 | 200 | 256 | 0.95 | 473 | 131 | 515 | 220 | 879 | 122 | 481 | 382 | 2019-06-12 | 142 | 37.8 | 905 | Y | 93 | 132 | 75 | 57 | 0.1 | 0.3 | 55.4 | 44.2 | 11 |  | 88.55 |  | 443.26 | 158.06 | 158.06 | 399.02 | 226.55 | 483.3 | 120.54 | 282.19 |  | 38.27 |  |  |  | 1.18 |  |  | 681.21 | 38.39 | 0.53 | 0.75
41 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2021 | 1S-DL-YP-ETC-DNNG-2903-LO2021 | D BLOCK KABIR NAGAR(SHAMSHAN GHAT) | TG-LO2021A-2 | 19505296 | 630 | 200 | 245 | 0.96 | 513 | 174 | 715 | 150 | 617 | 189 | 777 | 139 | 2019-06-26 13:00 | 175.8 | 38.4 | 827 | R | 116 | 83 | 101 | 33 |  |  | 24.4 | 75.6 |  | 1.3 |  |  | 127.09 | 401.5 | 401.5 | 254.39 | 528.01 | 288.13 | 444.25 | 435.54 | 36.23 |  | 0.59 | 1 |  |  |  |  | 691.34 | 28.26 | 0.57 | 0.81
42 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2021 | 1S-DL-YP-ETC-DNNG-2903-LO2021 | D BLOCK KABIR NAGAR(SHAMSHAN GHAT) | TG-LO2021A-1 | 19505805 | 990 | 320 | 249 | 0.97 | 972 | 368 | 1557 | 310 | 1294 | 294 | 1235 | 296 | 2019-06-01 23:30 | 257 | 87 | 1596 | R | 99 | 102 | 99 | 3 | 12.6 | 1.3 | 25.6 | 60.5 |  |  |  |  | 31.01 | 6 | 6 | 8.3 | 633.22 | 678.53 | 669.11 | 675.53 | 40.51 | 29.51 | 19.2 | 30.21 | 9.3 |  |  |  | 714.44 | 5.16 | 0.6 | 0.98
43 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2023 | 1S-DL-YP-ETC-DNNG-2903-LO2023 | A BLOCK KABIR NAGAR:ID | TG-LO2023A-1 | 19502671 | 990 | 320 | 256 | 0.96 | 975 | 331 | 1301 | 356 | 1417 | 288 | 1144 | 237 | 2019-06-01 | 226.7 | 93.5 | 1517 | Y | 100 | 112 | 88 | 24 |  | 0.7 | 40.2 | 59.1 |  |  |  |  | 1 |  |  |  | 626.41 | 502.04 | 682.02 | 629.41 | 64.21 | 171.36 | 6 | 62.51 | 0.3 | 18.52 |  |  | 715.23 | 4.37 | 0.65 | 0.98
44 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2026 | 1S-DL-YP-ETC-DNNG-2903-LO2026 | C BLOCK KABIR NAGAR | TG-LO2026A-1 | 19502709 | 990 | 320 | 237 | 0.96 | 960 | 351 | 1503 | 292 | 1308 | 317 | 1355 | 176 | 2019-06-01 01:00 | 253.9 | 84.6 | 1503 | R | 107 | 95 | 98 | 12 | 53.6 | 5.3 | 11.9 | 29.2 | [5 empty] | 46.39 | 46.39 | 3.3 | 597.34 | 641.25 | 664.5 | 665.04 | 110.07 | 24.2 | 47.04 | 43.5 | 4.43 |  | 0.3 |  | 712.24 | 7.36 | 0.64 | 0.97
45 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2029 | 1S-DL-YP-ETC-DNNG-2903-LO2029 | KARDAM MARG KHET WALA:-PL | TG-LO2029A-2 | 19506895 | 990 | 320 | 241 | 0.97 | 1018 | 291 | 1264 | 425 | 1883 | 302 | 1302 | 601 | 2019-06-11 23:00 | 302.7 | 65.9 | 1883 | Y | 92 | 107 | 101 | 15 | 0.7 | 0.3 | 57.3 | 41.7 |  |  |  |  | 231.53 | 88.09 | 88.09 | 142.01 | 414.01 | 498.54 | 482.46 | 468.23 | 41.44 | 86.05 | 79.14 | 77.14 | 1 | 15.3 | 1 | 1 | 688.38 | 31.22 | 0.53 | 1.03
46 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2030 | 1S-DL-YP-ETC-DNNG-2903-LO2030 | KARDAM PURI AZAD CHOWK:-ID | TG-LO2030A-1 | 19506684 | 990 | 320 | 243 | 0.96 | 892 | 253 | 1062 | 343 | 1453 | 296 | 1236 | 339 | 2019-06-01 | 268.8 | 95.4 | 1482 | Y | 87 | 118 | 95 | 31 | 0.3 | 16.3 | 33.7 | 49.7 |  |  |  |  | 35.4 |  |  | 1.47 | 657.03 | 560.31 | 675.16 | 676.16 |  | 124.52 | 5.4 | 14.4 |  | 7.2 |  |  | 692.43 | 27.17 | 0.65 | 0.9
47 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2032 | 1S-DL-YP-ETC-DNNG-2903-LO2032 | NORTH CHAJJUPUR:ID | TG-LO2032A-1 | 19502700 | 990 | 320 | 246 | 0.97 | 1029 | 337 | 1402 | 310 | 1286 | 382 | 1599 | 275 | 2019-06-11 02:00 | 204.6 | 61.8 | 1604 | B | 96 | 93 | 111 | 18 | 0 | 1.1 | 30.9 | 68.1 |  |  | 0.01 |  | 119.23 | 190.11 | 190.11 | 113.58 | 514 | 445.42 | 514.33 | 494.55 | 62.1 | 62.54 | 104.04 | 87.39 | 3.14 |  | 23.09 | 2.15 | 708.54 | 11.06 | 0.54 | 1.04
48 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2039 | 1S-DL-YP-ETC-DNNG-2903-LO2039 | NEW KARDAMPURI NO 2 GALI NO-8:PL | TG-LO2039A-1 | 19504913 | 990 | 320 | 243 | 0.96 | 692 | 188 | 800 | 183 | 765 | 321 | 1369 | 587 | 2019-06-30 | 156.8 | 75.1 | 1405 | B | 84 | 79 | 136 | 57 |  | 9.6 | 89.2 | 1.2 |  |  |  |  | 383.11 | 503.3 | 503.3 | 159.37 | 330.28 | 210.09 | 645.39 | 554.02 |  |  | 64.3 | [5 empty] | 713.39 | 6.21 | 0.67 | 0.7
49 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2041 | 1S-DL-YP-ETC-DNNG-2903-LO2041 | West Jyoti Ngr(Beh. Gopal Nur Home):-PL | TG-LO2041A-1 | 19506073 | 990 | 320 | 245 | 0.98 | 900 | 354 | 1474 | 295 | 1232 | 251 | 1046 | 372 | 2019-06-11 00:30 | 228.8 | 39.4 | 1499 | R | 118 | 101 | 81 | 37 | 0.2 | 0.1 | 0.9 | 98.8 |  |  |  |  | 63 | 142.26 | 142.26 | 161.19 | 550.2 | 557.23 | 338.3 | 543.29 | 91.29 | 15.48 | 0.3 | 10.49 | 10.48 |  |  |  | 715.37 | 4.23 | 0.56 | 0.91
50 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2044 | 1S-DL-YP-ETC-DNNG-2903-LO2044 | CNG STATION LONI ROAD:PM | TG-LO2044A-2 | 19506633 | 400 | 120 | 241 | 0.67 | 355 | 118 | 481 | 118 | 482 | 119 | 489 | 8 | 2019-06-04 06:00 | 334.2 | -121.2 | 518 | B | 99 | 100 | 102 | 3 |  |  | 0.9 | 99.1 | 16 | 15.3 | 15.3 | 15.3 | 456 | 455 | 455 | 455.3 | 194.56 | 195.26 | 187.56 | 193.56 | 27 | 28 | 36.3 | 29 |  |  |  |  | 693.56 | 26.04 | 0.44 | 0.89

## Loading Condition > 100%
MIS Report of Distribution Transformer - Jun19
Jun19 1260 NAND NAGARI (Loading Condition > 100% and 30 hours for 30 days)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1017 | 1S-DL-YP-ETC-DNNG-2902-LO1017 | E JYOTI NAGAR BEHAIND JOYATI NURSING:ID | TG-LO1017A-2 | 19504503 | 990 | 320 | 238 | 0.98 | 1223 | 299 | 1281 | 407 | 1753 | 517 | 2254 | 843 | 2019-06-11 23:30 | 219.3 | 44.9 | 2254 | B | 79 | 82 | 139 | 60 |  | 0.9 | 35 | 64.1 | 2.14 | 82.05 |  |  | 186.2 | 138.26 | 138.26 | 98.47 | 374.17 | 265.04 | 270.34 | 371.35 | 2.14 | 45.46 | 102.34 | 65.59 |  | 33.44 | 167.41 | 28.44 | 565.05 | 34.55 | 0.48 | 1.24
2 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1029 | 1S-DL-YP-ETC-DNNG-2902-LO1029 | B-BLOCK ASHOK NAGAR SCHOOL WALA:K | TG-LO1029A-3 | 19502205 | 990 | 320 | 242 | 0.97 | 1145 | 408 | 1689 | 281 | 1157 | 455 | 1898 | 662 | 2019-06-12 00:30 | 241.4 | 70.7 | 1916 | B | 107 | 77 | 116 | 39 |  |  | 3.8 | 96.2 |  |  |  |  | 53.32 | 266.43 | 266.43 | 74.02 | 495.15 | 404.35 | 490.14 | 509.13 | 98.39 | 7.3 | 98.31 | 83.13 | 31.22 |  | 73.03 | 12.2 | 700.56 | 19.04 | 0.51 | 1.16
3 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1032 | 1S-DL-YP-ETC-DNNG-2902-LO1032 | HARDEVPURI NO.2 ( JOSHI WALA):PL | TG-LO1032A-1 | 19506310 | 990 | 320 | 234 | 0.98 | 1146 | 375 | 1697 | 464 | 2148 | 306 | 1378 | 670 | 2019-06-29 23:00 | 305.9 | 66.9 | 2259 | Y | 99 | 118 | 83 | 35 | 3.1 | 14.9 | 60.4 | 21.5 |  |  | 83.41 |  | 49.51 | 7 | 7 | 40.51 | 473.33 | 431.22 | 466.18 | 490.44 | 105.27 | 115.29 | 69.42 | 93.42 | 28.56 | 103.56 | 11 | 32.3 | 662.12 | 57.48 | 0.55 | 1.16
4 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1034 | 1S-DL-YP-ETC-DNNG-2902-LO1034 | ASHOK NAGAR NO EXTN NO 1 KACHCHI CLY:PL | TG-LO1034A-2 | 19505269 | 630 | 200 | 237 | 0.97 | 711 | 186 | 850 | 201 | 900 | 324 | 1534 | 660 | 2019-06-10 23:30 | 245.6 | 42.8 | 1534 | B | 86 | 84 | 131 | 47 | 11.1 | 36.8 | 18.1 | 34 |  |  |  |  | 60.23 | 126.47 | 126.47 | 37.3 | 603.45 | 531.42 | 316.55 | 545.24 | 24.07 | 29.46 | 212.29 | 87.32 |  |  | 147.51 | 17.49 | 688.15 | 31.45 | 0.56 | 1.13
5 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1047 | 1S-DL-YP-ETC-DNNG-2902-LO1047 | D-1 ASHOK NAGAR WAZIRA BAD ROAD:PL | TG-LO1047A-1 | 19505923 | 630 | 200 | 244 | 0.96 | 725 | 206 | 895 | 283 | 1219 | 237 | 1051 | 281 | 2019-06-02 18:30 | 270 | 31.8 | 1310 | B | 93 | 113 | 95 | 20 | 0.2 | 14.7 | 84.3 | 0.8 | 5.3 | 0.45 | 1.3 | 0.3 | 180.42 | 147.13 | 147.13 | 185 | 454.26 | 308.17 | 413.05 | 409.43 | 51.14 | 168.36 | 68.14 | 87.44 | 8.55 | 75.56 | 4.13 | 17.5 | 700.47 | 19.13 | 0.5 | 1.15
6 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1055 | 1S-DL-YP-ETC-DNNG-2902-LO1055 | LONI BORDER S/S NO-1 | TG-LO1055A-1 | 19505051 | 630 | 200 | 247 | 0.97 | 653 | 272 | 1185 | 206 | 871 | 175 | 755 | 385 | 2019-06-10 22:30 | 153.6 | 54.3 | 1185 | R | 124 | 84 | 92 | 40 | 0.3 | 22.7 | 64.9 | 12 | [5 empty] | 24.42 | 24.42 |  | 382.16 | 665.02 | 680.09 | 662.21 | 276.3 | 2.55 | 10.29 | 30.07 | 33.53 |  |  | 0.11 | 692.39 | 27.21 | 0.62 | 1.04
7 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1056 | 1S-DL-YP-ETC-DNNG-2902-LO1056 | LONI BORDER S/S NO-2 | TG-LO1056A-1 | 19503678 | 630 | 200 | 244 | 0.96 | 875 | 357 | 1543 | 240 | 1023 | 279 | 1166 | 466 | 2019-06-18 17:30 | 213 | 14.3 | 1543 | R | 122 | 82 | 96 | 40 | 10.4 | 25 | 57 | 7.7 | 0.05 | 3.19 | 3 | 3.05 | 3.31 | 109.56 | 109.56 | 1.57 | 99.2 | 454.38 | 482.28 | 430.07 | 391.41 | 94.34 | 134.35 | 220.18 | 173.06 | 5.16 | 43.57 | 12.16 | 667.43 | 52.17 | 0.55 | 1.39
8 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1060 | 1S-DL-YP-ETC-DNNG-2902-LO1060 | DURGA PURI MAIN GALI - 10:ID | TG-LO1060A-2 | 19506308 | 990 | 320 | 239 | 0.98 | 1286 | 307 | 1392 | 465 | 2154 | 514 | 2263 | 822 | 2019-06-08 01:30 | 446.7 | 70.1 | 2263 | B | 88 | 98 | 114 | 26 | 96.7 | 2.3 | 1 | [5 empty] | 62.28 | 7 | 7 | 3.3 | 518.27 | 529.32 | 297.12 | 479.24 | 97.27 | 128.23 | 239.58 | 162.07 | 0.5 | 14.17 | 141.32 | 34.11 | 679.12 | 40.48 | 0.55 | 1.3
9 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2004 | 1S-DL-YP-ETC-DNNG-2903-LO2004 | JYOTI COLONY NO.1:K | TG-LO2004A-2 | 19505874 | 400 | 120 | 249 | 0.97 | 402 | 186 | 802 | 94 | 395 | 122 | 515 | 362 | 2019-06-11 01:00 | 107 | 24.6 | 883 | R | 119 | 87 | 94 | 32 | 1.3 | 0.7 | 11.7 | 86.4 | 1 | 3.3 |  |  | 96.31 | 328.33 | 328.33 | 189.15 | 487.14 | 358.22 | 493.12 | 487.07 | 83.07 | 21.41 | 5.38 | 35.44 | 44.44 | 0.3 |  | 0.3 | 712.36 | 7.24 | 0.51 | 1
10 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2004 | 1S-DL-YP-ETC-DNNG-2903-LO2004 | JYOTI COLONY NO.1:K | TG-LO2004A-1 | 19506079 | 630 | 200 | 240 | 0.97 | 874 | 295 | 1306 | 249 | 1085 | 330 | 1457 | 324 | 2019-06-11 00:30 | 227.2 | 68.2 | 1643 | B | 93 | 89 | 118 | 29 | 36.9 | 9.2 | 25.7 | 28.2 |  |  |  |  | 7.3 |  |  |  | 266.57 | 291.31 | 121.12 | 227.13 | 91.55 | 122.3 | 144.27 | 118.56 | 61.12 | 13.33 | 161.55 | 81.25 | 689.16 | 30.44 | 0.59 | 1.39
11 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2007 | 1S-DL-YP-ETC-DNNG-2903-LO2007 | AMBEDKAR PARK:PL | TG-LO2007A-2 | 19506514 | 630 | 200 | 243 | 0.97 | 774 | 262 | 1120 | 293 | 1233 | 218 | 916 | 279 | 2019-06-11 01:00 | 158 | 33.4 | 1254 | R | 111 | 104 | 85 | 26 | 0.4 | 4.2 | 82.7 | 12.7 |  |  |  |  | 22.3 | 24.3 | 24.3 | 40.3 | 462.43 | 504 | 498.11 | 505.27 | 122.09 | 96.16 | 69.38 | 104.14 | 82.49 | 65.25 | 0.47 | 40 | 690.11 | 29.49 | 0.52 | 1.23
12 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2007 | 1S-DL-YP-ETC-DNNG-2903-LO2007 | AMBEDKAR PARK:PL | TG-LO2007A-1 | 19506615 | 990 | 320 | 245 | 0.97 | 974 | 344 | 1494 | 437 | 1859 | 193 | 819 | 914 | 2019-06-10 23:00 | 238.7 | 73.9 | 1859 | Y | 119 | 115 | 66 | 53 | 8.7 | 51.5 | 39.3 | 0.6 |  |  | 7 |  | 23 | 32.3 | 32.3 | 86.03 | 537.01 | 519.01 | 219.3 | 546.26 | 111.02 | 102.22 |  | 58.33 | 19.59 | 37.09 |  |  | 691.02 | 28.58 | 0.56 | 0.98
13 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2009 | 1S-DL-YP-ETC-DNNG-2903-LO2009 | SHIV MANDIR 100 FT. RD:PL | TG-LO2009A-2 | 19506549 | 400 | 120 | 247 | 0.97 | 405 | 167 | 721 | 123 | 519 | 116 | 496 | 215 | 2019-06-10 23:00 | 118.9 | 26.5 | 896 | R | 119 | 96 | 84 | 35 | 1.2 | 15.4 | 57.5 | 25.9 |  |  |  |  | 17.1 | 40.38 | 40.38 | 13.5 | 465.56 | 613.52 | 578.22 | 608.18 | 133.32 | 34.3 | 7.3 | 66.22 | 72.22 |  |  | 0.3 | 689 | 31 | 0.6 | 1.01
14 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2013 | 1S-DL-YP-ETC-DNNG-2903-LO2013 | MAHA DEVI SCHOOL:PL | TG-LO2013A-1 | 19502715 | 630 | 200 | 240 | 0.96 | 716 | 263 | 1160 | 217 | 961 | 236 | 1053 | 172 | 2019-06-03 | 160.1 | 56.6 | 1160 | R | 106 | 101 | 93 | 13 | 0.2 | 0.8 | 79.2 | 19.7 |  |  |  |  | 41.3 | 50.24 | 50.24 | 52.53 | 528.59 | 561.21 | 550.22 | 556.21 | 100.57 | 88.36 | 60.1 | 92.23 | 40.54 | 11.59 | 2.3 | 10.43 | 712.2 | 7.4 | 0.53 | 1.14
15 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2018 | 1S-DL-YP-ETC-DNNG-2903-LO2018 | SUDAMAPURI NO. 4:PL | TG-LO2018A-1 | 19506829 | 400 | 120 | 242 | 0.96 | 481 | 178 | 755 | 130 | 552 | 174 | 735 | 194 | 2019-06-09 23:30 | 133.1 | 41.3 | 850 | R | 110 | 84 | 106 | 26 | 0.4 | 0.6 | 36.8 | 62.2 |  |  |  |  | 1 | 32.3 | 32.3 | 4.3 | 402.45 | 553.37 | 436.1 | 486.41 | 156.52 | 117.51 | 161.27 | 133.2 | 146.21 | 3 | 106.21 | 82.27 | 706.58 | 13.02 | 0.61 | 1.2
16 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2020 | 1S-DL-YP-ETC-DNNG-2903-LO2020 | JYOTI COLONY/ BALBIR NGR NO.2:PL | TG-LO2020A-1 | 19504551 | 990 | 320 | 247 | 0.97 | 1475 | 451 | 1824 | 478 | 1967 | 546 | 2289 | 412 | 2019-06-11 00:30 | 325.3 | 86.1 | 2289 | B | 95 | 102 | 103 | 8 | 0.2 | 2.7 | 22.2 | 74.9 |  |  |  |  | 6 | 2 | 2 |  | 386 | 338.36 | 325.53 | 355.54 | 179.14 | 176.23 | 205.22 | 187.41 | 133.33 | 187.48 | 173.32 | 161.12 | 704.47 | 15.13 | 0.56 | 1.49
17 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2028 | 1S-DL-YP-ETC-DNNG-2903-LO2028 | HARIJAN BASTI WEST JYOTI NARAR:ID | TG-LO2028A-2 | 19502719 | 400 | 120 | 237 | 0.98 | 467 | 95 | 398 | 187 | 817 | 186 | 807 | 414 | 2019-06-11 00:30 | 74.5 | 18.2 | 925 | B | 65 | 114 | 121 | 56 | 7.4 | 48.6 | 43.7 | 0.2 | 10.3 |  |  |  | 288.57 | 17 | 17 | 28.3 | 420 | 450.57 | 419.57 | 515.27 |  | 117.3 | 117.3 | 112 |  | 134 | 174 | 63.3 | 719.27 | 0.33 | 0.57 | 1.17
18 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2028 | 1S-DL-YP-ETC-DNNG-2903-LO2028 | HARIJAN BASTI WEST JYOTI NARAR:ID | TG-LO2028A-1 | 19502724 | 630 | 200 | 243 | 0.97 | 622 | 234 | 985 | 190 | 795 | 197 | 822 | 178 | 2019-06-29 23:30 | 113.6 | 40.5 | 985 | R | 111 | 87 | 102 | 24 |  |  | 2.8 | 97.2 |  |  |  |  | 16.3 | 155 | 155 | 36 | 535.56 | 534.26 | 605.26 | 586.26 | 136 | 30 | 88.3 | 97 | 31 |  |  |  | 719.26 | 0.34 | 0.61 | 0.99
19 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2031 | 1S-DL-YP-ETC-DNNG-2903-LO2031 | NEW KARDAMPURI NO 1 GALI NO -4:PL | TG-LO2031A-1 | 19506465 | 630 | 200 | 238 | 0.97 | 603 | 176 | 784 | 259 | 1183 | 168 | 699 | 448 | 2019-06-29 23:30 | 195.6 | 0.2 | 1183 | Y | 127 | 103 | 70 | 57 | 17.4 | 20.3 | 55.4 | 6.9 | 2.43 | 2.43 | 2.43 | 2.43 | 1.25 | 1.25 | 1.25 | 1.25 | 182.58 | 378.18 | 350.35 | 397.18 | 181.51 | 71.3 | 7.3 | 75 | 107.29 | 22.3 |  |  | 681.18 | 38.42 | 0.71 | 0.96
20 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2046 | 1S-DL-YP-ETC-DNNG-2903-LO2046 | SUDAMAPURI S/S- 5 Nr. BABARPUR BUS TERM. | TG-LO2046A-1 | 19505667 | 630 | 200 | 252 | 0.97 | 886 | 312 | 1364 | 250 | 1077 | 324 | 1419 | 319 | 2019-06-08 01:30 | 291.4 | 38 | 1579 | B | 99 | 81 | 120 | 39 | 0.4 | 0.3 | 5.5 | 93.8 |  |  |  |  | 33.3 | 102 | 102 | 11 | 499.57 | 567.15 | 347.26 | 533 | 140.25 | 41.1 | 266.22 | 152.37 | 37.03 | 0.3 | 97.07 | 14.18 | 710.55 | 9.05 | 0.48 | 1.41