## Underload DTs
MIS Report of Distribution Transformer - Jun19
Jun19 1260 NAND NAGARI (Underload DTs)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR039 | 1S-DL-YP-ETC-DNNG-2901-NGR039 | ST LTG GAGAN CINEMA WAZIRABAD RD:PM | TG-NGR039A-1 | 19505418 | 400 | 120 | 247 | 0.92 | 227 | 117 | 486 | 109 | 473 | 1 | 4 | 475 | 2019-06-09 09:00 | 166.3 | -0.4 | 486 | R | 135 | 76 | 89 | 59 | 98.9 | 0.8 | 0.3 |  | 617.17 | 629.47 | 629.47 | 626.17 | 59.4 | 56.1 | 56.1 | 58.4 | 15 | 6 | 6.3 | 7.3 | 0.3 | 0.3 | [6 empty] | 692.27 | 27.33 | 0.16 | 0.57
2 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR052 | 1S-DL-YP-ETC-DNNG-2901-NGR052 | D1 SAFAI KARMCHARI NNG-1:ID | TG-NGR052A-1 | 19502691 | 400 | 120 | 243 | 0.97 | 49 | 23 | 94 | 17 | 73 | 9 | 39 | 48 | 2019-06-11 23:00 | 11.6 | 1.1 | 96 | R | 124 | 99 | 76 | 48 |  |  | 36.1 | 63.9 | 719.44 | 719.44 | 719.44 | 719.44 | [16 empty] | 719.44 | 0.16 | 0.6 | 0.12
3 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR053 | 1S-DL-YP-ETC-DNNG-2901-NGR053 | D1 SAFAI KARMCHARI NNG-2:ID | TG-NGR053A-1 | 19504504 | 400 | 120 | 244 | 0.27 | 8 | 0 | 0 | 8 | 31 | 0 | 0 | 31 | 2019-06-27 21:30 | -0.3 | -7.7 | 31 | Y | 0 | 300 | 0 | 300 |  |  | 62.7 | 37.3 | 719.43 | 719.43 | 719.43 | 719.43 | [16 empty] | 719.43 | 0.17 | 0.21 | 0.02
4 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR094 | 1S-DL-YP-ETC-DNNG-2901-NGR094 | Police Housing Complex S/Stn No.1 | TG-NGR094A-1 | 19506086 | 630 | 200 | 248 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [5 empty] | 1.2 | 9.4 | 47.9 | 41.6 | 693.53 | 693.53 | 693.53 | 693.53 | [16 empty] | 693.53 | 26.07 |  | 0
5 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR094 | 1S-DL-YP-ETC-DNNG-2901-NGR094 | Police Housing Complex S/Stn No.1 | TG-NGR094A-2 | 19506087 | 630 | 200 | 247 | 0.96 | 33 | 27 | 108 | 3 | 11 | 3 | 13 | 96 | 2019-06-02 | 10.6 | 0.6 | 111 | R | 265 | 18 | 17 | 248 |  |  | 2.2 | 97.8 | 693.53 | 693.53 | 693.53 | 693.53 | [16 empty] | 693.53 | 26.07 | 0.46 | 0.05
6 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR095 | 1S-DL-YP-ETC-DNNG-2901-NGR095 | Police Housing Complex S/Stn No.2 | TG-NGR095A-1 | 19506088 | 630 | 200 | 248 | 0.95 | 17 | 4 | 16 | 4 | 15 | 9 | 38 | 23 | 2019-06-30 23:00 | 6.4 | 0.2 | 39 | Y | 102 | 110 | 88 | 22 |  |  | 0.6 | 99.4 | 694.39 | 694.39 | 694.39 | 694.39 | [16 empty] | 694.39 | 25.21 | 0.53 | 0.03
7 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR095 | 1S-DL-YP-ETC-DNNG-2901-NGR095 | Police Housing Complex S/Stn No.2 | TG-NGR095A-2 | 19506089 | 630 | 200 | 248 | 0.96 | 29 | 18 | 72 | 1 | 3 | 10 | 41 | 59 | 2019-06-21 22:30 | 9 | -0.6 | 72 | R | 153 | 13 | 134 | 140 |  |  | 1.1 | 98.9 | 694.39 | 694.39 | 694.39 | 694.39 | [16 empty] | 694.39 | 25.21 | 0.43 | 0.05
8 | 2019-06-12 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1003 | 1S-DL-YP-ETC-DNNG-2902-LO1003 | HARIJAN BASTI AMAR CLY BHUSA WALA:PL | TG-LO1003A-1 | 19502170 | 630 | 200 | 246 | 0.96 | 110 | 34 | 138 | 42 | 169 | 33 | 135 | 33 | 2019-06-26 18:30 | 36.3 | 8.7 | 185 | Y | 98 | 120 | 82 | 38 | 0.1 | 2.6 | 76.1 | 21.2 | 441.4 | 440.15 | 442.1 | 442.1 | 0.3 | 1.55 | 1.55 | [13 empty] | 442.1 | 13.5 | 0.61 | 0.17
9 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1005 | 1S-DL-YP-ETC-DNNG-2902-LO1005 | HARIJAN BASTI G PUR(BHAWANI WALA):PL | TG-LO1005A-1 | 19506879 | 630 | 200 | 246 | 0.97 | 111 | 33 | 141 | 59 | 255 | 19 | 78 | 155 | 2019-06-11 01:00 | 33.2 | 0.2 | 260 | Y | 96 | 132 | 72 | 60 | 0.1 | 4.6 | 80.5 | 14.8 | 677.42 | 644 | 677.42 | 677.42 |  | 33.42 | 33.42 | [13 empty] | 677.42 | 42.18 | 0.6 | 0.18
10 | 2019-06-01 | 2019-06-20 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1023 | 1S-DL-YP-ETC-DNNG-2902-LO1023 | EAST OF LONI ROAD,MIG,S/STN-6:ID | TG-LO1023A-2 | 19501770 | 400 | 120 | 237 | 0.98 | 92 | 27 | 122 | 28 | 126 | 37 | 164 | 40 | 2019-06-02 22:30 | 12.4 | 2.8 | 167 | B | 77 | 90 | 133 | 56 |  |  | 7.1 | 92.9 | 477.05 | 478.05 | 375.08 | 473.35 | 1.3 | 0.3 | 0.3 | 5 | [12 empty] | 478.35 | 1.25 | 0.47 | 0.23
11 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1026 | 1S-DL-YP-ETC-DNNG-2902-LO1026 | MTNL S/S,EAST OF LONI ROAD:PL | TG-LO1026A-1 | 19502165 | 400 | 120 | 238 | 0.98 | 38 | 13 | 58 | 13 | 57 | 11 | 49 | 9 | 2019-06-01 15:00 | 11.9 | 1.4 | 62 | Y | 109 | 82 | 109 | 27 |  |  | 21.8 | 78.2 | 719.48 | 719.48 | 719.48 | 719.48 | [16 empty] | 719.48 | 0.12 | 0.71 | 0.09
12 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1059 | 1S-DL-YP-ETC-DNNG-2902-LO1059 | D.P Kundan Lal Petrol Pump East Gokalpur | TG-LO1059A-1 | 19505021 | 400 | 200 | 246 | 0.99 | 54 | 20 | 81 | 18 | 72 | 16 | 63 | 16 | 2019-06-15 11:30 | 13.8 | 0.5 | 88 | B | 93 | 103 | 103 | 10 |  | 2 | 83.9 | 14.1 | 698.19 | 698.19 | 698.19 | 698.19 | [16 empty] | 698.19 | 21.41 | 0.59 | 0.13
13 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1064 | 1S-DL-YP-ETC-DNNG-2902-LO1064 | PRIMARY SCHOOL WALA MEET NAGAR | TG-LO1064A-1 | 19506670 | 990 | 320 | 243 | 0.99 | 114 | 75 | 296 | 16 | 64 | 23 | 93 | 219 | 2019-06-17 10:30 | 24 | 0.3 | 296 | R | 78 | 123 | 99 | 45 | 0.1 | 0.1 | 72.9 | 26.9 | 704.23 | 704.53 | 704.53 | 704.53 | 0.3 | [15 empty] | 704.53 | 15.07 | 0.47 | 0.12
14 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | MIG EAST OF LONI ROAD | 1260 | LO1073 | 1S-DL-YP-ETC-DNNG-2902-LO1073 | POLICE STATION GOKULPURI | TG-LO1073A-1 | 19506028 | 990 | 300 | 244 | 0.99 | 115 | 11 | 48 | 8 | 33 | 96 | 405 | 365 | 2019-06-29 15:30 | 16.5 | -0.6 | 405 | B | 83 | 68 | 149 | 81 |  |  | 8.4 | 91.6 | 719.11 | 719.11 | 718.41 | 719.11 | [16 empty] | 719.11 | 0.49 | 0.27 | 0.12
15 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO1070 | 1S-DL-YP-ETC-DNNG-2902-LO1070 | EDMC DISPENSARY NEAR AMBEDKAR COLLEGE | TG-LO1070A-1 | 19506359 | 100 | 40 | 247 | 0.94 | 6 | 6 | 23 | 0 | 0 | 1 | 3 | 22 | 2019-06-28 12:30 | 1.6 | 0 | 23 | R | 189 | 0 | 111 | 189 |  | 0.1 | 4.7 | 95.3 | 718.21 | 718.21 | 718.21 | 718.21 | [16 empty] | 718.21 | 1.39 | 0.29 | 0.06
16 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2015 | 1S-DL-YP-ETC-DNNG-2903-LO2015 | SUDAMA PURI NO.2:PL | TG-LO2015A-1 | 19506010 | 630 | 200 | 237 | 0.99 | 454 | 204 | 908 | 28 | 121 | 222 | 968 | 819 | 2019-06-07 01:30 | 176.6 | -0.2 | 968 | B | 122 | 93 | 85 | 37 | 0.1 | 0.4 | 70.5 | 29 | 682.03 | 709.03 | 705.33 | 708.33 | 26.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 1 | 0.3 | [5 empty] | 0.3 |  | 709.33 | 10.27 | 0.14 | 0.72
17 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2040 | 1S-DL-YP-ETC-DNNG-2903-LO2040 | STORM WATER PUMPING STN ( NAHAR ROAD):PL | TG-LO2040A-1 | 19504771 | 400 | 120 | 240 | 0.86 | 22 | 6 | 24 | 12 | 49 | 4 | 16 | 30 | 2019-06-11 19:30 | 13.8 | 0.6 | 62 | Y | 62 | 164 | 74 | 102 |  |  | 12.3 | 87.7 | 718.45 | 718.45 | 718.45 | 718.45 | [16 empty] | 718.45 | 1.15 | 0.57 | 0.05
18 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2044 | 1S-DL-YP-ETC-DNNG-2903-LO2044 | CNG STATION LONI ROAD:PM | TG-LO2044A-1 | 19503385 | 400 | 120 | 242 | 0.84 | 16 | 6 | 25 | 3 | 11 | 7 | 29 | 17 | 2019-06-14 03:30 | 5.8 | -9.1 | 31 | B | 91 | 85 | 124 | 39 |  | 0.1 | 50.7 | 49.2 | 719.4 | 719.4 | 719.4 | 719.4 | [16 empty] | 719.4 | 0.2 | 0.74 | 0.04
19 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2048 | 1S-DL-YP-ETC-DNNG-2903-LO2048 | WEST JYOTI NAGAR THANA | TG-LO2048A-2 | 19506257 | 400 | 120 | 251 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [6 empty] | 0.1 | 75 | 24.9 | 719.51 | 719.51 | 719.51 | 719.51 | [16 empty] | 719.51 | 0.09 |  | 0
20 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2048 | 1S-DL-YP-ETC-DNNG-2903-LO2048 | WEST JYOTI NAGAR THANA | TG-LO2048A-1 | 19506233 | 400 | 120 | 251 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-06-30 23:30 |  |  | 0 | [7 empty] | 81.8 | 18.2 | 707.51 | 707.51 | 707.51 | 707.51 | [16 empty] | 707.51 | 12.09 |  | 0