## Complete Report
MIS Report of Distribution Transformer - Jun19
Jun19 1260 NAND NAGARI (Complete Report)
Sn. | Study Period |  | Division Name | Zone | Div Code | Sap Code | Sap Function Code | DT Name | DT Code | Meter Serial No. | KVA Rating | MF | VOLTAGE | POWER FACTOR | Peak Loading Conditions | [8 empty] | Reactive Demand (KVAR) |  | Highest Phase Current |  | % Relative Phase Unbalance |  |  | %Unbalance | % Voltage Unbalance (%Time of total study period) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) |  |  |  | Loading Condition ( in HH:MI) | [5 empty] | LF | UF
[15 empty] | Peak KVA | R Phase |  | Y Phase |  | B Phase |  | Neutral Current (AMP) | Date and Time
[16 empty] | KVA | I (AMP) | KVA | I (AMP) | KVA | I (AMP) |  |  | MAX | MIN | Current(AMP) | Phase | R-Ph | Y-Ph | B-Ph | {I(Max)-I(Min)} / I(Average) | >3% | <=3% and >2% | <=2% and >1% | <=1% | < 20% |  |  |  | 20%-40% |  |  |  | 40%-80% |  |  |  | 80%-100% |  |  |  | >100% |  |  |  | ON ( in HH:MI) | OFF ( in HH:MI)
[36 empty] | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer | R-Ph | Y-Ph | B-Ph | Total Transformer
1 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | C-4 NANDNAGRI | 1260 | NGR053 | 1S-DL-YP-ETC-DNNG-2901-NGR053 | D1 SAFAI KARMCHARI NNG-2:ID | TG-NGR053A-1 | 19504504 | 400 | 120 | 244 | 0.27 | 8 | 0 | 0 | 8 | 31 | 0 | 0 | 31 | 2019-06-27 21:30 | -0.3 | -7.7 | 31 | Y | 0 | 300 | 0 | 300 |  |  | 62.7 | 37.3 | 719.43 | 719.43 | 719.43 | 719.43 | [16 empty] | 719.43 | 0.17 | 0.21 | 0.02
2 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2044 | 1S-DL-YP-ETC-DNNG-2903-LO2044 | CNG STATION LONI ROAD:PM | TG-LO2044A-1 | 19503385 | 400 | 120 | 242 | 0.84 | 16 | 6 | 25 | 3 | 11 | 7 | 29 | 17 | 2019-06-14 03:30 | 5.8 | -9.1 | 31 | B | 91 | 85 | 124 | 39 |  | 0.1 | 50.7 | 49.2 | 719.4 | 719.4 | 719.4 | 719.4 | [16 empty] | 719.4 | 0.2 | 0.74 | 0.04
3 | 2019-06-01 | 2019-06-30 23:30 | NAND NAGARI | SUDAMA PURI | 1260 | LO2044 | 1S-DL-YP-ETC-DNNG-2903-LO2044 | CNG STATION LONI ROAD:PM | TG-LO2044A-2 | 19506633 | 400 | 120 | 241 | 0.67 | 355 | 118 | 481 | 118 | 482 | 119 | 489 | 8 | 2019-06-04 06:00 | 334.2 | -121.2 | 518 | B | 99 | 100 | 102 | 3 |  |  | 0.9 | 99.1 | 16 | 15.3 | 15.3 | 15.3 | 456 | 455 | 455 | 455.3 | 194.56 | 195.26 | 187.56 | 193.56 | 27 | 28 | 36.3 | 29 |  |  |  |  | 693.56 | 26.04 | 0.44 | 0.89