## Summary
BYPL : Overloaded DTs(Loading >70% for >24 Hrs ) Across Loss Bands_June2019
SDO | Division | Zone | OverLoaded DTs (Count)
|  |  | Loss 0-5% | Loss 5-10% | Loss 10-20% | Loss 20-30% | Loss >30% | Chronic Cases
1110 | Chandni Chowk | HAMILTON ROAD |  | 2 | 2 |  |  |  | Note:-
|  | LAHORI GATE | 2 | 3 | 10 | 10 | 1 |  | * Chronic Cases:-Continuous Overloaded DTs from last 6 months(Jan19 To June19)
|  | TOWN HALL | 6 | 6 | 2
Chandni Chowk Total |  |  | 8 | 11 | 14 | 10 | 1
1120 | Daryaganj | DARYAGANJ | 2 | 1 | 1
|  | JAMA MASJID | 1 | 2 | 3 | 8 | 32
|  | MINTO ROAD | 1 |  |  |  | 1
Daryaganj Total |  |  | 4 | 3 | 4 | 8 | 33
1130 | Paharganj | B G ROAD | 2 | 1 | 3 | 2 | 2
|  | CHUNA MANDI & RAM NAGAR | 8 | 13 | 6
|  | PP QUARTERS |  | 2 | 2 | 2 | 2
Paharganj Total |  |  | 10 | 16 | 11 | 4 | 4
1140 | Shankar Road | CHHAPARWALAN | 8 | 10
|  | PUSA ROAD | 8 | 9 | 5
|  | R BLOCK NEW RAJENDER NAGAR | 3 | 11
Shankar Raod Total |  |  | 19 | 30 | 5 | 0 | 0
1141 | Patel Nagar | KIKARWALAN | 11 | 5 | 6
|  | PATEL NAGAR | 15 | 15 | 9
|  | SARAI ROHILLA | 12 | 14 |  |  |  | 7
Patel Nagar Total |  |  | 38 | 34 | 15 | 0 | 0 | 7
Central Total |  |  | 79 | 94 | 49 | 22 | 38 | 7
1210 | Karkardooma | B-BLOCK VIVEK VIHAR | 6 | 7
|  | JWALA NAGAR | 10 | 17 | 1
|  | SAINI ENCLAVE | 10 | 6 | 1
Karkardooma Total |  |  | 26 | 30 | 2 | 0 | 0
1220 | Krishna Nagar | GAGAN VIHAR | 7 | 27 | 5 | 1
|  | GANDHI NAGAR | 8 | 14 | 12 |  | 1 | 2
|  | GEETA COLONY | 8 | 22
|  | KANTI NAGAR | 5 | 15 | 1 | 1
|  | Krishna Nagar | 8 | 7 | 8 | 1 | 2 | 1
Krishna Nagar Total |  |  | 36 | 85 | 26 | 3 | 3 | 3
1230 | Laxmi Nagar | ANAND VIHAR ISBT | 14 | 4 | 2 |  | 2 | 2
|  | LAXMI NAGAR | 24 | 39 | 7
|  | MANDAWALI | 24 | 21 | 3 |  |  | 1
|  | PREET VIHAR | 12 | 4
Laxmi Nagar Total |  |  | 74 | 68 | 12 | 0 | 2 | 3
1240 | Mayur Vihar I & II | S/STN 8 POCKET C | 6 | 7 | 7 | 1 |  | 1
|  | SADAR APPARTMENTS | 8 | 7 | 3 |  | 2
|  | TRILOKPURI | 8 | 10 | 2 | 1
Mayur Vihar I & II Total |  |  | 22 | 24 | 12 | 2 | 2 | 1
1241 | Mayur Vihar III | MVR-III | 6 | 5 | 5 | 1
|  | NEW ASHOK NAGAR | 8 | 10
|  | VASUNDHARA ENCLAVE | 1 | 1 |  |  | 4
Mayur Vihar III Total |  |  | 15 | 16 | 5 | 1 | 4 | 0
South East Total |  |  | 173 | 223 | 57 | 6 | 11 | 7
1211 | G T Raod | E&F DILSHAD GARDEN | 37 | 25 | 1 |  |  | 22
|  | GT ROAD SHAHDRA | 23 | 22 |  |  |  | 17
|  | ZAFFRABAD | 20 | 21
G T Road Total |  |  | 80 | 68 | 1 | 0 | 0 | 39
1250 | Yamuna Vihar | C-12 YAMUNA VIHAR | 2 | 27 | 19
|  | GHONDA | 1 | 14 | 18 | 6 | 4 | 2
|  | NEW SEELAMPUR |  |  | 4 | 3 | 11
|  | SHASTRI PARK | 1 | 3 | 3
Yamuna Vihar Total |  |  | 4 | 44 | 44 | 9 | 15 | 2
1251 | Karawal Nagar | GOKUL PURI | 4 | 18 | 5 |  |  | 4
|  | KARAWAL NAGAR | 2 | 4 | 11 |  |  | 6
|  | SONIA VIHAR | 8 | 17 | 14 | 2 |  | 1
Karawal Nagar Total |  |  | 14 | 39 | 30 | 2 | 0 | 11
1260 | Nand Nagri | C-4 NANDNAGRI | 4 | 18 | 2
|  | MIG EAST OF LONI ROAD | 9 | 15 | 5 | 2 | 1
|  | SUDAMA PURI |  | 18 | 6 | 1
Nand Nagri Total |  |  | 13 | 51 | 13 | 3 | 1 | 0
North East Total |  |  | 111 | 202 | 88 | 14 | 16 | 52
BYPL Total |  |  | 363 | 519 | 194 | 42 | 65 | 66

## Overloaded DTs Details June2019
Overloaded DTs June2019(Loading>70% for >24 Hrs in the month)
[11 empty] | Peak KVA Condition | [8 empty] | Load Category Wise Duration (Hours) |  |  |  |  | Peak Load % Across Time-Slots | [5 empty] | Last Summer Peak Loading KVA (>70% Overloading Hrs)
Sr.No. | SDO | DIVISION | ZONE | SSTN SAP CODE | DT CODE | DT | SSTN NAME | Total DTs In Sstn | KVA RATING | DT METER NO. | Peak KVA | Peak KVA Date and Time | KVA_R | I (AMP)_R | KVA_Y | I (AMP)_Y | KVA_B | I (AMP)_B | Neutral Current | Loading<70% | 70%Loading90% | 90%Loading100% | Loading>100% | > 70% Total Overloading Hours | 00:00 to 06:00 | 06:00 to 09:00 | 09:00 to 21:00 | 21:00 to 00:00 | Rolling T&D Loss May 2019 | Loss Band | 2018-04-01 | 2018-05-01 | 2018-06-01 | 2018-07-01 | 2018-08-01 | 2018-09-01
1 | 1110 | CCK | HAMILTON ROAD | HAM003 | TG-HAM003A-2 | DT-2 | HAMILTON ROAD STN:ID | 2 | 990 | 19500269 | 809 | 2019-06-13 15:30 | 297 | 1288 | 271 | 1177 | 242 | 1028 | 226 | 647 | 72 |  |  | 72 | 38% | 28% | 82% | 38% | 9.7403 | Loss 5-10% |  |  | 827(90.5) | 850(58.5)
2 | 1110 | CCK | HAMILTON ROAD | HAM009 | TG-HAM009A-1 | DT-1 | CHABBI GANJ:PL | 1 | 990 | 19503476 | 970 | 2019-06-13 15:00 | 333 | 1326 | 335 | 1393 | 302 | 1238 | 134 | 648.5 | 66 | 4 |  | 70 | 19% | 17% | 98% | 21% | 5.4569 | Loss 5-10% |  |  | 733(28.5)
3 | 1110 | CCK | HAMILTON ROAD | HAM017 | TG-HAM017A-1 | DT-1 | KASHMERE GATE POLICE THANA:PL | 1 | 990 | 19500234 | 763 | 2019-06-15 16:00 | 213 | 871 | 269 | 1110 | 281 | 1145 | 258 | 638.5 | 57.5 |  |  | 57.5 | 15% | 13% | 77% | 16% | 10.6668 | Loss 10-20% |  |  | 787(82) | 810(48)
4 | 1110 | CCK | HAMILTON ROAD | HAM034 | TG-HAM034A-1 | DT-1 | YAMUNA BAZAR GHAT DELHI 6 | 1 | 630 | 19505145 | 928.7217 | 2019-06-15 13:00 | 326.9159 | 1458.3392 | 334.054 | 1525.2215 | 267.7518 | 1168.0488 | 328.8724 | 672 | 47 |  | 0.5 | 47.5 | 74% | 59% | 147% | 75% | 12.3222 | Loss 10-20%
5 | 1110 | CCK | LAHORI GATE | LHR001 | TG-LHR001A-1 | DT-1 | MOHALLA NIHARIYAN:K | 2 | 990 | 19505697 | 996 | 2019-06-11 01:30 | 333 | 1383 | 328 | 1371 | 335 | 1408 | 32 | 312.5 | 377.5 | 27.5 | 0.5 | 405.5 | 101% | 89% | 97% | 90% | 27.2996 | Loss 20-30% |  |  |  |  | 965(264.5) | 1330(127)
6 | 1110 | CCK | LAHORI GATE | LHR003 | TG-LHR003A-1 | DT-1 | MOHALLA SHAHGANJ:K | 2 | 990 | 19505363 | 878 | 2019-06-17 23:00 | 377 | 1612 | 172 | 713 | 329 | 1478 | 840 | 617.5 | 99 |  |  | 99 | 77% | 70% | 83% | 89% | 17.3245 | Loss 10-20% |  | 1075(132) | 981(295) | 898(208) | 917(75)
7 | 1110 | CCK | LAHORI GATE | LHR015 | TG-LHR015A-1 | DT-1 | ZEENAT MAHAL:K | 2 | 990 | 19501530 | 879 | 2019-06-03 04:00 | 304 | 1254 | 280 | 1148 | 295 | 1212 | 93 | 587.5 | 132 |  |  | 132 | 89% | 77% | 73% | 77% | 21.8345 | Loss 20-30% |  |  | 805(113.5) | 834(75.5)
8 | 1110 | CCK | LAHORI GATE | LHR017 | TG-LHR017A-1 | DT-1 | LAL QUAN:PL | 1 | 990 | 19506435 | 1085 | 2019-06-05 02:30 | 324 | 1380 | 244 | 1043 | 517 | 2313 | 1140 | 641.5 | 75.5 | 1 | 0.5 | 77 | 110% | 67% | 96% | 78% | 27.2272 | Loss 20-30% |  |  | 894(38.5)
9 | 1110 | CCK | LAHORI GATE | LHR018 | TG-LHR018A-1 | DT-1 | BARSHABULLA:ID | 2 | 990 | 19501501 | 842 | 2019-06-12 16:30 | 245 | 1096 | 286 | 1296 | 311 | 1422 | 285 | 622.5 | 97.5 |  |  | 97.5 | 36% | 29% | 85% | 34% | 7.0473 | Loss 5-10% |  | 891(73) | 934(79) | 911(83.5) | 797(66.5)
10 | 1110 | CCK | LAHORI GATE | LHR018 | TG-LHR018A-2 | DT-2 | BARSHABULLA:ID | 2 | 990 | 19505696 | 1156 | 2019-06-26 17:30 | 408 | 1794 | 396 | 1739 | 352 | 1518 | 253 | 540 | 130.5 | 49 | 0.5 | 180 | 19% | 12% | 117% | 16% | 7.0473 | Loss 5-10% |  | 1081(149.5) | 1050(203.5) | 1336(182) |  | 893(143)
11 | 1110 | CCK | LAHORI GATE | LHR019 | TG-LHR019A-2 | DT-2 | CHARKHE WALAN:PL | 2 | 990 | 19504961 | 817 | 2019-06-11 01:30 | 269 | 1147 | 265 | 1116 | 283 | 1208 | 81 | 598 | 120.5 |  |  | 120.5 | 83% | 69% | 76% | 80% | 10.896 | Loss 10-20% | 791(25) | 902(204) | 993(465) | 1032(378) | 880(273)
12 | 1110 | CCK | LAHORI GATE | LHR023 | TG-LHR023A-1 | DT-1 | JOGIWARA:ID | 3 | 990 | 19501520 | 990 | 2019-06-11 17:00 | 340 | 1468 | 343 | 1478 | 306 | 1323 | 150 | 462 | 132 | 54 |  | 186 | 55% | 46% | 100% | 57% | 15.2846 | Loss 10-20% | 1068(204.5) | 1173(133.5) | 1272(221.5) | 831(63.5) | 888(78)
13 | 1110 | CCK | LAHORI GATE | LHR023 | TG-LHR023A-2 | DT-2 | JOGIWARA:ID | 3 | 990 | 19505551 | 904 | 2019-06-01 13:00 | 324 | 1439 | 293 | 1294 | 287 | 1277 | 154 | 644 | 73 | 1 |  | 74 | 8% | 7% | 91% | 24% | 15.2846 | Loss 10-20% | 925(176) | 1050(216) | 1119(212) | 1316(147.5) | 929(111.5) | 837(99.5)
14 | 1110 | CCK | LAHORI GATE | LHR024 | TG-LHR024A-1 | DT-1 | PANDIT BROS:K | 2 | 990 | 19503227 | 814 | 2019-06-15 17:00 | 255 | 1022 | 304 | 1223 | 255 | 1028 | 198 | 613 | 105 |  |  | 105 | 5% | 6% | 82% | 13% | 3.7151 | Loss 0-5% |  | 852(104) | 914(190.5) | 904(126.5) | 931(111) | 775(57.5)
15 | 1110 | CCK | LAHORI GATE | LHR024 | TG-LHR024A-2 | DT-2 | PANDIT BROS:K | 2 | 990 | 19503236 | 871 | 2019-06-01 14:30 | 260 | 1162 | 339 | 1505 | 272 | 1222 | 317 | 663.5 | 53.5 |  |  | 53.5 | 9% | 15% | 88% | 13% | 3.7151 | Loss 0-5% |  |  | 731(32)
16 | 1110 | CCK | LAHORI GATE | LHR025 | TG-LHR025A-1 | DT-1 | CYCLE STAND:ID | 2 | 990 | 19501167 | 735 | 2019-06-03 14:00 | 257 | 1161 | 246 | 1098 | 232 | 1046 | 100 | 687 | 32 |  |  | 32 | 4% | 6% | 74% | 16% | 28.3054 | Loss 20-30%
17 | 1110 | CCK | LAHORI GATE | LHR025 | TG-LHR025A-2 | DT-2 | CYCLE STAND:ID | 2 | 990 | 19501166 | 911 | 2019-06-29 18:00 | 302 | 1302 | 332 | 1459 | 277 | 1207 | 221 | 480.5 | 234 | 1 |  | 235 | 90% | 81% | 92% | 82% | 28.3054 | Loss 20-30% |  | 849(88.5) | 992(433) | 930(240) | 791(87)
18 | 1110 | CCK | LAHORI GATE | LHR026 | TG-LHR026A-1 | DT-1 | OLD KRISHNA MARKET:ID | 1 | 990 | 19501852 | 815 | 2019-06-03 17:00 | 284 | 1202 | 221 | 922 | 310 | 1316 | 352 | 557.5 | 162.5 |  |  | 162.5 | 8% | 8% | 82% | 14% | 14.7889 | Loss 10-20% |  | 790(96) | 844(158.5) | 839(138.5) | 831(147) | 741(30.5)
19 | 1110 | CCK | LAHORI GATE | LHR027 | TG-LHR027A-1 | DT-1 | NEW KRISHNA MKT:ID | 2 | 990 | 19504835 | 939 | 2019-06-07 15:00 | 292 | 1316 | 315 | 1429 | 332 | 1483 | 148 | 539.5 | 167.5 | 13 |  | 180.5 | 8% | 11% | 95% | 16% | 14.7252 | Loss 10-20%
20 | 1110 | CCK | LAHORI GATE | LHR032 | TG-LHR032A-1 | DT-1 | HAVELI HYDERQULI:PM | 1 | 630 | 19506524 | 524.6712 | 2019-06-13 14:00 | 264.1057 | 1178.6225 | 136.5367 | 595.684 | 124.0287 | 540.8779 | 612.1843 | 641 | 77.5 |  |  | 77.5 | 74% | 45% | 83% | 76% | 5.9911 | Loss 5-10% |  |  |  | 525(47.5)
21 | 1110 | CCK | LAHORI GATE | LHR034 | TG-LHR034A-1 | DT-1 | KATRA BARYIAN PLINTH:PL | 1 | 630 | 19501572 | 599 | 2019-06-12 16:00 | 218 | 900 | 210 | 873 | 171 | 718 | 170 | 324.5 | 111.5 | 6.5 |  | 118 | 57% | 48% | 95% | 59% | 14.0195 | Loss 10-20% |  | 481(27.5) | 555(154.5) | 584(150) | 539(96.5)
22 | 1110 | CCK | LAHORI GATE | LHR043 | TG-LHR043A-1 | DT-1 | GADODIA KIOSK:K | 1 | 990 | 19506662 | 947.8727 | 2019-06-06 16:00 | 347.9285 | 1554.2928 | 285.6446 | 1246.5942 | 314.2996 | 1399.7489 | 266.4758 | 580.5 | 124.5 | 8.5 |  | 133 | 15% | 15% | 96% | 17% | 12.0706 | Loss 10-20% |  | 924(29.5) | 988(163.5) | 945(63) | 955(134)
23 | 1110 | CCK | LAHORI GATE | LHR046 | TG-LHR046A-1 | DT-1 | LAL DARWAZA:PM | 2 | 400 | 19506181 | 333.0715 | 2019-06-02 10:00 | 188.3708 | 758.3976 | 82.5021 | 323.3727 | 62.1987 | 243.6202 | 479.8973 | 686.5 | 33 |  |  | 33 | 69% | 59% | 83% | 76% | 31.4545 | Loss >30% | 474(194) |  | 367(46)
24 | 1110 | CCK | LAHORI GATE | LHR047 | TG-LHR047A-1 | DT-1 | LAMBI GALI:PL | 1 | 990 | 19501516 | 884 | 2019-06-03 04:30 | 287 | 1183 | 317 | 1314 | 280 | 1148 | 152 | 493.5 | 226 |  |  | 226 | 89% | 83% | 81% | 83% | 18.9247 | Loss 10-20% |  | 853(150.5) | 921(289.5) | 914(209.5) | 795(93)
25 | 1110 | CCK | LAHORI GATE | LHR048 | TG-LHR048A-2 | DT-2 | P.S HAUZ QUAZI:PL | 3 | 990 | 19501648 | 892 | 2019-06-02 04:00 | 357 | 1590 | 262 | 1168 | 273 | 1211 | 402 | 504 | 215 | 0.5 |  | 215.5 | 90% | 82% | 82% | 83% | 25.5668 | Loss 20-30% | 846(115) | 1027(391) | 1099(444) | 929(289.5) | 846(201)
26 | 1110 | CCK | LAHORI GATE | LHR051 | TG-LHR051A-3 | DT-3 | NEW HAUZ QUAZI:ID | 3 | 630 | 19505507 | 693 | 2019-06-28 15:00 | 223 | 1044 | 218 | 1040 | 252 | 1236 | 194 | 485.5 | 233.5 |  | 0.5 | 234 | 86% | 77% | 110% | 80% | 17.62 | Loss 10-20% |  | 765(179) | 760(340) | 627(245.5) | 564(105.5)
27 | 1110 | CCK | LAHORI GATE | LHR054 | TG-LHR054A-1 | DT-1 | HAMDARD:ID | 1 | 400 | 19501504 | 337 | 2019-06-11 05:00 | 178 | 782 | 78 | 319 | 80 | 337 | 454 | 682 | 37.5 |  |  | 37.5 | 84% | 68% | 73% | 69% | 23.5342 | Loss 20-30% |  |  | 341(88.5)
28 | 1110 | CCK | LAHORI GATE | LHR055 | TG-LHR055A-1 | DT-1 | GALI KASIM JAAN:ID | 2 | 990 | 19501574 | 966.7434 | 2019-06-02 04:30 | 345.9584 | 1528.6248 | 308.2865 | 1358.0305 | 312.4985 | 1369.6464 | 165.0931 | 470 | 152.5 | 17.5 |  | 170 | 98% | 91% | 88% | 89% | 20.2202 | Loss 20-30%
29 | 1110 | CCK | LAHORI GATE | LHR055 | TG-LHR055A-2 | DT-2 | GALI KASIM JAAN:ID | 2 | 990 | 19501573 | 934 | 2019-06-02 04:00 | 308 | 1387 | 336 | 1522 | 290 | 1285 | 206 | 435.5 | 278.5 | 4.5 |  | 283 | 94% | 81% | 86% | 87% | 20.2202 | Loss 20-30% |  | 904(249) | 1012(448) | 955(301) | 870(182)
30 | 1110 | CCK | LAHORI GATE | LHR056 | TG-LHR056A-1 | DT-1 | GALI HASHMUDDIN:PKG | 1 | 990 | 19500694 | 1138.5187 | 2019-06-30 01:00 | 395.903 | 1664.7171 | 413.7793 | 1782.9935 | 328.8364 | 1333.6971 | 403.3799 | 282 | 239 | 97 | 99 | 435 | 115% | 101% | 92% | 113% | 22.505 | Loss 20-30% | 933(66) | 1053(233.5) | 1151(507) | 1127(173) | 1039(336) | 993(123.5)
31 | 1110 | CCK | TOWN HALL | THL004 | TG-THL004A-2 | DT-2 | KATRA KUSHAL RAI:ID | 3 | 990 | 19500225 | 877 | 2019-06-08 17:00 | 287 | 1242 | 310 | 1355 | 280 | 1223 | 123 | 608.5 | 108.5 |  |  | 108.5 | 34% | 30% | 89% | 34% | 14.747 | Loss 10-20% |  | 801(25.5) |  | 882(105.5) | 862(108) | 805(58.5)
32 | 1110 | CCK | TOWN HALL | THL006 | TG-THL006A-1 | DT-1 | NEW LAJPAT RAI MKT:ID | 1 | 990 | 19500223 | 866 | 2019-06-03 16:00 | 395 | 1692 | 200 | 843 | 271 | 1161 | 744 | 650.5 | 67.5 |  |  | 67.5 | 18% | 15% | 87% | 30% | 11.7994 | Loss 10-20% |  |  |  | 780(42)
33 | 1110 | CCK | TOWN HALL | THL007 | TG-THL007A-1 | DT-1 | MALIWARA : PKG | 1 | 990 | 19505462 | 819 | 2019-06-29 17:00 | 294 | 1256 | 266 | 1143 | 259 | 1108 | 134 | 634.5 | 85.5 |  |  | 85.5 | 15% | 10% | 83% | 16% | 5.2475 | Loss 5-10% |  |  | 785(77.5)
34 | 1110 | CCK | TOWN HALL | THL010 | TG-THL010A-1 | DT-1 | KUCHHA NALWA:PKG | 1 | 990 | 19506919 | 941.4822 | 2019-06-27 14:30 | 381.6131 | 1681.3372 | 286.9879 | 1267.5585 | 272.8812 | 1200.8502 | 450.8496 | 330.5 | 101.5 | 7.5 |  | 109 | 9% | 7% | 95% | 11% | 4.2988 | Loss 0-5% | 853(116.5) | 987(178.5) | 963(44) | 939(159) | 925(168.5)
35 | 1110 | CCK | TOWN HALL | THL014 | TG-THL014A-1 | DT-1 | KUMAR CINEMA:PKG | 1 | 990 | 19500231 | 840 | 2019-06-25 16:00 | 285 | 1226 | 265 | 1150 | 290 | 1240 | 84 | 580 | 115 |  |  | 115 | 12% | 21% | 85% | 18% | 8.9216 | Loss 5-10% |  |  | 797(108) | 821(79) | 781(61.5)
36 | 1110 | CCK | TOWN HALL | THL015 | TG-THL015A-1 | DT-1 | MAHARASHTRA BANK:PKG | 1 | 990 | 19500561 | 887.9624 | 2019-06-12 16:00 | 292.7948 | 1245.6174 | 303.7032 | 1306.082 | 291.4644 | 1220.8443 | 75.9445 | 606 | 112 |  |  | 112 | 34% | 26% | 90% | 41% | 4.4886 | Loss 0-5% |  | 808(51.5) | 862(147.5) | 874(111.5) | 825(92.5)
37 | 1110 | CCK | TOWN HALL | THL019 | TG-THL019A-1 | DT-1 | KINARI BAZAR:PM | 2 | 400 | 19503057 | 384 | 2019-06-21 17:00 | 118 | 520 | 118 | 518 | 148 | 664 | 145 | 603.5 | 104.5 | 11.5 |  | 116 | 46% | 34% | 96% | 46% | 4.6231 | Loss 0-5% |  | 354(47.5)
38 | 1110 | CCK | TOWN HALL | THL019 | TG-THL019A-2 | DT-2 | KINARI BAZAR:PM | 2 | 400 | 19503058 | 371 | 2019-06-14 15:30 | 116 | 511 | 149 | 662 | 106 | 463 | 180 | 537.5 | 165.5 | 16 |  | 181.5 | 19% | 15% | 93% | 44% | 4.6231 | Loss 0-5% |  | 336(70) | 354(157.5) | 365(175) | 346(138.5)
39 | 1110 | CCK | TOWN HALL | THL020 | TG-THL020A-1 | DT-1 | DIWAN HALL:PM | 3 | 400 | 19501226 | 344 | 2019-06-29 16:00 | 121 | 536 | 94 | 417 | 129 | 576 | 143 | 598.5 | 113 |  |  | 113 | 8% | 7% | 86% | 12% | 4.212 | Loss 0-5% |  | 339(60) | 408(142.5) | 371(122) | 337(108.5)
40 | 1110 | CCK | TOWN HALL | THL021 | TG-THL021A-2 | DT-2 | TIKONA PARK:PL | 2 | 630 | 19501176 | 497 | 2019-06-14 15:30 | 136 | 595 | 150 | 653 | 211 | 931 | 311 | 634.5 | 82.5 |  |  | 82.5 | 6% | 4% | 79% | 10% | 6.9356 | Loss 5-10% |  |  | 483(46.5) | 484(30.5)
41 | 1110 | CCK | TOWN HALL | THL025 | TG-THL025A-1 | DT-1 | SHRI RAM:PL | 1 | 990 | 19501100 | 843 | 2019-06-29 13:30 | 243 | 1071 | 321 | 1435 | 278 | 1244 | 315 | 687.5 | 30.5 |  |  | 30.5 | 5% | 5% | 85% | 11% | 4.255 | Loss 0-5%
42 | 1110 | CCK | TOWN HALL | THL028 | TG-THL028A-1 | DT-1 | MOTI BAZAR:PKG | 1 | 990 | 19506477 | 772 | 2019-06-29 16:00 | 247 | 1063 | 257 | 1107 | 268 | 1162 | 86 | 613 | 104.5 |  |  | 104.5 | 8% | 7% | 78% | 10% | 7.7219 | Loss 5-10% |  |  | 899(79.5)
43 | 1110 | CCK | TOWN HALL | THL029 | TG-THL029A-1 | DT-1 | GALI PARATHE:PKG | 1 | 990 | 19501182 | 769 | 2019-06-06 15:30 | 288 | 1302 | 258 | 1175 | 223 | 1017 | 247 | 684 | 32.5 |  |  | 32.5 | 13% | 10% | 78% | 28% | 5.2131 | Loss 5-10% |  |  | 809(77.5) | 777(26.5)
44 | 1110 | CCK | TOWN HALL | THL035 | TG-THL035A-1 | DT-1 | CHARHAT:PKG | 1 | 990 | 19501855 | 875.7033 | 2019-06-11 23:30 | 281.4418 | 1193.8147 | 289.1169 | 1223.9824 | 305.1446 | 1304.5384 | 99.144 | 554 | 165.5 |  |  | 165.5 | 87% | 62% | 88% | 88% | 5.83 | Loss 5-10% |  | 864(96.5) | 943(289) | 934(166) | 891(69.5)
45 | 1120 | DRG | DARYAGANJ | DRY007 | TG-DRY007A-2 | DT-2 | BACHHO KA GHAR:PKG | 2 | 630 | 19504372 | 582 | 2019-06-10 15:00 | 219 | 943 | 191 | 822 | 171 | 740 | 177 | 566 | 150.5 | 3.5 |  | 154 | 18% | 20% | 92% | 27% | 4.7658 | Loss 0-5%
46 | 1120 | DRG | DARYAGANJ | DRY011 | TG-DRY011A-1 | DT-1 | DARYA GANJ KOTWALI:PL | 1 | 630 | 19501677 | 581 | 2019-06-12 15:00 | 187 | 780 | 210 | 916 | 184 | 801 | 127 | 561 | 155.5 | 3.5 |  | 159 | 45% | 41% | 92% | 42% | 3.0901 | Loss 0-5% | 504(28.5) | 675(189.5) | 731(218.5) | 676(195) | 607(176.5) | 541(77.5)
47 | 1120 | DRG | DARYAGANJ | DRY035 | TG-DRY035A-2 | DT-2 | VIKRAM NAGAR:PACKAGE S/STN | 2 | 990 | 19505152 | 806 | 2019-06-12 00:30 | 199 | 834 | 219 | 929 | 388 | 1670 | 793 | 686 | 34 |  |  | 34 | 81% | 52% | 58% | 81% | 10.0599 | Loss 10-20%
48 | 1120 | DRG | DARYAGANJ | DRY089 | TG-DRY089A-1 | DT-1 | GHATA MASJID:PG | 1 | 990 | 19500136 | 948 | 2019-06-03 15:30 | 331 | 1418 | 308 | 1316 | 308 | 1320 | 100 | 538 | 169.5 | 12 |  | 181.5 | 45% | 42% | 96% | 51% | 7.3755 | Loss 5-10% |  | 893(87.5) | 955(201.5) | 916(131.5) | 800(81.5)
49 | 1120 | DRG | JAMA MASJID | HAU001 | TG-HAU001A-1 | DT-1 | 84 GHANTA:K | 3 | 990 | 19500381 | 1063 | 2019-06-11 01:00 | 322 | 1486 | 452 | 1919 | 289 | 1202 | 625 | 514 | 159 | 39.5 | 6.5 | 205 | 107% | 71% | 82% | 102% | 21.4421 | Loss 20-30% | 845(33) | 1160(309) | 1194(409.5) | 1119(298) | 926(175.5)
50 | 1120 | DRG | JAMA MASJID | HAU001 | TG-HAU001A-2 | DT-2 | 84 GHANTA:K | 3 | 990 | 19501686 | 1036 | 2019-06-15 00:30 | 297 | 1348 | 342 | 1556 | 398 | 1833 | 421 | 310 | 311.5 | 82.5 | 16 | 410 | 105% | 81% | 89% | 104% | 21.4421 | Loss 20-30% | 816(24.5) | 971(231) | 1074(408) | 1078(369) | 950(321.5) | 865(76.5)
51 | 1120 | DRG | JAMA MASJID | HAU001 | TG-HAU001A-3 | DT-3 | 84 GHANTA:K | 3 | 990 | 19503790 | 981 | 2019-06-12 02:30 | 394 | 1632 | 250 | 1018 | 337 | 1393 | 536 | 355 | 318 | 45 |  | 363 | 99% | 85% | 83% | 96% | 21.4421 | Loss 20-30% |  |  | 947(354) | 928(293.5) | 810(147.5)
52 | 1120 | DRG | JAMA MASJID | HAU003 | TG-HAU003A-2 | DT-2 | DDA HOUSING COMP.TURKMAN GATE:ID | 4 | 990 | 19501667 | 793 | 2019-06-02 04:30 | 209 | 916 | 257 | 1138 | 327 | 1455 | 470 | 610 | 107.5 |  |  | 107.5 | 80% | 80% | 76% | 68% | 61.0258 | Loss >30%
53 | 1120 | DRG | JAMA MASJID | HAU006 | TG-HAU006A-1 | DT-1 | GALI DAKOTAN:PM | 1 | 990 | 19500348 | 901 | 2019-06-06 | 304 | 1245 | 286 | 1169 | 311 | 1277 | 96 | 591.5 | 123 | 1.5 |  | 124.5 | 91% | 65% | 70% | 91% | 25.312 | Loss 20-30% |  |  |  | 798(27)
54 | 1120 | DRG | JAMA MASJID | HAU008 | TG-HAU008A-1 | DT-1 | GALI SHANKAR:ID | 2 | 990 | 19506161 | 965 | 2019-06-03 13:00 | 252 | 1194 | 323 | 1522 | 389 | 1739 | 476 | 482 | 221 | 17 |  | 238 | 96% | 93% | 97% | 85% | 31.2111 | Loss >30% |  |  | 1077(303.5) | 900(110) | 1036(33) | 1142(88.5)
55 | 1120 | DRG | JAMA MASJID | HAU010 | TG-HAU010A-2 | DT-2 | HAMMATGARH:K | 2 | 990 | 19500332 | 779 | 2019-06-10 23:30 | 197 | 846 | 300 | 1298 | 281 | 1219 | 418 | 638 | 79 |  |  | 79 | 77% | 68% | 66% | 79% | 4.5512 | Loss 0-5% |  |  | 795(90.5) | 806(64.5)
56 | 1120 | DRG | JAMA MASJID | HAU011 | TG-HAU011A-1 | DT-1 | RAJ ENGINEERING:ID | 2 | 990 | 19500218 | 808 | 2019-06-05 15:00 | 266 | 1188 | 254 | 1131 | 288 | 1281 | 131 | 654.5 | 65.5 |  |  | 65.5 | 65% | 49% | 82% | 66% | 9.3831 | Loss 5-10% |  |  | 818(55) | 870(36)
57 | 1120 | DRG | JAMA MASJID | HAU011 | TG-HAU011A-2 | DT-2 | RAJ ENGINEERING:ID | 2 | 990 | 19504377 | 767 | 2019-06-05 15:00 | 215 | 965 | 321 | 1458 | 230 | 1034 | 462 | 675.5 | 44.5 |  |  | 44.5 | 72% | 54% | 77% | 74% | 9.3831 | Loss 5-10% |  |  | 858(59) | 872(42)
58 | 1120 | DRG | JAMA MASJID | HAU012 | TG-HAU012A-1 | DT-1 | SARAK PREM NARAIN:PL | 1 | 990 | 19501687 | 1042 | 2019-06-27 05:30 | 296 | 1219 | 384 | 1543 | 362 | 1504 | 306 | 314.5 | 327.5 | 73 | 3.5 | 404 | 105% | 102% | 85% | 93% | 28.5473 | Loss 20-30% | 793(28) | 979(290.5) | 1055(542.5) | 1060(412) | 920(355.5) | 824(59.5)
59 | 1120 | DRG | JAMA MASJID | HAU014 | TG-HAU014A-1 | DT-1 | BARSHABULLA:ID DRG | 1 | 990 | 19503477 | 968 | 2019-06-13 17:00 | 316 | 1432 | 317 | 1428 | 335 | 1529 | 99 | 549 | 145 | 25.5 |  | 170.5 | 65% | 50% | 98% | 64% | 13.7338 | Loss 10-20% |  | 975(130) | 1055(202) | 998(173) | 930(177.5) | 828(75)
60 | 1120 | DRG | JAMA MASJID | HAU015 | TG-HAU015A-1 | DT-1 | NEW HAUZ QUAZI:ID DRG | 1 | 990 | 19502903 | 945 | 2019-06-01 15:00 | 360 | 1575 | 329 | 1438 | 255 | 1114 | 410 | 482 | 233.5 | 4 |  | 237.5 | 88% | 58% | 95% | 83% | 10.0516 | Loss 10-20% |  |  | 941(116.5)
61 | 1120 | DRG | JAMA MASJID | JMS001 | TG-JMS001A-1 | DT-1 | BULIBULI KHANA:ID | 2 | 990 | 19505784 | 879 | 2019-06-03 13:30 | 483 | 2022 | 12 | 50 | 384 | 1608 | 1801 | 656 | 64 |  |  | 64 | 78% | 76% | 89% | 75% | 44.7575 | Loss >30% | 1068(133.5) | 1506(556) | 1502(689.5) | 1524(636) |  | 1268(353.5)
62 | 1120 | DRG | JAMA MASJID | JMS001 | TG-JMS001A-2 | DT-2 | BULIBULI KHANA:ID | 2 | 990 | 19501700 | 984 | 2019-06-04 04:30 | 351 | 1500 | 327 | 1393 | 306 | 1308 | 167 | 268.5 | 400 | 51.5 |  | 451.5 | 99% | 93% | 87% | 90% | 44.7575 | Loss >30% |  | 1003(335.5) | 1176(622) | 993(475.5) | 933(443) | 875(106.5)
63 | 1120 | DRG | JAMA MASJID | JMS002 | TG-JMS002A-2 | DT-2 | CHANDNI MAHAL:ID | 4 | 990 | 19505094 | 1253 | 2019-06-02 18:00 | 374 | 1718 | 447 | 2153 | 431 | 2127 | 422 | 665 | 42.5 | 1 | 0.5 | 44 | 94% | 77% | 127% | 72% | 60.2944 | Loss >30%
64 | 1120 | DRG | JAMA MASJID | JMS002 | TG-JMS002A-4 | DT-4 | CHANDNI MAHAL:ID | 4 | 630 | 19505203 | 805 | 2019-06-29 02:30 | 395 | 1790 | 216 | 938 | 193 | 839 | 905 | 137.5 | 346.5 | 154.5 | 80 | 581 | 128% | 116% | 119% | 109% | 60.2944 | Loss >30% | 605(121.5) | 862(505.5) | 775(672.5) | 1078(598)
65 | 1120 | DRG | JAMA MASJID | JMS003 | TG-JMS003A-1 | DT-1 | CHANDNI MAHAL [K]:K | 1 | 990 | 19504749 | 1090 | 2019-06-03 04:00 | 374 | 1564 | 381 | 1596 | 336 | 1391 | 191 | 267 | 292 | 113 | 48 | 453 | 110% | 96% | 93% | 102% | 48.1255 | Loss >30% | 806(30.5) | 1051(351) | 1147(547) | 1124(384) | 986(347) | 884(102)
66 | 1120 | DRG | JAMA MASJID | JMS004 | TG-JMS004A-1 | DT-1 | DELHI GATE TELEPHONE EXCHANGE PM:K | 2 | 990 | 19505683 | 1090 | 2019-06-17 03:00 | 345 | 1448 | 363 | 1506 | 383 | 1617 | 148 | 408 | 281.5 | 16 | 8 | 305.5 | 110% | 105% | 110% | 108% | 12.0291 | Loss 10-20% |  |  | 920(34.5) | 973(135) | 1026(375.5) | 846(76)
67 | 1120 | DRG | JAMA MASJID | JMS006 | TG-JMS006A-1 | DT-1 | GANJ MEER KHAN:PM | 1 | 990 | 19505263 | 1234 | 2019-06-12 02:00 | 425 | 1527 | 468 | 1763 | 341 | 1290 | 409 | 58 | 280 | 144 | 238 | 662 | 125% | 122% | 108% | 112% | 50.8784 | Loss >30% | 1187(147) |  | 1161(39) |  | 1225(572.5) | 1068(157)
68 | 1120 | DRG | JAMA MASJID | JMS008 | TG-JMS008A-3 | DT-3 | GIRDHAR PANNA:ID | 3 | 630 | 19506160 | 775.4229 | 2019-06-03 04:30 | 247.0648 | 1089.5914 | 297.1256 | 1343.244 | 231.2325 | 1025.0123 | 291.3601 | 186.5 | 318 | 134.5 | 80.5 | 533 | 123% | 103% | 105% | 104% | 45.4574 | Loss >30% |  |  | 787(409.5) | 781(495)
69 | 1120 | DRG | JAMA MASJID | JMS010 | TG-JMS010A-3 | DT-3 | JAMA MASJID:ID | 3 | 630 | 19505361 | 514 | 2019-06-14 05:30 | 224 | 1001 | 137 | 585 | 152 | 620 | 400 | 694.5 | 25.5 |  |  | 25.5 | 82% | 66% | 75% | 74% | 29.402 | Loss 20-30% | 927(95) | 1065(425.5) | 1094(89.5) | 608(57.5)
70 | 1120 | DRG | JAMA MASJID | JMS013 | TG-JMS013A-1 | DT-1 | KASTURBA P/M:PM | 1 | 990 | 19500206 | 784 | 2019-06-03 04:30 | 287 | 1191 | 238 | 978 | 259 | 1066 | 186 | 635.5 | 84.5 |  |  | 84.5 | 79% | 71% | 67% | 72% | 37.6689 | Loss >30% |  | 846(98.5) | 919(292.5) | 853(122.5) | 781(52)
71 | 1120 | DRG | JAMA MASJID | JMS015 | TG-JMS015A-1 | DT-1 | KUCHA CHELAN-2:PL | 3 | 990 | 19506158 | 1004 | 2019-06-05 04:30 | 329 | 1292 | 339 | 1320 | 335 | 1307 | 24 | 342.5 | 335.5 | 39.5 | 1 | 376 | 101% | 92% | 97% | 92% | 68.3145 | Loss >30% | 808(33.5) | 974(351.5) | 1103(575) | 1027(452) | 972(358.5) | 1087(93)
72 | 1120 | DRG | JAMA MASJID | JMS015 | TG-JMS015A-2 | DT-2 | KUCHA CHELAN-2:PL | 3 | 400 | 19500358 | 429 | 2019-06-01 21:00 | 167 | 721 | 140 | 599 | 122 | 519 | 177 | 346 | 310 | 61.5 | 1.5 | 373 | 89% | 78% | 105% | 107% | 68.3145 | Loss >30% | 330(44.5) | 397(283.5) | 406(170.5) | 430(405) |  | 346(126.5)
73 | 1120 | DRG | JAMA MASJID | JMS015 | TG-JMS015A-3 | DT-3 | KUCHA CHELAN-2:PL | 3 | 990 | 19505512 | 1339 | 2019-06-26 22:30 | 499 | 2126 | 386 | 1633 | 454 | 1920 | 429 | 55 | 342 | 179.5 | 140.5 | 662 | 126% | 122% | 111% | 135% | 68.3145 | Loss >30% | 896(105) |  | 1248(665)
74 | 1120 | DRG | JAMA MASJID | JMS017 | TG-JMS017A-1 | DT-1 | KUCHA DAKHINI RAI:PL | 2 | 990 | 19506016 | 1081 | 2019-06-01 19:00 | 454 | 2200 | 219 | 1004 | 408 | 2140 | 1168 | 418 | 260 | 40.5 | 1 | 301.5 | 101% | 92% | 109% | 92% | 50.4237 | Loss >30% | 977(38) |  | 1341(697.5)
75 | 1120 | DRG | JAMA MASJID | JMS017 | TG-JMS017A-2 | DT-2 | KUCHA DAKHINI RAI:PL | 2 | 990 | 19506022 | 826 | 2019-06-11 05:00 | 234 | 1026 | 391 | 1793 | 201 | 861 | 862 | 672 | 47.5 |  |  | 47.5 | 83% | 67% | 83% | 71% | 50.4237 | Loss >30% |  |  | 1042(253.5) |  | 1150(595) | 1096(262)
76 | 1120 | DRG | JAMA MASJID | JMS018 | TG-JMS018A-1 | DT-1 | MOHALLA QUABRISTAN:PL | 1 | 990 | 19501666 | 909 | 2019-06-05 05:00 | 348 | 1504 | 270 | 1167 | 292 | 1264 | 300 | 330.5 | 388.5 | 1 |  | 389.5 | 92% | 84% | 83% | 88% | 59.2166 | Loss >30% |  | 914(251.5) | 985(522) | 971(360) | 916(336) | 843(84.5)
77 | 1120 | DRG | JAMA MASJID | JMS019 | TG-JMS019A-1 | DT-1 | MOTHER DAIRY:K | 1 | 630 | 19500379 | 635 | 2019-06-05 02:00 | 283 | 1194 | 169 | 704 | 183 | 769 | 461 | 447.5 | 259.5 | 9 | 1 | 269.5 | 101% | 77% | 89% | 96% | 40.1033 | Loss >30% |  | 569(44) | 677(444.5) | 597(321.5) | 558(174) | 486(25.5)
78 | 1120 | DRG | JAMA MASJID | JMS021 | TG-JMS021A-3 | DT-3 | NEW DUJANA HOUSE 8 PANEL:ID | 8 | 990 | 19503567 | 810 | 2019-06-03 04:00 | 308 | 1352 | 270 | 1160 | 233 | 1005 | 301 | 651 | 68.5 |  |  | 68.5 | 82% | 75% | 74% | 72% | 50.6818 | Loss >30% |  | 792(69) | 858(242) | 821(99)
79 | 1120 | DRG | JAMA MASJID | JMS021 | TG-JMS021A-4 | DT-4 | NEW DUJANA HOUSE 8 PANEL:ID | 8 | 990 | 19500203 | 1022 | 2019-06-02 04:30 | 377 | 1608 | 272 | 1157 | 373 | 1597 | 445 | 266 | 368 | 82 | 3.5 | 453.5 | 103% | 93% | 89% | 95% | 50.6818 | Loss >30% | 808(36) | 977(334) | 1122(578) | 1018(466) | 924(398.5) | 876(84.5)
80 | 1120 | DRG | JAMA MASJID | JMS021 | TG-JMS021A-5 | DT-5 | NEW DUJANA HOUSE 8 PANEL:ID | 8 | 990 | 19500202 | 1084 | 2019-06-11 00:30 | 416 | 1832 | 328 | 1436 | 341 | 1479 | 377 | 152.5 | 378.5 | 138 | 50.5 | 567 | 109% | 100% | 95% | 104% | 50.6818 | Loss >30% |  |  | 1163(463) | 1112(582.5) | 1023(560) | 943(144.5)
81 | 1120 | DRG | JAMA MASJID | JMS021 | TG-JMS021A-6 | DT-6 | NEW DUJANA HOUSE 8 PANEL:ID | 8 | 990 | 19500201 | 830 | 2019-06-10 23:30 | 334 | 1473 | 282 | 1220 | 214 | 930 | 471 | 637.5 | 82.5 |  |  | 82.5 | 82% | 68% | 80% | 84% | 50.6818 | Loss >30% |  | 845(119.5) | 949(349.5) | 933(279)
82 | 1120 | DRG | JAMA MASJID | JMS021 | TG-JMS021A-8 | DT-8 | NEW DUJANA HOUSE 8 PANEL:ID | 8 | 990 | 19506157 | 824 | 2019-06-02 03:00 | 299 | 1208 | 189 | 771 | 336 | 1400 | 558 | 649.5 | 68 |  |  | 68 | 83% | 75% | 72% | 72% | 50.6818 | Loss >30% |  |  | 1016(169.5) | 949(97.5) | 873(31)
83 | 1120 | DRG | JAMA MASJID | JMS022 | TG-JMS022A-1 | DT-1 | OLD DUJANA:K | 2 | 990 | 19506594 | 1180 | 2019-06-02 04:00 | 361 | 1524 | 308 | 1305 | 510 | 2227 | 834 | 193.5 | 352 | 144.5 | 29 | 525.5 | 119% | 104% | 114% | 100% | 51.5596 | Loss >30% | 837(42.5) | 900(97.5) |  |  | 902(88.5)
84 | 1120 | DRG | JAMA MASJID | JMS022 | TG-JMS022A-2 | DT-2 | OLD DUJANA:K | 2 | 990 | 19500383 | 1002 | 2019-06-03 | 355 | 1585 | 266 | 1167 | 381 | 1717 | 497 | 269.5 | 393.5 | 53.5 | 3.5 | 450.5 | 101% | 90% | 96% | 101% | 51.5596 | Loss >30% | 875(61) | 1020(371) | 1115(560) | 1069(468.5) | 923(409) | 894(133.5)
85 | 1120 | DRG | JAMA MASJID | JMS023 | TG-JMS023A-1 | DT-1 | SHEESH MAHAL:K | 2 | 990 | 19501661 | 1003 | 2019-06-30 01:30 | 384 | 1613 | 335 | 1410 | 284 | 1187 | 369 | 292.5 | 330 | 93.5 | 3.5 | 427 | 101% | 90% | 88% | 96% | 41.1752 | Loss >30% | 828(32) | 929(298.5) | 1048(506.5) | 999(311.5) | 927(301) | 865(85)
86 | 1120 | DRG | JAMA MASJID | JMS023 | TG-JMS023A-2 | DT-2 | SHEESH MAHAL:K | 2 | 990 | 19506663 | 839 | 2019-06-30 01:30 | 231 | 975 | 296 | 1261 | 312 | 1332 | 327 | 587.5 | 132 |  |  | 132 | 85% | 75% | 71% | 74% | 41.1752 | Loss >30% |  | 905(170.5) | 878(181) | 874(128.5) | 758(29)
87 | 1120 | DRG | JAMA MASJID | JMS024 | TG-JMS024A-1 | DT-1 | SSA ROAD:PL:PG | 2 | 990 | 19503516 | 1035 | 2019-06-30 02:30 | 388 | 1702 | 307 | 1336 | 341 | 1473 | 321 | 517 | 183 | 18 | 1 | 202 | 105% | 96% | 87% | 95% | 25.9097 | Loss 20-30% |  |  | 1091(477) | 1085(496.5) | 949(407)
88 | 1120 | DRG | JAMA MASJID | JMS024 | TG-JMS024A-2 | DT-2 | SSA ROAD:PL:PG | 2 | 990 | 19500074 | 933 | 2019-06-03 | 283 | 1225 | 389 | 1691 | 260 | 1104 | 537 | 672 | 40 | 3.5 |  | 43.5 | 94% | 77% | 84% | 93% | 25.9097 | Loss 20-30% |  | 938(27)
89 | 1120 | DRG | JAMA MASJID | JMS025 | TG-JMS025A-1 | DT-1 | TIRAHA BAIRAM KHAN:ID | 2 | 990 | 19500357 | 810 | 2019-06-30 00:30 | 278 | 1188 | 269 | 1146 | 263 | 1113 | 65 | 630 | 86 |  |  | 86 | 82% | 72% | 71% | 77% | 49.4643 | Loss >30% |  | 766(29.5) | 832(134.5) | 831(80)
90 | 1120 | DRG | JAMA MASJID | JMS025 | TG-JMS025A-2 | DT-2 | TIRAHA BAIRAM KHAN:ID | 2 | 990 | 19500359 | 1407 | 2019-06-01 22:30 | 433 | 1843 | 488 | 2078 | 486 | 2085 | 239 | 33.5 | 194 | 156.5 | 335 | 685.5 | 140% | 116% | 140% | 142% | 49.4643 | Loss >30% | 1180(365.5) | 1501(626) | 1458(579) |  |  | 1108(382)
91 | 1120 | DRG | JAMA MASJID | JMS026 | TG-JMS026A-1 | DT-1 | URDU BAZAR:PG | 3 | 990 | 19506156 | 1074 | 2019-06-11 05:00 | 272 | 1161 | 284 | 1164 | 519 | 2367 | 1205 | 492 | 223.5 | 3.5 | 0.5 | 227.5 | 109% | 81% | 86% | 91% | 36.017 | Loss >30% | 965(113.5) |  | 782(43.5) |  | 1028(78) | 807(37)
92 | 1120 | DRG | JAMA MASJID | JMS033 | TG-JMS033A-1 | DT-1 | HOTEL BROADWAY:K | 4 | 990 | 19500330 | 1013 | 2019-06-27 01:30 | 382 | 1671 | 348 | 1533 | 283 | 1218 | 402 | 386.5 | 249 | 83 | 1.5 | 333.5 | 102% | 90% | 82% | 94% | 58.7006 | Loss >30% |  | 891(89.5) | 996(379) | 941(235.5) | 909(228) | 834(71.5)
93 | 1120 | DRG | JAMA MASJID | JMS033 | TG-JMS033A-2 | DT-2 | HOTEL BROADWAY:K | 4 | 990 | 19503512 | 806 | 2019-06-26 17:00 | 256 | 1070 | 277 | 1162 | 273 | 1132 | 81 | 625.5 | 94.5 |  |  | 94.5 | 41% | 57% | 81% | 37% | 58.7006 | Loss >30%
94 | 1120 | DRG | JAMA MASJID | JMS033 | TG-JMS033A-3 | DT-3 | HOTEL BROADWAY:K | 4 | 990 | 19506159 | 1087 | 2019-06-02 03:00 | 471 | 2110 | 322 | 1386 | 294 | 1272 | 787 | 598.5 | 100.5 | 12 | 6 | 118.5 | 110% | 106% | 100% | 99% | 58.7006 | Loss >30% | 965(83) |  | 1155(583.5) | 1180(444.5) | 1032(418.5)
95 | 1120 | DRG | MINTO ROAD | MRD012 | TG-MRD012A-1 | DT-1 | KOTLA RD.:PL | 1 | 630 | 19500331 | 535 | 2019-06-06 14:30 | 173 | 744 | 189 | 819 | 173 | 749 | 72 | 654.5 | 65.5 |  |  | 65.5 | 41% | 55% | 85% | 47% | 4.1506 | Loss 0-5%
96 | 1120 | DRG | MINTO ROAD | MRD073 | TG-MRD073A-1 | DT-1 | SHAKOOR KI DANDI P/M | 1 | 630 | 19506142 | 586 | 2019-06-24 15:00 | 206 | 853 | 198 | 824 | 181 | 754 | 88 | 651 | 68 | 0.5 |  | 68.5 | 76% | 73% | 93% | 77% | 44.3119 | Loss >30% |  | 626(90) | 611(280.5) | 666(206) | 547(38)
97 | 1130 | PHG | B G ROAD | BGR003 | TG-BGR003A-1 | DT-1 | GALI BAHUJI: PL | 1 | 990 | 19506463 | 869 | 2019-06-12 17:30 | 295 | 1212 | 246 | 1006 | 328 | 1340 | 292 | 619.5 | 100.5 |  |  | 100.5 | 69% | 56% | 88% | 71% | 18.2556 | Loss 10-20% |  | 830(41.5) | 880(133) | 866(108.5) | 834(66.5)
98 | 1130 | PHG | B G ROAD | BGR004 | TG-BGR004A-2 | DT-2 | MODEL BASTI:PL | 2 | 990 | 19503047 | 804 | 2019-06-26 16:00 | 287 | 1192 | 245 | 1026 | 272 | 1139 | 146 | 652.5 | 67.5 |  |  | 67.5 | 71% | 57% | 81% | 71% | 23.5321 | Loss 20-30% |  | 825(59.5) | 886(25) | 855(154) | 764(64.5)
99 | 1130 | PHG | B G ROAD | BGR005 | TG-BGR005A-1 | DT-1 | CHIMNI MIL PL/M:PL | 2 | 990 | 19503586 | 861 | 2019-06-25 17:30 | 296 | 1304 | 286 | 1249 | 278 | 1226 | 69 | 512.5 | 206 |  |  | 206 | 64% | 55% | 87% | 66% | 36.0781 | Loss >30% |  |  | 851(87) | 902(176) | 926(169) | 901(112.5)
100 | 1130 | PHG | B G ROAD | BGR005 | TG-BGR005A-2 | DT-2 | CHIMNI MIL PL/M:PL | 2 | 990 | 19500047 | 839 | 2019-06-02 04:30 | 267 | 1199 | 289 | 1291 | 282 | 1269 | 84 | 564 | 155 |  |  | 155 | 85% | 79% | 77% | 77% | 36.0781 | Loss >30% |  | 820(91.5) | 861(287.5) | 818(115.5) | 774(25)
101 | 1130 | PHG | B G ROAD | BGR013 | TG-BGR013A-1 | DT-1 | FOOTA ROAD KIOSK:K | 1 | 990 | 19504867 | 996 | 2019-06-04 15:30 | 313 | 1331 | 405 | 1735 | 278 | 1167 | 506 | 536 | 131.5 | 50 | 0.5 | 182 | 39% | 36% | 101% | 39% | 4.0636 | Loss 0-5% |  | 935(134.5) | 1004(131) | 1026(70) | 951(163) | 839(118)
102 | 1130 | PHG | B G ROAD | BGR016 | TG-BGR016A-1 | DT-1 | GALI NEEM WALI:K | 1 | 990 | 19500079 | 850 | 2019-06-30 18:00 | 291 | 1200 | 267 | 1110 | 292 | 1220 | 101 | 628 | 91.5 |  |  | 91.5 | 66% | 73% | 86% | 78% | 11.0281 | Loss 10-20% |  |  | 798(59) | 797(36.5)
103 | 1130 | PHG | B G ROAD | BGR020 | TG-BGR020A-1 | DT-1 | AHATA KIDARA UNIT I:PM | 1 | 400 | 19506187 | 463 | 2019-06-01 19:00 | 238 | 1022 | 119 | 483 | 105 | 456 | 553 | 26.5 | 376.5 | 191.5 | 125 | 693 | 115% | 112% | 116% | 111% | 14.2431 | Loss 10-20% | 383(194) | 540(534) | 486(684) | 466(659.5) | 453(638.5) | 467(443.5)
104 | 1130 | PHG | B G ROAD | BGR021 | TG-BGR021A-1 | DT-1 | FILMISTAN:ID | 1 | 990 | 19505640 | 767 | 2019-06-29 16:00 | 254 | 1035 | 254 | 1039 | 260 | 1051 | 14 | 693 | 25 |  |  | 25 | 69% | 54% | 78% | 70% | 7.1012 | Loss 5-10% | 870(193) | 948(313.5) | 981(332.5) | 885(222) | 810(163) | 756(48)
105 | 1130 | PHG | B G ROAD | BGR022 | TG-BGR022A-4 | DT-4 | B. G. ROAD COMP CTR:ID | 4 | 630 | 19505002 | 511 | 2019-06-11 03:30 | 181 | 749 | 172 | 707 | 159 | 656 | 80 | 621 | 97 |  |  | 97 | 81% | 72% | 73% | 77% | 26.9675 | Loss 20-30% |  | 507(69) | 564(207.5) | 532(114) | 494(57)
106 | 1130 | PHG | B G ROAD | BGR027 | TG-BGR027A-1 | DT-1 | JHABBAR MAL P/M:PKG | 1 | 990 | 19504832 | 900 | 2019-06-25 15:30 | 309 | 1305 | 285 | 1202 | 306 | 1289 | 96 | 573 | 142 | 3 |  | 145 | 5% | 19% | 91% | 8% | 4.698 | Loss 0-5% |  | 858(81) | 933(173) | 947(154.5) | 905(148.5) | 762(55.5)
107 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN007 | TG-CHN007A-3 | DT-3 | CHUNA MANDI:ID | 5 | 990 | 19500085 | 912 | 2019-06-11 | 302 | 1302 | 303 | 1303 | 308 | 1321 | 19 | 498.5 | 219 | 2.5 |  | 221.5 | 92% | 71% | 84% | 90% | 9.8821 | Loss 5-10% |  | 924(128) | 990(297.5) | 974(82) | 822(58.5)
108 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN008 | TG-CHN008A-1 | DT-1 | GALI NALWA:K | 1 | 990 | 19500138 | 784 | 2019-06-16 | 303 | 1257 | 255 | 1053 | 226 | 925 | 290 | 678.5 | 36 |  |  | 36 | 79% | 58% | 68% | 78% | 7.8738 | Loss 5-10% |  | 818(36) | 838(113.5) | 825(52)
109 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN009 | TG-CHN009A-1 | DT-1 | KRISHNA MKT. (K):K | 1 | 990 | 19506843 | 1032 | 2019-06-29 22:00 | 353 | 1532 | 337 | 1451 | 343 | 1472 | 73 | 335 | 325.5 | 51 | 8.5 | 385 | 101% | 76% | 102% | 104% | 3.9596 | Loss 0-5% |  |  | 797(62)
110 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN015 | TG-CHN015A-1 | DT-1 | LADOO GHATI:PL | 1 | 630 | 19500137 | 663 | 2019-06-11 23:30 | 228 | 1005 | 230 | 1007 | 206 | 896 | 110 | 475.5 | 184 | 54 | 5 | 243 | 105% | 80% | 74% | 105% | 6.5367 | Loss 5-10% |  | 587(93) | 664(213) | 633(172.5) | 547(109.5)
111 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN016 | TG-CHN016A-2 | DT-2 | 6: TOOTI PL/M:PL | 2 | 990 | 19504706 | 818 | 2019-06-30 00:30 | 258 | 1164 | 311 | 1404 | 249 | 1113 | 270 | 668 | 51.5 |  |  | 51.5 | 83% | 70% | 79% | 79% | 9.4765 | Loss 5-10% |  | 849(85) | 897(184.5) | 807(71.5)
112 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN020 | TG-CHN020A-1 | DT-1 | BASANT ROAD:K | 2 | 990 | 19504708 | 872 | 2019-06-05 23:30 | 306 | 1253 | 273 | 1116 | 294 | 1204 | 120 | 614 | 104 |  |  | 104 | 87% | 57% | 65% | 88% | 4.6607 | Loss 0-5% |  |  | 878(92) | 791(35)
113 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN022 | TG-CHN022A-1 | DT-1 | GALI MANTOLA:PL | 3 | 630 | 19500029 | 542 | 2019-06-06 01:00 | 219 | 893 | 194 | 791 | 129 | 523 | 331 | 609 | 109 |  |  | 109 | 86% | 72% | 65% | 81% | 8.2009 | Loss 5-10% |  |  | 511(67) | 538(32)
114 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN023 | TG-CHN023A-3 | DT-3 | DARIBA PAN KIOSK:K | 3 | 630 | 19506193 | 568 | 2019-06-11 01:00 | 205 | 846 | 201 | 821 | 162 | 658 | 176 | 646.5 | 71.5 | 1 |  | 72.5 | 90% | 71% | 64% | 89% | 3.1092 | Loss 0-5% | 545(61.5) | 733(250.5) | 787(336) | 560(151.5) | 515(68)
115 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN025 | TG-CHN025A-3 | DT-3 | PHG DISP.:ID | 4 | 990 | 19504675 | 1066 | 2019-06-10 22:30 | 344 | 1548 | 369 | 1675 | 353 | 1592 | 111 | 366 | 301 | 44 | 8.5 | 353.5 | 105% | 81% | 94% | 108% | 15.5206 | Loss 10-20% |  |  | 890(99) | 911(166) | 790(27)
116 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN025 | TG-CHN025A-4 | DT-4 | PHG DISP.:ID | 4 | 630 | 19506038 | 920 | 2019-06-11 23:30 | 293 | 1287 | 265 | 1163 | 363 | 1655 | 443 | 549 | 148.5 | 9.5 | 13 | 171 | 144% | 114% | 103% | 146% | 15.5206 | Loss 10-20% |  | 534(31.5) | 621(111.5) | 678(85)
117 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN026 | TG-CHN026A-1 | DT-1 | GALI SCHOOL WALI:PL | 2 | 990 | 19504851 | 910 | 2019-06-29 23:00 | 373 | 1578 | 278 | 1164 | 260 | 1087 | 458 | 629 | 85.5 | 2 |  | 87.5 | 91% | 71% | 84% | 92% | 5.4223 | Loss 5-10% |  |  | 812(76)
118 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN026 | TG-CHN026A-2 | DT-2 | GALI SCHOOL WALI:PL | 2 | 990 | 19500026 | 978 | 2019-06-02 23:30 | 300 | 1317 | 297 | 1304 | 382 | 1719 | 409 | 577.5 | 121 | 11 |  | 132 | 95% | 74% | 84% | 99% | 5.4223 | Loss 5-10% |  | 865(63.5) | 914(225.5) | 826(109) | 778(39)
119 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM001 | TG-RAM001A-1 | DT-1 | HANUMAN MANDIR:PL | 2 | 630 | 19502877 | 593 | 2019-06-10 23:30 | 190 | 845 | 199 | 889 | 204 | 905 | 54 | 514.5 | 194 | 9 |  | 203 | 93% | 80% | 88% | 94% | 4.8984 | Loss 0-5% |  | 602(143.5) | 614(323.5) | 583(177.5) | 506(39.5)
120 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM001 | TG-RAM001A-2 | DT-2 | HANUMAN MANDIR:PL | 2 | 990 | 19506112 | 839 | 2019-06-30 00:30 | 247 | 1055 | 329 | 1405 | 264 | 1119 | 323 | 668.5 | 48.5 |  |  | 48.5 | 85% | 70% | 70% | 83% | 4.8984 | Loss 0-5% | 965(209.5) | 1121(355) | 857(63)
121 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM003 | TG-RAM003A-1 | DT-1 | KILA KADAM SHARIF:PG | 1 | 990 | 19500294 | 811 | 2019-06-28 23:30 | 313 | 1342 | 281 | 1258 | 218 | 962 | 345 | 654 | 65.5 |  |  | 65.5 | 81% | 62% | 74% | 82% | 7.2088 | Loss 5-10% |  | 817(44) | 869(129.5) | 846(75) | 767(28.5)
122 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM010 | TG-RAM010A-3 | DT-3 | MCD PARK:PG | 3 | 630 | 19504836 | 582 | 2019-06-30 06:30 | 189 | 775 | 181 | 745 | 211 | 870 | 113 | 479 | 238 | 2 |  | 240 | 91% | 92% | 91% | 90% | 10.7832 | Loss 10-20% | [5 empty] | 527(27.5)
123 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM011 | TG-RAM011A-1 | DT-1 | YOG MAYA:PG | 1 | 990 | 19505128 | 864 | 2019-06-27 01:00 | 348 | 1504 | 249 | 1080 | 267 | 1158 | 391 | 191 | 84.5 |  |  | 84.5 | 87% | 78% | 79% | 84% | 14.8706 | Loss 10-20% |  | 806(113) | 851(275.5) | 879(304) | 842(111)
124 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM025 | TG-RAM025A-2 | DT-2 | CHARA MANDI:K | 2 | 630 | 19505958 | 555 | 2019-06-27 23:30 | 206 | 865 | 174 | 737 | 174 | 731 | 132 | 530 | 190 |  |  | 190 | 86% | 72% | 69% | 88% | 6.2134 | Loss 5-10% |  | 524(71) | 1004(151) | 529(117) | 502(89.5) | 484(26.5)
125 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM026 | TG-RAM026A-1 | DT-1 | BAGICHI ALLUDDIN:K | 2 | 990 | 19504530 | 757 | 2019-06-06 04:30 | 222 | 925 | 277 | 1149 | 258 | 1070 | 197 | 687 | 31.5 |  |  | 31.5 | 77% | 74% | 73% | 76% | 6.8634 | Loss 5-10% |  |  | 791(61)
126 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM026 | TG-RAM026A-2 | DT-2 | BAGICHI ALLUDDIN:K | 2 | 990 | 19504529 | 805 | 2019-06-29 23:00 | 317 | 1310 | 249 | 1023 | 238 | 984 | 308 | 556.5 | 67.5 |  |  | 67.5 | 81% | 64% | 78% | 81% | 6.8634 | Loss 5-10% |  |  | 782(45.5) | 791(34)
127 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM027 | TG-RAM027A-2 | DT-2 | ARP QUARTERS.:K | 2 | 990 | 19504649 | 851 | 2019-06-11 23:30 | 297 | 1276 | 229 | 985 | 325 | 1400 | 370 | 614 | 81.5 |  |  | 81.5 | 83% | 51% | 60% | 86% | 14.1865 | Loss 10-20%
128 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM029 | TG-RAM029A-1 | DT-1 | JHANDEWALAN P/M:PL | 1 | 630 | 19503789 | 524 | 2019-06-03 16:00 | 164 | 698 | 164 | 705 | 196 | 837 | 135 | 673.5 | 46 |  |  | 46 | 45% | 32% | 83% | 47% | 4.3876 | Loss 0-5% |  |  | 499(36.5) | 527(40)
129 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM030 | TG-RAM030A-1 | DT-1 | KABIR BASTI:PL | 1 | 630 | 19504709 | 503 | 2019-06-03 21:30 | 141 | 598 | 202 | 872 | 160 | 689 | 241 | 669.5 | 26 |  |  | 26 | 57% | 37% | 75% | 80% | 6.2921 | Loss 5-10%
130 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM031 | TG-RAM031A-1 | DT-1 | GALI NO. 5 MULTANI DHANDA:PKG | 1 | 990 | 19506192 | 965.3712 | 2019-06-03 02:30 | 429.1978 | 1810.5028 | 257.1789 | 1050.9537 | 278.9945 | 1149.4499 | 715.4045 | 387 | 303.5 | 28 |  | 331.5 | 98% | 78% | 97% | 97% | 11.9669 | Loss 10-20% |  | 944(50.5) | 954(237) | 1143(197.5) | 982(83)
131 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM035 | TG-RAM035A-1 | DT-1 | AARAKASHA ROAD:PKG | 2 | 990 | 19505996 | 1011.4528 | 2019-06-12 01:00 | 398.7016 | 1631.2153 | 306.5522 | 1233.5606 | 306.199 | 1241.3307 | 393.8271 | 481.5 | 178 | 52.5 | 5 | 235.5 | 102% | 92% | 83% | 99% | 4.0248 | Loss 0-5% | 914(32) | 1159(282.5) | 1145(259.5) | 1016(238) | 1060(226) | 860(110)
132 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM035 | TG-RAM035A-2 | DT-2 | AARAKASHA ROAD:PKG | 2 | 990 | 19505638 | 908 | 2019-06-28 23:30 | 105 | 450 | 434 | 1873 | 369 | 1584 | 1303 | 680.5 | 38 | 0.5 |  | 38.5 | 89% | 72% | 75% | 92% | 4.0248 | Loss 0-5% |  |  | 1076(131) | 1229(169)
133 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM044 | TG-RAM044A-1 | DT-1 | DB GUPTA ROAD BUS STOP | 1 | 630 | 19506758 | 757 | 2019-06-06 02:30 | 177 | 724 | 225 | 997 | 355 | 1680 | 852 | 565 | 107.5 | 29 | 18.5 | 155 | 120% | 94% | 91% | 109% | 7.8851 | Loss 5-10%
134 | 1130 | PHG | PP QUARTERS | PPQ001 | TG-PPQ001A-2 | DT-2 | RAILWAY BOOKING P/M:PL | 2 | 400 | 19504817 | 366 | 2019-06-15 16:00 | 114 | 426 | 133 | 489 | 120 | 451 | 55 | 572.5 | 143.5 | 1 |  | 144.5 | 7% | 12% | 92% | 15% | 9.722 | Loss 5-10% |  | 314(47) | 347(144.5) | 355(106.5) | 322(71.5)
135 | 1130 | PHG | PP QUARTERS | PPQ003 | TG-PPQ003A-1 | DT-1 | KHURSHEED MARKET:ID | 3 | 990 | 19500125 | 811 | 2019-06-29 15:00 | 285 | 1228 | 264 | 1129 | 262 | 1126 | 100 | 617 | 103 |  |  | 103 | 3% | 4% | 82% | 9% | 24.4113 | Loss 20-30% |  |  | 802(139.5) | 838(96.5) | 810(63)
136 | 1130 | PHG | PP QUARTERS | PPQ005 | TG-PPQ005A-1 | DT-1 | 12 TOOTI CHOWK:PKG | 2 | 990 | 19505684 | 975 | 2019-06-29 15:00 | 325 | 1417 | 310 | 1345 | 341 | 1478 | 116 | 565 | 104 | 46.5 |  | 150.5 | 4% | 19% | 99% | 10% | 6.912 | Loss 5-10% |  | 905(98.5) | 1185(197) | 1274(115) |  | 990(130.5)
137 | 1130 | PHG | PP QUARTERS | PPQ006 | TG-PPQ006A-1 | DT-1 | WEST END CINEMA:ID | 2 | 630 | 19500135 | 512 | 2019-06-29 13:00 | 199 | 843 | 157 | 658 | 157 | 661 | 183 | 642.5 | 77.5 |  |  | 77.5 | 18% | 30% | 81% | 19% | 32.8844 | Loss >30% |  |  | 510(76) | 494(63.5) | 488(37.5)
138 | 1130 | PHG | PP QUARTERS | PPQ006 | TG-PPQ006A-2 | DT-2 | WEST END CINEMA:ID | 2 | 630 | 19506190 | 981 | 2019-06-14 16:30 | 359 | 1521 | 364 | 1549 | 258 | 1079 | 456 | 494 | 24 | 12 | 188.5 | 224.5 | 10% | 33% | 156% | 14% | 32.8844 | Loss >30% | 707(203) | 862(241) | 906(228.5) | 906(239.5)
139 | 1130 | PHG | PP QUARTERS | PPQ012 | TG-PPQ012A-4 | DT-4 | A K TANKI P/M:ID | 4 | 400 | 19504724 | 328 | 2019-06-14 17:30 | 111 | 488 | 106 | 470 | 111 | 490 | 19 | 669 | 49.5 |  |  | 49.5 | 76% | 78% | 82% | 1% | 12.954 | Loss 10-20% |  |  | 290(25) |  | 305(44) | 301(37)
140 | 1130 | PHG | PP QUARTERS | PPQ015 | TG-PPQ015A-1 | DT-1 | OLD QASAB PURA:K | 2 | 990 | 19503520 | 776 | 2019-06-12 02:00 | 283 | 1182 | 224 | 934 | 269 | 1124 | 225 | 678.5 | 39.5 |  |  | 39.5 | 78% | 72% | 68% | 68% | 17.3046 | Loss 10-20% |  |  | 751(55) | 772(27)
141 | 1130 | PHG | PP QUARTERS | PPQ023 | TG-PPQ023A-1 | DT-1 | NARIAN MARKET:K | 2 | 990 | 19504809 | 914 | 2019-06-25 16:00 | 277 | 1181 | 265 | 1110 | 371 | 1561 | 420 | 661.5 | 55.5 | 1 |  | 56.5 | 22% | 27% | 92% | 24% | 20.3662 | Loss 20-30%
142 | 1140 | SRD | CHHAPARWALAN | CPW032 | TG-CPW032A-1 | DT-1 | JOSHI ROAD KIOSK:K | 2 | 990 | 19506293 | 870 | 2019-06-03 | 287 | 1191 | 257 | 1079 | 326 | 1377 | 261 | 602 | 118 |  |  | 118 | 88% | 59% | 79% | 86% | 3.3209 | Loss 0-5%
143 | 1140 | SRD | CHHAPARWALAN | CPW035 | TG-CPW035A-2 | DT-2 | AJMAL KHAN KIOSK | 2 | 400 | 19505173 | 314 | 2019-06-03 14:30 | 155 | 685 | 80 | 354 | 78 | 342 | 337 | 693 | 27 |  |  | 27 | 28% | 35% | 78% | 35% | 6.1661 | Loss 5-10% |  | 323(37) | 333(97.5) | 380(48.5)
144 | 1140 | SRD | CHHAPARWALAN | CPW037 | TG-CPW037A-1 | DT-1 | 53 BLOCK RAMJAS ROAD:K | 1 | 990 | 19500315 | 923 | 2019-06-03 02:00 | 248 | 1003 | 268 | 1103 | 407 | 1664 | 617 | 626.5 | 88 | 1 |  | 89 | 93% | 80% | 67% | 82% | 4.1262 | Loss 0-5% |  |  | 804(54)
145 | 1140 | SRD | CHHAPARWALAN | CPW038 | TG-CPW038A-1 | DT-1 | 61 BLOCK RAMJAS ROAD PL/M:PL | 1 | 990 | 19504948 | 799 | 2019-06-03 00:30 | 290 | 1238 | 254 | 1086 | 256 | 1058 | 167 | 667 | 53 |  |  | 53 | 81% | 58% | 72% | 79% | 3.3351 | Loss 0-5% |  |  | 841(67.5)
146 | 1140 | SRD | CHHAPARWALAN | KKW001 | TG-KKW001A-1 | DT-1 | NANAK HOTEL K. BAGH:PL | 1 | 990 | 19503278 | 1029 | 2019-06-04 16:00 | 380 | 1675 | 319 | 1409 | 330 | 1452 | 248 | 528.5 | 121.5 | 40 | 5 | 166.5 | 23% | 51% | 104% | 29% | 2.5526 | Loss 0-5% |  | 911(139) | 941(162.5) | 917(110.5) | 889(77.5)
147 | 1140 | SRD | CHHAPARWALAN | KKW002 | TG-KKW002A-1 | DT-1 | MASJID WALA K. BAGH.:PL | 1 | 990 | 19506653 | 995 | 2019-06-15 16:00 | 328 | 1340 | 318 | 1305 | 349 | 1433 | 114 | 527.5 | 141.5 | 49.5 | 0.5 | 191.5 | 30% | 25% | 101% | 34% | 5.1071 | Loss 5-10% |  | 938(122) | 977(202) | 1037(83.5)
148 | 1140 | SRD | CHHAPARWALAN | KKW003 | TG-KKW003A-1 | DT-1 | ELAHI BUX:PL | 2 | 990 | 19503286 | 831 | 2019-06-29 15:30 | 271 | 1169 | 287 | 1235 | 273 | 1177 | 62 | 330.5 | 72 |  |  | 72 | 43% | 34% | 84% | 42% | 3.4866 | Loss 0-5%
149 | 1140 | SRD | CHHAPARWALAN | KKW004 | TG-KKW004A-1 | DT-1 | BIRLA FLATS K. BAGH:PL | 2 | 990 | 19504500 | 842 | 2019-06-29 16:30 | 238 | 1027 | 282 | 1225 | 323 | 1404 | 326 | 641 | 78.5 |  |  | 78.5 | 48% | 41% | 85% | 47% | 7.6676 | Loss 5-10% |  |  | 768(36)
150 | 1140 | SRD | CHHAPARWALAN | KKW004 | TG-KKW004A-2 | DT-2 | BIRLA FLATS K. BAGH:PL | 2 | 990 | 19500429 | 838 | 2019-06-15 15:30 | 247 | 1028 | 296 | 1234 | 294 | 1218 | 199 | 578.5 | 141 |  |  | 141 | 33% | 26% | 85% | 36% | 7.6676 | Loss 5-10% |  | 806(49.5) | 847(153.5) | 890(107) | 784(65)
151 | 1140 | SRD | CHHAPARWALAN | KKW010 | TG-KKW010A-1 | DT-1 | POLICE QTR. K. BAGH:PL | 3 | 990 | 19500312 | 743 | 2019-06-11 16:30 | 216 | 941 | 244 | 1065 | 283 | 1226 | 248 | 683.5 | 35.5 |  |  | 35.5 | 11% | 10% | 75% | 24% | 3.5235 | Loss 0-5% |  |  | 784(88.5) | 777(53) | 783(25.5)
152 | 1140 | SRD | CHHAPARWALAN | KKW013 | TG-KKW013A-2 | DT-2 | PO NO. 1 K. BAGH:PL | 2 | 990 | 19505447 | 817 | 2019-06-12 14:00 | 258 | 1091 | 300 | 1278 | 259 | 1089 | 188 | 630.5 | 88.5 |  |  | 88.5 | 15% | 15% | 83% | 19% | 7.6665 | Loss 5-10% | 802(27.5) | 1085(129) | 1034(148) | 874(71.5)
153 | 1140 | SRD | CHHAPARWALAN | KKW017 | TG-KKW017A-1 | DT-1 | PO NO. 5 K. BAGH:PG | 1 | 990 | 19503298 | 888 | 2019-06-29 13:00 | 310 | 1352 | 301 | 1308 | 276 | 1196 | 139 | 548 | 171.5 |  |  | 171.5 | 5% | 61% | 90% | 13% | 3.5948 | Loss 0-5% |  | 864(104) | 871(154.5) | 818(90) | 814(50)
154 | 1140 | SRD | CHHAPARWALAN | KKW018 | TG-KKW018A-1 | DT-1 | H S ROAD BASEMENT:ID | 6 | 990 | 19500620 | 949.1251 | 2019-06-04 16:30 | 316.2925 | 1364.2707 | 345.4483 | 1484.1396 | 287.3842 | 1222.5994 | 226.7626 | 515 | 178 | 25.5 |  | 203.5 | 6% | 8% | 96% | 38% | 6.961 | Loss 5-10% |  |  | 760(72) |  | 773(49)
155 | 1140 | SRD | CHHAPARWALAN | KKW018 | TG-KKW018A-2 | DT-2 | H S ROAD BASEMENT:ID | 6 | 990 | 19500417 | 808 | 2019-06-30 14:30 | 279 | 1105 | 260 | 1016 | 269 | 1063 | 77 | 583 | 136.5 |  |  | 136.5 | 5% | 6% | 82% | 37% | 6.961 | Loss 5-10% |  |  | 781(94.5) | 755(46.5)
156 | 1140 | SRD | CHHAPARWALAN | KKW018 | TG-KKW018A-3 | DT-3 | H S ROAD BASEMENT:ID | 6 | 990 | 19500418 | 988 | 2019-06-15 15:30 | 322 | 1341 | 294 | 1221 | 372 | 1543 | 282 | 512 | 148 | 59.5 |  | 207.5 | 9% | 7% | 100% | 29% | 6.961 | Loss 5-10% |  | 794(48) | 854(126.5) | 837(57.5)
157 | 1140 | SRD | CHHAPARWALAN | RJN030 | TG-RJN030A-2 | DT-2 | SP.MUKERJI MKT. FAIZ RD. P/M NO. 2:PL | 2 | 400 | 19505972 | 393 | 2019-06-02 02:00 | 76 | 311 | 112 | 458 | 206 | 881 | 513 | 631.5 | 82.5 | 3.5 |  | 86 | 98% | 59% | 90% | 96% | 5.1093 | Loss 5-10% |  | 398(201.5) | 436(404) | 490(260) |  | 357(41)
158 | 1140 | SRD | CHHAPARWALAN | RJN037 | TG-RJN037A-1 | DT-1 | 2E JHANDEWALAN PL/M(PARK):PL | 3 | 990 | 19500714 | 854.6998 | 2019-06-11 15:00 | 308.1731 | 1295.8252 | 263.9132 | 1106.508 | 282.6135 | 1182.6315 | 164.9979 | 684 | 36 |  |  | 36 | 21% | 37% | 86% | 27% | 5.453 | Loss 5-10%
159 | 1140 | SRD | CHHAPARWALAN | RJN041 | TG-RJN041A-1 | DT-1 | JHANDENWALAN NO. 1:ID | 2 | 990 | 19500386 | 812 | 2019-06-14 13:00 | 244 | 1049 | 250 | 1063 | 318 | 1367 | 311 | 679 | 40 |  |  | 40 | 21% | 28% | 82% | 32% | 3.9932 | Loss 0-5%
160 | 1140 | SRD | PUSA ROAD | KKW006 | TG-KKW006A-2 | DT-2 | SATBHRAWA (K) STN.:ID | 2 | 630 | 19505386 | 507 | 2019-06-11 16:00 | 171 | 717 | 175 | 725 | 162 | 680 | 41 | 693 | 27 |  |  | 27 | 55% | 57% | 80% | 55% | 7.6136 | Loss 5-10% |  | 574(28) | 779(86) | 506(32)
161 | 1140 | SRD | PUSA ROAD | KKW007 | TG-KKW007A-1 | DT-1 | SHASTRI PARK (INDOOR):ID | 3 | 990 | 19503317 | 825 | 2019-06-14 13:30 | 239 | 1019 | 300 | 1284 | 286 | 1216 | 239 | 614.5 | 105.5 |  |  | 105.5 | 19% | 30% | 83% | 33% | 4.4668 | Loss 0-5% |  | 803(53) | 883(128.5) | 861(92.5) | 780(45.5)
162 | 1140 | SRD | PUSA ROAD | KKW008 | TG-KKW008A-3 | DT-3 | JESSA RAM HOSPITAL PACKAGE S/STN | 3 | 630 | 19505210 | 731 | 2019-06-08 17:30 | 255 | 1060 | 235 | 987 | 241 | 1015 | 64 | 428.5 | 200.5 | 89.5 | 1.5 | 291.5 | 56% | 44% | 116% | 87% | 4.019 | Loss 0-5% |  |  | 521(120) | 549(102) | 523(63)
163 | 1140 | SRD | PUSA ROAD | KKW020 | TG-KKW020A-2 | DT-2 | 39, BEEDEN PURA (W):PL | 2 | 630 | 19505869 | 513 | 2019-06-29 15:30 | 158 | 678 | 183 | 782 | 172 | 734 | 90 | 622 | 96.5 |  |  | 96.5 | 34% | 29% | 81% | 44% | 4.0132 | Loss 0-5%
164 | 1140 | SRD | PUSA ROAD | KKW025 | TG-KKW025A-1 | DT-1 | 8 C WEA KAROL BAGH JASSA RAM | 2 | 990 | 19506095 | 1011 | 2019-06-11 14:00 | 346 | 1482 | 309 | 1320 | 356 | 1521 | 185 | 557.5 | 122 | 30.5 | 2 | 154.5 | 46% | 70% | 102% | 59% | 6.9893 | Loss 5-10% |  |  | 829(60) | 800(33.5)
165 | 1140 | SRD | PUSA ROAD | KKW025 | TG-KKW025A-2 | DT-2 | 8 C WEA KAROL BAGH JASSA RAM | 2 | 400 | 19506378 | 404 | 2019-06-24 16:00 | 131 | 553 | 145 | 618 | 128 | 536 | 75 | 601.5 | 89 | 27.5 | 1.5 | 118 | 61% | 63% | 101% | 66% | 6.9893 | Loss 5-10%
166 | 1140 | SRD | PUSA ROAD | KKW028 | TG-KKW028A-1 | DT-1 | H.S.RD. KHATTAWAL K. BAGH:PL | 2 | 990 | 19505272 | 959 | 2019-06-01 | 287 | 1205 | 390 | 1653 | 282 | 1188 | 457 | 383.5 | 311 | 25 |  | 336 | 97% | 73% | 95% | 91% | 7.0993 | Loss 5-10% |  | 894(134) | 1114(350.5) | 990(250) | 866(103.5)
167 | 1140 | SRD | PUSA ROAD | KKW028 | TG-KKW028A-2 | DT-2 | H.S.RD. KHATTAWAL K. BAGH:PL | 2 | 990 | 19505496 | 914 | 2019-06-29 16:00 | 296 | 1235 | 352 | 1473 | 265 | 1109 | 320 | 535 | 180 | 4.5 |  | 184.5 | 76% | 60% | 92% | 74% | 7.0993 | Loss 5-10% |  |  |  | 1085(165) | 1044(138) | 753(38)
168 | 1140 | SRD | PUSA ROAD | KKW030 | TG-KKW030A-1 | DT-1 | NALA WALA H. S. RD.:PL | 1 | 990 | 19503266 | 784 | 2019-06-30 14:30 | 228 | 940 | 259 | 1079 | 296 | 1232 | 253 | 656.5 | 39.5 |  |  | 39.5 | 60% | 45% | 79% | 62% | 7.0102 | Loss 5-10% |  | 823(54.5) | 909(170) | 904(140) | 945(113.5) | 751(30.5)
169 | 1140 | SRD | PUSA ROAD | KKW031 | TG-KKW031A-2 | DT-2 | 13 BLK WEA K. BAGH:PACKAGE S/STN | 4 | 990 | 19504549 | 862 | 2019-06-26 14:00 | 287 | 1217 | 316 | 1331 | 259 | 1093 | 206 | 537.5 | 182.5 |  |  | 182.5 | 11% | 12% | 87% | 29% | 4.8654 | Loss 0-5% |  | 804(73) | 865(176) | 860(108) | 789(40)
170 | 1140 | SRD | PUSA ROAD | KKW032 | TG-KKW032A-2 | DT-2 | 5WEA K BAGH KIOSK:PACKAGE S/STN | 3 | 990 | 19504614 | 893 | 2019-06-14 13:00 | 279 | 1135 | 314 | 1293 | 300 | 1228 | 137 | 595 | 124 | 0.5 |  | 124.5 | 35% | 28% | 90% | 55% | 5.8564 | Loss 5-10%
171 | 1140 | SRD | PUSA ROAD | KKW037 | TG-KKW037A-1 | DT-1 | 26 BEEDEN PURA P.L RD.:PL | 1 | 990 | 19504238 | 967 | 2019-06-12 16:00 | 356 | 1465 | 272 | 1155 | 339 | 1443 | 300 | 516 | 197 | 7 |  | 204 | 80% | 57% | 98% | 79% | 4.2336 | Loss 0-5% |  | 873(92) | 1052(265.5) | 1134(210) | 914(163.5) | 761(37.5)
172 | 1140 | SRD | PUSA ROAD | KKW039 | TG-KKW039A-1 | DT-1 | 40 REGER PURA P/M:PL | 1 | 990 | 19506093 | 950 | 2019-06-06 02:30 | 295 | 1301 | 231 | 968 | 423 | 1966 | 880 | 478 | 232.5 | 7.5 |  | 240 | 96% | 68% | 86% | 93% | 4.7152 | Loss 0-5% |  | 1143(88.5) | 937(214.5) | 1113(166) | 980(76)
173 | 1140 | SRD | PUSA ROAD | KKW046 | TG-KKW046A-1 | DT-1 | PUSA RD. CAMP CENTRE:ID | 4 | 990 | 19503332 | 875 | 2019-06-30 00:30 | 267 | 1101 | 289 | 1190 | 319 | 1330 | 200 | 600 | 96 |  |  | 96 | 88% | 66% | 68% | 86% | 11.22 | Loss 10-20% |  | 942(225.5) | 953(325) | 1025(293.5) | 873(133) | 818(62.5)
174 | 1140 | SRD | PUSA ROAD | KKW046 | TG-KKW046A-2 | DT-2 | PUSA RD. CAMP CENTRE:ID | 4 | 990 | 19503315 | 957 | 2019-06-11 23:30 | 279 | 1198 | 338 | 1472 | 340 | 1457 | 267 | 450 | 236.5 | 29 |  | 265.5 | 96% | 75% | 80% | 97% | 11.22 | Loss 10-20% |  | 963(154.5) | 1020(335) | 975(151.5)
175 | 1140 | SRD | PUSA ROAD | KKW046 | TG-KKW046A-4 | DT-4 | PUSA RD. CAMP CENTRE:ID | 4 | 990 | 19505842 | 1023 | 2019-06-30 15:00 | 353 | 1495 | 327 | 1380 | 343 | 1445 | 100 | 457.5 | 231.5 | 29.5 | 1.5 | 262.5 | 79% | 62% | 103% | 80% | 11.22 | Loss 10-20%
176 | 1140 | SRD | PUSA ROAD | KKW049 | TG-KKW049A-1 | DT-1 | R. K. DASS-1 K. BAGH:K | 2 | 990 | 19504998 | 1175 | 2019-06-30 00:30 | 393 | 1574 | 393 | 1574 | 389 | 1535 | 39 | 271.5 | 293.5 | 90 | 65 | 448.5 | 119% | 96% | 99% | 118% | 5.3418 | Loss 5-10% |  | 945(166) | 1003(330) | 1032(272) | 899(120.5) | 821(25.5)
177 | 1140 | SRD | PUSA ROAD | KKW049 | TG-KKW049A-2 | DT-2 | R. K. DASS-1 K. BAGH:K | 2 | 990 | 19503292 | 810 | 2019-06-30 15:00 | 271 | 1061 | 293 | 1158 | 246 | 970 | 163 | 622.5 | 72.5 |  |  | 72.5 | 72% | 56% | 82% | 71% | 5.3418 | Loss 5-10% |  | 809(30.5) | 860(120) | 858(77.5)
178 | 1140 | SRD | PUSA ROAD | KKW050 | TG-KKW050A-1 | DT-1 | R.K.DASS-1/2 K. BAGH:K | 2 | 990 | 19503319 | 780 | 2019-06-30 00:30 | 296 | 1208 | 240 | 980 | 244 | 986 | 225 | 695 | 25 |  |  | 25 | 79% | 53% | 70% | 76% | 3.7533 | Loss 0-5%
179 | 1140 | SRD | PUSA ROAD | KKW059 | TG-KKW059A-1 | DT-1 | BAPU BHAWAN S/ST.:PL | 1 | 990 | 19504541 | 852 | 2019-06-30 00:30 | 306 | 1337 | 279 | 1206 | 267 | 1123 | 187 | 631.5 | 88.5 |  |  | 88.5 | 86% | 61% | 77% | 86% | 3.4863 | Loss 0-5% |  | 844(50.5) | 848(116) | 887(52.5)
180 | 1140 | SRD | PUSA ROAD | KKW067 | TG-KKW067A-1 | DT-1 | 5 BLOCK WEA KAROL BAGH KIOSK | 3 | 990 | 19503314 | 929 | 2019-06-11 15:00 | 287 | 1250 | 289 | 1255 | 353 | 1534 | 281 | 547.5 | 141.5 | 7 |  | 148.5 | 8% | 7% | 94% | 74% | 11.9368 | Loss 10-20% | 852(38) |  | 820(125.5) | 827(96) | 781(33)
181 | 1140 | SRD | PUSA ROAD | KKW067 | TG-KKW067A-2 | DT-2 | 5 BLOCK WEA KAROL BAGH KIOSK | 3 | 990 | 19505495 | 1094 | 2019-06-12 19:00 | 527 | 2312 | 304 | 1252 | 264 | 1050 | 1173 | 517.5 | 175.5 | 26.5 | 0.5 | 202.5 | 57% | 51% | 111% | 62% | 11.9368 | Loss 10-20% | 834(44) | 927(162.5) | 989(223) | 978(168) | 1008(165) | 780(71.5)
182 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | EPN003 | TG-EPN003A-1 | DT-1 | 21 BLK. O. R. NAGAR:K | 3 | 990 | 19503328 | 923 | 2019-06-30 01:00 | 295 | 1240 | 318 | 1335 | 310 | 1295 | 83 | 610 | 105.5 | 4.5 |  | 110 | 93% | 70% | 75% | 91% | 6.3205 | Loss 5-10% |  | 833(30.5) | 920(94.5) | 890(46.5)
183 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | EPN003 | TG-EPN003A-3 | DT-3 | 21 BLK. O. R. NAGAR:K | 3 | 990 | 19504344 | 913 | 2019-06-10 13:00 | 327 | 1493 | 306 | 1402 | 280 | 1270 | 194 | 626.5 | 92.5 | 1 |  | 93.5 | 71% | 67% | 92% | 74% | 6.3205 | Loss 5-10% |  | 960(61.5)
184 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN006 | TG-RJN006A-1 | DT-1 | TIKONA PARK BAZAR MARG:PL | 3 | 990 | 19503361 | 917 | 2019-06-30 23:30 | 365 | 1577 | 256 | 1089 | 296 | 1261 | 429 | 619.5 | 98.5 | 2 |  | 100.5 | 90% | 62% | 75% | 93% | 8.2463 | Loss 5-10% |  | 977(79) | 978(159.5) | 1013(50.5)
185 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN006 | TG-RJN006A-2 | DT-2 | TIKONA PARK BAZAR MARG:PL | 3 | 990 | 19505747 | 791 | 2019-06-01 16:00 | 241 | 1075 | 307 | 1377 | 243 | 1079 | 300 | 685 | 35 |  |  | 35 | 72% | 54% | 80% | 75% | 8.2463 | Loss 5-10%
186 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN006 | TG-RJN006A-3 | DT-3 | TIKONA PARK BAZAR MARG:PL | 3 | 630 | 19505136 | 594 | 2019-06-06 03:00 | 106 | 435 | 288 | 1255 | 199 | 862 | 710 | 638.5 | 81 | 0.5 |  | 81.5 | 94% | 66% | 75% | 89% | 8.2463 | Loss 5-10%
187 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN007 | TG-RJN007A-2 | DT-2 | BAZAR MARG (K):K | 2 | 630 | 19505084 | 702 | 2019-06-30 00:30 | 253 | 1099 | 208 | 889 | 241 | 1032 | 186 | 471.5 | 173.5 | 38 | 13 | 224.5 | 111% | 75% | 83% | 111% | 4.1771 | Loss 0-5% |  |  | 590(36) | 581(48)
188 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN011 | TG-RJN011A-1 | DT-1 | SALWAN SCHOOL OLD:PL | 4 | 990 | 19506581 | 982 | 2019-06-01 12:30 | 321 | 1367 | 320 | 1357 | 341 | 1445 | 83 | 549 | 161 | 9.5 |  | 170.5 | 34% | 68% | 99% | 38% | 6.1005 | Loss 5-10% | 898(126) | 1014(210.5) | 1103(237.5) |  | 872(63) | 879(141.5)
189 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN012 | TG-RJN012A-1 | DT-1 | SALWAN SCHOOL NEW:K | 3 | 990 | 19503377 | 931 | 2019-06-30 | 273 | 1149 | 337 | 1426 | 322 | 1370 | 253 | 664.5 | 51 | 3 |  | 54 | 94% | 63% | 69% | 94% | 7.5304 | Loss 5-10%
190 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN013 | TG-RJN013A-2 | DT-2 | SETHI PETROL PUMP:ID | 3 | 990 | 19504685 | 1161 | 2019-06-30 01:00 | 355 | 1483 | 309 | 1276 | 497 | 2094 | 736 | 454.5 | 202 | 43 | 19 | 264 | 117% | 81% | 82% | 107% | 2.7739 | Loss 0-5% | 931(32.5) | 1240(312.5) | 1357(484) | 1017(154) | 821(48.5)
191 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN019 | TG-RJN019A-1 | DT-1 | SRD BUILDING OFFICE:ID | 2 | 990 | 19503282 | 872 | 2019-06-29 23:30 | 310 | 1318 | 247 | 1046 | 314 | 1340 | 284 | 637 | 83 |  |  | 83 | 87% | 64% | 76% | 88% | 5.408 | Loss 5-10%
192 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN023 | TG-RJN023A-1 | DT-1 | NPL MULTI STORIES:ID | 1 | 630 | 19503308 | 508 | 2019-06-11 22:30 | 193 | 836 | 141 | 604 | 173 | 738 | 201 | 675 | 45 |  |  | 45 | 76% | 49% | 61% | 81% | 2.9781 | Loss 0-5% |  | 552(25.5) | 567(90)
193 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN081 | TG-RJN081A-1 | DT-1 | HANDIWALA ORN : K | 3 | 990 | 19503379 | 1021 | 2019-06-03 02:00 | 350 | 1459 | 355 | 1475 | 316 | 1322 | 147 | 600.5 | 106.5 | 8 | 1 | 115.5 | 103% | 70% | 78% | 95% | 7.5914 | Loss 5-10% |  | 1217(206) | 1092(241) | 957(100)
194 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN081 | TG-RJN081A-2 | DT-2 | HANDIWALA ORN : K | 3 | 630 | 19504310 | 595 | 2019-06-02 00:30 | 187 | 801 | 172 | 735 | 236 | 1022 | 260 | 531.5 | 186.5 | 1.5 |  | 188 | 94% | 67% | 90% | 90% | 7.5914 | Loss 5-10% |  |  | 501(30)
195 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN081 | TG-RJN081A-3 | DT-3 | HANDIWALA ORN : K | 3 | 630 | 19505206 | 736 | 2019-06-06 03:00 | 301 | 1363 | 106 | 431 | 329 | 1537 | 1030 | 578.5 | 126 | 14 | 0.5 | 140.5 | 117% | 70% | 74% | 96% | 7.5914 | Loss 5-10% |  |  | 577(43) | 563(77.5)
196 | 1141 | PNR | KIKARWALAN | PNR002 | TG-PNR002A-3 | DT-3 | SABZIWALA P.S RD. K. BAGH:PL | 3 | 990 | 19505391 | 813 | 2019-06-02 16:00 | 265 | 1070 | 296 | 1205 | 252 | 1019 | 166 | 668.5 | 50.5 |  |  | 50.5 | 46% | 40% | 82% | 52% | 8.953 | Loss 5-10% |  |  | 1066(152) | 968(194.5) | 934(147.5) | 920(150)
197 | 1141 | PNR | KIKARWALAN | PNR003 | TG-PNR003A-1 | DT-1 | H.S. RD.P/M BAPA NGR:PL | 2 | 990 | 19506516 | 917 | 2019-06-30 | 280 | 1158 | 319 | 1317 | 318 | 1333 | 168 | 453.5 | 262 | 2.5 |  | 264.5 | 93% | 67% | 92% | 90% | 3.6771 | Loss 0-5% |  |  |  | 1019(268.5) | 957(207) | 816(43.5)
198 | 1141 | PNR | KIKARWALAN | PNR003 | TG-PNR003A-2 | DT-2 | H.S. RD.P/M BAPA NGR:PL | 2 | 990 | 19504414 | 1042 | 2019-06-30 | 329 | 1372 | 328 | 1367 | 385 | 1630 | 261 | 423.5 | 254 | 38.5 | 1.5 | 294 | 105% | 75% | 87% | 97% | 3.6771 | Loss 0-5% |  | 970(171) | 989(171.5) | 984(120) | 866(179.5) | 815(38.5)
199 | 1141 | PNR | KIKARWALAN | PNR005 | TG-PNR005A-1 | DT-1 | 17 B DEV NGR. K. BAGH:PL | 3 | 990 | 19504744 | 865 | 2019-06-29 23:00 | 266 | 1099 | 326 | 1347 | 273 | 1116 | 240 | 654 | 66 |  |  | 66 | 83% | 62% | 68% | 87% | 4.041 | Loss 0-5% |  | 806(37.5) | 885(89) | 862(84) | 774(33)
200 | 1141 | PNR | KIKARWALAN | PNR006 | TG-PNR006A-2 | DT-2 | 11 B DEV NGR. A.S RD.:PL | 3 | 990 | 19503773 | 885 | 2019-06-30 00:30 | 282 | 1143 | 343 | 1391 | 260 | 1041 | 312 | 627 | 93 |  |  | 93 | 89% | 55% | 60% | 81% | 10.9883 | Loss 10-20%
201 | 1141 | PNR | KIKARWALAN | PNR007 | TG-PNR007A-1 | DT-1 | 13-B DEV NAGAR K. BAGH:PL | 1 | 990 | 19504424 | 807 | 2019-06-29 23:30 | 248 | 1083 | 322 | 1426 | 237 | 1036 | 369 | 673.5 | 45.5 |  |  | 45.5 | 81% | 63% | 64% | 82% | 5.7668 | Loss 5-10% |  |  | 847(42.5)
202 | 1141 | PNR | KIKARWALAN | PNR008 | TG-PNR008A-1 | DT-1 | 14-B MCD QTR. P.L. RD.:PL | 2 | 990 | 19505956 | 1112 | 2019-06-03 02:00 | 382 | 1645 | 343 | 1483 | 386 | 1670 | 176 | 493.5 | 187 | 21 | 15.5 | 223.5 | 112% | 77% | 102% | 106% | 6.7397 | Loss 5-10% |  | 1134(235.5) | 1234(465) | 1141(308.5) | 1082(233.5) | 846(34)
203 | 1141 | PNR | KIKARWALAN | PNR008 | TG-PNR008A-2 | DT-2 | 14-B MCD QTR. P.L. RD.:PL | 2 | 990 | 19505037 | 833 | 2019-06-12 | 263 | 1087 | 259 | 1069 | 310 | 1289 | 212 | 633.5 | 85 |  |  | 85 | 84% | 57% | 79% | 84% | 6.7397 | Loss 5-10% |  | 554(108.5) | 594(274.5) | 591(145) | 577(61.5)
204 | 1141 | PNR | KIKARWALAN | PNR010 | TG-PNR010A-1 | DT-1 | MILITARY ROAD (K):PL | 2 | 990 | 19504865 | 862 | 2019-06-01 21:30 | 250 | 981 | 311 | 1220 | 301 | 1186 | 224 | 617.5 | 102 |  |  | 102 | 84% | 58% | 64% | 87% | 11.2187 | Loss 10-20% |  | 881(46.5) | 948(132) | 928(97) | 876(41)
205 | 1141 | PNR | KIKARWALAN | PNR010 | TG-PNR010A-2 | DT-2 | MILITARY ROAD (K):PL | 2 | 990 | 19505039 | 876 | 2019-06-02 00:30 | 335 | 1372 | 289 | 1189 | 253 | 1034 | 293 | 663.5 | 56 |  |  | 56 | 89% | 57% | 64% | 86% | 11.2187 | Loss 10-20% |  |  | 837(64.5) | 819(42)
206 | 1141 | PNR | KIKARWALAN | PNR012 | TG-PNR012A-1 | DT-1 | TANK RD. KHATTA S/ST.:PL | 2 | 990 | 19500318 | 1201 | 2019-06-02 15:00 | 429 | 1867 | 441 | 1947 | 330 | 1440 | 472 | 509.5 | 101 | 39 | 66 | 206 | 42% | 35% | 121% | 42% | 2.9744 | Loss 0-5% | 841(111) | 1065(224.5) | 1108(133) |  |  | 918(170.5)
207 | 1141 | PNR | KIKARWALAN | PNR012 | TG-PNR012A-2 | DT-2 | TANK RD. KHATTA S/ST.:PL | 2 | 990 | 19505751 | 1035.481 | 2019-06-21 15:00 | 342.5325 | 1376.6829 | 334.1621 | 1356.1225 | 358.7864 | 1459.7867 | 95.0664 | 553.5 | 102 | 51.5 | 6.5 | 160 | 22% | 21% | 105% | 26% | 2.9744 | Loss 0-5% | [5 empty] | 911(150)
208 | 1141 | PNR | KIKARWALAN | PNR013 | TG-PNR013A-1 | DT-1 | TANK RD .BOOSTER PUMP:PL | 3 | 990 | 19500291 | 1016 | 2019-06-02 16:00 | 327 | 1353 | 341 | 1407 | 347 | 1426 | 65 | 456.5 | 200.5 | 59.5 | 2 | 262 | 65% | 61% | 103% | 77% | 4.9234 | Loss 0-5% | 995(246) | 1165(315.5) | 1190(312) | 1066(280.5) | 1002(154) | 1022(243)
209 | 1141 | PNR | KIKARWALAN | PNR013 | TG-PNR013A-2 | DT-2 | TANK RD .BOOSTER PUMP:PL | 3 | 990 | 19505172 | 948 | 2019-06-02 15:30 | 315 | 1381 | 280 | 1223 | 353 | 1562 | 294 | 546.5 | 168 | 4 |  | 172 | 45% | 44% | 96% | 50% | 4.9234 | Loss 0-5% | 787(55) | 1004(217) | 1013(241.5) | 996(224) | 974(196) | 862(142.5)
210 | 1141 | PNR | KIKARWALAN | PNR013 | TG-PNR013A-3 | DT-3 | TANK RD .BOOSTER PUMP:PL | 3 | 990 | 19505343 | 851 | 2019-06-12 16:00 | 278 | 1146 | 284 | 1174 | 289 | 1203 | 50 | 593 | 125.5 |  |  | 125.5 | 22% | 21% | 86% | 22% | 4.9234 | Loss 0-5% | 638(89) | 827(227) | 722(230) | 698(223) |  | 603(200.5)
211 | 1141 | PNR | KIKARWALAN | PNR015 | TG-PNR015A-1 | DT-1 | KRISHNA TIRATH DEV NAGAR | 2 | 990 | 19502800 | 990 | 2019-06-02 14:00 | 294 | 1243 | 338 | 1439 | 358 | 1521 | 247 | 522.5 | 125.5 | 70.5 |  | 196 | 17% | 15% | 100% | 22% | 3.8317 | Loss 0-5%
212 | 1141 | PNR | KIKARWALAN | PNR015 | TG-PNR015A-2 | DT-2 | KRISHNA TIRATH DEV NAGAR | 2 | 1600 | 19506094 | 1463.8372 | 2019-06-01 15:00 | 475.3528 | 2045.8479 | 504.0647 | 2166.8088 | 484.4198 | 2092.7971 | 105.6255 | 555.5 | 158.5 | 1.5 |  | 160 | 16% | 15% | 91% | 22% | 3.8317 | Loss 0-5% | 1372(238.5) | 1365(56.5) | 1297(118.5) |  | 992(155.5)
213 | 1141 | PNR | KIKARWALAN | PNR016 | TG-PNR016A-1 | DT-1 | REGER PURA ZONAL OFF INDOOR S/ST:ID | 2 | 630 | 19504459 | 548 | 2019-06-12 16:00 | 225 | 1021 | 143 | 651 | 179 | 799 | 323 | 561 | 158.5 |  |  | 158.5 | 83% | 63% | 87% | 82% | 12.3796 | Loss 10-20% |  |  | 641(112.5) | 699(269.5) | 620(219) | 545(83.5)
214 | 1141 | PNR | KIKARWALAN | PNR016 | TG-PNR016A-2 | DT-2 | REGER PURA ZONAL OFF INDOOR S/ST:ID | 2 | 990 | 19503212 | 875 | 2019-06-12 14:30 | 329 | 1491 | 264 | 1201 | 282 | 1286 | 258 | 609.5 | 110 |  |  | 110 | 77% | 53% | 88% | 77% | 12.3796 | Loss 10-20% |  | 992(184) | 1123(331.5) | 910(64)
215 | 1141 | PNR | KIKARWALAN | PNR125 | TG-PNR125A-1 | DT-1 | MILITARY ROAD S/ST. NO. 3:PM | 1 | 630 | 19506708 | 575 | 2019-06-02 01:30 | 194 | 805 | 204 | 844 | 177 | 730 | 100 | 392 | 326 | 2 |  | 328 | 91% | 84% | 89% | 87% | 12.3467 | Loss 10-20%
216 | 1141 | PNR | KIKARWALAN | PNR155 | TG-PNR155A-1 | DT-1 | VIJAY CHOWK | 1 | 990 | 19500300 | 931 | 2019-06-01 22:00 | 240 | 994 | 379 | 1600 | 313 | 1319 | 525 | 589.5 | 121 | 4 |  | 125 | 92% | 61% | 83% | 94% | 4.4812 | Loss 0-5% |  | 954(84.5) | 1024(237.5) | 975(167) | 996(87.5) | 824(32)
217 | 1141 | PNR | KIKARWALAN | PNR157 | TG-PNR157A-1 | DT-1 | 10-B, RAJENDRAPLACE | 1 | 990 | 19503741 | 791 | 2019-06-10 16:00 | 299 | 1298 | 246 | 1054 | 246 | 1059 | 241 | 205.5 | 27.5 |  |  | 27.5 | 49% | 51% | 80% | 50% | 5.2836 | Loss 5-10% |  |  | 845(111) | 801(43)
218 | 1141 | PNR | PATEL NAGAR | PNR018 | TG-PNR018A-2 | DT-2 | FARID PURI KIOSK:PL | 2 | 990 | 19503573 | 875 | 2019-06-01 06:30 | 289 | 1189 | 261 | 1066 | 325 | 1344 | 241 | 667 | 53 |  |  | 53 | 84% | 88% | 75% | 85% | 3.51 | Loss 0-5% |  |  | 851(69.5) | 856(47)
219 | 1141 | PNR | PATEL NAGAR | PNR019 | TG-PNR019A-1 | DT-1 | FARID PURI NO.1 | 1 | 400 | 19506651 | 401 | 2019-06-29 17:30 | 133 | 559 | 138 | 575 | 130 | 544 | 27 | 646 | 54 | 17.5 | 0.5 | 72 | 99% | 95% | 100% | 97% | 13.9962 | Loss 10-20% |  | 357(41) | 378(57) | 378(50.5)
220 | 1141 | PNR | PATEL NAGAR | PNR020 | TG-PNR020A-1 | DT-1 | FARID PURI P/M NO. 2:PL | 1 | 990 | 19503407 | 1158 | 2019-06-02 05:30 | 376 | 1697 | 436 | 1997 | 346 | 1574 | 377 | 641.5 | 71.5 | 3 | 0.5 | 75 | 117% | 88% | 94% | 78% | 3.8215 | Loss 0-5% | 906(36) | 985(76) | 1056(211) | 1061(131) | 1071(103.5) | 982(32.5)
221 | 1141 | PNR | PATEL NAGAR | PNR021 | TG-PNR021A-2 | DT-2 | RAJASTHANI COLONY P/M-1:PM | 2 | 400 | 19506527 | 441 | 2019-06-13 05:30 | 144 | 590 | 132 | 544 | 165 | 690 | 129 | 630 | 51 | 17.5 | 21.5 | 90 | 110% | 108% | 109% | 86% | 5.9973 | Loss 5-10% |  |  |  | 498(218) |  | 495(66.5)
222 | 1141 | PNR | PATEL NAGAR | PNR028 | TG-PNR028A-2 | DT-2 | 12 BLOCK E.P. NAGAR P/M:PL | 2 | 990 | 19505843 | 830 | 2019-06-04 15:00 | 259 | 1098 | 292 | 1242 | 279 | 1171 | 125 | 637.5 | 82.5 |  |  | 82.5 | 62% | 53% | 84% | 64% | 4.7962 | Loss 0-5% |  |  | 839(56.5) | 872(78)
223 | 1141 | PNR | PATEL NAGAR | PNR029 | TG-PNR029A-2 | DT-2 | 10 BLOCK E. P. NAGAR (K):PL | 3 | 990 | 19506571 | 1030 | 2019-06-29 12:00 | 379 | 1751 | 243 | 1072 | 408 | 1837 | 726 | 565.5 | 148.5 | 5.5 | 0.5 | 154.5 | 60% | 48% | 104% | 66% | 4.3815 | Loss 0-5% | 1000(77.5) | 997(203) | 999(43.5)
224 | 1141 | PNR | PATEL NAGAR | PNR032 | TG-PNR032A-1 | DT-1 | 22 BLOCK W.P. NAGAR:PL | 2 | 990 | 19506441 | 864 | 2019-06-26 00:30 | 314 | 1301 | 275 | 1130 | 275 | 1132 | 170 | 626 | 94 |  |  | 94 | 87% | 69% | 71% | 86% | 5.4024 | Loss 5-10% |  |  | 1021(118) | 928(38.5)
225 | 1141 | PNR | PATEL NAGAR | PNR032 | TG-PNR032A-2 | DT-2 | 22 BLOCK W.P. NAGAR:PL | 2 | 990 | 19504944 | 845 | 2019-06-26 | 254 | 1095 | 274 | 1169 | 317 | 1367 | 244 | 656.5 | 63 |  |  | 63 | 85% | 62% | 62% | 82% | 5.4024 | Loss 5-10% |  | 877(43.5) | 873(97.5) | 888(24.5)
226 | 1141 | PNR | PATEL NAGAR | PNR043 | TG-PNR043A-1 | DT-1 | BALJIT NGR. BARAT GHAR:PL | 2 | 990 | 19505121 | 1120 | 2019-06-02 01:30 | 334 | 1414 | 442 | 1920 | 345 | 1480 | 476 | 434.5 | 188.5 | 64 | 33 | 285.5 | 113% | 74% | 89% | 103% | 8.2205 | Loss 5-10% |  | 1013(155.5) | 1171(309) | 1109(277) | 970(240) | 888(52.5)
227 | 1141 | PNR | PATEL NAGAR | PNR043 | TG-PNR043A-2 | DT-2 | BALJIT NGR. BARAT GHAR:PL | 2 | 990 | 19502619 | 869 | 2019-06-16 01:30 | 290 | 1199 | 336 | 1401 | 242 | 996 | 350 | 611 | 109 |  |  | 109 | 88% | 54% | 74% | 82% | 8.2205 | Loss 5-10% |  | 819(42) | 945(127) | 916(115.5) | 805(57)
228 | 1141 | PNR | PATEL NAGAR | PNR044 | TG-PNR044A-1 | DT-1 | BALJIT NAGAR AGGARWAL SWEET P/M:PM | 1 | 400 | 19506244 | 434 | 2019-06-10 02:00 | 134 | 612 | 129 | 588 | 172 | 792 | 193 | 539.5 | 157 | 18 | 5.5 | 180.5 | 109% | 82% | 72% | 98% | 3.4553 | Loss 0-5% |  | 340(51) | 363(148.5) | 354(99) | 331(93.5)
229 | 1141 | PNR | PATEL NAGAR | PNR047 | TG-PNR047A-2 | DT-2 | SHADI PUR DTC DEPOT:PL | 2 | 630 | 19506556 | 791 | 2019-06-02 23:30 | 242 | 960 | 213 | 845 | 336 | 1359 | 468 | 534.5 | 127 | 44 | 14.5 | 185.5 | 121% | 71% | 66% | 126% | 3.4432 | Loss 0-5%
230 | 1141 | PNR | PATEL NAGAR | PNR048 | TG-PNR048A-1 | DT-1 | BALJIT NAGAR SCHOOLWALA TR.1:PM | 2 | 990 | 19506083 | 1425 | 2019-06-05 06:00 | 555 | 2381 | 420 | 1791 | 450 | 1789 | 591 | 499 | 145 | 39.5 | 32.5 | 217 | 133% | 144% | 85% | 103% | 6.1794 | Loss 5-10% | 1048(30) | 1158(82) | 1292(172.5) | 1169(128.5) | 1145(119) | 1077(31)
231 | 1141 | PNR | PATEL NAGAR | PNR048 | TG-PNR048A-2 | DT-2 | BALJIT NAGAR SCHOOLWALA TR.1:PM | 2 | 990 | 19506082 | 1288 | 2019-06-02 01:00 | 464 | 2073 | 420 | 1848 | 405 | 1795 | 256 | 439.5 | 154.5 | 53 | 69 | 276.5 | 130% | 109% | 90% | 124% | 6.1794 | Loss 5-10% | 878(47) | 1165(207.5) | 1239(381.5) | 1124(321) | 1048(286.5) | 921(91)
232 | 1141 | PNR | PATEL NAGAR | PNR049 | TG-PNR049A-1 | DT-1 | BALJIT NAGAR JANTA PARK:PL | 2 | 990 | 19502781 | 1054 | 2019-06-30 05:00 | 354 | 1459 | 339 | 1396 | 361 | 1488 | 82 | 481 | 173 | 54.5 | 9.5 | 237 | 107% | 100% | 74% | 98% | 7.8778 | Loss 5-10% | 1363(56.5) | 1427(190) | 1284(199) | 1322(173.5) | 1248(133) | 1189(34.5)
233 | 1141 | PNR | PATEL NAGAR | PNR049 | TG-PNR049A-2 | DT-2 | BALJIT NAGAR JANTA PARK:PL | 2 | 990 | 19505937 | 1032 | 2019-06-18 01:00 | 309 | 1318 | 431 | 1885 | 293 | 1254 | 602 | 684 | 32.5 |  | 0.5 | 33 | 104% | 79% | 57% | 74% | 7.8778 | Loss 5-10% |  |  | 1149(52.5) | 795(29)
234 | 1141 | PNR | PATEL NAGAR | PNR050 | TG-PNR050A-1 | DT-1 | BALJIT NAGAR P/M J. WALAN CHOWK:PL | 2 | 990 | 19502614 | 1133 | 2019-06-05 05:00 | 374 | 1552 | 382 | 1587 | 378 | 1561 | 31 | 690.5 | 0.5 | 7 | 22 | 29.5 | 114% | 48% | 54% | 70% | 10.3622 | Loss 10-20% |  |  | 1090(24.5)
235 | 1141 | PNR | PATEL NAGAR | PNR051 | TG-PNR051A-1 | DT-1 | DAV MULTAN:PL | 3 | 990 | 19502782 | 857 | 2019-06-03 17:00 | 274 | 1175 | 309 | 1323 | 274 | 1175 | 148 | 596.5 | 119.5 |  |  | 119.5 | 77% | 59% | 87% | 77% | 5.9523 | Loss 5-10% |  | 869(75) | 947(222.5) | 910(89)
236 | 1141 | PNR | PATEL NAGAR | PNR051 | TG-PNR051A-2 | DT-2 | DAV MULTAN:PL | 3 | 990 | 19502859 | 960 | 2019-06-01 12:00 | 310 | 1337 | 341 | 1480 | 308 | 1335 | 144 | 603 | 109 | 2.5 |  | 111.5 | 42% | 61% | 97% | 54% | 5.9523 | Loss 5-10% |  | 903(82) | 969(144.5) | 1048(165) | 797(60)
237 | 1141 | PNR | PATEL NAGAR | PNR051 | TG-PNR051A-3 | DT-3 | DAV MULTAN:PL | 3 | 630 | 19506440 | 620 | 2019-06-10 14:30 | 236 | 1020 | 207 | 891 | 177 | 766 | 220 | 473.5 | 228.5 | 18 |  | 246.5 | 87% | 59% | 98% | 88% | 5.9523 | Loss 5-10%
238 | 1141 | PNR | PATEL NAGAR | PNR052 | TG-PNR052A-1 | DT-1 | MUFFATLAL:PL | 1 | 990 | 19502785 | 819 | 2019-06-01 14:30 | 290 | 1311 | 278 | 1246 | 251 | 1121 | 167 | 647.5 | 72.5 |  |  | 72.5 | 77% | 55% | 83% | 74% | 3.5122 | Loss 0-5% |  | 803(46) | 861(169) | 806(78.5)
239 | 1141 | PNR | PATEL NAGAR | PNR054 | TG-PNR054A-1 | DT-1 | POLICE STN. W.P.NAGAR:PL | 2 | 990 | 19502603 | 1191 | 2019-06-02 01:00 | 373 | 1526 | 378 | 1548 | 440 | 1803 | 267 | 371.5 | 270.5 | 53 | 24 | 347.5 | 120% | 83% | 91% | 112% | 4.2127 | Loss 0-5% |  | 1168(344) | 1248(579) |  | 1018(353) | 908(95.5)
240 | 1141 | PNR | PATEL NAGAR | PNR056 | TG-PNR056A-1 | DT-1 | F&G BLOCK W.P. NAGAR:PL | 2 | 990 | 19506652 | 948 | 2019-06-03 02:00 | 312 | 1311 | 305 | 1272 | 331 | 1403 | 117 | 546 | 159.5 | 14.5 |  | 174 | 96% | 74% | 82% | 95% | 10.2106 | Loss 10-20% |  | 922(60.5) | 966(168) | 901(86.5)
241 | 1141 | PNR | PATEL NAGAR | PNR057 | TG-PNR057A-2 | DT-2 | S- BLOCK W.P. NAGAR:PL | 3 | 990 | 19506245 | 1019 | 2019-06-04 15:30 | 423 | 1853 | 375 | 1717 | 221 | 966 | 828 | 602 | 115 | 2 | 0.5 | 117.5 | 91% | 60% | 103% | 93% | 10.55 | Loss 10-20% |  |  | 846(79) | 853(41.5)
242 | 1141 | PNR | PATEL NAGAR | PNR057 | TG-PNR057A-3 | DT-3 | S- BLOCK W.P. NAGAR:PL | 3 | 630 | 19505748 | 512 | 2019-06-29 23:00 | 225 | 1041 | 148 | 673 | 139 | 629 | 391 | 679.5 | 40 |  |  | 40 | 80% | 68% | 70% | 81% | 10.55 | Loss 10-20% |  | 665(28.5) | 605(71) | 596(58) | 551(31.5)
243 | 1141 | PNR | PATEL NAGAR | PNR059 | TG-PNR059A-1 | DT-1 | BALJIT NGR. NO. 1 (DOGWALA):PL | 2 | 990 | 19506705 | 960 | 2019-06-28 23:00 | 283 | 1221 | 316 | 1372 | 360 | 1571 | 304 | 603 | 109.5 | 5 |  | 114.5 | 94% | 67% | 62% | 97% | 3.8632 | Loss 0-5% |  |  | 1086(59)
244 | 1141 | PNR | PATEL NAGAR | PNR059 | TG-PNR059A-2 | DT-2 | BALJIT NGR. NO. 1 (DOGWALA):PL | 2 | 630 | 19506478 | 724 | 2019-06-11 23:30 | 235 | 971 | 230 | 961 | 258 | 1081 | 115 | 606.5 | 90.5 | 17 | 3.5 | 111 | 114% | 62% | 64% | 115% | 3.8632 | Loss 0-5% |  |  | 715(98) | 582(80) | 586(62.5)
245 | 1141 | PNR | PATEL NAGAR | PNR062 | TG-PNR062A-1 | DT-1 | NALA (K) W.P. NAGAR:PL | 1 | 990 | 19502808 | 1113 | 2019-06-11 00:30 | 336 | 1451 | 413 | 1823 | 364 | 1576 | 328 | 448 | 160 | 75 | 34.5 | 269.5 | 112% | 98% | 80% | 112% | 4.3615 | Loss 0-5% |  | 918(85.5) | 1088(202.5) | 963(113) | 860(68)
246 | 1141 | PNR | PATEL NAGAR | PNR063 | TG-PNR063A-1 | DT-1 | Z-BLOCK, W.P. NAGAR:PL | 1 | 990 | 19502755 | 875 | 2019-06-30 20:00 | 314 | 1311 | 281 | 1171 | 280 | 1172 | 139 | 566 | 154 |  |  | 154 | 69% | 50% | 88% | 88% | 4.4057 | Loss 0-5% |  | 800(32.5) | 832(115) | 870(35)
247 | 1141 | PNR | PATEL NAGAR | PNR064 | TG-PNR064A-1 | DT-1 | D-BLOCK, W.P. NAGAR P/M:PM | 1 | 630 | 19500297 | 609 | 2019-06-02 03:00 | 198 | 838 | 193 | 810 | 218 | 923 | 102 | 580 | 133.5 | 6.5 |  | 140 | 97% | 76% | 71% | 90% | 8.1197 | Loss 5-10% |  | 580(54) | 599(156.5) | 577(80.5) | 517(44.5)
248 | 1141 | PNR | PATEL NAGAR | PNR066 | TG-PNR066A-2 | DT-2 | WEST PATEL NAGAR INDOOR:PL | 2 | 630 | 19501641 | 743 | 2019-06-12 00:30 | 243 | 1060 | 253 | 1135 | 247 | 1098 | 65 | 240 | 327.5 | 90.5 | 62 | 480 | 118% | 92% | 100% | 116% | 5.7533 | Loss 5-10% |  |  |  |  | 627(209.5) | 538(34)
249 | 1141 | PNR | PATEL NAGAR | PNR067 | TG-PNR067A-2 | DT-2 | 30 BLOCK WEST PATEL NAGAR:PL | 2 | 630 | 19504734 | 536 | 2019-06-02 23:30 | 205 | 899 | 160 | 704 | 171 | 753 | 176 | 656 | 63 |  |  | 63 | 83% | 56% | 56% | 85% | 3.4221 | Loss 0-5% |  | 522(26.5) | 677(76)
250 | 1141 | PNR | PATEL NAGAR | PNR094 | TG-PNR094A-2 | DT-2 | 29 BLOCK W.P. NAGAR:PL | 2 | 990 | 19504444 | 949 | 2019-06-03 03:00 | 297 | 1243 | 299 | 1253 | 354 | 1492 | 244 | 615 | 99 | 3 |  | 102 | 96% | 70% | 61% | 87% | 3.51 | Loss 0-5% |  | 830(27.5) | 838(73) | 849(35)
251 | 1141 | PNR | PATEL NAGAR | PNR131 | TG-PNR131A-1 | DT-1 | HOLI CHOWK PATEL NAGAR | 1 | 990 | 19502792 | 819 | 2019-06-29 23:30 | 309 | 1331 | 306 | 1319 | 204 | 869 | 457 | 615.5 | 104.5 |  |  | 104.5 | 82% | 66% | 72% | 83% | 5.0059 | Loss 5-10% |  |  | 765(61) | 772(65.5) | 754(91.5)
252 | 1141 | PNR | PATEL NAGAR | PNR134 | TG-PNR134A-1 | DT-1 | NEPALI MANDIR BALJIT NAGAR | 1 | 630 | 19502798 | 494 | 2019-06-29 23:00 | 169 | 716 | 150 | 635 | 175 | 738 | 94 | 668.5 | 51.5 |  |  | 51.5 | 77% | 66% | 72% | 78% | 4.1143 | Loss 0-5% |  |  |  |  | 477(35.5)
253 | 1141 | PNR | PATEL NAGAR | PNR152 | TG-PNR152A-1 | DT-1 | 25 BLK WEST PATEL NAGAR | 2 | 990 | 19502853 | 1381 | 2019-06-11 00:30 | 416 | 1810 | 491 | 2170 | 474 | 2071 | 322 | 348 | 187 | 66 | 119 | 372 | 139% | 97% | 90% | 124% | 10.7339 | Loss 10-20% |  |  | 1271(245) | 1204(253) | 1036(132) | 890(42.5)
254 | 1141 | PNR | PATEL NAGAR | PNR152 | TG-PNR152A-2 | DT-2 | 25 BLK WEST PATEL NAGAR | 2 | 630 | 19505730 | 525 | 2019-06-11 00:30 | 168 | 738 | 176 | 765 | 182 | 793 | 48 | 692 | 27.5 |  |  | 27.5 | 83% | 66% | 64% | 76% | 10.7339 | Loss 10-20% |  |  | 658(37)
255 | 1141 | PNR | PATEL NAGAR | PNR153 | TG-PNR153A-1 | DT-1 | ROAD NO-20 BALJEET NAGAR | 2 | 990 | 19505847 | 1271 | 2019-06-13 05:30 | 401 | 1640 | 449 | 1856 | 421 | 1749 | 187 | 435 | 145.5 | 67.5 | 68 | 281 | 128% | 125% | 91% | 109% | 11.7715 | Loss 10-20% | 1105(32) | 1198(142.5) | 1391(273.5) | 1330(218) | 1239(210.5) | 1184(61.5)
256 | 1141 | PNR | PATEL NAGAR | PNR153 | TG-PNR153A-2 | DT-2 | ROAD NO-20 BALJEET NAGAR | 2 | 990 | 19502810 | 994 | 2019-06-14 06:00 | 342 | 1439 | 321 | 1346 | 330 | 1374 | 83 | 559.5 | 137 | 19.5 | 0.5 | 157 | 98% | 100% | 66% | 88% | 11.7715 | Loss 10-20% | 1210(27.5) | 1003(76.5) | 1141(158) | 985(52)
257 | 1141 | PNR | SARAI ROHILLA | PNR096 | TG-PNR096A-1 | DT-1 | DHAL WALA GALI NO-6 | 2 | 990 | 19505033 | 791 | 2019-06-20 16:00 | 253 | 1047 | 278 | 1151 | 261 | 1073 | 94 | 681 | 37 |  |  | 37 | 17% | 37% | 80% | 22% | 4.619 | Loss 0-5%
258 | 1141 | PNR | SARAI ROHILLA | PNR099 | TG-PNR099A-1 | DT-1 | K. PAHAR G. NO. 8 S/ST-7:PL | 1 | 990 | 19502852 | 753 | 2019-06-09 11:00 | 251 | 1053 | 256 | 1071 | 246 | 1027 | 39 | 682 | 37 |  |  | 37 | 16% | 25% | 76% | 25% | 5.7727 | Loss 5-10% | 767(35) | 752(24) | 773(51.5) | 762(48) |  | 780(50.5)
259 | 1141 | PNR | SARAI ROHILLA | PNR100 | TG-PNR100A-1 | DT-1 | K. PAHR G. NO. 9:PL | 1 | 990 | 19506285 | 1015 | 2019-06-26 12:30 | 321 | 1389 | 334 | 1447 | 360 | 1550 | 142 | 501.5 | 204.5 | 10 | 0.5 | 215 | 29% | 33% | 102% | 38% | 6.6916 | Loss 5-10% | 800(79) | 980(73) | 814(71.5) | 850(125.5) | 838(107) | 841(105)
260 | 1141 | PNR | SARAI ROHILLA | PNR101 | TG-PNR101A-1 | DT-1 | S/STN NO.15 GALI NO.8 KALA PAHAR | 2 | 990 | 19506290 | 815 | 2019-06-29 12:30 | 265 | 1114 | 263 | 1112 | 287 | 1218 | 105 | 656.5 | 61 |  |  | 61 | 50% | 32% | 82% | 37% | 6.6799 | Loss 5-10% | 1057(191) | 1040(151.5) | 912(103) | 817(117) | 852(144.5) | 901(133)
261 | 1141 | PNR | SARAI ROHILLA | PNR101 | TG-PNR101A-2 | DT-2 | S/STN NO.15 GALI NO.8 KALA PAHAR | 2 | 990 | 19505749 | 990 | 2019-06-15 14:00 | 320 | 1398 | 327 | 1434 | 343 | 1501 | 90 | 477 | 202.5 | 38 | 0.5 | 241 | 24% | 39% | 100% | 39% | 6.6799 | Loss 5-10% | 1043(198.5) | 1157(211) | 1165(273.5) | 1169(272.5) | 1163(226) | 1204(283)
262 | 1141 | PNR | SARAI ROHILLA | PNR102 | TG-PNR102A-1 | DT-1 | NAGARWALA GHATTI RD.:PL | 1 | 990 | 19505845 | 1035 | 2019-06-30 17:00 | 359 | 1508 | 353 | 1471 | 323 | 1346 | 147 | 374 | 258.5 | 79 | 3.5 | 341 | 102% | 99% | 105% | 103% | 4.3062 | Loss 0-5% |  | 938(119) | 943(265.5) | 928(88) | 875(24)
263 | 1141 | PNR | SARAI ROHILLA | PNR104 | TG-PNR104A-2 | DT-2 | ZONAL OFF. K. PAHAR:PL | 2 | 990 | 19506080 | 836 | 2019-06-19 16:30 | 283 | 1165 | 291 | 1192 | 262 | 1073 | 108 | 581.5 | 138.5 |  |  | 138.5 | 26% | 36% | 84% | 29% | 3.8856 | Loss 0-5% | 829(84.5) | 897(113) | 829(115.5) |  | 925(166.5) | 889(62.5)
264 | 1141 | PNR | SARAI ROHILLA | PNR105 | TG-PNR105A-1 | DT-1 | POLICE POST K. PAHAR:PL | 1 | 990 | 19502802 | 783 | 2019-06-01 12:30 | 248 | 1071 | 261 | 1134 | 274 | 1180 | 95 | 644 | 76 |  |  | 76 | 26% | 30% | 79% | 34% | 8.0391 | Loss 5-10%
265 | 1141 | PNR | SARAI ROHILLA | PNR106 | TG-PNR106A-2 | DT-2 | TIN MKT. K. PAHAR:PL | 2 | 630 | 19505104 | 714 | 2019-06-01 16:30 | 242 | 1065 | 208 | 906 | 264 | 1176 | 235 | 438 | 170.5 | 68 | 43.5 | 282 | 63% | 65% | 113% | 76% | 3.9892 | Loss 0-5% | 1034(136.5) | 930(190.5) | 619(244.5) | 764(269) |  | 642(283)
266 | 1141 | PNR | SARAI ROHILLA | PNR107 | TG-PNR107A-1 | DT-1 | BANGALI DHABA K. PAHAR:PL | 1 | 990 | 19502628 | 905 | 2019-06-26 16:00 | 286 | 1139 | 302 | 1207 | 317 | 1266 | 110 | 555 | 164 | 1 |  | 165 | 19% | 31% | 91% | 29% | 5.1953 | Loss 5-10% | 831(43) |  |  |  | 890(77.5) | 939(193.5)
267 | 1141 | PNR | SARAI ROHILLA | PNR110 | TG-PNR110A-1 | DT-1 | G. NO. 11 BABU RAM K. PAHAR:PL | 1 | 990 | 19502737 | 820 | 2019-06-28 16:30 | 285 | 1168 | 246 | 1006 | 288 | 1183 | 170 | 609 | 111 |  |  | 111 | 21% | 33% | 83% | 28% | 7.8695 | Loss 5-10% |  |  | 757(31) | 796(34) | 837(74.5) | 825(97.5)
268 | 1141 | PNR | SARAI ROHILLA | PNR113 | TG-PNR113A-1 | DT-1 | SARAI ROHILLA:PL | 1 | 990 | 19503210 | 911 | 2019-06-30 03:00 | 321 | 1348 | 259 | 1080 | 331 | 1397 | 295 | 534.5 | 182 | 3 |  | 185 | 92% | 74% | 78% | 91% | 5.9779 | Loss 5-10% |  | 854(64) | 1027(187) | 883(106.5) | 776(41)
269 | 1141 | PNR | SARAI ROHILLA | PNR114 | TG-PNR114A-1 | DT-1 | KAMAL (K) K.PAHAR:PL | 1 | 630 | 19504060 | 590 | 2019-06-29 16:00 | 264 | 1146 | 156 | 669 | 171 | 730 | 450 | 620.5 | 95 | 4 |  | 99 | 76% | 53% | 94% | 79% | 3.9651 | Loss 0-5% |  |  | 551(40.5)
270 | 1141 | PNR | SARAI ROHILLA | PNR116 | TG-PNR116A-2 | DT-2 | GALI NO.1 NANAKWALA:PL | 2 | 990 | 19506292 | 782 | 2019-06-30 11:00 | 266 | 1165 | 265 | 1162 | 250 | 1091 | 73 | 694 | 25.5 |  |  | 25.5 | 13% | 40% | 79% | 24% | 9.4164 | Loss 5-10% | 744(28) |  | 857(144.5) | 847(175) | 889(147) | 898(202.5)
271 | 1141 | PNR | SARAI ROHILLA | PNR120 | TG-PNR120A-1 | DT-1 | SOHAN SINGH K.PAHAR:PL | 3 | 630 | 19506568 | 599 | 2019-06-04 11:00 | 198 | 792 | 197 | 791 | 203 | 823 | 32 | 542.5 | 172 | 5.5 |  | 177.5 | 24% | 41% | 95% | 27% | 5.8034 | Loss 5-10% |  |  |  |  | 639(117.5) | 662(179)
272 | 1141 | PNR | SARAI ROHILLA | PNR120 | TG-PNR120A-3 | DT-3 | SOHAN SINGH K.PAHAR:PL | 3 | 630 | 19503574 | 569 | 2019-06-28 15:30 | 179 | 757 | 205 | 867 | 185 | 788 | 98 | 556.5 | 163 | 0.5 |  | 163.5 | 36% | 41% | 90% | 41% | 5.8034 | Loss 5-10% | 482(24.5) | 513(40.5) | 531(110.5) | 529(120.5) | 519(72) | 515(107)
273 | 1141 | PNR | SARAI ROHILLA | PNR121 | TG-PNR121A-1 | DT-1 | KHANNA S/STN, K.PAHAR:PL | 1 | 990 | 19503204 | 838 | 2019-06-29 16:00 | 299 | 1264 | 270 | 1145 | 269 | 1141 | 121 | 651 | 68.5 |  |  | 68.5 | 18% | 21% | 85% | 59% | 9.352 | Loss 5-10% | 789(88) | 825(87) | 817(119) | 844(151.5) | 848(100.5) | 837(163.5)
274 | 1141 | PNR | SARAI ROHILLA | PNR127 | TG-PNR127A-2 | DT-2 | MILITARY RD. P/M S/ST:PL | 2 | 990 | 19504393 | 998 | 2019-06-30 02:30 | 308 | 1213 | 280 | 1091 | 410 | 1620 | 480 | 626 | 86.5 | 4 | 0.5 | 91 | 101% | 75% | 72% | 93% | 3.7047 | Loss 0-5% |  |  | 851(33.5)
275 | 1141 | PNR | SARAI ROHILLA | PNR129 | TG-PNR129A-1 | DT-1 | GALI-4 POST OFFICE ANAND PARBAT | 1 | 990 | 19502933 | 793 | 2019-06-14 15:30 | 224 | 910 | 276 | 1123 | 293 | 1189 | 253 | 641.5 | 78.5 |  |  | 78.5 | 31% | 32% | 80% | 37% | 4.0156 | Loss 0-5% |  | 763(29) | 801(102) | 799(42.5) | 809(101) | 801(50)
276 | 1141 | PNR | SARAI ROHILLA | PNR130 | TG-PNR130A-1 | DT-1 | TAULUI WALA PATEL NAGAR | 1 | 990 | 19506739 | 865 | 2019-06-25 16:00 | 269 | 1091 | 289 | 1168 | 308 | 1257 | 144 | 550.5 | 169.5 |  |  | 169.5 | 38% | 42% | 87% | 45% | 4.7541 | Loss 0-5% |  |  |  |  | 863(91.5) | 806(77)
277 | 1141 | PNR | SARAI ROHILLA | PNR138 | TG-PNR138A-1 | DT-1 | RIWA GALI NO-4 | 1 | 990 | 19502594 | 806 | 2019-06-01 12:00 | 268 | 1111 | 270 | 1121 | 268 | 1107 | 12 | 647.5 | 72 |  |  | 72 | 18% | 23% | 81% | 43% | 8.3993 | Loss 5-10% | 798(49.5) | 804(50) | 831(127) | 909(185) | 942(118.5) | 957(181.5)
278 | 1141 | PNR | SARAI ROHILLA | PNR139 | TG-PNR139A-1 | DT-1 | POST OFFICE P/M GALI NO-2 | 1 | 400 | 19502809 | 335 | 2019-06-26 16:00 | 120 | 524 | 111 | 477 | 103 | 442 | 71 | 581.5 | 137 |  |  | 137 | 28% | 46% | 84% | 27% | 2.747 | Loss 0-5% | 310(26) | 327(59.5) | 454(117)
279 | 1141 | PNR | SARAI ROHILLA | PNR141 | TG-PNR141A-1 | DT-1 | TIKONA PARK GODODIA ROAD | 1 | 990 | 19502625 | 1113 | 2019-06-29 23:00 | 320 | 1362 | 439 | 1877 | 355 | 1510 | 459 | 322 | 280.5 | 73 | 42 | 395.5 | 110% | 79% | 95% | 112% | 3.884 | Loss 0-5% |  | 1030(207.5) | 1230(433) | 1116(349.5) | 976(174.5) | 799(40.5)
280 | 1141 | PNR | SARAI ROHILLA | PNR149 | TG-PNR149A-1 | DT-1 | HR. ROAD ANAND PARVAT | 2 | 630 | 19504684 | 651 | 2019-06-26 16:00 | 226 | 923 | 214 | 868 | 211 | 863 | 58 | 419 | 180 | 58 | 1.5 | 239.5 | 26% | 62% | 103% | 39% | 4.7164 | Loss 0-5% | 594(105.5) | 599(127.5) | 647(123.5) | 662(137) | 665(100.5) | 660(68)
281 | 1141 | PNR | SARAI ROHILLA | PNR149 | TG-PNR149A-2 | DT-2 | HR. ROAD ANAND PARVAT | 2 | 400 | 19505394 | 352 | 2019-06-22 16:00 | 121 | 502 | 105 | 435 | 126 | 525 | 82 | 612 | 106 |  |  | 106 | 68% | 54% | 88% | 65% | 4.7164 | Loss 0-5%
282 | 1141 | PNR | SARAI ROHILLA | PNR165 | TG-PNR165A-1 | DT-1 | Booster Pump Nai basti( Rajiv Vatika ) | 1 | 990 | 19504825 | 827 | 2019-06-11 23:30 | 278 | 1149 | 317 | 1298 | 232 | 951 | 302 | 616 | 104 |  |  | 104 | 82% | 65% | 70% | 84% | 7.861 | Loss 5-10% |  | 872(43) | 1078(164) | 886(79)
283 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI038 | TG-JHI038A-2 | DT-2 | D-BLK VIVEK VIHAR PLM:PL | 2 | 630 | 19505944 | 546 | 2019-06-16 03:30 | 91 | 376 | 306 | 1357 | 150 | 601 | 890 | 680 | 38 |  |  | 38 | 87% | 51% | 62% | 78% | 2.3245 | Loss 0-5%
284 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI039 | TG-JHI039A-3 | DT-3 | PRATAP KHAND:ID | 3 | 630 | 19506493 | 496 | 2019-06-30 00:30 | 183 | 754 | 176 | 728 | 137 | 567 | 175 | 666.5 | 53.5 |  |  | 53.5 | 79% | 57% | 58% | 77% | 8.5496 | Loss 5-10%
285 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI061 | TG-JHI061A-2 | DT-2 | C-BLK VIVEK VIHAR(PARK WALA):PG | 2 | 630 | 19504197 | 572 | 2019-06-29 23:00 | 196 | 823 | 203 | 851 | 173 | 716 | 123 | 647 | 70 | 0.5 |  | 70.5 | 88% | 57% | 71% | 91% | 4.3282 | Loss 0-5% |  |  | 536(53.5)
286 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI062 | TG-JHI062A-1 | DT-1 | JANTA QTR. VIVEK VIHAR:PL | 2 | 630 | 19501614 | 584 | 2019-06-30 23:30 | 202 | 915 | 172 | 779 | 211 | 963 | 165 | 578 | 106 | 3 |  | 109 | 91% | 65% | 67% | 93% | 7.0972 | Loss 5-10% |  | 556(47.5) | 589(122) | 572(69.5)
287 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI063 | TG-JHI063A-2 | DT-2 | MAHILA COLLEGE VIVEK VIHAR:PL | 2 | 630 | 19505797 | 557 | 2019-06-30 23:30 | 169 | 717 | 158 | 676 | 230 | 989 | 294 | 623 | 95 |  |  | 95 | 87% | 57% | 63% | 88% | 6.5748 | Loss 5-10% |  | 506(27.5) | 697(106.5) | 550(50)
288 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI064 | TG-JHI064A-1 | DT-1 | SHIVA KHAND:PL | 2 | 630 | 19501632 | 545 | 2019-06-30 | 178 | 744 | 145 | 605 | 222 | 946 | 296 | 642 | 78 |  |  | 78 | 86% | 54% | 62% | 84% | 4.6933 | Loss 0-5% |  |  | 537(79) | 506(30)
289 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI074 | TG-JHI074A-1 | DT-1 | C-BLK DSIDC JLM COLONY:ID | 2 | 400 | 19505838 | 402 | 2019-06-02 00:30 | 144 | 601 | 120 | 496 | 138 | 574 | 94 | 565.5 | 131.5 | 21.5 | 0.5 | 153.5 | 100% | 65% | 76% | 100% | 6.691 | Loss 5-10% |  | 331(24) | 359(119.5) | 366(75) | 339(60)
290 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI126 | TG-JHI126A-1 | DT-1 | A-BLK VIVEK VIHAR PH-2 | 2 | 990 | 19505009 | 811 | 2019-06-29 23:30 | 265 | 1115 | 279 | 1170 | 266 | 1130 | 49 | 685.5 | 34.5 |  |  | 34.5 | 77% | 51% | 70% | 82% | 4.7552 | Loss 0-5% |  |  | 804(45.5)
291 | 1210 | KKD | B-BLOCK VIVEK VIHAR | VNG002 | TG-VNG002A-1 | DT-1 | YOJNA VIHAR C-BLOCK:ID | 1 | 990 | 19504191 | 920 | 2019-06-11 23:00 | 287 | 1237 | 327 | 1408 | 305 | 1317 | 148 | 581 | 138 | 1 |  | 139 | 89% | 59% | 72% | 93% | 5.2078 | Loss 5-10% |  | 532(49.5) | 552(113.5) | 511(35.5)
292 | 1210 | KKD | B-BLOCK VIVEK VIHAR | VNG048 | TG-VNG048A-1 | DT-1 | SURAJ MAL VIHAR C-BLOCK:ID | 3 | 990 | 19502894 | 866 | 2019-06-03 02:00 | 314 | 1255 | 282 | 1126 | 270 | 1077 | 159 | 640 | 80 |  |  | 80 | 87% | 71% | 66% | 86% | 3.9787 | Loss 0-5% |  |  | 832(79.5)
293 | 1210 | KKD | B-BLOCK VIVEK VIHAR | VNG048 | TG-VNG048A-3 | DT-3 | SURAJ MAL VIHAR C-BLOCK:ID | 3 | 630 | 19504546 | 510 | 2019-06-08 23:30 | 123 | 524 | 210 | 914 | 176 | 750 | 339 | 673.5 | 42 |  |  | 42 | 80% | 54% | 59% | 81% | 3.9787 | Loss 0-5% |  |  | 553(42)
294 | 1210 | KKD | B-BLOCK VIVEK VIHAR | VNG104 | TG-VNG104A-2 | DT-2 | YOJANA VIHAR B-BLOCK:ID | 2 | 400 | 19503016 | 348 | 2019-06-16 00:30 | 85 | 365 | 115 | 497 | 148 | 647 | 244 | 620 | 100 |  |  | 100 | 87% | 55% | 66% | 86% | 7.2788 | Loss 5-10% |  | 388(67.5) | 411(174.5) | 372(85.5)
295 | 1210 | KKD | B-BLOCK VIVEK VIHAR | VNG115 | TG-VNG115A-1 | DT-1 | SURAJ MAL VIHAR B-BLOCK:PG | 1 | 990 | 19501029 | 1038 | 2019-06-01 00:30 | 337 | 1442 | 366 | 1554 | 336 | 1435 | 115 | 531.5 | 145.5 | 40 | 2 | 187.5 | 105% | 68% | 77% | 101% | 6.2168 | Loss 5-10% |  | 823(45.5) | 910(119.5) | 903(70.5)
296 | 1210 | KKD | JWALA NAGAR | VNG007 | TG-VNG007A-2 | DT-2 | RAMA BLOCK(BABU RAM SCHOOL):K | 2 | 990 | 19503651 | 928 | 2019-06-12 | 353 | 1476 | 258 | 1072 | 317 | 1318 | 352 | 604.5 | 114 | 1.5 |  | 115.5 | 94% | 62% | 69% | 93% | 7.9185 | Loss 5-10% |  |  | 811(44)
297 | 1210 | KKD | JWALA NAGAR | VNG010 | TG-VNG010A-2 | DT-2 | ANAJ MANDI:K | 2 | 990 | 19505882 | 954 | 2019-06-10 | 299 | 1242 | 365 | 1527 | 290 | 1205 | 305 | 620.5 | 96.5 | 3 |  | 99.5 | 96% | 59% | 86% | 92% | 6.5777 | Loss 5-10% |  | 847(31.5) | 914(105)
298 | 1210 | KKD | JWALA NAGAR | VNG011 | TG-VNG011A-1 | DT-1 | DELHI GATE:K | 2 | 990 | 19506806 | 792 | 2019-06-10 23:30 | 276 | 1180 | 291 | 1238 | 225 | 950 | 264 | 678 | 42 |  |  | 42 | 77% | 48% | 73% | 80% | 3.4264 | Loss 0-5% |  |  | 771(45.5)
299 | 1210 | KKD | JWALA NAGAR | VNG013 | TG-VNG013A-1 | DT-1 | BIHARI COLONY:K | 3 | 990 | 19503502 | 981 | 2019-06-11 23:30 | 378 | 1583 | 248 | 1041 | 355 | 1509 | 509 | 563 | 142 | 15 |  | 157 | 94% | 60% | 75% | 99% | 7.415 | Loss 5-10% |  | 943(79) | 1030(199.5) | 995(122) | 837(78.5)
300 | 1210 | KKD | JWALA NAGAR | VNG013 | TG-VNG013A-2 | DT-2 | BIHARI COLONY:K | 3 | 990 | 19506743 | 855 | 2019-06-30 23:00 | 339 | 1410 | 278 | 1149 | 238 | 971 | 383 | 664 | 56 |  |  | 56 | 82% | 58% | 66% | 86% | 7.415 | Loss 5-10% |  | 849(41.5) | 959(126.5) | 885(66.5) | 771(27)
301 | 1210 | KKD | JWALA NAGAR | VNG013 | TG-VNG013A-3 | DT-3 | BIHARI COLONY:K | 3 | 990 | 19504190 | 1048 | 2019-06-11 00:30 | 354 | 1571 | 353 | 1587 | 341 | 1522 | 59 | 501 | 164.5 | 50 | 4.5 | 219 | 106% | 74% | 81% | 104% | 7.415 | Loss 5-10% |  | 886(55.5) | 954(145) | 910(82) | 783(37)
302 | 1210 | KKD | JWALA NAGAR | VNG017 | TG-VNG017A-1 | DT-1 | MUKESH NAGAR:PL | 2 | 990 | 19506922 | 978 | 2019-06-30 23:30 | 320 | 1371 | 361 | 1581 | 298 | 1289 | 261 | 323 | 84 | 10.5 |  | 94.5 | 97% | 75% | 73% | 99% | 9.4921 | Loss 5-10% |  | 845(58) | 923(180) | 900(121.5) | 835(70)
303 | 1210 | KKD | JWALA NAGAR | VNG018 | TG-VNG018A-1 | DT-1 | TEL MILL:PL | 1 | 990 | 19505883 | 969 | 2019-06-09 | 443 | 1887 | 255 | 1072 | 271 | 1131 | 788 | 635 | 74.5 | 10.5 |  | 85 | 98% | 67% | 68% | 96% | 6.6391 | Loss 5-10% |  | 969(123) | 1053(235.5) | 999(176.5) | 991(126.5)
304 | 1210 | KKD | JWALA NAGAR | VNG022 | TG-VNG022A-1 | DT-1 | 4-POLE PANDAV ROAD:PL | 1 | 990 | 19505267 | 855 | 2019-06-10 23:30 | 232 | 1014 | 292 | 1283 | 331 | 1457 | 386 | 637.5 | 82.5 |  |  | 82.5 | 83% | 58% | 71% | 86% | 3.6933 | Loss 0-5%
305 | 1210 | KKD | JWALA NAGAR | VNG025 | TG-VNG025A-1 | DT-1 | MAHAVIR BLOCK:PL | 2 | 400 | 19505298 | 388 | 2019-06-02 23:30 | 109 | 437 | 172 | 698 | 107 | 428 | 265 | 618.5 | 95 | 6.5 |  | 101.5 | 95% | 62% | 67% | 97% | 4.7099 | Loss 0-5% |  | 318(26.5) | 348(104)
306 | 1210 | KKD | JWALA NAGAR | VNG026 | TG-VNG026A-1 | DT-1 | DALAI MOHALLA:PL | 1 | 990 | 19504081 | 792 | 2019-06-12 14:30 | 224 | 936 | 268 | 1127 | 300 | 1248 | 272 | 565.5 | 36.5 |  |  | 36.5 | 67% | 58% | 80% | 70% | 3.0076 | Loss 0-5% |  | 817(64.5) | 843(99.5) | 824(38.5)
307 | 1210 | KKD | JWALA NAGAR | VNG027 | TG-VNG027A-1 | DT-1 | SHALIMAR PARK:K | 2 | 990 | 19505963 | 981 | 2019-06-10 23:30 | 390 | 1661 | 248 | 1051 | 343 | 1465 | 540 | 569 | 129.5 | 20 |  | 149.5 | 96% | 62% | 97% | 99% | 5.0551 | Loss 5-10% |  | 894(63.5) | 992(141) | 894(63)
308 | 1210 | KKD | JWALA NAGAR | VNG028 | TG-VNG028A-1 | DT-1 | MANI RAM MANDIR:PL | 3 | 990 | 19506740 | 1245 | 2019-06-27 03:00 | 368 | 1467 | 360 | 1413 | 517 | 2088 | 649 | 484 | 141 | 51 | 44 | 236 | 126% | 79% | 81% | 114% | 4.9515 | Loss 0-5% |  |  | 857(69)
309 | 1210 | KKD | JWALA NAGAR | VNG028 | TG-VNG028A-3 | DT-3 | MANI RAM MANDIR:PL | 3 | 630 | 19505681 | 648 | 2019-06-12 | 280 | 1180 | 220 | 896 | 148 | 607 | 496 | 656.5 | 59 | 4 | 0.5 | 63.5 | 103% | 57% | 64% | 94% | 4.9515 | Loss 0-5% |  |  | 595(83.5) | 559(39)
310 | 1210 | KKD | JWALA NAGAR | VNG029 | TG-VNG029A-1 | DT-1 | IDGAH BHOLA NATH NAGAR:PL | 1 | 990 | 19505511 | 1160.112 | 2019-06-10 23:30 | 457.9477 | 2048.7998 | 309.9058 | 1380.5495 | 392.2585 | 1779.5959 | 582.3518 | 440.5 | 211 | 52.5 | 14.5 | 278 | 109% | 78% | 89% | 117% | 7.3987 | Loss 5-10% |  | 1154(298.5) | 1229(240.5) |  | 924(38) | 821(46.5)
311 | 1210 | KKD | JWALA NAGAR | VNG030 | TG-VNG030A-1 | DT-1 | TELEWARA:PM | 1 | 400 | 19504455 | 347 | 2019-06-12 | 120 | 519 | 115 | 497 | 112 | 487 | 29 | 617.5 | 102 |  |  | 102 | 87% | 60% | 75% | 86% | 2.6793 | Loss 0-5% |  | 445(186.5) | 483(394.5) | 462(257.5) | 412(210.5) | 338(37)
312 | 1210 | KKD | JWALA NAGAR | VNG031 | TG-VNG031A-1 | DT-1 | TEJAB MILL:PL | 3 | 990 | 19503074 | 942 | 2019-06-11 00:30 | 291 | 1285 | 376 | 1667 | 275 | 1213 | 423 | 568 | 145 | 3 |  | 148 | 95% | 66% | 73% | 91% | 10.8309 | Loss 10-20% |  | 882(35) | 992(133) | 878(79) | 829(33.5)
313 | 1210 | KKD | JWALA NAGAR | VNG032 | TG-VNG032A-2 | DT-2 | MAHA RAM MOHALLA:PL | 2 | 630 | 19506688 | 546 | 2019-06-30 00:30 | 204 | 830 | 159 | 645 | 183 | 747 | 161 | 622.5 | 96.5 |  |  | 96.5 | 87% | 61% | 64% | 84% | 3.0255 | Loss 0-5%
314 | 1210 | KKD | JWALA NAGAR | VNG036 | TG-VNG036A-1 | DT-1 | BHOLA NATH NAGAR:K | 3 | 990 | 19503515 | 809 | 2019-06-29 23:30 | 249 | 1051 | 261 | 1116 | 299 | 1249 | 175 | 666.5 | 53 |  |  | 53 | 81% | 55% | 64% | 82% | 9.4245 | Loss 5-10% |  |  | 755(26)
315 | 1210 | KKD | JWALA NAGAR | VNG036 | TG-VNG036A-2 | DT-2 | BHOLA NATH NAGAR:K | 3 | 990 | 19501600 | 805 | 2019-06-12 | 231 | 941 | 275 | 1142 | 300 | 1243 | 266 | 669 | 51 |  |  | 51 | 81% | 54% | 57% | 81% | 9.4245 | Loss 5-10% |  |  | 787(41)
316 | 1210 | KKD | JWALA NAGAR | VNG036 | TG-VNG036A-3 | DT-3 | BHOLA NATH NAGAR:K | 3 | 630 | 19506687 | 665 | 2019-06-10 01:30 | 210 | 887 | 169 | 710 | 285 | 1238 | 465 | 617 | 95.5 | 6.5 | 1 | 103 | 106% | 61% | 67% | 97% | 9.4245 | Loss 5-10%
317 | 1210 | KKD | JWALA NAGAR | VNG037 | TG-VNG037A-1 | DT-1 | PATHAN PURA:PL | 1 | 990 | 19505282 | 1165 | 2019-06-09 23:30 | 364 | 1656 | 500 | 2284 | 300 | 1321 | 847 | 590.5 | 126.5 | 2.5 | 0.5 | 129.5 | 91% | 65% | 72% | 118% | 5.2561 | Loss 5-10% |  | 934(87) | 1036(214.5) | 1285(148.5) | 895(89.5)
318 | 1210 | KKD | JWALA NAGAR | VNG038 | TG-VNG038A-1 | DT-1 | AGGARWAL BHAWAN:PM | 2 | 630 | 19501636 | 511 | 2019-06-11 23:30 | 179 | 744 | 176 | 732 | 156 | 656 | 83 | 688.5 | 31.5 |  |  | 31.5 | 77% | 54% | 61% | 81% | 7.2365 | Loss 5-10% |  |  | 514(45)
319 | 1210 | KKD | JWALA NAGAR | VNG064 | TG-VNG064A-1 | DT-1 | HALKANA KUNA NO-1:K | 4 | 630 | 19504605 | 540 | 2019-06-29 23:00 | 155 | 683 | 167 | 732 | 218 | 966 | 263 | 575.5 | 144 |  |  | 144 | 84% | 82% | 82% | 86% | 7.7783 | Loss 5-10% |  |  | 517(111.5) | 528(93) | 506(65.5)
320 | 1210 | KKD | JWALA NAGAR | VNG090 | TG-VNG090A-2 | DT-2 | GALI NO-10 VISHWAS NAGAR:PL | 2 | 990 | 19505959 | 920 | 2019-06-30 23:30 | 233 | 1014 | 272 | 1197 | 415 | 1887 | 797 | 548 | 170 | 2 |  | 172 | 90% | 66% | 76% | 93% | 2.957 | Loss 0-5% |  | 866(40.5) | 923(152) | 901(84)
321 | 1210 | KKD | JWALA NAGAR | VNG111 | TG-VNG111A-2 | DT-2 | BIHARI COLONY EXT.;PL | 2 | 630 | 19505884 | 562 | 2019-06-03 | 142 | 576 | 200 | 827 | 220 | 910 | 302 | 628 | 92 |  |  | 92 | 89% | 64% | 72% | 84% | 6.9857 | Loss 5-10% |  |  | 847(87.5) | 561(36)
322 | 1210 | KKD | JWALA NAGAR | VNG158 | TG-VNG158A-1 | DT-1 | CIVIL HOSPITAL SHAHDARA S/STN | 1 | 990 | 19501461 | 911 | 2019-06-30 16:00 | 341 | 1492 | 295 | 1277 | 275 | 1188 | 270 | 596 | 121 | 3 |  | 124 | 56% | 41% | 92% | 58% | 6.7082 | Loss 5-10% |  |  | 827(126)
323 | 1210 | KKD | JWALA NAGAR | VNG177 | TG-VNG177A-1 | DT-1 | TELIWARA PARK NEAR GURUDWARA :OD | 1 | 630 | 19501469 | 509 | 2019-06-11 23:30 | 206 | 872 | 118 | 497 | 185 | 762 | 334 | 677.5 | 42.5 |  |  | 42.5 | 81% | 56% | 68% | 81% | 3.6358 | Loss 0-5%
324 | 1210 | KKD | SAINI ENCLAVE | VNG012 | TG-VNG012A-1 | DT-1 | LSC MKT A-BLK SURAJ MAL VIHAR:ID | 2 | 630 | 19501049 | 546 | 2019-06-29 16:30 | 163 | 697 | 214 | 932 | 169 | 726 | 223 | 631.5 | 88 |  |  | 88 | 72% | 51% | 87% | 75% | 6.7244 | Loss 5-10% |  |  | 527(92.5) | 519(27.5)
325 | 1210 | KKD | SAINI ENCLAVE | VNG019 | TG-VNG019A-1 | DT-1 | ASHOKA NIKETAN:PG | 1 | 990 | 19504456 | 842 | 2019-06-11 23:30 | 330 | 1446 | 267 | 1169 | 246 | 1073 | 335 | 634.5 | 84 |  |  | 84 | 85% | 54% | 66% | 85% | 5.0128 | Loss 5-10% |  |  | 869(72.5) | 822(31)
326 | 1210 | KKD | SAINI ENCLAVE | VNG035 | TG-VNG035A-1 | DT-1 | KARKAR DOOMA VILLAGE:PM | 1 | 990 | 19506467 | 958 | 2019-06-29 23:30 | 349 | 1466 | 368 | 1551 | 241 | 1012 | 502 | 459.5 | 251 | 9.5 |  | 260.5 | 96% | 84% | 87% | 97% | 4.1713 | Loss 0-5% |  | 846(40) | 977(278.5) | 916(227) | 853(106.5)
327 | 1210 | KKD | SAINI ENCLAVE | VNG053 | TG-VNG053A-2 | DT-2 | ANAND VIHAR C-BLOCK:ID | 3 | 990 | 19502988 | 956 | 2019-06-11 00:30 | 325 | 1395 | 346 | 1477 | 285 | 1212 | 235 | 563.5 | 147.5 | 7.5 |  | 155 | 97% | 67% | 75% | 94% | 4.0445 | Loss 0-5% |  | 793(26.5) | 812(72.5)
328 | 1210 | KKD | SAINI ENCLAVE | VNG070 | TG-VNG070A-2 | DT-2 | AGCR ENCLAVE:ID | 3 | 630 | 19502991 | 531 | 2019-06-30 01:00 | 214 | 861 | 140 | 563 | 177 | 713 | 258 | 661.5 | 34.5 |  |  | 34.5 | 84% | 55% | 61% | 79% | 6.8619 | Loss 5-10% |  | 522(24) | 549(45)
329 | 1210 | KKD | SAINI ENCLAVE | VNG071 | TG-VNG071A-1 | DT-1 | HARGOVIND ENCLAVE:ID | 3 | 990 | 19501110 | 830 | 2019-06-11 00:30 | 306 | 1354 | 283 | 1256 | 241 | 1063 | 257 | 664.5 | 55 |  |  | 55 | 84% | 61% | 80% | 79% | 3.9773 | Loss 0-5%
330 | 1210 | KKD | SAINI ENCLAVE | VNG071 | TG-VNG071A-3 | DT-3 | HARGOVIND ENCLAVE:ID | 3 | 630 | 19503063 | 720 | 2019-06-27 17:00 | 228 | 927 | 268 | 1107 | 224 | 919 | 184 | 475.5 | 207 | 21.5 | 13.5 | 242 | 79% | 82% | 114% | 101% | 3.9773 | Loss 0-5% |  | 581(183.5) | 613(316) | 610(260.5) | 552(215.5) | 478(24.5)
331 | 1210 | KKD | SAINI ENCLAVE | VNG073 | TG-VNG073A-1 | DT-1 | DELHI ADMN FLATS:ID | 2 | 630 | 19501084 | 568 | 2019-06-30 23:30 | 211 | 895 | 158 | 669 | 199 | 843 | 205 | 606.5 | 113 | 0.5 |  | 113.5 | 88% | 63% | 68% | 90% | 14.8145 | Loss 10-20%
332 | 1210 | KKD | SAINI ENCLAVE | VNG076 | TG-VNG076A-2 | DT-2 | SURYA NIKETAN:ID | 3 | 990 | 19501023 | 1047 | 2019-06-06 | 361 | 1552 | 323 | 1384 | 364 | 1550 | 167 | 495 | 184 | 37 | 4 | 225 | 106% | 75% | 91% | 105% | 4.3465 | Loss 0-5% |  |  | 1005(123) | 931(123) | 793(53.5)
333 | 1210 | KKD | SAINI ENCLAVE | VNG078 | TG-VNG078A-3 | DT-3 | RAM VIHAR:ID | 3 | 630 | 19503470 | 492 | 2019-06-11 23:30 | 182 | 751 | 162 | 663 | 147 | 597 | 134 | 694 | 26 |  |  | 26 | 77% | 54% | 63% | 78% | 3.1225 | Loss 0-5%
334 | 1210 | KKD | SAINI ENCLAVE | VNG081 | TG-VNG081A-2 | DT-2 | ANAND VIHAR A-BLOCK:ID | 3 | 990 | 19501090 | 825 | 2019-06-11 | 270 | 1191 | 291 | 1277 | 264 | 1153 | 110 | 660 | 60 |  |  | 60 | 83% | 58% | 65% | 83% | 5.373 | Loss 5-10% |  |  | 756(28)
335 | 1210 | KKD | SAINI ENCLAVE | VNG099 | TG-VNG099A-2 | DT-2 | L.S.C SAINI ENCLAVE:ID | 2 | 630 | 19501086 | 562 | 2019-06-10 16:00 | 215 | 925 | 169 | 707 | 179 | 753 | 199 | 567.5 | 152.5 |  |  | 152.5 | 81% | 57% | 89% | 81% | 2.8496 | Loss 0-5%
336 | 1210 | KKD | SAINI ENCLAVE | VNG103 | TG-VNG103A-3 | DT-3 | DAYANAND VIHAR 2:ID | 3 | 630 | 19505437 | 570 | 2019-06-29 16:00 | 186 | 788 | 193 | 816 | 191 | 805 | 25 | 625 | 94.5 | 0.5 |  | 95 | 55% | 55% | 90% | 72% | 3.6475 | Loss 0-5% |  | 590(81.5) | 630(210) | 557(118.5) | 526(69)
337 | 1210 | KKD | SAINI ENCLAVE | VNG109 | TG-VNG109A-2 | DT-2 | SURAJ MAL VIHAR A-BLOCK:ID | 2 | 990 | 19504391 | 869 | 2019-06-01 01:00 | 347 | 1553 | 282 | 1251 | 240 | 1056 | 434 | 664 | 55.5 |  |  | 55.5 | 88% | 58% | 66% | 82% | 8.9516 | Loss 5-10% |  |  | 784(37)
338 | 1210 | KKD | SAINI ENCLAVE | VNG131 | TG-VNG131A-1 | DT-1 | MANAK VIHAR (VIGYAN LOK) | 2 | 630 | 19501109 | 532 | 2019-06-05 23:30 | 102 | 411 | 195 | 800 | 234 | 964 | 492 | 657 | 63 |  |  | 63 | 82% | 52% | 67% | 84% | 8.6591 | Loss 5-10%
339 | 1210 | KKD | SAINI ENCLAVE | VNG133 | TG-VNG133A-1 | DT-1 | D BLOCK ANAND VIHAR | 1 | 990 | 19501012 | 1199 | 2019-06-11 23:30 | 468 | 2030 | 353 | 1517 | 378 | 1626 | 469 | 462 | 168.5 | 58.5 | 29.5 | 256.5 | 120% | 76% | 90% | 121% | 4.6595 | Loss 0-5% |  | 946(98) | 1024(194.5) | 1034(115) | 801(34.5)
340 | 1210 | KKD | SAINI ENCLAVE | VNG147 | TG-VNG147A-1 | DT-1 | AGCR ENCLAVE:PKG STN | 1 | 990 | 19501011 | 871 | 2019-06-11 23:00 | 266 | 1103 | 344 | 1438 | 261 | 1085 | 345 | 601 | 119 |  |  | 119 | 87% | 62% | 71% | 88% | 4.9881 | Loss 0-5%
341 | 1211 | GTR | E&F DILSHAD GARDEN | DGN069 | TG-DGN069A-2 | DT-2 | A-BLOCK JHILMIL INDILSHAD AREA:ID | 4 | 990 | 19501371 | 856 | 2019-06-01 13:00 | 298 | 1273 | 278 | 1194 | 280 | 1194 | 79 | 640 | 80 |  |  | 80 | 43% | 43% | 86% | 62% | 5.5581 | Loss 5-10% |  |  | 967(63) | 971(79) | 1314(122) | 1431(233.5)
342 | 1211 | GTR | E&F DILSHAD GARDEN | DGN069 | TG-DGN069A-3 | DT-3 | A-BLOCK JHILMIL INDILSHAD AREA:ID | 4 | 990 | 19506328 | 1088 | 2019-06-01 11:30 | 367 | 1571 | 361 | 1542 | 360 | 1532 | 35 | 384 | 200.5 | 116 | 14.5 | 331 | 81% | 79% | 110% | 78% | 5.5581 | Loss 5-10% | 1119(160.5) | 1151(204) |  |  |  | 857(165.5)
343 | 1211 | GTR | E&F DILSHAD GARDEN | DGN069 | TG-DGN069A-4 | DT-4 | A-BLOCK JHILMIL INDILSHAD AREA:ID | 4 | 990 | 19506858 | 893 | 2019-06-28 14:30 | 309 | 1323 | 302 | 1296 | 282 | 1201 | 111 | 656.5 | 60.5 | 0.5 |  | 61 | 42% | 47% | 90% | 42% | 5.5581 | Loss 5-10%
344 | 1211 | GTR | E&F DILSHAD GARDEN | DGN071 | TG-DGN071A-1 | DT-1 | B-BLK COMPLAINT CENTER JLM IND AREA:ID | 3 | 990 | 19506356 | 953 | 2019-06-29 15:00 | 313 | 1265 | 317 | 1274 | 324 | 1315 | 46 | 554 | 156 | 10 |  | 166 | 57% | 76% | 96% | 68% | 3.5863 | Loss 0-5% | 1124(230) |  | 1280(237) | 1230(207.5) | 1179(223.5) | 1144(224.5)
345 | 1211 | GTR | E&F DILSHAD GARDEN | DGN071 | TG-DGN071A-3 | DT-3 | B-BLK COMPLAINT CENTER JLM IND AREA:ID | 3 | 990 | 19506610 | 1127 | 2019-06-22 12:30 | 380 | 1631 | 378 | 1608 | 369 | 1575 | 48 | 437.5 | 103.5 | 125.5 | 53.5 | 282.5 | 52% | 60% | 114% | 55% | 3.5863 | Loss 0-5%
346 | 1211 | GTR | E&F DILSHAD GARDEN | DGN072 | TG-DGN072A-1 | DT-1 | PREM ICE FACTORY:ID | 1 | 990 | 19506735 | 1024 | 2019-06-29 15:30 | 343 | 1409 | 339 | 1397 | 342 | 1412 | 13 | 615 | 75.5 | 26 | 2.5 | 104 | 42% | 43% | 103% | 52% | 3.8128 | Loss 0-5% | 910(123.5) | 986(170.5) | 1027(195.5) | 987(182) | 952(158.5) | 939(144.5)
347 | 1211 | GTR | E&F DILSHAD GARDEN | DGN073 | TG-DGN073A-1 | DT-1 | SARDAR ALUMINIUM:ID | 1 | 990 | 19501448 | 911 | 2019-06-22 15:00 | 312 | 1298 | 308 | 1286 | 291 | 1215 | 78 | 524.5 | 192.5 | 1.5 |  | 194 | 45% | 47% | 92% | 64% | 4.1295 | Loss 0-5% |  |  |  |  | 887(66) | 866(53.5)
348 | 1211 | GTR | E&F DILSHAD GARDEN | DGN077 | TG-DGN077A-2 | DT-2 | SANSAR:K | 3 | 990 | 19505904 | 867 | 2019-06-21 15:30 | 290 | 1200 | 297 | 1232 | 279 | 1157 | 65 | 635.5 | 84.5 |  |  | 84.5 | 41% | 53% | 88% | 45% | 2.7204 | Loss 0-5% | 978(123) | 1000(146.5) | 1030(175.5) | 1053(203) | 1106(215.5) | 1082(62.5)
349 | 1211 | GTR | E&F DILSHAD GARDEN | DGN077 | TG-DGN077A-3 | DT-3 | SANSAR:K | 3 | 990 | 19506621 | 1125 | 2019-06-26 12:00 | 383 | 1551 | 367 | 1477 | 375 | 1513 | 64 | 456.5 | 199 | 57.5 | 6.5 | 263 | 68% | 78% | 114% | 80% | 2.7204 | Loss 0-5%
350 | 1211 | GTR | E&F DILSHAD GARDEN | DGN080 | TG-DGN080A-2 | DT-2 | SITA FLATS,DILSHAD GARDEN:ID | 3 | 630 | 19504241 | 549 | 2019-06-22 18:30 | 178 | 766 | 187 | 805 | 185 | 797 | 35 | 663 | 57 |  |  | 57 | 52% | 43% | 87% | 58% | 3.2709 | Loss 0-5% | 537(43.5) | 540(37.5) |  | 579(28) | 526(34) | 564(34)
351 | 1211 | GTR | E&F DILSHAD GARDEN | DGN081 | TG-DGN081A-3 | DT-3 | DILSHAD GDN S/STN-4:ID | 4 | 630 | 19504435 | 623 | 2019-06-13 11:30 | 221 | 903 | 209 | 847 | 193 | 783 | 103 | 489 | 217 | 14 |  | 231 | 81% | 78% | 99% | 80% | 5.3544 | Loss 5-10% | 558(71.5) | 642(114.5) | 653(151.5) | 640(156) | 576(46.5) | 658(188.5)
352 | 1211 | GTR | E&F DILSHAD GARDEN | DGN081 | TG-DGN081A-4 | DT-4 | DILSHAD GDN S/STN-4:ID | 4 | 990 | 19504966 | 881 | 2019-06-27 11:00 | 270 | 1114 | 326 | 1346 | 285 | 1177 | 208 | 655.5 | 64 |  |  | 64 | 44% | 53% | 89% | 48% | 5.3544 | Loss 5-10%
353 | 1211 | GTR | E&F DILSHAD GARDEN | DGN083 | TG-DGN083A-2 | DT-2 | R.BLK DILSHAD GARDEN S/S NO-1:ID | 2 | 630 | 19503033 | 552 | 2019-06-29 16:00 | 212 | 877 | 180 | 741 | 160 | 659 | 191 | 614.5 | 105.5 |  |  | 105.5 | 67% | 56% | 88% | 66% | 5.1265 | Loss 5-10% |  | 524(40) | 548(124.5) | 515(42.5)
354 | 1211 | GTR | E&F DILSHAD GARDEN | DGN085 | TG-DGN085A-1 | DT-1 | A-PKT,DILSHAD GDN:ID | 3 | 630 | 19501381 | 558 | 2019-06-11 01:30 | 193 | 850 | 216 | 954 | 149 | 647 | 271 | 667 | 52.5 |  |  | 52.5 | 89% | 50% | 56% | 87% | 3.2962 | Loss 0-5% |  | 577(63) | 768(162) | 653(96.5) | 497(29)
355 | 1211 | GTR | E&F DILSHAD GARDEN | DGN091 | TG-DGN091A-1 | DT-1 | O&P PKT DILSHAD GARDEN:ID | 2 | 630 | 19506580 | 647 | 2019-06-03 06:00 | 221 | 911 | 245 | 999 | 181 | 738 | 230 | 640 | 78.5 | 1 | 0.5 | 80 | 96% | 103% | 70% | 93% | 5.5108 | Loss 5-10% |  | 1059(24) | 515(27)
356 | 1211 | GTR | E&F DILSHAD GARDEN | DGN091 | TG-DGN091A-2 | DT-2 | O&P PKT DILSHAD GARDEN:ID | 2 | 630 | 19506560 | 585 | 2019-06-02 01:00 | 244 | 1009 | 159 | 647 | 181 | 741 | 325 | 612 | 106.5 | 1.5 |  | 108 | 93% | 61% | 83% | 91% | 5.5108 | Loss 5-10% |  |  | 565(82)
357 | 1211 | GTR | E&F DILSHAD GARDEN | DGN092 | TG-DGN092A-2 | DT-2 | Q-POCKET DILSHAD GARDEN:ID | 2 | 400 | 19505791 | 371 | 2019-06-02 | 164 | 697 | 96 | 399 | 110 | 456 | 274 | 666 | 53.5 | 0.5 |  | 54 | 93% | 51% | 61% | 82% | 3.9793 | Loss 0-5%
358 | 1211 | GTR | E&F DILSHAD GARDEN | DGN098 | TG-DGN098A-1 | DT-1 | OLD SEEMAPURI (BUS STOP):ID | 3 | 990 | 19504962 | 912 | 2019-06-11 23:30 | 391 | 1606 | 259 | 1058 | 262 | 1064 | 545 | 421 | 246.5 | 3.5 |  | 250 | 91% | 82% | 83% | 92% | 9.7418 | Loss 5-10% |  | 882(105.5) | 947(267.5)
359 | 1211 | GTR | E&F DILSHAD GARDEN | DGN099 | TG-DGN099A-1 | DT-1 | POLICE STATION OLD SEEMAPURI:ID | 1 | 990 | 19505491 | 761 | 2019-06-11 23:30 | 278 | 1144 | 249 | 1015 | 234 | 958 | 165 | 680.5 | 39 |  |  | 39 | 76% | 62% | 76% | 77% | 6.0772 | Loss 5-10%
360 | 1211 | GTR | E&F DILSHAD GARDEN | DGN101 | TG-DGN101A-2 | DT-2 | B-BLK DSIDC SHED JLM IA NO-3:ID | 2 | 630 | 19501353 | 758 | 2019-06-29 11:00 | 247 | 1057 | 260 | 1106 | 251 | 1076 | 42 | 500.5 | 122.5 | 64.5 | 29 | 216 | 57% | 59% | 120% | 57% | 3.5132 | Loss 0-5% | 721(153.5) | 624(113.5) | 713(162.5) | 831(185.5) | 811(139) | 801(190)
361 | 1211 | GTR | E&F DILSHAD GARDEN | DGN103 | TG-DGN103A-2 | DT-2 | A BLK TAHIRPUR(JLM IND AREA) S/STN-1:ID | 3 | 630 | 19501356 | 672 | 2019-06-21 13:00 | 230 | 986 | 221 | 953 | 221 | 945 | 38 | 529 | 168.5 | 19 | 3.5 | 191 | 54% | 59% | 107% | 64% | 4.9492 | Loss 0-5% | 902(213) | 918(149.5) | 614(127.5) | 633(110) | 615(83) | 645(100)
362 | 1211 | GTR | E&F DILSHAD GARDEN | DGN104 | TG-DGN104A-1 | DT-1 | A BLK TAHIRPUR(JLM IND AREA) S/STN-3:ID | 4 | 630 | 19505489 | 637 | 2019-06-09 16:30 | 209 | 893 | 216 | 929 | 212 | 909 | 31 | 568.5 | 145.5 | 5.5 | 0.5 | 151.5 | 61% | 62% | 101% | 64% | 3.5456 | Loss 0-5% | 1019(163) | 696(129) | 595(113) | 661(100) | 687(114) | 690(215)
363 | 1211 | GTR | E&F DILSHAD GARDEN | DGN104 | TG-DGN104A-2 | DT-2 | A BLK TAHIRPUR(JLM IND AREA) S/STN-3:ID | 4 | 630 | 19501369 | 577 | 2019-06-29 16:00 | 195 | 723 | 199 | 741 | 184 | 683 | 51 | 609.5 | 109.5 | 1 |  | 110.5 | 29% | 49% | 92% | 44% | 3.5456 | Loss 0-5% | 622(107.5) | 653(128) | 663(160) | 592(100.5) | 657(96.5) | 668(131.5)
364 | 1211 | GTR | E&F DILSHAD GARDEN | DGN107 | TG-DGN107A-1 | DT-1 | B BLK OPP SWAHNEY IND.:PL | 3 | 990 | 19505328 | 876 | 2019-06-13 17:00 | 292 | 1266 | 268 | 1161 | 316 | 1366 | 178 | 424.5 | 62.5 |  |  | 62.5 | 39% | 47% | 89% | 36% | 3.5087 | Loss 0-5% |  | 779(31)
365 | 1211 | GTR | E&F DILSHAD GARDEN | DGN109 | TG-DGN109A-1 | DT-1 | B-34 JLM INDUSTRIAL AREA | 1 | 990 | 19501836 | 1088 | 2019-06-24 11:30 | 355 | 1525 | 367 | 1581 | 366 | 1568 | 51 | 481 | 162 | 64.5 | 12.5 | 239 | 35% | 44% | 110% | 38% | 4.5922 | Loss 0-5% | 1018(132.5) | 1016(120) | 1106(154.5) | 1122(196.5) | 1219(164) | 1166(209)
366 | 1211 | GTR | E&F DILSHAD GARDEN | DGN112 | TG-DGN112A-1 | DT-1 | DAMODAR PARK,DILSHAD GARDEN:PL | 4 | 990 | 19506505 | 1313 | 2019-06-21 16:00 | 440 | 1846 | 430 | 1805 | 443 | 1861 | 51 | 436 | 63 | 84 | 137 | 284 | 72% | 72% | 133% | 72% | 4.3892 | Loss 0-5% | 1302(267) |  | 1324(96) | 1466(279.5)
367 | 1211 | GTR | E&F DILSHAD GARDEN | DGN112 | TG-DGN112A-2 | DT-2 | DAMODAR PARK,DILSHAD GARDEN:PL | 4 | 990 | 19502279 | 1045 | 2019-06-08 11:00 | 348 | 1518 | 348 | 1523 | 349 | 1521 | 4 | 482 | 193 | 41 | 3.5 | 237.5 | 61% | 65% | 106% | 61% | 4.3892 | Loss 0-5% | 1052(203) | 1141(193) | 1214(165.5) | 1283(287.5) | 1298(285) | 1216(357.5)
368 | 1211 | GTR | E&F DILSHAD GARDEN | DGN112 | TG-DGN112A-3 | DT-3 | DAMODAR PARK,DILSHAD GARDEN:PL | 4 | 990 | 19505439 | 1327 | 2019-06-23 11:30 | 480 | 1954 | 431 | 1738 | 416 | 1696 | 240 | 383.5 | 76 | 73 | 187.5 | 336.5 | 85% | 88% | 134% | 81% | 4.3892 | Loss 0-5% | 1084(153) | 1193(188.5) | 1117(225.5) | 1213(234.5) | 1268(229) | 1374(269.5)
369 | 1211 | GTR | E&F DILSHAD GARDEN | DGN112 | TG-DGN112A-4 | DT-4 | DAMODAR PARK,DILSHAD GARDEN:PL | 4 | 990 | 19502634 | 852 | 2019-06-22 11:30 | 283 | 1186 | 284 | 1187 | 284 | 1191 | 5 | 695 | 25 |  |  | 25 | 52% | 51% | 86% | 49% | 4.3892 | Loss 0-5% | 940(49) |  | 1033(93.5) | 1162(202) | 1184(167) | 1275(170)
370 | 1211 | GTR | E&F DILSHAD GARDEN | DGN114 | TG-DGN114A-1 | DT-1 | JHULFE BENGAL S/S NO. 2:PL | 3 | 630 | 19506419 | 789 | 2019-06-28 15:30 | 250 | 1037 | 279 | 1166 | 261 | 1092 | 112 | 326.5 | 226.5 | 89.5 | 68.5 | 384.5 | 88% | 93% | 125% | 89% | 4.4184 | Loss 0-5% |  | 782(269) | 1030(339) | 832(352)
371 | 1211 | GTR | E&F DILSHAD GARDEN | DGN114 | TG-DGN114A-3 | DT-3 | JHULFE BENGAL S/S NO. 2:PL | 3 | 990 | 19500063 | 1146 | 2019-06-22 15:30 | 386 | 1651 | 384 | 1635 | 376 | 1594 | 52 | 446.5 | 160 | 84.5 | 26.5 | 271 | 77% | 78% | 116% | 75% | 4.4184 | Loss 0-5% | 955(109) | 880(74.5) | 840(86) | 939(101) | 875(41.5)
372 | 1211 | GTR | E&F DILSHAD GARDEN | DGN116 | TG-DGN116A-1 | DT-1 | E-BLK NEW SEEMA PURI:PL | 2 | 630 | 19506588 | 645 | 2019-06-25 23:00 | 230 | 1003 | 219 | 949 | 196 | 849 | 135 | 607.5 | 108.5 | 0.5 | 0.5 | 109.5 | 81% | 76% | 91% | 102% | 4.3756 | Loss 0-5% |  | 561(41.5) | 582(115.5)
373 | 1211 | GTR | E&F DILSHAD GARDEN | DGN124 | TG-DGN124A-1 | DT-1 | G.T ROAD SEEMA PURI BORDER:PM | 1 | 630 | 19506420 | 637 | 2019-06-15 15:30 | 228 | 953 | 205 | 848 | 203 | 844 | 108 | 589 | 122 | 5.5 | 0.5 | 128 | 60% | 64% | 101% | 52% | 2.7242 | Loss 0-5%
374 | 1211 | GTR | E&F DILSHAD GARDEN | DGN125 | TG-DGN125A-1 | DT-1 | NEW SEEMAPURI DDA FLAT:ID | 2 | 990 | 19504891 | 779 | 2019-06-30 | 240 | 1016 | 313 | 1326 | 226 | 945 | 351 | 465.5 | 26 |  |  | 26 | 79% | 54% | 56% | 78% | 7.9928 | Loss 5-10%
375 | 1211 | GTR | E&F DILSHAD GARDEN | DGN128 | TG-DGN128A-1 | DT-1 | JULFE BENGAL S/S NO.I | 3 | 990 | 19505545 | 847 | 2019-06-28 15:00 | 274 | 1156 | 293 | 1232 | 280 | 1175 | 69 | 650.5 | 58 |  |  | 58 | 65% | 68% | 86% | 70% | 3.8325 | Loss 0-5% | 1043(150) | 1135(220) | 1127(215.5) | 1121(217) | 1111(246.5)
376 | 1211 | GTR | E&F DILSHAD GARDEN | DGN128 | TG-DGN128A-2 | DT-2 | JULFE BENGAL S/S NO.I | 3 | 990 | 19505758 | 1181 | 2019-06-07 12:30 | 395 | 1698 | 400 | 1708 | 386 | 1661 | 43 | 479 | 122.5 | 82.5 | 24 | 229 | 43% | 53% | 119% | 44% | 3.8325 | Loss 0-5% |  | 819(53.5) | 840(40) | 925(123) |  | 938(118.5)
377 | 1211 | GTR | E&F DILSHAD GARDEN | DGN128 | TG-DGN128A-3 | DT-3 | JULFE BENGAL S/S NO.I | 3 | 630 | 19506329 | 906 | 2019-06-07 17:00 | 313 | 1340 | 295 | 1255 | 298 | 1291 | 73 | 454.5 | 159 | 49 | 45 | 253 | 111% | 109% | 144% | 95% | 3.8325 | Loss 0-5% | 562(61) | 623(105.5) | 610(130) | 786(152.5) | 696(168.5) | 787(187)
378 | 1211 | GTR | E&F DILSHAD GARDEN | DGN130 | TG-DGN130A-1 | DT-1 | LOCAL SHOPPING CENTER DILSHAD GARDEN:ID | 2 | 990 | 19504967 | 857 | 2019-06-03 13:30 | 278 | 1194 | 280 | 1190 | 299 | 1278 | 86 | 610 | 107.5 |  |  | 107.5 | 36% | 51% | 87% | 40% | 3.9027 | Loss 0-5% |  | 868(48) | 926(62.5) | 890(90) | 893(75) | 803(34.5)
379 | 1211 | GTR | E&F DILSHAD GARDEN | DGN132 | TG-DGN132A-1 | DT-1 | E&F PKT. DILSHAD GARDEN:ID | 2 | 990 | 19501450 | 860 | 2019-06-10 22:30 | 338 | 1486 | 288 | 1276 | 233 | 1024 | 401 | 618 | 77.5 |  |  | 77.5 | 84% | 45% | 70% | 87% | 3.8043 | Loss 0-5%
380 | 1211 | GTR | E&F DILSHAD GARDEN | DGN133 | TG-DGN133A-4 | DT-4 | B-BLOCK OLD SEEMAPURI :PL | 4 | 630 | 19504208 | 656 | 2019-06-29 22:30 | 240 | 1039 | 172 | 733 | 245 | 1053 | 313 | 324 | 289.5 | 54 | 4.5 | 348 | 102% | 84% | 89% | 104% | 11.9552 | Loss 10-20% | 487(30) | 614(292) | 665(444) | 662(407.5) | 648(392) | 606(236.5)
381 | 1211 | GTR | E&F DILSHAD GARDEN | DGN134 | TG-DGN134A-1 | DT-1 | TAHIRPUR SARAI:PM | 1 | 400 | 19504602 | 445 | 2019-06-14 02:00 | 193 | 794 | 122 | 494 | 131 | 532 | 283 | 430.5 | 163 | 95 | 25 | 283 | 111% | 77% | 81% | 109% | 9.8294 | Loss 5-10% |  | 371(152.5) | 405(261) | 422(218.5) | 380(209) | 329(59)
382 | 1211 | GTR | E&F DILSHAD GARDEN | DGN135 | TG-DGN135A-1 | DT-1 | KHERA VILLAGE:PM | 1 | 630 | 19506547 | 585 | 2019-06-10 21:30 | 224 | 935 | 164 | 687 | 197 | 841 | 217 | 498 | 220 | 2 |  | 222 | 92% | 92% | 84% | 93% | 5.6496 | Loss 5-10% |  | 534(65.5) |  |  | 582(177.5) | 489(42.5)
383 | 1211 | GTR | E&F DILSHAD GARDEN | DGN141 | TG-DGN141A-2 | DT-2 | B-BLK DILSHAD CLY:PM | 3 | 990 | 19505287 | 1031 | 2019-06-30 00:30 | 321 | 1342 | 352 | 1477 | 359 | 1500 | 148 | 573 | 108 | 34 | 3.5 | 145.5 | 104% | 61% | 69% | 103% | 5.3249 | Loss 5-10% |  | 911(40.5) | 1114(138) |  | 831(51.5)
384 | 1211 | GTR | E&F DILSHAD GARDEN | DGN147 | TG-DGN147A-1 | DT-1 | SATISH STEEL ROLLING MILL:ID | 2 | 630 | 19506363 | 510 | 2019-06-13 15:30 | 172 | 718 | 171 | 708 | 167 | 696 | 19 | 643.5 | 73.5 |  |  | 73.5 | 64% | 62% | 81% | 63% | 7.0939 | Loss 5-10% |  |  |  |  | 584(48) | 575(130.5)
385 | 1211 | GTR | E&F DILSHAD GARDEN | DGN162 | TG-DGN162A-1 | DT-1 | F-BLOCK DILSHAD COLONY:ID | 4 | 990 | 19504839 | 908 | 2019-06-29 23:30 | 364 | 1510 | 299 | 1236 | 245 | 1006 | 437 | 591 | 77 | 1.5 |  | 78.5 | 89% | 53% | 72% | 92% | 6.1394 | Loss 5-10% |  |  | 861(61) | 880(40.5)
386 | 1211 | GTR | E&F DILSHAD GARDEN | DGN162 | TG-DGN162A-2 | DT-2 | F-BLOCK DILSHAD COLONY:ID | 4 | 990 | 19505806 | 799 | 2019-06-30 | 287 | 1170 | 232 | 947 | 279 | 1145 | 212 | 685.5 | 30.5 |  |  | 30.5 | 81% | 46% | 56% | 80% | 6.1394 | Loss 5-10% |  |  | 818(24.5)
387 | 1211 | GTR | E&F DILSHAD GARDEN | DGN162 | TG-DGN162A-3 | DT-3 | F-BLOCK DILSHAD COLONY:ID | 4 | 990 | 19501791 | 1139 | 2019-06-30 01:30 | 340 | 1363 | 432 | 1756 | 367 | 1467 | 353 | 543 | 105 | 17.5 | 3 | 125.5 | 115% | 67% | 73% | 101% | 6.1394 | Loss 5-10% |  | 901(56.5) | 971(120.5) | 978(85.5) | 782(30)
388 | 1211 | GTR | E&F DILSHAD GARDEN | DGN190 | TG-DGN190A-1 | DT-1 | NEW POLICE BOTH DILSHAD CLY | 1 | 990 | 19506003 | 996 | 2019-06-30 23:30 | 340 | 1464 | 325 | 1408 | 331 | 1436 | 49 | 565 | 136 | 18.5 | 0.5 | 155 | 94% | 61% | 74% | 101% | 7.985 | Loss 5-10% |  | 909(64.5) | 1101(183) | 1015(116.5) | 834(56)
389 | 1211 | GTR | E&F DILSHAD GARDEN | DGN197 | TG-DGN197A-1 | DT-1 | C- BLK DILSHAD COLONY SSTN NO.-2:PL | 2 | 630 | 19506596 | 582 | 2019-06-29 23:30 | 192 | 768 | 185 | 740 | 205 | 816 | 66 | 626 | 83 | 1.5 |  | 84.5 | 91% | 57% | 77% | 92% | 6.5746 | Loss 5-10% |  | 546(27) | 561(81.5) | 582(50)
390 | 1211 | GTR | E&F DILSHAD GARDEN | DGN207 | TG-DGN207A-1 | DT-1 | SHANKAR KE DP,A-BLK.JLM IA. | 1 | 990 | 19506501 | 960 | 2019-06-29 11:00 | 303 | 1322 | 325 | 1422 | 332 | 1449 | 116 | 664.5 | 54.5 | 1 |  | 55.5 | 16% | 39% | 97% | 21% | 5.468 | Loss 5-10%
391 | 1211 | GTR | E&F DILSHAD GARDEN | DGN225 | TG-DGN225A-1 | DT-1 | Oberai compound | 2 | 990 | 19504360 | 1039 | 2019-06-01 11:30 | 352 | 1478 | 352 | 1490 | 335 | 1416 | 70 | 639.5 | 66 | 11.5 | 0.5 | 78 | 33% | 39% | 105% | 45% | 5.6285 | Loss 5-10% | 922(97) | 966(125.5) | 1023(164.5) | 1013(161.5) | 1112(168) | 1247(251)
392 | 1211 | GTR | E&F DILSHAD GARDEN | DGN225 | TG-DGN225A-2 | DT-2 | Oberai compound | 2 | 990 | 19506760 | 1093 | 2019-06-20 11:00 | 367 | 1614 | 365 | 1611 | 361 | 1595 | 17 | 491.5 | 117 | 23.5 | 1.5 | 142 | 43% | 43% | 110% | 45% | 5.6285 | Loss 5-10% | 637(157) | 733(226) | 784(242.5) | 840(283.5) | 750(213) | 831(249)
393 | 1211 | GTR | E&F DILSHAD GARDEN | DGN228 | TG-DGN228A-1 | DT-1 | A-BLK DILSHAD COLONY | 1 | 990 | 19504330 | 1053 | 2019-06-30 00:30 | 292 | 1155 | 342 | 1369 | 420 | 1692 | 469 | 556 | 115.5 | 42.5 | 6 | 164 | 106% | 71% | 72% | 104% | 6.9048 | Loss 5-10% | 626(36.5) | 855(245.5) | 1057(424.5) | 997(360) |  | 715(106.5)
394 | 1211 | GTR | E&F DILSHAD GARDEN | DGN232 | TG-DGN232A-1 | DT-1 | DSIDC SUBSTATION NO-2 | 4 | 630 | 19506918 | 700 | 2019-06-07 16:30 | 230 | 1029 | 234 | 1040 | 235 | 1049 | 17 | 601 | 24.5 | 5.5 | 4 | 34 | 59% | 58% | 111% | 57% | 4.0223 | Loss 0-5% | 535(40) | 543(52) | 566(85.5) | 559(77) | 603(104.5)
395 | 1211 | GTR | E&F DILSHAD GARDEN | DGN232 | TG-DGN232A-2 | DT-2 | DSIDC SUBSTATION NO-2 | 4 | 990 | 19501354 | 978 | 2019-06-24 12:00 | 331 | 1468 | 317 | 1408 | 330 | 1474 | 63 | 551.5 | 152 | 15 |  | 167 | 22% | 30% | 99% | 33% | 4.0223 | Loss 0-5%
396 | 1211 | GTR | E&F DILSHAD GARDEN | DGN232 | TG-DGN232A-3 | DT-3 | DSIDC SUBSTATION NO-2 | 4 | 990 | 19505129 | 1313 | 2019-06-22 18:00 | 436 | 1823 | 435 | 1808 | 442 | 1838 | 26 | 344.5 | 166.5 | 77.5 | 129.5 | 373.5 | 89% | 92% | 133% | 88% | 4.0223 | Loss 0-5% | 1055(103.5) |  | 919(55.5) | 1144(236) | 1311(410.5) | 1402(353.5)
397 | 1211 | GTR | E&F DILSHAD GARDEN | DGN232 | TG-DGN232A-4 | DT-4 | DSIDC SUBSTATION NO-2 | 4 | 990 | 19504958 | 958 | 2019-06-15 10:30 | 318 | 1292 | 331 | 1345 | 310 | 1257 | 77 | 592 | 121 | 5 |  | 126 | 42% | 49% | 97% | 43% | 4.0223 | Loss 0-5% | 1281(190.5) | 1189(180.5) | 1188(153) | 1165(161) | 1377(128.5) | 1399(188)
398 | 1211 | GTR | E&F DILSHAD GARDEN | DGN233 | TG-DGN233A-1 | DT-1 | G Block Dilshad Colony ( Park Wala) | 1 | 990 | 19505277 | 1188.5711 | 2019-06-11 23:30 | 425.769 | 1889.0323 | 391.2125 | 1735.6368 | 371.5896 | 1640.4997 | 217.1977 | 499 | 143 | 47.5 | 29 | 219.5 | 114% | 81% | 86% | 120% | 4.4493 | Loss 0-5% |  |  | 1216(190) | 1136(158.5) | 911(98.5)
399 | 1211 | GTR | E&F DILSHAD GARDEN | DGN237 | TG-DGN237A-1 | DT-1 | B-42 JHILMIL IND AREA NEARRAILWAY LINE | 2 | 630 | 19505962 | 577 | 2019-06-21 10:30 | 188 | 811 | 190 | 823 | 200 | 868 | 52 | 687 | 32.5 | 0.5 |  | 33 | 34% | 36% | 92% | 39% | 3.0408 | Loss 0-5% | 698(41.5) | 768(243) | 766(103.5) | 625(87.5) | 587(90.5) | 604(113.5)
400 | 1211 | GTR | E&F DILSHAD GARDEN | DGN237 | TG-DGN237A-2 | DT-2 | B-42 JHILMIL IND AREA NEARRAILWAY LINE | 2 | 990 | 19505961 | 895 | 2019-06-19 11:00 | 298 | 1200 | 297 | 1199 | 300 | 1207 | 8 | 650 | 69.5 | 0.5 |  | 70 | 31% | 42% | 90% | 37% | 3.0408 | Loss 0-5% |  |  |  | 842(60) | 979(120.5) | 1062(213.5)
401 | 1211 | GTR | E&F DILSHAD GARDEN | DGN249 | TG-DGN249A-1 | DT-1 | Police Booth A BLK JLM IA | 1 | 990 | 19506423 | 956 | 2019-06-17 14:00 | 310 | 1320 | 328 | 1393 | 318 | 1354 | 63 | 558.5 | 157.5 | 2.5 |  | 160 | 52% | 58% | 97% | 50% | 2.329 | Loss 0-5%
402 | 1211 | GTR | E&F DILSHAD GARDEN | DGN252 | TG-DGN252A-1 | DT-1 | RAILWAY LINE IN FRONT OF B-43 JHILMIL | 1 | 990 | 19506619 | 1135 | 2019-06-08 18:00 | 375 | 1531 | 371 | 1519 | 390 | 1604 | 79 | 467 | 205.5 | 43.5 | 4 | 253 | 66% | 86% | 115% | 67% | 9.2448 | Loss 5-10%
403 | 1211 | GTR | E&F DILSHAD GARDEN | DGN254 | TG-DGN254A-2 | DT-2 | DAMODAR PARK S/S NO. 2 | 2 | 630 | 19506876 | 837 | 2019-06-10 12:30 | 279 | 1159 | 283 | 1173 | 275 | 1140 | 29 | 422 | 74.5 | 57 | 166.5 | 298 | 83% | 90% | 133% | 82% | 4.2761 | Loss 0-5%
404 | 1211 | GTR | GT ROAD SHAHDRA | DGN032 | TG-DGN032A-1 | DT-1 | J-Block MS Park Package Near Dispensary | 1 | 990 | 19501019 | 989 | 2019-06-11 | 349 | 1520 | 316 | 1375 | 324 | 1393 | 136 | 548 | 141 | 29.5 |  | 170.5 | 100% | 76% | 74% | 99% | 5.4789 | Loss 5-10% |  | 963(46.5) | 897(120.5) | 897(56)
405 | 1211 | GTR | GT ROAD SHAHDRA | DGN038 | TG-DGN038A-2 | DT-2 | MOTI RAM ROAD G.T.ROAD FLYOVER S/STN | 2 | 990 | 19501708 | 844 | 2019-06-29 23:30 | 250 | 1067 | 340 | 1478 | 254 | 1092 | 399 | 580 | 113 |  |  | 113 | 85% | 69% | 74% | 85% | 6.0809 | Loss 5-10% |  |  | 878(121.5) | 835(71.5)
406 | 1211 | GTR | GT ROAD SHAHDRA | DGN039 | TG-DGN039A-1 | DT-1 | MANSAROVER PARK MOTHER DAIRY | 3 | 990 | 19506343 | 907 | 2019-06-10 23:00 | 343 | 1513 | 315 | 1383 | 250 | 1089 | 376 | 593.5 | 122.5 | 2.5 |  | 125 | 91% | 71% | 69% | 92% | 4.0829 | Loss 0-5% |  | 955(107) | 930(83)
407 | 1211 | GTR | GT ROAD SHAHDRA | DGN039 | TG-DGN039A-2 | DT-2 | MANSAROVER PARK MOTHER DAIRY | 3 | 990 | 19506342 | 865.8276 | 2019-06-29 23:30 | 299.3608 | 1261.5289 | 319.1749 | 1346.3888 | 247.2919 | 1036.7329 | 277.1473 | 618 | 100 |  |  | 100 | 87% | 62% | 74% | 87% | 4.0829 | Loss 0-5% |  |  | 900(68.5)
408 | 1211 | GTR | GT ROAD SHAHDRA | DGN042 | TG-DGN042A-2 | DT-2 | MOTI RAM PEER WALA S/STN | 2 | 630 | 19505471 | 592 | 2019-06-11 | 93 | 411 | 286 | 1312 | 212 | 956 | 786 | 602.5 | 112.5 | 2 |  | 114.5 | 94% | 58% | 81% | 91% | 5.0023 | Loss 5-10%
409 | 1211 | GTR | GT ROAD SHAHDRA | DGN044 | TG-DGN044A-1 | DT-1 | JAISWAL MARG:PM | 2 | 990 | 19501798 | 866 | 2019-06-03 01:00 | 290 | 1185 | 278 | 1156 | 298 | 1232 | 67 | 650.5 | 68 |  |  | 68 | 87% | 52% | 58% | 86% | 5.8442 | Loss 5-10%
410 | 1211 | GTR | GT ROAD SHAHDRA | DGN044 | TG-DGN044A-2 | DT-2 | JAISWAL MARG:PM | 2 | 630 | 19506422 | 504 | 2019-06-03 00:30 | 189 | 784 | 176 | 730 | 139 | 567 | 196 | 672 | 46 |  |  | 46 | 80% | 54% | 75% | 78% | 5.8442 | Loss 5-10%
411 | 1211 | GTR | GT ROAD SHAHDRA | DGN045 | TG-DGN045A-1 | DT-1 | MANDOLI ROAD:PL | 2 | 990 | 19501758 | 921 | 2019-06-30 23:30 | 346 | 1489 | 257 | 1094 | 319 | 1349 | 347 | 212.5 | 38.5 | 2 |  | 40.5 | 90% | 59% | 75% | 93% | 7.5003 | Loss 5-10% |  | 865(36.5) | 998(102.5) | 838(28.5)
412 | 1211 | GTR | GT ROAD SHAHDRA | DGN046 | TG-DGN046A-1 | DT-1 | RAM NAGAR SCHOOL:PL | 2 | 990 | 19501705 | 1481 | 2019-06-11 23:30 | 549 | 2221 | 434 | 1779 | 498 | 2044 | 385 | 224.5 | 246.5 | 61.5 | 186.5 | 494.5 | 148% | 93% | 105% | 150% | 8.7649 | Loss 5-10% |  | 1005(79.5) | 1206(166) | 997(89.5) | 921(74.5)
413 | 1211 | GTR | GT ROAD SHAHDRA | DGN047 | TG-DGN047A-1 | DT-1 | BHAGWANPUR KHERA NO-1:PL | 1 | 990 | 19500681 | 1004 | 2019-06-09 23:30 | 318 | 1357 | 322 | 1393 | 364 | 1564 | 191 | 547 | 152.5 | 19.5 | 0.5 | 172.5 | 95% | 68% | 75% | 101% | 7.8723 | Loss 5-10% |  | 799(34) | 941(137) | 926(84) | 817(42)
414 | 1211 | GTR | GT ROAD SHAHDRA | DGN049 | TG-DGN049A-1 | DT-1 | BHAGWANPUR KHERA NO-3:PL | 1 | 990 | 19506736 | 1058 | 2019-06-29 23:30 | 342 | 1487 | 388 | 1694 | 328 | 1426 | 243 | 178 | 58 | 14 | 3 | 75 | 104% | 66% | 93% | 107% | 6.1923 | Loss 5-10% |  | 912(75) |  |  | 858(70)
415 | 1211 | GTR | GT ROAD SHAHDRA | DGN050 | TG-DGN050A-1 | DT-1 | NEW MODERN SHAHDRA NO I GALI NO 13:PL | 2 | 990 | 19505901 | 966 | 2019-06-08 01:30 | 307 | 1384 | 299 | 1345 | 360 | 1626 | 263 | 626 | 89 | 4.5 |  | 93.5 | 98% | 63% | 67% | 94% | 5.4409 | Loss 5-10% |  | 845(33.5) | 1025(111) | 849(57.5) | 807(29.5)
416 | 1211 | GTR | GT ROAD SHAHDRA | DGN051 | TG-DGN051A-1 | DT-1 | NEW MODERN SHAHDARA NO 2 GALI NO7,8 | 2 | 990 | 19505900 | 947.9923 | 2019-06-08 00:30 | 179.0657 | 780.1066 | 238.6608 | 1018.786 | 530.2659 | 2188.8297 | 1305.8466 | 649.5 | 60.5 | 4 |  | 64.5 | 96% | 55% | 68% | 93% | 4.8269 | Loss 0-5% |  | 814(31) | 997(87) | 883(43)
417 | 1211 | GTR | GT ROAD SHAHDRA | DGN052 | TG-DGN052A-2 | DT-2 | SUBHASH MARG NEW MODERN SHAHDARA:PL | 2 | 990 | 19505898 | 949 | 2019-06-11 23:30 | 266 | 1103 | 328 | 1395 | 355 | 1536 | 382 | 607.5 | 107.5 | 5 |  | 112.5 | 95% | 60% | 76% | 96% | 4.1816 | Loss 0-5% |  | 885(28.5) | 957(66) | 883(35.5)
418 | 1211 | GTR | GT ROAD SHAHDRA | DGN074 | TG-DGN074A-1 | DT-1 | RAJ ENGG.COMPOUND | 2 | 990 | 19501787 | 1072 | 2019-06-23 11:00 | 355 | 1456 | 361 | 1490 | 355 | 1455 | 34 | 500 | 194.5 | 23.5 | 1.5 | 219.5 | 68% | 64% | 108% | 69% | 4.7376 | Loss 0-5% |  |  |  |  | 858(53) | 993(154)
419 | 1211 | GTR | GT ROAD SHAHDRA | DGN075 | TG-DGN075A-1 | DT-1 | PAPER PRODUCT | 2 | 990 | 19505761 | 1026 | 2019-06-23 11:00 | 350 | 1525 | 342 | 1487 | 334 | 1446 | 69 | 566.5 | 138 | 11.5 | 0.5 | 150 | 45% | 61% | 104% | 51% | 3.2598 | Loss 0-5% |  | 923(84.5) | 951(124) | 987(80.5) | 906(98.5) | 1010(169.5)
420 | 1211 | GTR | GT ROAD SHAHDRA | DGN105 | TG-DGN105A-1 | DT-1 | SHAMBU NATH COMP.(F.COL):ID | 5 | 990 | 19505392 | 1187 | 2019-06-02 14:00 | 391 | 1784 | 392 | 1792 | 404 | 1842 | 54 | 425 | 191 | 67 | 36 | 294 | 81% | 82% | 120% | 82% | 4.2685 | Loss 0-5% |  |  |  | 1133(56.5) | 1322(248)
421 | 1211 | GTR | GT ROAD SHAHDRA | DGN105 | TG-DGN105A-2 | DT-2 | SHAMBU NATH COMP.(F.COL):ID | 5 | 990 | 19505488 | 914 | 2019-06-09 16:00 | 299 | 1346 | 304 | 1362 | 311 | 1404 | 52 | 660 | 59.5 | 0.5 |  | 60 | 58% | 64% | 92% | 59% | 4.2685 | Loss 0-5% | 975(161.5) | 1040(198) | 1029(232.5) | 1018(214.5) | 1073(220)
422 | 1211 | GTR | GT ROAD SHAHDRA | DGN105 | TG-DGN105A-3 | DT-3 | SHAMBU NATH COMP.(F.COL):ID | 5 | 990 | 19505434 | 1021 | 2019-06-26 11:00 | 332 | 1421 | 336 | 1422 | 354 | 1509 | 87 | 645 | 65.5 | 4.5 | 2 | 72 | 54% | 65% | 103% | 56% | 4.2685 | Loss 0-5% | 1141(229) | 1027(170) | 1123(230) | 1108(233.5) | 1117(240.5) | 1259(357.5)
423 | 1211 | GTR | GT ROAD SHAHDRA | DGN105 | TG-DGN105A-4 | DT-4 | SHAMBU NATH COMP.(F.COL):ID | 5 | 990 | 19505076 | 856 | 2019-06-24 15:00 | 279 | 1139 | 292 | 1193 | 285 | 1158 | 48 | 600 | 120 |  |  | 120 | 39% | 43% | 86% | 42% | 4.2685 | Loss 0-5% | 845(34.5) | 807(38) | 815(32.5) | 939(121.5) | 915(136.5) | 987(165)
424 | 1211 | GTR | GT ROAD SHAHDRA | DGN110 | TG-DGN110A-1 | DT-1 | VERMA CASTLE:PL | 6 | 990 | 19503035 | 1150 | 2019-06-01 12:00 | 370 | 1470 | 374 | 1500 | 406 | 1636 | 153 | 581 | 76.5 | 19 | 10 | 105.5 | 44% | 73% | 116% | 41% | 3.7951 | Loss 0-5% | 1022(172.5) | 1129(224) | 1229(245) | 1240(166.5) | 1231(140.5) | 1336(204)
425 | 1211 | GTR | GT ROAD SHAHDRA | DGN110 | TG-DGN110A-2 | DT-2 | VERMA CASTLE:PL | 6 | 990 | 19506744 | 974.8176 | 2019-06-02 11:00 | 328.8769 | 1448.0951 | 333.0491 | 1462.6022 | 312.8916 | 1359.3345 | 96.8326 | 593 | 109.5 | 3.5 |  | 113 | 59% | 58% | 98% | 42% | 3.7951 | Loss 0-5% | 900(37) | 988(105.5) | 1004(97.5) | 1007(104) | 1166(128.5) | 1151(110)
426 | 1211 | GTR | GT ROAD SHAHDRA | DGN110 | TG-DGN110A-3 | DT-3 | VERMA CASTLE:PL | 6 | 630 | 19505004 | 552 | 2019-06-26 16:00 | 185 | 766 | 179 | 741 | 188 | 781 | 35 | 645.5 | 63.5 |  |  | 63.5 | 32% | 42% | 88% | 33% | 3.7951 | Loss 0-5% | 579(79) | 596(82) | 648(155) | 600(136) | 631(149.5) | 653(182.5)
427 | 1211 | GTR | GT ROAD SHAHDRA | DGN110 | TG-DGN110A-5 | DT-5 | VERMA CASTLE:PL | 6 | 990 | 19506053 | 1118 | 2019-06-23 12:30 | 376 | 1606 | 369 | 1588 | 373 | 1608 | 19 | 502.5 | 145.5 | 52 | 17 | 214.5 | 57% | 52% | 113% | 57% | 3.7951 | Loss 0-5% | 1010(145.5) | 945(86) | 907(108.5) | 1167(185) | 1211(166)
428 | 1211 | GTR | GT ROAD SHAHDRA | DGN110 | TG-DGN110A-6 | DT-6 | VERMA CASTLE:PL | 6 | 990 | 19501793 | 991 | 2019-06-17 11:30 | 329 | 1310 | 327 | 1305 | 335 | 1335 | 27 | 561 | 128.5 | 26 | 0.5 | 155 | 48% | 84% | 100% | 48% | 3.7951 | Loss 0-5%
429 | 1211 | GTR | GT ROAD SHAHDRA | DGN111 | TG-DGN111A-1 | DT-1 | FRIENDS COLONY GALI NO.1 | 3 | 990 | 19500654 | 883 | 2019-06-23 12:00 | 295 | 1206 | 299 | 1220 | 290 | 1179 | 37 | 576.5 | 142 |  |  | 142 | 40% | 49% | 89% | 58% | 5.5303 | Loss 5-10% | 828(41.5) |  | 879(30.5) | 836(26.5) | 968(107.5) | 996(126)
430 | 1211 | GTR | GT ROAD SHAHDRA | DGN111 | TG-DGN111A-3 | DT-3 | FRIENDS COLONY GALI NO.1 | 3 | 990 | 19505689 | 867 | 2019-06-28 11:30 | 284 | 1152 | 287 | 1164 | 295 | 1206 | 50 | 688 | 30.5 |  |  | 30.5 | 62% | 61% | 88% | 64% | 5.5303 | Loss 5-10%
431 | 1211 | GTR | GT ROAD SHAHDRA | DGN120 | TG-DGN120A-1 | DT-1 | GALI NO.3 FRIENDS COLONY:PL | 2 | 990 | 19503629 | 1010 | 2019-06-24 11:30 | 339 | 1398 | 341 | 1410 | 330 | 1355 | 50 | 482 | 201.5 | 34.5 | 2 | 238 | 52% | 55% | 102% | 57% | 6.5453 | Loss 5-10% | [5 empty] | 949(156)
432 | 1211 | GTR | GT ROAD SHAHDRA | DGN127 | TG-DGN127A-2 | DT-2 | GALI NO.1B FRIENDS COLONY:PL | 4 | 990 | 19504119 | 889 | 2019-06-27 16:30 | 283 | 1211 | 317 | 1351 | 290 | 1240 | 128 | 622 | 98 |  |  | 98 | 35% | 43% | 90% | 38% | 2.8373 | Loss 0-5% | 904(28.5) | 893(48.5) | 831(33) | 899(55) | 975(121.5) | 976(179)
433 | 1211 | GTR | GT ROAD SHAHDRA | DGN127 | TG-DGN127A-3 | DT-3 | GALI NO.1B FRIENDS COLONY:PL | 4 | 990 | 19505853 | 939 | 2019-06-27 15:30 | 319 | 1375 | 317 | 1364 | 303 | 1313 | 57 | 612.5 | 105 | 2.5 |  | 107.5 | 61% | 48% | 95% | 57% | 2.8373 | Loss 0-5% | 926(69.5) | 918(78) | 947(105.5) |  | 1003(109.5) | 1010(127.5)
434 | 1211 | GTR | GT ROAD SHAHDRA | DGN129 | TG-DGN129A-2 | DT-2 | FRIENDS COLONY GALI NO-5-6 NEAR RLY.LINE:PM | 6 | 990 | 19506017 | 1201 | 2019-06-21 12:00 | 412 | 1798 | 399 | 1728 | 390 | 1703 | 86 | 480 | 108 | 63 | 66 | 237 | 45% | 64% | 121% | 44% | 4.5058 | Loss 0-5% | 1126(178.5) |  | 1149(214) | 1209(239.5) | 1193(66.5) | 1345(44.5)
435 | 1211 | GTR | GT ROAD SHAHDRA | DGN129 | TG-DGN129A-4 | DT-4 | FRIENDS COLONY GALI NO-5-6 NEAR RLY.LINE:PM | 6 | 990 | 19505079 | 1131 | 2019-06-27 15:00 | 377 | 1525 | 375 | 1505 | 379 | 1526 | 20 | 471.5 | 130.5 | 82 | 36 | 248.5 | 53% | 60% | 114% | 58% | 4.5058 | Loss 0-5% | 841(29) | 894(68.5) | 876(45) | 1070(69) | 979(87) | 984(137)
436 | 1211 | GTR | GT ROAD SHAHDRA | DGN129 | TG-DGN129A-6 | DT-6 | FRIENDS COLONY GALI NO-5-6 NEAR RLY.LINE:PM | 6 | 990 | 19506813 | 1099 | 2019-06-22 11:30 | 360 | 1558 | 380 | 1644 | 359 | 1560 | 85 | 505.5 | 162.5 | 42 | 10 | 214.5 | 53% | 65% | 111% | 54% | 4.5058 | Loss 0-5%
437 | 1211 | GTR | GT ROAD SHAHDRA | DGN131 | TG-DGN131A-1 | DT-1 | GALI NO.1A FRIENDS COLONY UNDER FLYOVER: PL | 2 | 990 | 19504318 | 1141 | 2019-06-19 15:00 | 384 | 1607 | 370 | 1545 | 387 | 1621 | 70 | 600 | 113 | 3 | 4 | 120 | 46% | 61% | 115% | 49% | 5.5513 | Loss 5-10% |  |  | 1142(43.5) | 1180(134.5) | 1272(111) | 1256(182.5)
438 | 1211 | GTR | GT ROAD SHAHDRA | DGN131 | TG-DGN131A-2 | DT-2 | GALI NO.1A FRIENDS COLONY UNDER FLYOVER: PL | 2 | 630 | 19504366 | 554 | 2019-06-12 12:00 | 174 | 729 | 187 | 788 | 193 | 816 | 76 | 628 | 92 |  |  | 92 | 45% | 54% | 88% | 47% | 5.5513 | Loss 5-10%
439 | 1211 | GTR | GT ROAD SHAHDRA | DGN178 | TG-DGN178A-1 | DT-1 | HANSRAJ COMPOUND S/STN | 4 | 990 | 19505895 | 980 | 2019-06-01 15:00 | 344 | 1472 | 325 | 1392 | 311 | 1341 | 115 | 569 | 149.5 | 1 |  | 150.5 | 47% | 50% | 99% | 49% | 4.4256 | Loss 0-5% | 927(92.5) | 931(75.5) | 1033(201.5) | 1045(200) | 1084(149)
440 | 1211 | GTR | GT ROAD SHAHDRA | DGN178 | TG-DGN178A-3 | DT-3 | HANSRAJ COMPOUND S/STN | 4 | 630 | 19503413 | 701 | 2019-06-29 12:00 | 247 | 982 | 239 | 945 | 215 | 852 | 116 | 486.5 | 142.5 | 72 | 17 | 231.5 | 41% | 51% | 111% | 58% | 4.4256 | Loss 0-5%
441 | 1211 | GTR | GT ROAD SHAHDRA | DGN178 | TG-DGN178A-4 | DT-4 | HANSRAJ COMPOUND S/STN | 4 | 990 | 19505688 | 915 | 2019-06-07 16:00 | 294 | 1259 | 316 | 1359 | 304 | 1298 | 87 | 620.5 | 98 | 1 |  | 99 | 34% | 38% | 92% | 35% | 4.4256 | Loss 0-5%
442 | 1211 | GTR | GT ROAD SHAHDRA | DGN198 | TG-DGN198A-1 | DT-1 | GALI NO-1 METRO PARKING SS-2 | 3 | 990 | 19506421 | 1183 | 2019-06-28 14:30 | 393 | 1723 | 392 | 1717 | 397 | 1737 | 18 | 442.5 | 120.5 | 81 | 69.5 | 271 | 81% | 94% | 119% | 84% | 5.8289 | Loss 5-10%
443 | 1211 | GTR | GT ROAD SHAHDRA | DGN198 | TG-DGN198A-2 | DT-2 | GALI NO-1 METRO PARKING SS-2 | 3 | 990 | 19506921 | 1082 | 2019-06-20 16:00 | 351 | 1527 | 372 | 1631 | 359 | 1567 | 91 | 184.5 | 66.5 | 20.5 | 4 | 91 | 38% | 57% | 109% | 42% | 5.8289 | Loss 5-10% | 897(26.5) | 934(69) |  | 875(83.5) | 886(59) | 1036(125.5)
444 | 1211 | GTR | GT ROAD SHAHDRA | DGN198 | TG-DGN198A-3 | DT-3 | GALI NO-1 METRO PARKING SS-2 | 3 | 990 | 19504954 | 994 | 2019-06-27 12:30 | 334 | 1384 | 327 | 1343 | 333 | 1382 | 40 | 489 | 191.5 | 37 | 0.5 | 229 | 67% | 63% | 100% | 66% | 5.8289 | Loss 5-10%
445 | 1211 | GTR | GT ROAD SHAHDRA | DGN231 | TG-DGN231A-1 | DT-1 | GALI NO-1 RAILWAY LINE FRIENDS COLONY | 2 | 990 | 19504996 | 916 | 2019-06-20 16:00 | 294 | 1256 | 306 | 1305 | 316 | 1349 | 80 | 522 | 186.5 | 6.5 |  | 193 | 44% | 48% | 93% | 43% | 6.6913 | Loss 5-10% | [5 empty] | 1029(114)
446 | 1211 | GTR | GT ROAD SHAHDRA | DGN231 | TG-DGN231A-2 | DT-2 | GALI NO-1 RAILWAY LINE FRIENDS COLONY | 2 | 630 | 19506054 | 696 | 2019-06-07 11:30 | 231 | 989 | 235 | 1006 | 230 | 979 | 23 | 487 | 169.5 | 50 | 8 | 227.5 | 78% | 80% | 110% | 76% | 6.6913 | Loss 5-10% | 567(66) | 745(104.5) | 678(164) | 671(154.5) | 655(217) | 725(256)
447 | 1211 | GTR | GT ROAD SHAHDRA | DGN236 | TG-DGN236A-1 | DT-1 | 1B Friends colony near railway line. | 1 | 990 | 19505054 | 893 | 2019-06-24 14:30 | 307 | 1246 | 301 | 1221 | 285 | 1156 | 81 | 602.5 | 117 | 0.5 |  | 117.5 | 46% | 55% | 90% | 48% | 6.8449 | Loss 5-10% | 709(127.5) | 752(190) | 760(191.5) | 728(183) | 716(131) | 776(220.5)
448 | 1211 | GTR | GT ROAD SHAHDRA | DGN255 | TG-DGN255A-1 | DT-1 | GALI NO. 00 FRIENDS COLONY(THAKUR WALA) | 1 | 990 | 19506892 | 967 | 2019-06-24 17:00 | 329 | 1379 | 317 | 1331 | 321 | 1337 | 46 | 603.5 | 112 | 2 |  | 114 | 47% | 57% | 98% | 48% | 5.1 | Loss 5-10%
449 | 1211 | GTR | ZAFFRABAD | DGN001 | TG-DGN001A-1 | DT-1 | ZAFRABAD AE OFFICE | 1 | 990 | 19501728 | 925 | 2019-06-30 01:30 | 349 | 1428 | 339 | 1403 | 237 | 969 | 447 | 587.5 | 128.5 | 4 |  | 132.5 | 93% | 74% | 67% | 88% | 5.3432 | Loss 5-10% |  | 789(41) | 862(134) | 876(76)
450 | 1211 | GTR | ZAFFRABAD | DGN002 | TG-DGN002A-2 | DT-2 | ZAFRABAD CONSTRUCTION OFFICE:ID | 3 | 990 | 19505261 | 1011 | 2019-06-03 00:30 | 311 | 1351 | 291 | 1255 | 410 | 1762 | 467 | 686 | 22.5 | 8 | 1.5 | 32 | 102% | 74% | 75% | 96% | 8.0384 | Loss 5-10% |  | 1017(120) | 1095(219) | 875(77) | 875(109)
451 | 1211 | GTR | ZAFFRABAD | DGN003 | TG-DGN003A-1 | DT-1 | NAV DURGA MANDIR | 3 | 990 | 19501845 | 819 | 2019-06-11 23:30 | 318 | 1296 | 213 | 868 | 289 | 1181 | 383 | 681.5 | 38 |  |  | 38 | 82% | 49% | 53% | 83% | 6.7313 | Loss 5-10% |  | 1150(134.5) | 1297(273.5)
452 | 1211 | GTR | ZAFFRABAD | DGN003 | TG-DGN003A-2 | DT-2 | NAV DURGA MANDIR | 3 | 990 | 19506346 | 1091 | 2019-06-11 | 352 | 1486 | 417 | 1785 | 322 | 1353 | 383 | 493.5 | 136.5 | 62.5 | 27.5 | 226.5 | 110% | 73% | 76% | 110% | 6.7313 | Loss 5-10% | 1099(69)
453 | 1211 | GTR | ZAFFRABAD | DGN003 | TG-DGN003A-3 | DT-3 | NAV DURGA MANDIR | 3 | 630 | 19506487 | 511 | 2019-06-30 23:30 | 203 | 870 | 138 | 584 | 170 | 721 | 248 | 674.5 | 45.5 |  |  | 45.5 | 79% | 54% | 56% | 81% | 6.7313 | Loss 5-10% |  |  | 574(34.5)
454 | 1211 | GTR | ZAFFRABAD | DGN004 | TG-DGN004A-1 | DT-1 | GORAKH PARK NALA (ASHOK WALA) | 1 | 630 | 19504422 | 550 | 2019-06-10 23:30 | 235 | 1064 | 158 | 703 | 157 | 708 | 359 | 667 | 53 |  |  | 53 | 87% | 57% | 66% | 87% | 3.3467 | Loss 0-5% |  |  | 552(68)
455 | 1211 | GTR | ZAFFRABAD | DGN008 | TG-DGN008A-1 | DT-1 | SUBHASH PARK CHAND RAM | 1 | 990 | 19506345 | 1071 | 2019-06-30 23:30 | 349 | 1446 | 349 | 1455 | 373 | 1556 | 106 | 311 | 298 | 82.5 | 28.5 | 409 | 107% | 85% | 96% | 108% | 4.0856 | Loss 0-5% | 851(42) | 1047(264.5) | 1112(458.5) | 1013(229.5) | 1012(347.5) | 890(105.5)
456 | 1211 | GTR | ZAFFRABAD | DGN009 | TG-DGN009A-1 | DT-1 | SUBHASH PARK ICE FACTORY | 2 | 990 | 19501797 | 961 | 2019-06-12 01:30 | 319 | 1305 | 247 | 997 | 395 | 1630 | 548 | 577 | 133 | 10 |  | 143 | 97% | 61% | 74% | 95% | 4.3033 | Loss 0-5% |  | 798(24) | 937(86)
457 | 1211 | GTR | ZAFFRABAD | DGN009 | TG-DGN009A-2 | DT-2 | SUBHASH PARK ICE FACTORY | 2 | 990 | 19506593 | 816 | 2019-06-08 02:30 | 200 | 795 | 448 | 1901 | 167 | 682 | 1166 | 671.5 | 48.5 |  |  | 48.5 | 82% | 52% | 61% | 82% | 4.3033 | Loss 0-5% |  | 820(27) | 889(60)
458 | 1211 | GTR | ZAFFRABAD | DGN010 | TG-DGN010A-1 | DT-1 | PANCH SHEEL PARK (JHULE WALA):K | 3 | 990 | 19501710 | 1071 | 2019-06-12 | 408 | 1650 | 398 | 1585 | 266 | 1060 | 560 | 519.5 | 119 | 52 | 29 | 200 | 108% | 70% | 75% | 108% | 3.9722 | Loss 0-5% |  | 1027(106) | 1163(207) | 936(34) | 889(72.5)
459 | 1211 | GTR | ZAFFRABAD | DGN010 | TG-DGN010A-2 | DT-2 | PANCH SHEEL PARK (JHULE WALA):K | 3 | 990 | 19505472 | 1195 | 2019-06-11 01:00 | 321 | 1387 | 498 | 2201 | 376 | 1611 | 728 | 504 | 121 | 52 | 42.5 | 215.5 | 121% | 69% | 84% | 117% | 3.9722 | Loss 0-5% |  | 1032(90) | 1076(185) | 974(59) | 915(102.5)
460 | 1211 | GTR | ZAFFRABAD | DGN011 | TG-DGN011A-1 | DT-1 | H-BLOCK NAVEEN SHAHDARA:PL | 4 | 990 | 19501828 | 811 | 2019-06-03 | 267 | 1154 | 242 | 1054 | 302 | 1323 | 236 | 564.5 | 25 |  |  | 25 | 82% | 55% | 63% | 82% | 2.9524 | Loss 0-5%
461 | 1211 | GTR | ZAFFRABAD | DGN011 | TG-DGN011A-3 | DT-3 | H-BLOCK NAVEEN SHAHDARA:PL | 4 | 990 | 19505334 | 866 | 2019-06-01 01:00 | 285 | 1139 | 258 | 1035 | 323 | 1285 | 218 | 650.5 | 66.5 |  |  | 66.5 | 87% | 51% | 61% | 84% | 2.9524 | Loss 0-5% |  |  | 860(55)
462 | 1211 | GTR | ZAFFRABAD | DGN011 | TG-DGN011A-4 | DT-4 | H-BLOCK NAVEEN SHAHDARA:PL | 4 | 630 | 19506255 | 666 | 2019-06-12 | 286 | 1238 | 219 | 929 | 161 | 682 | 483 | 614 | 95 | 7 | 1 | 103 | 106% | 65% | 78% | 93% | 2.9524 | Loss 0-5%
463 | 1211 | GTR | ZAFFRABAD | DGN012 | TG-DGN012A-1 | DT-1 | MOHAN PARK | 2 | 990 | 19505755 | 1057 | 2019-06-09 | 294 | 1252 | 387 | 1682 | 377 | 1645 | 412 | 529.5 | 137 | 45.5 | 6.5 | 189 | 107% | 69% | 87% | 106% | 4.9652 | Loss 0-5% | 1062(66) | 1362(301.5) | 1420(462) | 1333(327) | 1095(44)
464 | 1211 | GTR | ZAFFRABAD | DGN012 | TG-DGN012A-2 | DT-2 | MOHAN PARK | 2 | 400 | 19506546 | 449 | 2019-06-11 23:30 | 149 | 623 | 112 | 459 | 189 | 801 | 296 | 519.5 | 135.5 | 52.5 | 11.5 | 199.5 | 107% | 66% | 88% | 112% | 4.9652 | Loss 0-5%
465 | 1211 | GTR | ZAFFRABAD | DGN013 | TG-DGN013A-2 | DT-2 | K-BLOCK NAVEEN SHAHDARA:PL | 2 | 630 | 19506402 | 495 | 2019-06-13 22:30 | 123 | 530 | 220 | 958 | 151 | 657 | 381 | 694 | 26 |  |  | 26 | 78% | 46% | 56% | 79% | 5.5503 | Loss 5-10%
466 | 1211 | GTR | ZAFFRABAD | DGN014 | TG-DGN014A-2 | DT-2 | LONI ROAD KHATTEWALA:PL | 2 | 630 | 19505770 | 622 | 2019-06-04 23:30 | 199 | 832 | 133 | 542 | 289 | 1213 | 582 | 513 | 176 | 31 |  | 207 | 96% | 64% | 75% | 99% | 5.2176 | Loss 5-10% |  | 602(87.5) | 733(219) | 836(147.5) | 621(93)
467 | 1211 | GTR | ZAFFRABAD | DGN018 | TG-DGN018A-2 | DT-2 | R. BLOCK NAVEEN SHAHDARA:PL | 2 | 630 | 19505754 | 481 | 2019-06-12 | 118 | 487 | 248 | 1048 | 114 | 475 | 568 | 690.5 | 27.5 |  |  | 27.5 | 76% | 45% | 60% | 74% | 7.0892 | Loss 5-10% |  | 625(88) | 709(182.5) | 654(46)
468 | 1211 | GTR | ZAFFRABAD | DGN019 | TG-DGN019A-1 | DT-1 | KABOOL NAGAR KIOSK | 2 | 990 | 19506055 | 949 | 2019-06-02 23:30 | 268 | 1125 | 256 | 1090 | 425 | 1843 | 736 | 591 | 126.5 | 2 |  | 128.5 | 93% | 71% | 81% | 96% | 7.7523 | Loss 5-10% |  |  | 930(90.5)
469 | 1211 | GTR | ZAFFRABAD | DGN020 | TG-DGN020A-2 | DT-2 | KABOOL NAGAR MOTHER DAIRY:PL | 2 | 990 | 19506492 | 967 | 2019-06-12 | 359 | 1507 | 296 | 1234 | 311 | 1289 | 250 | 567.5 | 132 | 20.5 |  | 152.5 | 98% | 63% | 73% | 97% | 3.1479 | Loss 0-5% |  |  | 933(80.5)
470 | 1211 | GTR | ZAFFRABAD | DGN021 | TG-DGN021A-1 | DT-1 | KABOOL NAGAR RAIN BASERA:PM | 2 | 630 | 19506755 | 629 | 2019-06-27 01:00 | 102 | 407 | 324 | 1341 | 203 | 833 | 810 | 543.5 | 167.5 | 3 |  | 170.5 | 100% | 61% | 88% | 95% | 7.9972 | Loss 5-10%
471 | 1211 | GTR | ZAFFRABAD | DGN022 | TG-DGN022A-1 | DT-1 | SHAHI MOHALLA:K | 4 | 990 | 19504163 | 875 | 2019-06-01 23:30 | 321 | 1342 | 343 | 1422 | 212 | 871 | 515 | 600 | 116 |  |  | 116 | 88% | 53% | 81% | 88% | 5.0084 | Loss 5-10%
472 | 1211 | GTR | ZAFFRABAD | DGN022 | TG-DGN022A-2 | DT-2 | SHAHI MOHALLA:K | 4 | 990 | 19501765 | 973 | 2019-06-30 | 367 | 1597 | 307 | 1324 | 299 | 1294 | 289 | 585 | 118.5 | 14 |  | 132.5 | 98% | 67% | 72% | 97% | 5.0084 | Loss 5-10% |  |  | 867(73)
473 | 1211 | GTR | ZAFFRABAD | DGN022 | TG-DGN022A-4 | DT-4 | SHAHI MOHALLA:K | 4 | 630 | 19503146 | 548 | 2019-06-02 22:00 | 208 | 915 | 179 | 786 | 161 | 705 | 183 | 684.5 | 32.5 |  |  | 32.5 | 79% | 51% | 84% | 87% | 5.0084 | Loss 5-10%
474 | 1211 | GTR | ZAFFRABAD | DGN023 | TG-DGN023A-1 | DT-1 | SHIVAJI PARK ARYA SAMAJ MANDIR | 1 | 1600 | 19501792 | 1612 | 2019-06-11 00:30 | 534 | 2155 | 471 | 1903 | 606 | 2441 | 466 | 607 | 106.5 | 2.5 | 0.5 | 109.5 | 101% | 63% | 64% | 88% | 4.6009 | Loss 0-5% | 902(25.5) | 1241(228) | 1325(237) |  |  | 911(34.5)
475 | 1211 | GTR | ZAFFRABAD | DGN024 | TG-DGN024A-1 | DT-1 | GORAKH PARK HANUMAN MANDIR PM | 1 | 400 | 19502520 | 363 | 2019-06-02 21:00 | 114 | 472 | 122 | 509 | 127 | 531 | 52 | 512.5 | 206.5 | 1 |  | 207.5 | 81% | 51% | 90% | 91% | 2.7036 | Loss 0-5% |  |  |  |  | 373(113.5)
476 | 1211 | GTR | ZAFFRABAD | DGN025 | TG-DGN025A-2 | DT-2 | GORAKH PARK KISOK:K | 4 | 990 | 19505562 | 969 | 2019-06-12 | 358 | 1441 | 325 | 1314 | 285 | 1152 | 251 | 570 | 129 | 20.5 |  | 149.5 | 98% | 67% | 67% | 98% | 5.6429 | Loss 5-10% |  | 1036(36.5) | 946(122.5) | 810(28.5) | 761(26.5)
477 | 1211 | GTR | ZAFFRABAD | DGN025 | TG-DGN025A-4 | DT-4 | GORAKH PARK KISOK:K | 4 | 630 | 19504758 | 683 | 2019-06-11 23:30 | 257 | 1080 | 212 | 884 | 213 | 881 | 198 | 538 | 127.5 | 42 | 12.5 | 182 | 105% | 66% | 71% | 108% | 5.6429 | Loss 5-10% |  |  | 763(144) | 569(27) | 550(69.5)
478 | 1211 | GTR | ZAFFRABAD | DGN026 | TG-DGN026A-1 | DT-1 | BALBIR NAGA NALA GALI NO.14:PL | 2 | 990 | 19505547 | 1089 | 2019-06-12 | 339 | 1353 | 355 | 1411 | 394 | 1589 | 214 | 501.5 | 134 | 53 | 31.5 | 218.5 | 110% | 68% | 92% | 110% | 4.5736 | Loss 0-5% |  |  | 1168(131) | 1087(152) | 989(112)
479 | 1211 | GTR | ZAFFRABAD | DGN027 | TG-DGN027A-1 | DT-1 | BALBIR NAGAR NALA GALI NO. 16:PL | 1 | 990 | 19505217 | 1179 | 2019-06-06 22:30 | 352 | 1509 | 387 | 1639 | 439 | 1929 | 372 | 498.5 | 123.5 | 59.5 | 38.5 | 221.5 | 117% | 75% | 85% | 119% | 7.4796 | Loss 5-10% |  | 886(28.5) | 1139(161) | 967(94.5) | 833(46.5)
480 | 1211 | GTR | ZAFFRABAD | DGN028 | TG-DGN028A-1 | DT-1 | BALBIR NAGAR NALA GALI.4 GORAKH PUR:PL | 2 | 990 | 19506685 | 951 | 2019-06-29 23:30 | 247 | 1058 | 356 | 1553 | 349 | 1520 | 480 | 615 | 99.5 | 5 |  | 104.5 | 94% | 58% | 60% | 96% | 6.7345 | Loss 5-10% |  | 866(44.5) | 1055(118)
481 | 1211 | GTR | ZAFFRABAD | DGN028 | TG-DGN028A-2 | DT-2 | BALBIR NAGAR NALA GALI.4 GORAKH PUR:PL | 2 | 630 | 19505945 | 605 | 2019-06-11 00:30 | 209 | 857 | 160 | 652 | 236 | 968 | 278 | 648 | 70.5 | 1 |  | 71.5 | 96% | 54% | 60% | 90% | 6.7345 | Loss 5-10%
482 | 1211 | GTR | ZAFFRABAD | DGN029 | TG-DGN029A-1 | DT-1 | BEHAL GALI | 1 | 990 | 19506361 | 1221 | 2019-06-06 22:00 | 332 | 1467 | 501 | 2295 | 387 | 1711 | 736 | 439 | 154 | 60.5 | 66.5 | 281 | 117% | 76% | 80% | 123% | 4.7932 | Loss 0-5% |  | 986(81.5) | 1072(193.5) | 875(57) | 871(95.5)
483 | 1211 | GTR | ZAFFRABAD | DGN030 | TG-DGN030A-1 | DT-1 | BALBIR NAGAR EXTN. 60 F ROAD:PM:PL | 2 | 990 | 19505863 | 1159.4614 | 2019-06-11 23:00 | 355.9034 | 1529.1233 | 403.4672 | 1734.4477 | 400.0907 | 1734.7732 | 205.4873 | 459 | 144 | 58.5 | 54 | 256.5 | 114% | 75% | 99% | 117% | 4.0457 | Loss 0-5% |  |  |  | 1162(132) | 995(118)
484 | 1211 | GTR | ZAFFRABAD | DGN030 | TG-DGN030A-2 | DT-2 | BALBIR NAGAR EXTN. 60 F ROAD:PM:PL | 2 | 630 | 19505007 | 840 | 2019-06-29 04:30 | 234 | 998 | 302 | 1315 | 304 | 1314 | 316 | 547.5 | 124 | 37.5 | 7 | 168.5 | 133% | 115% | 80% | 103% | 4.0457 | Loss 0-5% | 621(41) | 786(201) | 918(145.5) | 566(44.5) | 509(26)
485 | 1211 | GTR | ZAFFRABAD | DGN031 | TG-DGN031A-1 | DT-1 | BALBIR NAGAR SCHOOL:K | 3 | 990 | 19506056 | 1328 | 2019-06-30 | 497 | 2051 | 421 | 1750 | 410 | 1696 | 331 | 420.5 | 148 | 47.5 | 103.5 | 299 | 134% | 75% | 95% | 133% | 5.4471 | Loss 5-10% |  | 1270(149.5) | 1121(178) | 928(52) | 940(115) | 928(35)
486 | 1211 | GTR | ZAFFRABAD | DGN031 | TG-DGN031A-2 | DT-2 | BALBIR NAGAR SCHOOL:K | 3 | 990 | 19504165 | 985 | 2019-06-03 | 319 | 1278 | 316 | 1249 | 350 | 1397 | 135 | 573 | 122.5 | 24.5 |  | 147 | 100% | 59% | 64% | 98% | 5.4471 | Loss 5-10% |  | 970(37.5) | 979(100)
487 | 1211 | GTR | ZAFFRABAD | DGN031 | TG-DGN031A-3 | DT-3 | BALBIR NAGAR SCHOOL:K | 3 | 630 | 19506057 | 672 | 2019-06-11 22:00 | 199 | 822 | 224 | 943 | 249 | 1064 | 210 | 575 | 121.5 | 21 | 2.5 | 145 | 101% | 60% | 71% | 107% | 5.4471 | Loss 5-10% |  | 652(104.5) | 949(239.5) | 590(69.5) | 593(111)
488 | 1211 | GTR | ZAFFRABAD | DGN034 | TG-DGN034A-1 | DT-1 | LONI ROAD TIKONA PARK:PL | 2 | 630 | 19506828 | 573 | 2019-06-03 02:00 | 236 | 988 | 192 | 785 | 145 | 601 | 336 | 682.5 | 31 | 1.5 |  | 32.5 | 91% | 62% | 63% | 86% | 4.3398 | Loss 0-5% |  |  | 540(63)
489 | 1211 | GTR | ZAFFRABAD | DGN053 | TG-DGN053A-1 | DT-1 | EAST ROHTAS NAGAR:PL | 2 | 990 | 19501729 | 1084 | 2019-06-15 | 383 | 1567 | 372 | 1535 | 330 | 1350 | 202 | 561.5 | 126 | 28.5 | 3 | 157.5 | 109% | 69% | 65% | 98% | 4.3141 | Loss 0-5% |  | 925(54) | 1020(127) | 924(64.5)
490 | 1220 | KNR | GAGAN VIHAR | JAG001 | TG-JAG001A-1 | DT-1 | ARAM PARK:PL | 1 | 990 | 19500853 | 1406 | 2019-06-11 23:00 | 463 | 1979 | 504 | 2156 | 439 | 1857 | 260 | 296.5 | 212 | 50 | 158.5 | 420.5 | 142% | 99% | 95% | 142% | 8.8418 | Loss 5-10% |  |  |  |  | 1083(178) | 948(72)
491 | 1220 | KNR | GAGAN VIHAR | JAG002 | TG-JAG002A-1 | DT-1 | BEDI MKT:ID | 3 | 990 | 19506105 | 1022 | 2019-06-03 02:00 | 303 | 1265 | 415 | 1772 | 304 | 1279 | 501 | 566 | 129.5 | 16 | 1.5 | 147 | 103% | 86% | 76% | 95% | 5.5705 | Loss 5-10% |  | 881(54) | 901(92) | 875(48.5)
492 | 1220 | KNR | GAGAN VIHAR | JAG002 | TG-JAG002A-2 | DT-2 | BEDI MKT:ID | 3 | 1600 | 19506104 | 2307 | 2019-06-08 23:00 | 457 | 1978 | 874 | 4198 | 976 | 4330 | 2289 | 554.5 | 123.5 | 31 | 5.5 | 160 | 107% | 80% | 74% | 144% | 5.5705 | Loss 5-10% |  | 1075(167) | 1167(278.5) | 1196(154) | 934(137.5)
493 | 1220 | KNR | GAGAN VIHAR | JAG002 | TG-JAG002A-3 | DT-3 | BEDI MKT:ID | 3 | 990 | 19506656 | 1057 | 2019-06-11 00:30 | 398 | 1668 | 337 | 1408 | 321 | 1339 | 300 | 549 | 129.5 | 31.5 | 4.5 | 165.5 | 107% | 84% | 72% | 104% | 5.5705 | Loss 5-10% |  |  | 948(120) | 928(39.5)
494 | 1220 | KNR | GAGAN VIHAR | JAG003 | TG-JAG003A-2 | DT-2 | BALDEV PARK:K | 2 | 990 | 19500831 | 907.8625 | 2019-06-12 | 287.0211 | 1240.4751 | 313.2638 | 1351.2067 | 307.5776 | 1322.7436 | 99.5986 | 596.5 | 121 | 1.5 |  | 122.5 | 92% | 59% | 68% | 91% | 6.6039 | Loss 5-10% |  | 807(33.5) | 834(85)
495 | 1220 | KNR | GAGAN VIHAR | JAG004 | TG-JAG004A-1 | DT-1 | BALDEV PARK(PARK WALA):PL | 2 | 990 | 19504993 | 760 | 2019-06-30 23:30 | 182 | 801 | 239 | 1078 | 340 | 1537 | 643 | 693.5 | 26 |  |  | 26 | 75% | 49% | 51% | 77% | 6.7151 | Loss 5-10% |  |  | 782(34)
496 | 1220 | KNR | GAGAN VIHAR | JAG005 | TG-JAG005A-1 | DT-1 | BRIJPURI:PL | 1 | 990 | 19500854 | 1081.0185 | 2019-06-30 02:00 | 413.5829 | 1807.2226 | 350.7725 | 1525.098 | 316.6631 | 1378.1742 | 377.6661 | 420.5 | 233 | 53 | 12.5 | 298.5 | 109% | 87% | 82% | 104% | 3.827 | Loss 0-5% |  | 949(195.5) | 1030(363.5) | 1006(278.5) | 889(177)
497 | 1220 | KNR | GAGAN VIHAR | JAG006 | TG-JAG006A-2 | DT-2 | CHANDER NAGAR:ID | 2 | 990 | 19500787 | 983 | 2019-06-11 18:30 | 296 | 1284 | 362 | 1590 | 325 | 1416 | 266 | 554 | 130 | 35.5 |  | 165.5 | 76% | 60% | 99% | 94% | 15.4489 | Loss 10-20% | 1464(403.5) |  |  |  | 1332(480.5) | 1134(212)
498 | 1220 | KNR | GAGAN VIHAR | JAG008 | TG-JAG008A-2 | DT-2 | GAGAN VIHAR:ID | 3 | 990 | 19506108 | 889 | 2019-06-12 00:30 | 237 | 985 | 391 | 1659 | 262 | 1099 | 624 | 630.5 | 89.5 |  |  | 89.5 | 90% | 56% | 60% | 89% | 5.504 | Loss 5-10% |  |  | 981(91.5) | 832(31.5)
499 | 1220 | KNR | GAGAN VIHAR | JAG008 | TG-JAG008A-3 | DT-3 | GAGAN VIHAR:ID | 3 | 630 | 19505113 | 511 | 2019-06-03 | 156 | 672 | 125 | 531 | 230 | 1001 | 417 | 693 | 27 |  |  | 27 | 81% | 55% | 55% | 80% | 5.504 | Loss 5-10% |  |  | 566(57)
500 | 1220 | KNR | GAGAN VIHAR | JAG009 | TG-JAG009A-2 | DT-2 | GAGAN VIHAR EXT:ID | 2 | 990 | 19506155 | 1397 | 2019-06-11 01:30 | 464 | 1946 | 416 | 1740 | 517 | 2199 | 398 | 495.5 | 104 | 29 | 91 | 224 | 141% | 84% | 85% | 134% | 5.363 | Loss 5-10% |  | 972(102.5) | 1086(201.5) | 1008(113) | 911(51) | 857(42)
501 | 1220 | KNR | GAGAN VIHAR | JAG010 | TG-JAG010A-1 | DT-1 | GANDHI PARK:PL | 2 | 990 | 19500851 | 845 | 2019-06-11 00:30 | 222 | 966 | 227 | 963 | 395 | 1694 | 729 | 637.5 | 82 |  |  | 82 | 85% | 62% | 62% | 84% | 18.5044 | Loss 10-20% |  | 864(32.5) | 865(101.5) | 848(54)
502 | 1220 | KNR | GAGAN VIHAR | JAG010 | TG-JAG010A-2 | DT-2 | GANDHI PARK:PL | 2 | 990 | 19500750 | 869 | 2019-06-11 | 269 | 1143 | 278 | 1190 | 322 | 1366 | 203 | 640.5 | 78.5 |  |  | 78.5 | 88% | 66% | 63% | 84% | 18.5044 | Loss 10-20% |  |  | 813(43.5)
503 | 1220 | KNR | GAGAN VIHAR | JAG011 | TG-JAG011A-1 | DT-1 | GANESH PARK:PL | 2 | 990 | 19500776 | 1006.82 | 2019-06-30 | 267.321 | 1068.2586 | 338.3303 | 1370.924 | 401.1686 | 1630.1041 | 487.058 | 503 | 161.5 | 28.5 | 2 | 192 | 102% | 73% | 69% | 101% | 4.8945 | Loss 0-5% |  | 915(57.5) | 976(194.5) | 959(150.5)
504 | 1220 | KNR | GAGAN VIHAR | JAG011 | TG-JAG011A-2 | DT-2 | GANESH PARK:PL | 2 | 990 | 19505000 | 926 | 2019-06-30 | 303 | 1251 | 343 | 1409 | 280 | 1142 | 232 | 579 | 134.5 | 5.5 |  | 140 | 94% | 68% | 71% | 92% | 4.8945 | Loss 0-5% |  | 1003(86.5) | 1002(179.5) | 881(79) | 774(30)
505 | 1220 | KNR | GAGAN VIHAR | JAG012 | TG-JAG012A-2 | DT-2 | GOLDEN PARK:ID | 2 | 990 | 19500817 | 827 | 2019-06-03 | 260 | 1135 | 262 | 1134 | 305 | 1312 | 178 | 647.5 | 72.5 |  |  | 72.5 | 84% | 56% | 67% | 83% | 21.1299 | Loss 20-30%
506 | 1220 | KNR | GAGAN VIHAR | JAG013 | TG-JAG013A-1 | DT-1 | GOPAL PARK:PL | 2 | 990 | 19506543 | 1408.0413 | 2019-06-02 02:00 | 492.6622 | 2114.4301 | 459.5723 | 1942.9766 | 455.8068 | 1954.7424 | 165.8838 | 468.5 | 111 | 53.5 | 83.5 | 248 | 142% | 92% | 88% | 129% | 5.9213 | Loss 5-10% |  |  |  |  | 982(103.5) | 820(28)
507 | 1220 | KNR | GAGAN VIHAR | JAG013 | TG-JAG013A-2 | DT-2 | GOPAL PARK:PL | 2 | 990 | 19506648 | 998.2955 | 2019-06-02 23:30 | 271.1006 | 1164.972 | 466.6589 | 2100.553 | 260.536 | 1140.8504 | 947.8721 | 589.5 | 118 | 10 | 0.5 | 128.5 | 99% | 62% | 66% | 101% | 5.9213 | Loss 5-10%
508 | 1220 | KNR | GAGAN VIHAR | JAG016 | TG-JAG016A-2 | DT-2 | GOVIND PURA(OLD):ID | 2 | 990 | 19505580 | 884 | 2019-06-10 03:00 | 320 | 1330 | 313 | 1296 | 251 | 1025 | 290 | 632.5 | 87.5 |  |  | 87.5 | 89% | 64% | 61% | 83% | 6.7925 | Loss 5-10% |  |  | 920(63.5)
509 | 1220 | KNR | GAGAN VIHAR | JAG018 | TG-JAG018A-1 | DT-1 | JAGAT PURI A BLK:PL | 3 | 990 | 19504763 | 870 | 2019-06-30 01:00 | 258 | 1051 | 280 | 1130 | 331 | 1344 | 262 | 646 | 74 |  |  | 74 | 88% | 69% | 71% | 81% | 4.2076 | Loss 0-5% |  | 960(127.5) | 1128(315) | 938(79.5) | 927(158.5) | 774(30)
510 | 1220 | KNR | GAGAN VIHAR | JAG018 | TG-JAG018A-3 | DT-3 | JAGAT PURI A BLK:PL | 3 | 630 | 19505712 | 824 | 2019-06-30 06:00 | 307 | 1262 | 283 | 1142 | 234 | 944 | 278 | 481.5 | 153.5 | 48 | 36.5 | 238 | 125% | 131% | 81% | 117% | 4.2076 | Loss 0-5%
511 | 1220 | KNR | GAGAN VIHAR | JAG020 | TG-JAG020A-1 | DT-1 | JAGAT PURI F BLK:PL | 2 | 990 | 19506790 | 930 | 2019-06-30 14:00 | 351 | 1433 | 290 | 1175 | 289 | 1182 | 254 | 451.5 | 267.5 | 1 |  | 268.5 | 87% | 66% | 94% | 87% | 7.4305 | Loss 5-10% |  | 962(171.5) | 942(124) | 789(24) | 782(27)
512 | 1220 | KNR | GAGAN VIHAR | JAG022 | TG-JAG022A-2 | DT-2 | JITAR NAGAR:K | 2 | 990 | 19506650 | 1053 | 2019-06-18 17:00 | 477 | 2083 | 394 | 1927 | 183 | 793 | 1219 | 531.5 | 146.5 | 39.5 | 2 | 188 | 101% | 66% | 106% | 101% | 5.1934 | Loss 5-10% |  | 883(61) | 938(126.5) | 899(70.5)
513 | 1220 | KNR | GAGAN VIHAR | JAG023 | TG-JAG023A-1 | DT-1 | KHUREJI:ID | 2 | 630 | 19506153 | 544 | 2019-06-12 | 193 | 801 | 179 | 741 | 171 | 712 | 79 | 567 | 152 |  |  | 152 | 86% | 73% | 78% | 84% | 8.8305 | Loss 5-10% |  |  |  | 529(83)
514 | 1220 | KNR | GAGAN VIHAR | JAG023 | TG-JAG023A-2 | DT-2 | KHUREJI:ID | 2 | 990 | 19503528 | 1014 | 2019-06-30 | 298 | 1265 | 361 | 1555 | 355 | 1528 | 278 | 302 | 356.5 | 56.5 | 3.5 | 416.5 | 102% | 89% | 90% | 100% | 8.8305 | Loss 5-10% |  | 934(233) | 991(485) | 989(397.5) | 942(253.5) | 788(34)
515 | 1220 | KNR | GAGAN VIHAR | JAG024 | TG-JAG024A-2 | DT-2 | MAUSAM VIHAR:ID | 2 | 630 | 19505721 | 533 | 2019-06-11 00:30 | 202 | 861 | 149 | 633 | 183 | 785 | 202 | 683.5 | 36 |  |  | 36 | 85% | 50% | 57% | 81% | 4.3993 | Loss 0-5% |  |  | 522(40)
516 | 1220 | KNR | GAGAN VIHAR | JAG025 | TG-JAG025A-1 | DT-1 | NEW LAYALPUR:K | 3 | 990 | 19506786 | 931 | 2019-06-01 00:30 | 271 | 1160 | 293 | 1262 | 367 | 1594 | 394 | 609 | 103.5 | 7.5 |  | 111 | 94% | 60% | 93% | 94% | 7.2161 | Loss 5-10%
517 | 1220 | KNR | GAGAN VIHAR | JAG025 | TG-JAG025A-2 | DT-2 | NEW LAYALPUR:K | 3 | 990 | 19506781 | 904 | 2019-06-30 | 275 | 1151 | 247 | 1038 | 382 | 1639 | 553 | 610 | 107 | 1 |  | 108 | 91% | 61% | 65% | 91% | 7.2161 | Loss 5-10% |  | 891(24.5) | 1130(210.5) | 1153(111)
518 | 1220 | KNR | GAGAN VIHAR | JAG027 | TG-JAG027A-1 | DT-1 | RADHEY SHAYAM PARK:PL | 1 | 990 | 19506867 | 1075 | 2019-06-11 00:30 | 329 | 1400 | 515 | 2252 | 231 | 986 | 1118 | 556 | 130.5 | 28.5 | 4 | 163 | 109% | 63% | 63% | 105% | 4.6912 | Loss 0-5% | 860(40.5) | 1148(194) | 1219(296.5) |  | 1028(199.5) | 931(48)
519 | 1220 | KNR | GAGAN VIHAR | JAG028 | TG-JAG028A-1 | DT-1 | RAM NAGAR EXT:K | 2 | 990 | 19505825 | 883 | 2019-06-12 02:00 | 269 | 1076 | 379 | 1529 | 235 | 941 | 533 | 668 | 51.5 |  |  | 51.5 | 89% | 55% | 56% | 81% | 13.9584 | Loss 10-20% |  | 878(53.5) | 1231(226.5) | 1122(164.5) | 1047(102.5)
520 | 1220 | KNR | GAGAN VIHAR | JAG029 | TG-JAG029A-1 | DT-1 | SHIV PURI:PM | 1 | 990 | 19506151 | 976 | 2019-06-29 23:00 | 320 | 1424 | 407 | 1856 | 249 | 1106 | 652 | 587.5 | 127 | 3.5 |  | 130.5 | 93% | 62% | 88% | 99% | 7.0254 | Loss 5-10%
521 | 1220 | KNR | GAGAN VIHAR | JAG030 | TG-JAG030A-1 | DT-1 | SILVER PARK:ID | 1 | 990 | 19506008 | 944 | 2019-06-02 15:30 | 202 | 907 | 373 | 1742 | 369 | 1702 | 815 | 627 | 88 | 2 |  | 90 | 95% | 65% | 95% | 88% | 14.4604 | Loss 10-20% |  | 804(38.5) | 920(204) | 971(49)
522 | 1220 | KNR | GAGAN VIHAR | JAG031 | TG-JAG031A-1 | DT-1 | SOUTH ANARKALI:PL | 3 | 990 | 19506660 | 1035 | 2019-06-05 02:30 | 346 | 1464 | 378 | 1597 | 311 | 1301 | 256 | 545.5 | 133 | 35.5 | 2 | 170.5 | 105% | 70% | 71% | 98% | 5.5306 | Loss 5-10%
523 | 1220 | KNR | GAGAN VIHAR | JAG031 | TG-JAG031A-2 | DT-2 | SOUTH ANARKALI:PL | 3 | 990 | 19506868 | 1166 | 2019-06-10 00:30 | 395 | 1779 | 355 | 1587 | 416 | 1875 | 254 | 497.5 | 131 | 55.5 | 32.5 | 219 | 118% | 89% | 74% | 112% | 5.5306 | Loss 5-10% | 882(35) | 1165(162.5) | 1042(183) | 1066(151) | 943(107.5)
524 | 1220 | KNR | GAGAN VIHAR | JAG031 | TG-JAG031A-3 | DT-3 | SOUTH ANARKALI:PL | 3 | 630 | 19506472 | 712 | 2019-06-10 00:30 | 266 | 1192 | 226 | 1001 | 220 | 981 | 202 | 497.5 | 136 | 61 | 22 | 219 | 113% | 86% | 76% | 112% | 5.5306 | Loss 5-10% |  |  | 524(40)
525 | 1220 | KNR | GAGAN VIHAR | JAG032 | TG-JAG032A-1 | DT-1 | SOUTH ANARKALI (NALAH):PL | 1 | 990 | 19506107 | 778 | 2019-06-11 00:30 | 254 | 1111 | 231 | 999 | 293 | 1276 | 242 | 690.5 | 29.5 |  |  | 29.5 | 79% | 54% | 54% | 77% | 6.2049 | Loss 5-10% |  | 872(52) | 935(102.5) | 961(68.5)
526 | 1220 | KNR | GAGAN VIHAR | JAG034 | TG-JAG034A-1 | DT-1 | JAGAT PURI G BLK:PL | 2 | 990 | 19505835 | 971 | 2019-06-30 | 299 | 1282 | 331 | 1432 | 342 | 1483 | 180 | 588.5 | 124 | 7.5 |  | 131.5 | 98% | 64% | 62% | 96% | 5.5243 | Loss 5-10% |  | 912(72) | 1049(170) | 1018(111.5) | 854(67)
527 | 1220 | KNR | GAGAN VIHAR | JAG034 | TG-JAG034A-2 | DT-2 | JAGAT PURI G BLK:PL | 2 | 990 | 19505711 | 818 | 2019-06-11 23:30 | 237 | 995 | 351 | 1474 | 230 | 958 | 499 | 650.5 | 69.5 |  |  | 69.5 | 82% | 58% | 56% | 83% | 5.5243 | Loss 5-10%
528 | 1220 | KNR | GAGAN VIHAR | JAG039 | TG-JAG039A-1 | DT-1 | R.S. PARK (PARKWALA) | 2 | 990 | 19505833 | 1009.759 | 2019-06-11 00:30 | 329.1388 | 1437.35 | 360.5541 | 1575.0223 | 320.0661 | 1411.6618 | 152.1515 | 538 | 143 | 30.5 | 4 | 177.5 | 102% | 72% | 71% | 99% | 9.419 | Loss 5-10% |  | 1063(85.5) | 983(167.5) |  | 813(54)
529 | 1220 | KNR | GAGAN VIHAR | JAG039 | TG-JAG039A-2 | DT-2 | R.S. PARK (PARKWALA) | 2 | 630 | 19506106 | 584 | 2019-06-11 23:30 | 141 | 577 | 177 | 728 | 266 | 1120 | 486 | 627.5 | 87.5 | 3 |  | 90.5 | 92% | 72% | 59% | 93% | 9.419 | Loss 5-10%
530 | 1220 | KNR | GANDHI NAGAR | GAN001 | TG-GAN001A-1 | DT-1 | AHATA KARAM CHAND:PL | 1 | 990 | 19505208 | 759 | 2019-06-30 16:00 | 247 | 1054 | 284 | 1207 | 228 | 948 | 225 | 680 | 40 |  |  | 40 | 48% | 60% | 77% | 66% | 15.4387 | Loss 10-20% | 776(106) | 1226(184.5) | 1220(145) | 816(150.5) | 785(98) | 825(102.5)
531 | 1220 | KNR | GANDHI NAGAR | GAN002 | TG-GAN002A-1 | DT-1 | AJIT NAGAR GALI NO 8:PL | 1 | 990 | 19506803 | 924 | 2019-06-02 12:30 | 311 | 1362 | 285 | 1232 | 328 | 1428 | 172 | 439 | 275 | 5.5 |  | 280.5 | 76% | 72% | 93% | 83% | 14.8639 | Loss 10-20%
532 | 1220 | KNR | GANDHI NAGAR | GAN003 | TG-GAN003A-1 | DT-1 | AMAR MOHALLA:PL | 2 | 990 | 19506101 | 1237 | 2019-06-30 17:30 | 457 | 2015 | 378 | 1640 | 402 | 1740 | 336 | 443.5 | 218.5 | 53.5 | 3 | 275 | 70% | 66% | 125% | 84% | 15.1922 | Loss 10-20% | 765(85) | 927(224.5) | 1021(277.5) | 980(268) | 968(170.5) | 844(50.5)
533 | 1220 | KNR | GANDHI NAGAR | GAN003 | TG-GAN003A-2 | DT-2 | AMAR MOHALLA:PL | 2 | 630 | 19506348 | 532 | 2019-06-02 16:00 | 156 | 664 | 160 | 671 | 217 | 939 | 272 | 682 | 36.5 |  |  | 36.5 | 58% | 60% | 84% | 71% | 15.1922 | Loss 10-20% | 555(237) | 879(348.5) | 676(378) | 952(359.5) |  | 611(316.5)
534 | 1220 | KNR | GANDHI NAGAR | GAN005 | TG-GAN005A-1 | DT-1 | CHEMALI DEVI (INSIDE):PL | 1 | 990 | 19500172 | 947 | 2019-06-30 16:00 | 313 | 1345 | 320 | 1369 | 314 | 1350 | 21 | 482.5 | 223 | 14.5 |  | 237.5 | 73% | 57% | 96% | 75% | 11.8238 | Loss 10-20% | 790(62) | 997(203.5) | 1036(292.5) | 1027(267) | 955(189) | 779(39)
535 | 1220 | KNR | GANDHI NAGAR | GAN007 | TG-GAN007A-1 | DT-1 | DUDLELA CHOWK:PL | 2 | 990 | 19506102 | 796 | 2019-06-02 14:30 | 227 | 994 | 271 | 1198 | 298 | 1315 | 282 | 678.5 | 41.5 |  |  | 41.5 | 62% | 60% | 80% | 67% | 9.0319 | Loss 5-10%
536 | 1220 | KNR | GANDHI NAGAR | GAN008 | TG-GAN008A-2 | DT-2 | GALI GURDWARA NO. 2:ID | 4 | 1600 | 19506796 | 1217 | 2019-06-02 16:00 | 406 | 1692 | 388 | 1619 | 423 | 1753 | 116 | 689.5 | 30.5 |  |  | 30.5 | 60% | 50% | 76% | 63% | 4.6064 | Loss 0-5% | 863(152.5) | 1030(372.5) | 1092(474) | 1025(422) | 1015(334) | 881(219.5)
537 | 1220 | KNR | GANDHI NAGAR | GAN008 | TG-GAN008A-3 | DT-3 | GALI GURDWARA NO. 2:ID | 4 | 400 | 19505541 | 393 | 2019-06-30 15:00 | 142 | 599 | 101 | 427 | 149 | 640 | 196 | 537.5 | 163.5 | 15.5 |  | 179 | 27% | 34% | 98% | 38% | 4.6064 | Loss 0-5% | 413(249) | 532(286) | 548(261) | 405(232) | 407(212.5) | 384(215)
538 | 1220 | KNR | GANDHI NAGAR | GAN008 | TG-GAN008A-4 | DT-4 | GALI GURDWARA NO. 2:ID | 4 | 400 | 19504381 | 322 | 2019-06-02 16:30 | 67 | 277 | 152 | 652 | 104 | 440 | 326 | 632 | 84.5 |  |  | 84.5 | 16% | 21% | 81% | 27% | 4.6064 | Loss 0-5% |  |  |  | 322(87) | 327(104.5) | 304(26.5)
539 | 1220 | KNR | GANDHI NAGAR | GAN010 | TG-GAN010A-1 | DT-1 | GANDHI NAGAR POLICE ST.:PL | 2 | 990 | 19506799 | 786 | 2019-06-02 15:00 | 230 | 1024 | 324 | 1440 | 233 | 1025 | 416 | 658 | 61 |  |  | 61 | 18% | 21% | 79% | 25% | 5.0528 | Loss 5-10% |  |  | 865(172) | 830(46)
540 | 1220 | KNR | GANDHI NAGAR | GAN010 | TG-GAN010A-2 | DT-2 | GANDHI NAGAR POLICE ST.:PL | 2 | 990 | 19506802 | 832 | 2019-06-29 15:00 | 282 | 1229 | 204 | 884 | 346 | 1524 | 555 | 608.5 | 110.5 |  |  | 110.5 | 16% | 24% | 84% | 25% | 5.0528 | Loss 5-10% |  |  |  | 796(57) | 802(95.5) | 771(52)
541 | 1220 | KNR | GANDHI NAGAR | GAN012 | TG-GAN012A-1 | DT-1 | JANTA PARK NO. 1:PL | 3 | 990 | 19505864 | 1057 | 2019-06-30 11:30 | 314 | 1369 | 360 | 1571 | 383 | 1683 | 275 | 585.5 | 131.5 |  | 0.5 | 132 | 11% | 19% | 107% | 19% | 6.8672 | Loss 5-10% |  | 1032(103.5) | 1091(181) | 890(137.5) | 862(148.5) | 786(53)
542 | 1220 | KNR | GANDHI NAGAR | GAN012 | TG-GAN012A-2 | DT-2 | JANTA PARK NO. 1:PL | 3 | 990 | 19506604 | 810 | 2019-06-28 17:00 | 259 | 1116 | 298 | 1279 | 253 | 1087 | 180 | 618 | 99.5 |  |  | 99.5 | 9% | 14% | 82% | 15% | 6.8672 | Loss 5-10% | 925(114.5) | 1096(215.5) | 1120(220.5) |  | 1074(36) | 1080(240)
543 | 1220 | KNR | GANDHI NAGAR | GAN012 | TG-GAN012A-3 | DT-3 | JANTA PARK NO. 1:PL | 3 | 990 | 19505184 | 805 | 2019-06-30 14:30 | 362 | 1744 | 219 | 993 | 224 | 971 | 763 | 657 | 60.5 |  |  | 60.5 | 4% | 5% | 81% | 11% | 6.8672 | Loss 5-10% |  | 807(41.5)
544 | 1220 | KNR | GANDHI NAGAR | GAN014 | TG-GAN014A-1 | DT-1 | KAILASH NAGAR NO. 1:PL | 3 | 990 | 19505517 | 811 | 2019-06-26 14:30 | 262 | 1117 | 266 | 1136 | 283 | 1200 | 76 | 675 | 45 |  |  | 45 | 76% | 49% | 82% | 76% | 5.0521 | Loss 5-10%
545 | 1220 | KNR | GANDHI NAGAR | GAN015 | TG-GAN015A-1 | DT-1 | KAILASH NAGAR NO. 15:PL | 3 | 990 | 19505931 | 846 | 2019-06-03 01:00 | 208 | 857 | 285 | 1184 | 354 | 1467 | 529 | 639 | 81 |  |  | 81 | 85% | 57% | 76% | 85% | 3.9055 | Loss 0-5% |  |  | 843(130)
546 | 1220 | KNR | GANDHI NAGAR | GAN015 | TG-GAN015A-3 | DT-3 | KAILASH NAGAR NO. 15:PL | 3 | 990 | 19506875 | 795 | 2019-06-30 14:00 | 369 | 1672 | 208 | 860 | 218 | 929 | 779 | 693.5 | 26 |  |  | 26 | 73% | 53% | 80% | 75% | 3.9055 | Loss 0-5% | 781(87) | 1021(356)
547 | 1220 | KNR | GANDHI NAGAR | GAN016 | TG-GAN016A-1 | DT-1 | KAILASH NAGAR SCHOOL:PL | 2 | 990 | 19506801 | 953 | 2019-06-30 14:00 | 276 | 1178 | 328 | 1446 | 350 | 1601 | 370 | 506 | 191.5 | 22.5 |  | 214 | 42% | 43% | 96% | 52% | 5.437 | Loss 5-10% |  |  | 782(44.5) | 744(35.5)
548 | 1220 | KNR | GANDHI NAGAR | GAN023 | TG-GAN023A-1 | DT-1 | PEEPAL WALA SCHOOL:PL | 2 | 990 | 19506794 | 811 | 2019-06-02 12:00 | 275 | 1127 | 259 | 1061 | 276 | 1132 | 68 | 638.5 | 81.5 |  |  | 81.5 | 29% | 31% | 82% | 40% | 3.806 | Loss 0-5% |  | 901(58.5) | 858(143.5) | 808(78.5) | 878(146.5) | 851(162.5)
549 | 1220 | KNR | GANDHI NAGAR | GAN023 | TG-GAN023A-2 | DT-2 | PEEPAL WALA SCHOOL:PL | 2 | 630 | 19506795 | 575 | 2019-06-02 17:30 | 302 | 1283 | 127 | 525 | 146 | 597 | 725 | 666 | 53.5 | 0.5 |  | 54 | 15% | 33% | 91% | 32% | 3.806 | Loss 0-5% |  |  | 527(55.5) | 507(57) | 542(127.5) | 522(143)
550 | 1220 | KNR | GANDHI NAGAR | GAN024 | TG-GAN024A-1 | DT-1 | R. PURA GALI NO. 8:PL | 1 | 990 | 19506002 | 920 | 2019-06-02 15:30 | 300 | 1229 | 311 | 1286 | 309 | 1279 | 54 | 542.5 | 174 | 3.5 |  | 177.5 | 48% | 43% | 93% | 66% | 10.9652 | Loss 10-20% | 790(55) | 950(176.5) | 969(487) |  | 937(231) | 913(186)
551 | 1220 | KNR | GANDHI NAGAR | GAN025 | TG-GAN025A-1 | DT-1 | R.PURA GALI NO 6 (IN SIDE):PL | 1 | 990 | 19506600 | 1025 | 2019-06-01 12:30 | 333 | 1403 | 335 | 1423 | 356 | 1516 | 105 | 468 | 178 | 72.5 | 1.5 | 252 | 30% | 47% | 103% | 64% | 6.8535 | Loss 5-10% | 973(263) | 1151(291.5) | 1278(275.5) |  | 1044(43) | 1149(287)
552 | 1220 | KNR | GANDHI NAGAR | GAN028 | TG-GAN028A-1 | DT-1 | SEELAMPUR OLD PR. SCHOOL NO. 1:K | 4 | 990 | 19505116 | 907 | 2019-06-02 16:30 | 310 | 1292 | 305 | 1288 | 292 | 1244 | 46 | 642.5 | 74.5 | 3 |  | 77.5 | 81% | 78% | 92% | 82% | 18.9796 | Loss 10-20% |  | 913(257.5) | 954(444) | 932(473.5) |  | 829(244)
553 | 1220 | KNR | GANDHI NAGAR | GAN028 | TG-GAN028A-2 | DT-2 | SEELAMPUR OLD PR. SCHOOL NO. 1:K | 4 | 990 | 19505099 | 823 | 2019-06-01 16:30 | 321 | 1413 | 252 | 1112 | 250 | 1105 | 304 | 640.5 | 79.5 |  |  | 79.5 | 62% | 68% | 83% | 74% | 18.9796 | Loss 10-20% |  | 773(33) | 774(39.5)
554 | 1220 | KNR | GANDHI NAGAR | GAN029 | TG-GAN029A-1 | DT-1 | SEELAMPUR PHATAK:PL | 2 | 990 | 19506480 | 965 | 2019-06-29 15:00 | 292 | 1292 | 360 | 1583 | 313 | 1399 | 255 | 402 | 148 | 3 |  | 151 | 59% | 77% | 97% | 68% | 65.3141 | Loss >30% | 1063(422.5) |  | 1265(247) |  | 1364(597) | 1251(527)
555 | 1220 | KNR | GANDHI NAGAR | GAN032 | TG-GAN032A-2 | DT-2 | SHIV KUTI R.L.G. NO. 1:ID | 7 | 990 | 19506574 | 863 | 2019-06-30 16:00 | 262 | 1107 | 311 | 1312 | 289 | 1215 | 178 | 565.5 | 154.5 |  |  | 154.5 | 29% | 16% | 87% | 18% | 10.0398 | Loss 10-20% |  | 940(172.5) | 910(25) |  |  | 939(205.5)
556 | 1220 | KNR | GANDHI NAGAR | GAN032 | TG-GAN032A-4 | DT-4 | SHIV KUTI R.L.G. NO. 1:ID | 7 | 990 | 19505384 | 1009 | 2019-06-02 12:00 | 329 | 1389 | 375 | 1585 | 305 | 1291 | 259 | 470 | 173 | 76.5 | 0.5 | 250 | 36% | 52% | 102% | 59% | 10.0398 | Loss 10-20% |  | 863(106.5) | 901(189) | 866(208) | 881(195) | 879(206)
557 | 1220 | KNR | GANDHI NAGAR | GAN032 | TG-GAN032A-6 | DT-6 | SHIV KUTI R.L.G. NO. 1:ID | 7 | 990 | 19505140 | 795 | 2019-06-26 16:00 | 276 | 1160 | 215 | 902 | 304 | 1281 | 335 | 601.5 | 118.5 |  |  | 118.5 | 13% | 13% | 80% | 40% | 10.0398 | Loss 10-20% |  | 979(152.5) | 1088(233.5) | 977(241) | 1084(239) | 1007(238.5)
558 | 1220 | KNR | GANDHI NAGAR | GAN033 | TG-GAN033A-2 | DT-2 | SUBHASH MOHALLA NO.1:PM | 4 | 990 | 19505124 | 855 | 2019-06-01 18:00 | 301 | 1242 | 294 | 1208 | 260 | 1056 | 172 | 570 | 147.5 |  |  | 147.5 | 42% | 41% | 86% | 59% | 7.4512 | Loss 5-10% |  | 863(153.5) | 1002(204) | 859(223.5) | 870(183) | 824(147.5)
559 | 1220 | KNR | GANDHI NAGAR | GAN033 | TG-GAN033A-3 | DT-3 | SUBHASH MOHALLA NO.1:PM | 4 | 990 | 19506659 | 863 | 2019-06-01 12:00 | 268 | 1125 | 294 | 1245 | 300 | 1269 | 133 | 555 | 164.5 |  |  | 164.5 | 30% | 41% | 87% | 50% | 7.4512 | Loss 5-10% | 1153(279) | 1166(219.5) | 920(164) | 942(239) | 948(205)
560 | 1220 | KNR | GANDHI NAGAR | GAN033 | TG-GAN033A-4 | DT-4 | SUBHASH MOHALLA NO.1:PM | 4 | 990 | 19505135 | 926 | 2019-06-23 15:30 | 298 | 1237 | 323 | 1337 | 305 | 1271 | 89 | 659 | 60.5 | 0.5 |  | 61 | 59% | 47% | 94% | 73% | 7.4512 | Loss 5-10% |  |  | 530(96.5) | 526(130) | 507(78) | 468(34.5)
561 | 1220 | KNR | GANDHI NAGAR | GAN034 | TG-GAN034A-1 | DT-1 | AJIT NAGAR GALI NO 10:PL | 2 | 990 | 19506811 | 757 | 2019-06-29 22:00 | 273 | 1137 | 270 | 1127 | 214 | 894 | 239 | 691 | 27.5 |  |  | 27.5 | 71% | 64% | 75% | 76% | 12.4562 | Loss 10-20% |  | 761(24) | 752(58) | 761(29.5)
562 | 1220 | KNR | GANDHI NAGAR | GAN036 | TG-GAN036A-1 | DT-1 | KOTHI BHAGWAN DAS OUTSIDE:PL | 1 | 990 | 19506539 | 1099 | 2019-06-02 16:00 | 397 | 1665 | 353 | 1501 | 349 | 1470 | 182 | 506 | 94.5 | 76 | 41 | 211.5 | 11% | 19% | 111% | 38% | 9.7321 | Loss 5-10%
563 | 1220 | KNR | GANDHI NAGAR | GAN040 | TG-GAN040A-1 | DT-1 | GYAN MOHLLA | 1 | 990 | 19502011 | 924 | 2019-06-01 16:30 | 327 | 1448 | 313 | 1373 | 284 | 1256 | 168 | 539 | 178.5 | 2.5 |  | 181 | 34% | 39% | 93% | 55% | 4.1193 | Loss 0-5% | 885(218.5) | 1007(256) | 1093(210.5) |  | 967(107.5) | 931(219)
564 | 1220 | KNR | GANDHI NAGAR | GAN045 | TG-GAN045A-1 | DT-1 | SJ/STN RATTEY WALA SUBHASH MOHALLA | 1 | 990 | 19506863 | 840 | 2019-06-02 16:30 | 253 | 1056 | 297 | 1258 | 289 | 1225 | 187 | 593.5 | 126.5 |  |  | 126.5 | 13% | 31% | 85% | 31% | 9.7229 | Loss 5-10% |  | 866(124.5) | 870(158.5) | 827(152.5) | 869(175.5) | 974(203)
565 | 1220 | KNR | GEETA COLONY | GCL002 | TG-GCL002A-1 | DT-1 | ALOK BHARTI | 1 | 990 | 19503703 | 941 | 2019-06-30 | 376 | 1596 | 307 | 1293 | 259 | 1081 | 448 | 549.5 | 167 | 3.5 |  | 170.5 | 95% | 75% | 77% | 95% | 5.9868 | Loss 5-10% |  | 835(95.5) | 908(235.5) | 895(158) | 832(84)
566 | 1220 | KNR | GEETA COLONY | GCL004 | TG-GCL004A-2 | DT-2 | B.T.S MULTANI MOHOLLA:PL | 2 | 400 | 19506538 | 324 | 2019-06-05 | 163 | 736 | 74 | 317 | 88 | 382 | 391 | 686 | 34 |  |  | 34 | 81% | 56% | 80% | 77% | 8.7685 | Loss 5-10%
567 | 1220 | KNR | GEETA COLONY | GCL005 | TG-GCL005A-1 | DT-1 | JHEEL (BHOOSA MANDI):PL | 2 | 990 | 19506909 | 880 | 2019-06-27 | 251 | 1048 | 348 | 1451 | 281 | 1183 | 355 | 693 | 27 |  |  | 27 | 89% | 55% | 69% | 88% | 6.0827 | Loss 5-10% |  |  | 863(77) | 847(41)
568 | 1220 | KNR | GEETA COLONY | GCL005 | TG-GCL005A-2 | DT-2 | JHEEL (BHOOSA MANDI):PL | 2 | 400 | 19505932 | 443 | 2019-06-12 00:30 | 165 | 695 | 85 | 359 | 193 | 826 | 418 | 553 | 105 | 41 | 21 | 167 | 111% | 71% | 88% | 108% | 6.0827 | Loss 5-10%
569 | 1220 | KNR | GEETA COLONY | GCL011 | TG-GCL011A-1 | DT-1 | GEETA COLONY, 14 BLK:ID | 1 | 990 | 19505719 | 955 | 2019-06-11 01:00 | 290 | 1294 | 224 | 1043 | 440 | 2230 | 1084 | 605 | 113.5 | 0.5 |  | 114 | 96% | 65% | 74% | 85% | 9.7752 | Loss 5-10% |  | 829(54.5) | 901(141.5) | 864(79) | 751(25.5)
570 | 1220 | KNR | GEETA COLONY | GCL014 | TG-GCL014A-1 | DT-1 | GEETA COLONY,11, BLK:PL | 1 | 990 | 19502875 | 996 | 2019-06-11 01:00 | 332 | 1381 | 293 | 1249 | 371 | 1587 | 296 | 593 | 121.5 | 3.5 | 1 | 126 | 101% | 81% | 62% | 97% | 4.896 | Loss 0-5% |  | 886(63) | 909(132) | 886(68.5)
571 | 1220 | KNR | GEETA COLONY | GCL015 | TG-GCL015A-2 | DT-2 | GEETA COLONY,12, BLK:K | 2 | 630 | 19506809 | 556 | 2019-06-29 23:30 | 102 | 433 | 168 | 726 | 286 | 1238 | 705 | 615.5 | 104.5 |  |  | 104.5 | 87% | 57% | 73% | 88% | 5.5539 | Loss 5-10%
572 | 1220 | KNR | GEETA COLONY | GCL016 | TG-GCL016A-1 | DT-1 | GEETA COLONY,13, BLK:ID | 4 | 990 | 19506146 | 815 | 2019-06-11 01:30 | 265 | 1147 | 280 | 1220 | 270 | 1166 | 65 | 681 | 39 |  |  | 39 | 82% | 50% | 60% | 77% | 4.4645 | Loss 0-5%
573 | 1220 | KNR | GEETA COLONY | GCL016 | TG-GCL016A-2 | DT-2 | GEETA COLONY,13, BLK:ID | 4 | 990 | 19506110 | 1134.3448 | 2019-06-12 00:30 | 322.5094 | 1425.3297 | 523.7515 | 2336.8203 | 288.0839 | 1253.5743 | 1008.399 | 579.5 | 82.5 | 38 | 16.5 | 137 | 115% | 76% | 67% | 112% | 4.4645 | Loss 0-5% |  |  | 1097(201) |  | 887(101.5)
574 | 1220 | KNR | GEETA COLONY | GCL017 | TG-GCL017A-2 | DT-2 | GEETA COLONY,15, BLK:PL | 2 | 630 | 19506379 | 666 | 2019-06-11 01:00 | 200 | 902 | 292 | 1384 | 174 | 750 | 574 | 621 | 98.5 |  | 0.5 | 99 | 106% | 55% | 64% | 90% | 6.7417 | Loss 5-10%
575 | 1220 | KNR | GEETA COLONY | GCL018 | TG-GCL018A-1 | DT-1 | GEETA COLONY,17, BLK COM CENTRE:PL | 2 | 630 | 19505190 | 590 | 2019-06-30 00:30 | 194 | 856 | 197 | 870 | 198 | 871 | 14 | 662 | 50 | 3 |  | 53 | 94% | 66% | 66% | 90% | 6.3725 | Loss 5-10% |  | 668(101) | 694(187) | 616(109) | 520(52.5)
576 | 1220 | KNR | GEETA COLONY | GCL019 | TG-GCL019A-1 | DT-1 | GEETA COLONY,17,BLK:PL | 2 | 990 | 19506130 | 1196 | 2019-06-30 02:00 | 393 | 1666 | 439 | 1973 | 364 | 1635 | 323 | 393 | 205 | 78.5 | 42.5 | 326 | 121% | 87% | 82% | 115% | 7.6169 | Loss 5-10% |  |  | 1062(305) |  | 956(190.5) | 854(35.5)
577 | 1220 | KNR | GEETA COLONY | GCL019 | TG-GCL019A-2 | DT-2 | GEETA COLONY,17,BLK:PL | 2 | 630 | 19504388 | 621 | 2019-06-12 | 209 | 882 | 237 | 1007 | 175 | 735 | 235 | 644.5 | 64 | 10.5 |  | 74.5 | 99% | 63% | 63% | 91% | 7.6169 | Loss 5-10% |  | 634(74.5) | 659(161) | 646(96) | 564(78)
578 | 1220 | KNR | GEETA COLONY | GCL022 | TG-GCL022A-1 | DT-1 | GEETA COLONY,3, BLK:K | 2 | 990 | 19505141 | 794 | 2019-06-12 01:00 | 295 | 1235 | 262 | 1154 | 236 | 988 | 218 | 685 | 34.5 |  |  | 34.5 | 80% | 53% | 55% | 73% | 4.4618 | Loss 0-5%
579 | 1220 | KNR | GEETA COLONY | GCL024 | TG-GCL024A-1 | DT-1 | GEETA COLONY,6, BLK:PL | 2 | 990 | 19506114 | 801 | 2019-06-11 23:30 | 287 | 1252 | 246 | 1074 | 268 | 1158 | 154 | 655 | 65 |  |  | 65 | 80% | 56% | 70% | 81% | 4.7657 | Loss 0-5%
580 | 1220 | KNR | GEETA COLONY | GCL024 | TG-GCL024A-2 | DT-2 | GEETA COLONY,6, BLK:PL | 2 | 630 | 19505716 | 586.4537 | 2019-06-12 | 184.7647 | 786.3332 | 184.0559 | 779.6995 | 217.6331 | 919.2527 | 136.3575 | 606 | 110.5 | 2.5 |  | 113 | 93% | 71% | 63% | 92% | 4.7657 | Loss 0-5% | 733(78) | 817(159.5) | 672(199.5) | 632(123.5) | 550(80.5)
581 | 1220 | KNR | GEETA COLONY | GCL025 | TG-GCL025A-1 | DT-1 | GEETA COLONY,7, BLK:PL | 1 | 990 | 19506865 | 1022 | 2019-06-11 01:00 | 230 | 1032 | 383 | 1880 | 409 | 1978 | 901 | 645 | 74.5 |  | 0.5 | 75 | 103% | 52% | 58% | 84% | 5.6796 | Loss 5-10% |  | 946(94) | 962(174.5) | 950(110.5) | 805(51)
582 | 1220 | KNR | GEETA COLONY | GCL026 | TG-GCL026A-2 | DT-2 | GEETA COLONY,8,BLK;PL | 2 | 400 | 19506115 | 357 | 2019-06-16 01:00 | 108 | 444 | 142 | 591 | 107 | 447 | 146 | 550 | 170 |  |  | 170 | 89% | 78% | 80% | 87% | 7.0832 | Loss 5-10%
583 | 1220 | KNR | GEETA COLONY | GCL027 | TG-GCL027A-1 | DT-1 | GEETA COLONY,8-A,BLK:ID | 2 | 990 | 19506019 | 919 | 2019-06-11 23:30 | 363 | 1555 | 243 | 1029 | 313 | 1336 | 458 | 598.5 | 120 | 1.5 |  | 121.5 | 92% | 87% | 67% | 93% | 8.665 | Loss 5-10% |  |  | 963(106.5) | 830(52)
584 | 1220 | KNR | GEETA COLONY | GCL028 | TG-GCL028A-1 | DT-1 | GEETA COLONY,POL.STATION | 2 | 630 | 19505717 | 550 | 2019-06-04 01:30 | 129 | 537 | 250 | 1065 | 171 | 715 | 465 | 671.5 | 48.5 |  |  | 48.5 | 87% | 56% | 76% | 83% | 9.3711 | Loss 5-10% |  |  | 536(57.5)
585 | 1220 | KNR | GEETA COLONY | GCL028 | TG-GCL028A-2 | DT-2 | GEETA COLONY,POL.STATION | 2 | 630 | 19504342 | 671.9452 | 2019-06-03 | 130.8245 | 572.2357 | 196.0723 | 848.2469 | 345.0484 | 1492.7469 | 818.2003 | 438.5 | 32.5 |  |  | 32.5 | 78% | 54% | 72% | 79% | 9.3711 | Loss 5-10%
586 | 1220 | KNR | GEETA COLONY | GCL030 | TG-GCL030A-1 | DT-1 | NEW LAHORE (MUNSHI COLONY):PL | 1 | 990 | 19506789 | 1099 | 2019-06-10 02:00 | 383 | 1722 | 351 | 1549 | 365 | 1643 | 149 | 476.5 | 166 | 64.5 | 11.5 | 242 | 111% | 86% | 83% | 108% | 5.3845 | Loss 5-10% |  | 963(153.5) | 1070(235.5) |  | 891(143)
587 | 1220 | KNR | GEETA COLONY | GCL031 | TG-GCL031A-2 | DT-2 | NEW LAHORE EXTENSION:PL | 2 | 990 | 19506866 | 1078 | 2019-06-28 | 389 | 1625 | 375 | 1546 | 314 | 1303 | 291 | 572 | 134 | 5.5 | 4 | 143.5 | 109% | 84% | 69% | 107% | 4.9099 | Loss 0-5% |  |  | 825(49) | 844(75)
588 | 1220 | KNR | GEETA COLONY | GCL032 | TG-GCL032A-1 | DT-1 | RANI GARDEN NO.2,PARK WALA:PL | 2 | 990 | 19506148 | 838 | 2019-06-30 01:30 | 267 | 1111 | 250 | 1043 | 321 | 1329 | 259 | 612.5 | 106.5 |  |  | 106.5 | 85% | 76% | 75% | 84% | 5.0761 | Loss 5-10% |  | 903(161) | 920(151) | 822(78)
589 | 1220 | KNR | GEETA COLONY | GCL034 | TG-GCL034A-1 | DT-1 | RANI GARDEN SWITCHING S/STN:PL | 1 | 630 | 19506864 | 598 | 2019-06-30 | 183 | 788 | 215 | 930 | 200 | 862 | 123 | 586 | 125.5 | 7.5 |  | 133 | 95% | 63% | 77% | 94% | 4.7581 | Loss 0-5% |  | 526(45.5) | 572(115.5) | 532(51.5)
590 | 1220 | KNR | GEETA COLONY | GCL035 | TG-GCL035A-1 | DT-1 | SARASWATI BHANDAR:PL | 1 | 630 | 19505989 | 580 | 2019-06-02 14:30 | 179 | 751 | 196 | 820 | 205 | 862 | 97 | 521 | 198 | 1 |  | 199 | 15% | 34% | 92% | 19% | 6.5743 | Loss 5-10% |  |  |  |  | 540(82.5)
591 | 1220 | KNR | GEETA COLONY | GCL036 | TG-GCL036A-1 | DT-1 | SAROJINI PARK:PKG | 1 | 990 | 19506408 | 820 | 2019-06-11 23:30 | 256 | 1069 | 270 | 1161 | 294 | 1241 | 149 | 654 | 66 |  |  | 66 | 82% | 54% | 61% | 83% | 6.2642 | Loss 5-10% |  |  | 858(73) | 859(44.5)
592 | 1220 | KNR | GEETA COLONY | GCL038 | TG-GCL038A-1 | DT-1 | SHASTRI PARK NAGAR, NO-2:K | 1 | 990 | 19506782 | 914 | 2019-06-09 00:30 | 319 | 1395 | 319 | 1379 | 276 | 1192 | 196 | 646 | 73.5 | 0.5 |  | 74 | 92% | 64% | 63% | 88% | 6.1171 | Loss 5-10% |  | 829(43.5) | 811(41)
593 | 1220 | KNR | GEETA COLONY | GCL041 | TG-GCL041A-1 | DT-1 | SUBASH ROAD, TIKONA PARK:K | 4 | 990 | 19505574 | 936 | 2019-06-29 16:00 | 322 | 1353 | 313 | 1328 | 301 | 1264 | 79 | 510 | 188.5 | 18.5 |  | 207 | 20% | 22% | 95% | 27% | 5.2095 | Loss 5-10% |  | 768(35) | 936(153.5) | 786(78) | 825(47.5)
594 | 1220 | KNR | GEETA COLONY | GCL041 | TG-GCL041A-2 | DT-2 | SUBASH ROAD, TIKONA PARK:K | 4 | 990 | 19501917 | 944 | 2019-06-02 15:00 | 288 | 1256 | 307 | 1333 | 349 | 1510 | 226 | 557.5 | 125.5 | 33.5 |  | 159 | 19% | 39% | 95% | 20% | 5.2095 | Loss 5-10% |  |  | 891(33) |  | 961(113.5) | 817(69)
595 | 1220 | KNR | KANTI NAGAR | GAN017 | TG-GAN017A-1 | DT-1 | KAUSHIK PURI KIOSK:K | 1 | 990 | 19502029 | 813 | 2019-06-01 19:30 | 350 | 1476 | 232 | 979 | 231 | 938 | 519 | 687 | 33 |  |  | 33 | 74% | 69% | 82% | 79% | 5.5284 | Loss 5-10% |  | 839(82) | 778(45.5)
596 | 1220 | KNR | KANTI NAGAR | GAN018 | TG-GAN018A-2 | DT-2 | KAUSHIK PURI PARK:PL | 2 | 630 | 19504747 | 491 | 2019-06-01 19:30 | 151 | 610 | 140 | 564 | 201 | 807 | 224 | 692 | 28 |  |  | 28 | 73% | 67% | 78% | 77% | 20.6085 | Loss 20-30% |  | 478(29.5) |  | 467(24.5)
597 | 1220 | KNR | KANTI NAGAR | GAN026 | TG-GAN026A-1 | DT-1 | SATSANG MARG:PL | 2 | 990 | 19500930 | 850 | 2019-06-30 00:30 | 329 | 1437 | 260 | 1120 | 261 | 1133 | 311 | 685.5 | 34 |  |  | 34 | 86% | 59% | 78% | 84% | 4.3717 | Loss 0-5%
598 | 1220 | KNR | KANTI NAGAR | GAN026 | TG-GAN026A-2 | DT-2 | SATSANG MARG:PL | 2 | 630 | 19500966 | 669 | 2019-06-01 23:30 | 231 | 1023 | 206 | 905 | 233 | 1026 | 120 | 571.5 | 96 | 37.5 | 14 | 147.5 | 106% | 68% | 74% | 106% | 4.3717 | Loss 0-5% |  |  |  | 646(94) | 554(95)
599 | 1220 | KNR | KANTI NAGAR | GAN027 | TG-GAN027A-1 | DT-1 | SEELAMPUR DOUBLE STORY:ID | 2 | 990 | 19505501 | 1179 | 2019-06-30 15:30 | 384 | 1728 | 428 | 1927 | 367 | 1627 | 264 | 416.5 | 117.5 | 80 | 17.5 | 215 | 55% | 48% | 119% | 74% | 10.3226 | Loss 10-20% | 986(234.5) | 1074(269) | 902(118) | 838(82.5)
600 | 1220 | KNR | KANTI NAGAR | GAN035 | TG-GAN035A-1 | DT-1 | CHAMELI DEVI OUTSIDE:PL | 1 | 990 | 19506068 | 809 | 2019-06-30 15:30 | 274 | 1174 | 219 | 941 | 316 | 1371 | 373 | 669 | 49 |  |  | 49 | 51% | 45% | 82% | 54% | 6.9158 | Loss 5-10% |  |  |  |  | 853(104.5) | 794(82.5)
601 | 1220 | KNR | KANTI NAGAR | KRI002 | TG-KRI002A-1 | DT-1 | AZAD NAGAR WATER TANK:PL | 1 | 990 | 19503599 | 895 | 2019-06-29 23:30 | 311 | 1257 | 275 | 1108 | 309 | 1237 | 140 | 597.5 | 121.5 | 1 |  | 122.5 | 89% | 59% | 67% | 90% | 4.773 | Loss 0-5% |  | 854(51) | 886(115.5) | 891(69.5)
602 | 1220 | KNR | KANTI NAGAR | KRI006 | TG-KRI006A-1 | DT-1 | BHAGAT SINGH PARK NO 1:PL | 2 | 990 | 19501914 | 1127 | 2019-06-14 | 383 | 1618 | 366 | 1532 | 378 | 1601 | 79 | 530.5 | 126 | 50 | 11 | 187 | 114% | 75% | 79% | 110% | 4.4852 | Loss 0-5% |  | 934(66.5) | 1067(190) | 897(31.5) | 876(89)
603 | 1220 | KNR | KANTI NAGAR | KRI023 | TG-KRI023A-2 | DT-2 | JHEEL NO. 4 NO 1:ID | 2 | 990 | 19501978 | 781 | 2019-06-29 16:30 | 246 | 1103 | 258 | 1164 | 278 | 1238 | 117 | 687 | 32.5 |  |  | 32.5 | 63% | 42% | 79% | 64% | 8.2995 | Loss 5-10% |  |  | 796(42)
604 | 1220 | KNR | KANTI NAGAR | KRI026 | TG-KRI026A-1 | DT-1 | KANTI NAGAR EXT. GALI NO. 5:PL | 1 | 990 | 19504956 | 925 | 2019-06-02 00:30 | 303 | 1242 | 296 | 1215 | 326 | 1329 | 104 | 422 | 285.5 | 11 |  | 296.5 | 93% | 70% | 92% | 93% | 7.3476 | Loss 5-10% |  | 892(186.5) | 959(304.5) | 916(221.5) | 826(149.5)
605 | 1220 | KNR | KANTI NAGAR | KRI027 | TG-KRI027A-2 | DT-2 | KANTI NAGAR EXT. GALI NO. 9:PL | 2 | 990 | 19505347 | 892 | 2019-06-30 23:30 | 274 | 1114 | 243 | 975 | 374 | 1532 | 503 | 665.5 | 54 | 0.5 |  | 54.5 | 90% | 65% | 73% | 90% | 5.327 | Loss 5-10% |  | 790(32) | 861(64.5) | 807(29.5)
606 | 1220 | KNR | KANTI NAGAR | KRI039 | TG-KRI039A-2 | DT-2 | RAJGARH EXTN.(MINI STADIUM):ID | 2 | 990 | 19505976 | 1007 | 2019-06-29 23:00 | 441 | 2016 | 259 | 1145 | 307 | 1347 | 789 | 339.5 | 47.5 | 3.5 | 1 | 52 | 95% | 58% | 66% | 102% | 5.2021 | Loss 5-10% |  |  | 1204(216.5) | 1033(82) | 974(131.5)
607 | 1220 | KNR | KANTI NAGAR | KRI040 | TG-KRI040A-1 | DT-1 | RAJGARH MOTHER DAIRY GALI NO 6:PL | 2 | 990 | 19500881 | 963 | 2019-06-11 | 334 | 1476 | 337 | 1503 | 292 | 1297 | 194 | 582.5 | 125.5 | 10.5 |  | 136 | 97% | 74% | 69% | 94% | 6.7233 | Loss 5-10% |  | 1047(69) | 1050(149.5) | 905(70.5) | 787(26.5)
608 | 1220 | KNR | KANTI NAGAR | KRI040 | TG-KRI040A-2 | DT-2 | RAJGARH MOTHER DAIRY GALI NO 6:PL | 2 | 990 | 19504387 | 836 | 2019-06-12 02:30 | 334 | 1416 | 246 | 1031 | 257 | 1087 | 360 | 665.5 | 53.5 |  |  | 53.5 | 84% | 60% | 57% | 79% | 6.7233 | Loss 5-10%
609 | 1220 | KNR | KANTI NAGAR | KRI045 | TG-KRI045A-2 | DT-2 | SHANKAR NAGAR MAIN ROAD SCHOOL NO 1:PL | 2 | 990 | 19506354 | 1018 | 2019-06-01 01:00 | 335 | 1366 | 432 | 1765 | 251 | 1018 | 647 | 578 | 138.5 | 1.5 | 1 | 141 | 103% | 66% | 82% | 91% | 8.1425 | Loss 5-10% |  |  |  |  | 902(127)
610 | 1220 | KNR | KANTI NAGAR | KRI052 | TG-KRI052A-1 | DT-1 | WEST AZAD NAGAR (RASGULLA):PL | 1 | 990 | 19506565 | 882 | 2019-06-11 23:30 | 252 | 1015 | 318 | 1268 | 312 | 1256 | 247 | 620.5 | 96.5 |  |  | 96.5 | 87% | 68% | 60% | 89% | 3.9573 | Loss 0-5%
611 | 1220 | KNR | KANTI NAGAR | KRI053 | TG-KRI053A-2 | DT-2 | WEST AZAD NAGAR SHD ROAD B&D BL NO. 1:ID | 3 | 990 | 19501884 | 954 | 2019-06-10 03:00 | 322 | 1346 | 281 | 1151 | 351 | 1463 | 273 | 603 | 109.5 | 5 |  | 114.5 | 96% | 62% | 69% | 95% | 5.0986 | Loss 5-10% |  | 1045(119) | 939(66) | 866(53.5)
612 | 1220 | KNR | KANTI NAGAR | KRI053 | TG-KRI053A-3 | DT-3 | WEST AZAD NAGAR SHD ROAD B&D BL NO. 1:ID | 3 | 630 | 19505228 | 768 | 2019-06-11 01:00 | 253 | 1090 | 258 | 1129 | 257 | 1123 | 36 | 406.5 | 191.5 | 66 | 53 | 310.5 | 122% | 86% | 86% | 112% | 5.0986 | Loss 5-10% | 732(93) | 976(628) | 1013(579.5) | 701(284) | 691(222.5) | 545(50)
613 | 1220 | KNR | KANTI NAGAR | KRI055 | TG-KRI055A-1 | DT-1 | WEST AZAD NAGAR(KEHAR SINGH)RLG NO 1:ID | 2 | 990 | 19501973 | 888 | 2019-06-30 23:30 | 290 | 1237 | 300 | 1302 | 298 | 1286 | 59 | 657 | 62.5 |  |  | 62.5 | 90% | 57% | 59% | 90% | 6.0902 | Loss 5-10%
614 | 1220 | KNR | KANTI NAGAR | KRI055 | TG-KRI055A-2 | DT-2 | WEST AZAD NAGAR(KEHAR SINGH)RLG NO 1:ID | 2 | 990 | 19501602 | 785 | 2019-06-11 23:30 | 296 | 1262 | 210 | 882 | 279 | 1194 | 351 | 688.5 | 31 |  |  | 31 | 78% | 53% | 60% | 79% | 6.0902 | Loss 5-10% |  |  | 799(44.5)
615 | 1220 | KNR | KANTI NAGAR | KRI057 | TG-KRI057A-1 | DT-1 | WEST KANTI NAGAR:ID | 1 | 990 | 19504088 | 866 | 2019-06-29 22:30 | 244 | 990 | 280 | 1140 | 342 | 1390 | 350 | 614 | 106 |  |  | 106 | 82% | 73% | 79% | 87% | 8.4094 | Loss 5-10% | 858(106) | 1084(521) | 987(529.5) | 992(523) | 939(445.5) | 858(130.5)
616 | 1220 | KNR | KANTI NAGAR | KRI066 | TG-KRI066A-1 | DT-1 | East Azad Nagar Primary School | 1 | 990 | 19506021 | 874 | 2019-06-02 23:00 | 268 | 1102 | 283 | 1170 | 323 | 1324 | 197 | 614 | 105 |  |  | 105 | 88% | 77% | 71% | 88% | 7.0287 | Loss 5-10% |  |  | 1101(40) | 818(32)
617 | 1220 | KNR | KRISHNA NAGAR | KRI001 | TG-KRI001A-1 | DT-1 | A-BLOCK KRN:PL | 2 | 990 | 19505570 | 896 | 2019-06-11 01:00 | 249 | 1104 | 372 | 1718 | 275 | 1254 | 555 | 589.5 | 129.5 | 0.5 |  | 130 | 91% | 74% | 76% | 88% | 4.7581 | Loss 0-5%
618 | 1220 | KNR | KRISHNA NAGAR | KRI003 | TG-KRI003A-1 | DT-1 | B-BLOCK KRISHNA NAGAR 8/24:PM | 1 | 630 | 19505516 | 587 | 2019-06-12 00:30 | 205 | 877 | 201 | 866 | 180 | 769 | 103 | 583.5 | 133.5 | 3 |  | 136.5 | 93% | 62% | 67% | 87% | 4.7734 | Loss 0-5% |  | 507(39) | 591(110.5) | 539(56.5)
619 | 1220 | KNR | KRISHNA NAGAR | KRI004 | TG-KRI004A-1 | DT-1 | K-BLK KRN GHONOLI CHOWK:PL | 2 | 990 | 19500863 | 953 | 2019-06-12 | 300 | 1254 | 351 | 1475 | 302 | 1265 | 216 | 407.5 | 298.5 | 14 |  | 312.5 | 96% | 72% | 84% | 95% | 18.6935 | Loss 10-20% |  | 859(78.5) | 899(267.5) | 905(168) | 817(85.5)
620 | 1220 | KNR | KRISHNA NAGAR | KRI008 | TG-KRI008A-1 | DT-1 | C-BLOCK KRISHNA NAGAR NO 1:ID | 2 | 990 | 19505740 | 876 | 2019-06-01 20:30 | 303 | 1253 | 285 | 1171 | 288 | 1194 | 74 | 608 | 112 |  |  | 112 | 84% | 53% | 89% | 87% | 7.0106 | Loss 5-10% |  | 768(26.5) | 849(44)
621 | 1220 | KNR | KRISHNA NAGAR | KRI008 | TG-KRI008A-2 | DT-2 | C-BLOCK KRISHNA NAGAR NO 1:ID | 2 | 990 | 19506020 | 1185 | 2019-06-01 19:30 | 220 | 927 | 438 | 2069 | 527 | 2370 | 1319 | 480 | 204 | 34.5 | 1.5 | 240 | 78% | 52% | 120% | 96% | 7.0106 | Loss 5-10% |  | 872(99.5) | 932(165.5) | 1023(123.5)
622 | 1220 | KNR | KRISHNA NAGAR | KRI011 | TG-KRI011A-1 | DT-1 | D-BLOCK KRISHNA NAGAR:PL | 1 | 990 | 19506772 | 1201 | 2019-06-01 19:00 | 449 | 1967 | 309 | 1313 | 444 | 2053 | 701 | 579.5 | 138 | 0.5 | 0.5 | 139 | 86% | 50% | 121% | 82% | 19.0766 | Loss 10-20%
623 | 1220 | KNR | KRISHNA NAGAR | KRI013 | TG-KRI013A-1 | DT-1 | F-BLOCK KRISHNA NAGAR:K | 2 | 990 | 19506776 | 1058.1356 | 2019-06-01 19:00 | 364.2844 | 1638.8537 | 424.5189 | 1845.574 | 269.3322 | 1131.6956 | 636.2252 | 389 | 262.5 | 54.5 | 8 | 325 | 104% | 66% | 107% | 105% | 14.4912 | Loss 10-20% |  | 1008(144) | 1133(312) | 1044(193.5) | 885(117)
624 | 1220 | KNR | KRISHNA NAGAR | KRI014 | TG-KRI014A-1 | DT-1 | E-BLOCK KRN (PARK) E 15,16:PL | 1 | 990 | 19506370 | 899 | 2019-06-11 23:00 | 210 | 886 | 265 | 1145 | 423 | 1807 | 823 | 675.5 | 44 | 0.5 |  | 44.5 | 79% | 46% | 55% | 91% | 4.7829 | Loss 0-5% |  |  | 804(42.5)
625 | 1220 | KNR | KRISHNA NAGAR | KRI015 | TG-KRI015A-2 | DT-2 | E-BLOCK KRN LAJ PAT RAI CHOWK:PL | 2 | 630 | 19505772 | 537 | 2019-06-11 01:00 | 228 | 1103 | 172 | 794 | 136 | 607 | 433 | 673 | 45.5 |  |  | 45.5 | 85% | 62% | 84% | 78% | 9.579 | Loss 5-10%
626 | 1220 | KNR | KRISHNA NAGAR | KRI017 | TG-KRI017A-1 | DT-1 | F-BLOCK KRN PLM:PL | 2 | 990 | 19506778 | 986 | 2019-06-11 03:30 | 427 | 2101 | 297 | 1384 | 262 | 1224 | 809 | 686.5 | 27.5 | 0.5 |  | 28 | 100% | 52% | 67% | 86% | 15.218 | Loss 10-20% |  | 932(40.5)
627 | 1220 | KNR | KRISHNA NAGAR | KRI017 | TG-KRI017A-2 | DT-2 | F-BLOCK KRN PLM:PL | 2 | 630 | 19506503 | 556 | 2019-06-11 01:00 | 147 | 652 | 228 | 1011 | 181 | 799 | 312 | 673.5 | 41 |  |  | 41 | 88% | 52% | 69% | 86% | 15.218 | Loss 10-20%
628 | 1220 | KNR | KRISHNA NAGAR | KRI018 | TG-KRI018A-2 | DT-2 | H-BLOCK KRISHNA NAGAR (MOTHER DAIRY):K | 2 | 630 | 19506531 | 629 | 2019-06-11 00:30 | 167 | 751 | 222 | 995 | 240 | 1074 | 291 | 633 | 80.5 | 4 |  | 84.5 | 100% | 64% | 73% | 93% | 6.6704 | Loss 5-10% |  | 481(25)
629 | 1220 | KNR | KRISHNA NAGAR | KRI019 | TG-KRI019A-1 | DT-1 | J-BLOCK KRN:PL | 2 | 1600 | 19506883 | 1299 | 2019-06-03 | 382 | 1663 | 360 | 1564 | 556 | 2455 | 846 | 689.5 | 29.5 |  |  | 29.5 | 81% | 49% | 54% | 78% | 4.7205 | Loss 0-5% |  | 1180(176) | 1230(285) | 1139(91)
630 | 1220 | KNR | KRISHNA NAGAR | KRI019 | TG-KRI019A-2 | DT-2 | J-BLOCK KRN:PL | 2 | 990 | 19505280 | 1013 | 2019-06-11 03:30 | 335 | 1417 | 334 | 1419 | 343 | 1445 | 27 | 507 | 189.5 | 20.5 | 1 | 211 | 102% | 75% | 86% | 94% | 4.7205 | Loss 0-5% |  | 870(43.5) | 980(142.5) | 866(76.5)
631 | 1220 | KNR | KRISHNA NAGAR | KRI020 | TG-KRI020A-1 | DT-1 | JHEEL NO. 1:PL | 1 | 630 | 19503581 | 528 | 2019-06-02 16:00 | 172 | 729 | 183 | 775 | 173 | 723 | 49 | 594 | 126 |  |  | 126 | 65% | 44% | 84% | 74% | 10.0607 | Loss 10-20% |  | 489(31.5) | 539(122.5) | 530(71) | 493(47.5)
632 | 1220 | KNR | KRISHNA NAGAR | KRI021 | TG-KRI021A-1 | DT-1 | JHEEL NO. 2:PL | 2 | 990 | 19506780 | 885 | 2019-06-30 16:00 | 298 | 1255 | 279 | 1176 | 307 | 1303 | 110 | 510.5 | 208 |  |  | 208 | 89% | 67% | 89% | 84% | 15.2796 | Loss 10-20% |  | 814(36.5) | 904(147) | 847(99.5)
633 | 1220 | KNR | KRISHNA NAGAR | KRI034 | TG-KRI034A-2 | DT-2 | OLD ANARKALI:ID | 3 | 990 | 19506681 | 1155.2748 | 2019-06-11 23:30 | 434.2842 | 1825.3371 | 333.0169 | 1392.2691 | 387.9737 | 1609.5823 | 375.0487 | 499.5 | 116 | 53 | 49.5 | 218.5 | 116% | 71% | 78% | 117% | 5.2244 | Loss 5-10% |  | 1076(71.5) | 1119(216) | 1089(152.5) | 943(114)
634 | 1220 | KNR | KRISHNA NAGAR | KRI034 | TG-KRI034A-3 | DT-3 | OLD ANARKALI:ID | 3 | 630 | 19506766 | 538 | 2019-06-30 23:30 | 214 | 918 | 170 | 721 | 153 | 649 | 241 | 635.5 | 84.5 |  |  | 84.5 | 85% | 61% | 66% | 85% | 5.2244 | Loss 5-10%
635 | 1220 | KNR | KRISHNA NAGAR | KRI035 | TG-KRI035A-1 | DT-1 | PANDIT PARK:PM | 1 | 990 | 19500865 | 1067.1793 | 2019-06-01 16:00 | 324.445 | 1399.4348 | 368.913 | 1605.5751 | 373.8213 | 1604.4523 | 205.5812 | 423.5 | 259.5 | 33.5 | 3 | 296 | 78% | 63% | 108% | 77% | 36.8993 | Loss >30% | 848(119) | 990(192) | 1138(298) | 1052(286) | 998(281)
636 | 1220 | KNR | KRISHNA NAGAR | KRI036 | TG-KRI036A-1 | DT-1 | RADHA PURI EXTN.(NALAH) NO. 1:PL | 2 | 990 | 19506680 | 915 | 2019-06-30 23:00 | 224 | 969 | 361 | 1583 | 329 | 1449 | 559 | 581 | 132.5 | 6 |  | 138.5 | 92% | 62% | 63% | 92% | 4.2564 | Loss 0-5% |  | 819(43) | 920(134) | 899(74) | 783(28.5)
637 | 1220 | KNR | KRISHNA NAGAR | KRI038 | TG-KRI038A-1 | DT-1 | RADHA PURI NEW KRISHNA NAGAR:PL | 1 | 990 | 19506679 | 849 | 2019-06-30 23:30 | 164 | 705 | 285 | 1228 | 399 | 1723 | 882 | 650.5 | 69.5 |  |  | 69.5 | 84% | 52% | 58% | 86% | 3.4673 | Loss 0-5%
638 | 1220 | KNR | KRISHNA NAGAR | KRI041 | TG-KRI041A-1 | DT-1 | RAM NAGAR L.N.MANDIR:PL | 1 | 1600 | 19506779 | 1465 | 2019-06-11 01:00 | 776 | 3572 | 313 | 1264 | 375 | 1596 | 2161 | 665 | 54.5 | 0.5 |  | 55 | 92% | 53% | 58% | 82% | 19.8907 | Loss 10-20% |  | 964(101.5) | 1176(198) | 1052(134.5) | 868(87.5)
639 | 1220 | KNR | KRISHNA NAGAR | KRI042 | TG-KRI042A-2 | DT-2 | RAM NAGAR PARK(PLM) | 2 | 990 | 19505114 | 826.7989 | 2019-06-11 19:30 | 208.5421 | 891.8152 | 297.6415 | 1280.1783 | 320.6154 | 1381.308 | 447.5804 | 683.5 | 36 |  |  | 36 | 71% | 47% | 84% | 75% | 20.721 | Loss 20-30% |  |  | 821(29)
640 | 1220 | KNR | KRISHNA NAGAR | KRI047 | TG-KRI047A-1 | DT-1 | SHASTRI PARK:PL | 1 | 990 | 19502447 | 989 | 2019-06-11 23:30 | 315 | 1363 | 336 | 1466 | 338 | 1472 | 106 | 405.5 | 282.5 | 30 |  | 312.5 | 99% | 73% | 93% | 100% | 36.7223 | Loss >30% |  | 966(192.5) | 976(447) | 1014(336) | 893(275.5) | 810(69.5)
641 | 1220 | KNR | KRISHNA NAGAR | KRI048 | TG-KRI048A-1 | DT-1 | ST.LIGHT OPP SWARN CINEMA ROAD NO 57:PM | 1 | 630 | 19505726 | 569 | 2019-06-26 23:30 | 150 | 649 | 129 | 557 | 289 | 1288 | 690 | 640.5 | 79 | 0.5 |  | 79.5 | 90% | 55% | 60% | 90% | 2.465 | Loss 0-5%
642 | 1220 | KNR | KRISHNA NAGAR | KRI051 | TG-KRI051A-2 | DT-2 | WEST ARJUN NAGAR:ID | 2 | 630 | 19506784 | 621 | 2019-06-09 23:30 | 198 | 813 | 193 | 794 | 230 | 952 | 149 | 459.5 | 236.5 | 23 |  | 259.5 | 96% | 64% | 95% | 99% | 7.9875 | Loss 5-10% |  | 644(129) |  |  | 544(112.5)
643 | 1230 | LNR | ANAND VIHAR ISBT | MAN022 | TG-MAN022A-2 | DT-2 | JOSHI COLONY:ID | 2 | 990 | 19505405 | 900 | 2019-06-29 23:00 | 316 | 1382 | 300 | 1324 | 285 | 1248 | 116 | 595.5 | 123 | 1 |  | 124 | 90% | 71% | 76% | 91% | 4.1643 | Loss 0-5%
644 | 1230 | LNR | ANAND VIHAR ISBT | MAN049 | TG-MAN049A-1 | DT-1 | MADHU VIHAR S/STN-1:ID | 2 | 990 | 19506121 | 801 | 2019-06-29 16:00 | 248 | 1042 | 267 | 1120 | 286 | 1209 | 145 | 600 | 118.5 |  |  | 118.5 | 51% | 39% | 81% | 70% | 3.836 | Loss 0-5% |  |  |  |  | 853(57)
645 | 1230 | LNR | ANAND VIHAR ISBT | MAN049 | TG-MAN049A-2 | DT-2 | MADHU VIHAR S/STN-1:ID | 2 | 990 | 19501135 | 917 | 2019-06-12 17:00 | 324 | 1306 | 299 | 1205 | 294 | 1185 | 113 | 511.5 | 205.5 | 2 |  | 207.5 | 70% | 64% | 93% | 80% | 3.836 | Loss 0-5% |  | 1004(82.5) | 997(183.5) | 985(199.5) | 781(54.5)
646 | 1230 | LNR | ANAND VIHAR ISBT | MAN052 | TG-MAN052A-1 | DT-1 | HASANPUR VILLAGE:PL | 1 | 990 | 19504543 | 847 | 2019-06-11 15:00 | 280 | 1155 | 266 | 1089 | 300 | 1234 | 126 | 615.5 | 104.5 |  |  | 104.5 | 48% | 40% | 86% | 50% | 4.2201 | Loss 0-5% |  |  | 853(66)
647 | 1230 | LNR | ANAND VIHAR ISBT | MAN053 | TG-MAN053A-1 | DT-1 | GAZIPUR VILLAGE NEAR TEMPEL:PL | 1 | 990 | 19506444 | 876 | 2019-06-27 22:30 | 295 | 1224 | 298 | 1230 | 282 | 1168 | 59 | 548.5 | 170.5 |  |  | 170.5 | 88% | 72% | 85% | 88% | 16.9067 | Loss 10-20% |  | 805(28.5) | 872(402) | 939(225) | 844(62.5)
648 | 1230 | LNR | ANAND VIHAR ISBT | MAN054 | TG-MAN054A-1 | DT-1 | GAZIPUR VILLAGE NEAR SCHOOL:PL | 2 | 990 | 19502869 | 991 | 2019-06-13 15:00 | 371 | 1488 | 285 | 1232 | 336 | 1415 | 228 | 143 | 532.5 | 42 | 0.5 | 575 | 87% | 79% | 100% | 91% | 36.1615 | Loss >30% | 752(29.5) | 904(318) | 911(522) | 937(544) | 969(482.5) | 849(237)
649 | 1230 | LNR | ANAND VIHAR ISBT | MAN066 | TG-MAN066A-2 | DT-2 | S/STN.NO-9, PPG CGHS:ID | 2 | 630 | 19506561 | 791 | 2019-06-30 23:30 | 245 | 1039 | 259 | 1103 | 288 | 1219 | 158 | 384.5 | 207.5 | 71 | 57 | 335.5 | 116% | 91% | 96% | 126% | 13.1165 | Loss 10-20% |  |  |  |  | 679(132.5) | 537(40)
650 | 1230 | LNR | ANAND VIHAR ISBT | MAN068 | TG-MAN068A-1 | DT-1 | S/STN.NO-13, PPG CGHS:ID | 1 | 400 | 19502466 | 312 | 2019-06-30 23:00 | 92 | 408 | 128 | 568 | 91 | 403 | 162 | 679.5 | 40.5 |  |  | 40.5 | 73% | 64% | 69% | 78% | 4.8531 | Loss 0-5% |  |  |  | 313(64.5) | 294(40.5)
651 | 1230 | LNR | ANAND VIHAR ISBT | MAN252 | TG-MAN252A-2 | DT-2 | S/STN NO-10, CGHS, PPG | 2 | 630 | 19504305 | 714 | 2019-06-30 23:30 | 210 | 953 | 276 | 1274 | 227 | 1037 | 289 | 206.5 | 401.5 | 90 | 22 | 513.5 | 108% | 82% | 98% | 113% | 4.0334 | Loss 0-5%
652 | 1230 | LNR | ANAND VIHAR ISBT | MAN292 | TG-MAN292A-1 | DT-1 | GAZIPUR PARK NEAR ASHOK DAIRY STN:OD | 1 | 990 | 19506443 | 868 | 2019-06-29 16:00 | 265 | 1058 | 276 | 1113 | 328 | 1327 | 247 | 404 | 314 |  |  | 314 | 78% | 69% | 88% | 87% | 37.9141 | Loss >30% |  | 832(139.5) | 822(595) | 1040(283) | 840(272) | 767(91.5)
653 | 1230 | LNR | ANAND VIHAR ISBT | PVR032 | TG-PVR032A-1 | DT-1 | S/STN. NO.7 F.I.E., PPG:ID | 2 | 990 | 19505236 | 841 | 2019-06-20 14:30 | 220 | 923 | 306 | 1300 | 316 | 1328 | 392 | 656 | 57.5 |  |  | 57.5 | 26% | 27% | 85% | 26% | 5.6528 | Loss 5-10%
654 | 1230 | LNR | ANAND VIHAR ISBT | PVR034 | TG-PVR034A-1 | DT-1 | S/STN. NO.8 F.I.E., PPG:ID | 3 | 630 | 19505921 | 577 | 2019-06-12 15:00 | 191 | 806 | 190 | 798 | 195 | 820 | 19 | 596 | 121 | 3 |  | 124 | 42% | 50% | 92% | 44% | 8.0328 | Loss 5-10% | 556(53) | 599(102.5) | 590(45.5) | 654(27) | 702(111) | 705(158)
655 | 1230 | LNR | ANAND VIHAR ISBT | PVR035 | TG-PVR035A-1 | DT-1 | S/STN. NO.9 F.I.E., PPG:ID | 1 | 990 | 19504874 | 799 | 2019-06-27 12:30 | 250 | 1006 | 280 | 1129 | 268 | 1078 | 107 | 678 | 36.5 |  |  | 36.5 | 17% | 31% | 81% | 19% | 2.9671 | Loss 0-5% |  |  | 875(104) | 832(56) | 851(70.5) | 814(26)
656 | 1230 | LNR | ANAND VIHAR ISBT | PVR039 | TG-PVR039A-1 | DT-1 | S/STN. NO.14 F.I.E., PPG:ID | 2 | 630 | 19505920 | 539 | 2019-06-28 17:00 | 183 | 757 | 170 | 698 | 186 | 767 | 65 | 686.5 | 33.5 |  |  | 33.5 | 46% | 44% | 85% | 43% | 4.5327 | Loss 0-5% | 562(156.5) | 639(191) | 654(226.5) | 661(221) | 630(211) | 654(186)
657 | 1230 | LNR | ANAND VIHAR ISBT | PVR040 | TG-PVR040A-2 | DT-2 | S/STN. NO.15 F.I.E., PPG:ID | 2 | 400 | 19504783 | 384 | 2019-06-06 11:30 | 121 | 520 | 149 | 640 | 114 | 491 | 137 | 598 | 118 | 4 |  | 122 | 32% | 35% | 96% | 35% | 3.361 | Loss 0-5% | 388(118.5) | 440(123) | 445(187.5) | 460(220) |  | 475(198.5)
658 | 1230 | LNR | ANAND VIHAR ISBT | PVR041 | TG-PVR041A-2 | DT-2 | S/STN. NO.16 F.I.E., PPG:ID | 2 | 630 | 19502874 | 573 | 2019-06-29 13:00 | 195 | 801 | 180 | 738 | 198 | 818 | 74 | 611.5 | 108 | 0.5 |  | 108.5 | 34% | 30% | 91% | 35% | 3.4315 | Loss 0-5% | 525(47) | 543(56) | 581(110) | 534(92.5) | 538(72.5) | 512(41)
659 | 1230 | LNR | ANAND VIHAR ISBT | PVR045 | TG-PVR045A-1 | DT-1 | S/STN. NO.20 F.I.E., PPG:ID | 3 | 400 | 19505036 | 351 | 2019-06-13 12:30 | 121 | 516 | 117 | 503 | 113 | 488 | 24 | 627.5 | 92.5 |  |  | 92.5 | 36% | 43% | 88% | 42% | 3.8502 | Loss 0-5%
660 | 1230 | LNR | ANAND VIHAR ISBT | PVR045 | TG-PVR045A-3 | DT-3 | S/STN. NO.20 F.I.E., PPG:ID | 3 | 630 | 19505035 | 589 | 2019-06-03 15:30 | 199 | 827 | 216 | 903 | 174 | 724 | 156 | 580 | 136.5 | 3.5 |  | 140 | 43% | 43% | 94% | 43% | 3.8502 | Loss 0-5% |  | 544(54.5) | 576(125) | 527(98.5) | 548(114) | 554(87)
661 | 1230 | LNR | ANAND VIHAR ISBT | PVR046 | TG-PVR046A-1 | DT-1 | S/STN. NO.21 F.I.E., PPG:ID | 2 | 630 | 19506665 | 485 | 2019-06-07 16:00 | 164 | 716 | 164 | 723 | 157 | 689 | 32 | 693.5 | 26.5 |  |  | 26.5 | 14% | 31% | 77% | 15% | 3.0005 | Loss 0-5% |  | 533(52) | 501(70) | 522(83)
662 | 1230 | LNR | ANAND VIHAR ISBT | PVR047 | TG-PVR047A-1 | DT-1 | S/STN. NO.22 F.I.E., PPG:ID | 2 | 630 | 19506769 | 782 | 2019-06-06 17:00 | 271 | 1097 | 257 | 1032 | 254 | 1028 | 67 | 469.5 | 69.5 | 67.5 | 113.5 | 250.5 | 30% | 51% | 124% | 38% | 5.8263 | Loss 5-10% |  | 567(45) | 748(228.5) | 730(229.5) | 712(222.5) | 714(194)
663 | 1230 | LNR | ANAND VIHAR ISBT | PVR047 | TG-PVR047A-2 | DT-2 | S/STN. NO.22 F.I.E., PPG:ID | 2 | 630 | 19504981 | 643 | 2019-06-08 14:00 | 193 | 799 | 228 | 956 | 222 | 925 | 144 | 521 | 135.5 | 59.5 | 1.5 | 196.5 | 25% | 36% | 102% | 25% | 5.8263 | Loss 5-10% | 653(183) | 741(240.5) | 563(62.5)
664 | 1230 | LNR | ANAND VIHAR ISBT | PVR049 | TG-PVR049A-2 | DT-2 | S/STN. NO.24 F.I.E., PPG:ID | 2 | 630 | 19506489 | 576 | 2019-06-14 14:30 | 190 | 808 | 174 | 745 | 212 | 911 | 145 | 591 | 127.5 | 1.5 |  | 129 | 18% | 35% | 91% | 22% | 4.0718 | Loss 0-5% |  |  | 745(197) | 747(241.5) | 725(253.5)
665 | 1230 | LNR | LAXMI NAGAR | LGR001 | TG-LGR001A-1 | DT-1 | PRIYADARSHINI VIHAR:ID | 2 | 990 | 19505699 | 961.7521 | 2019-06-27 | 302.3323 | 1368.8865 | 327.9906 | 1485.734 | 331.4292 | 1493.1933 | 120.7501 | 672.5 | 42.5 | 3 |  | 45.5 | 97% | 61% | 70% | 90% | 3.5476 | Loss 0-5% |  |  | 844(35.5)
666 | 1230 | LNR | LAXMI NAGAR | LGR002 | TG-LGR002A-3 | DT-3 | PNB BANK ENCLAVE:ID | 3 | 990 | 19504436 | 1045 | 2019-06-12 00:30 | 391 | 1644 | 320 | 1326 | 334 | 1396 | 289 | 491.5 | 143 | 45 | 12 | 200 | 106% | 86% | 80% | 105% | 4.3519 | Loss 0-5% |  | 1050(111) | 1044(211.5) | 1058(136.5) | 879(66.5)
667 | 1230 | LNR | LAXMI NAGAR | LGR003 | TG-LGR003A-1 | DT-1 | LNR COMPLAINT CENTER:ID | 3 | 630 | 19502778 | 523 | 2019-06-30 20:00 | 239 | 988 | 145 | 586 | 139 | 569 | 410 | 613.5 | 106.5 |  |  | 106.5 | 76% | 52% | 83% | 83% | 3.5995 | Loss 0-5% |  |  | 527(62.5)
668 | 1230 | LNR | LAXMI NAGAR | LGR004 | TG-LGR004A-1 | DT-1 | KISHAN KUNJ:K | 3 | 990 | 19505542 | 1036 | 2019-06-30 00:30 | 355 | 1502 | 336 | 1409 | 345 | 1445 | 82 | 580.5 | 129.5 | 5.5 | 2 | 137 | 105% | 72% | 65% | 93% | 8.7407 | Loss 5-10% |  | 1051(107.5) | 939(135.5) | 889(78)
669 | 1230 | LNR | LAXMI NAGAR | LGR004 | TG-LGR004A-2 | DT-2 | KISHAN KUNJ:K | 3 | 990 | 19505955 | 1288 | 2019-06-30 00:30 | 470 | 2013 | 417 | 1756 | 401 | 1689 | 296 | 490.5 | 132.5 | 62 | 33 | 227.5 | 130% | 82% | 77% | 111% | 8.7407 | Loss 5-10% |  | 934(27) | 1190(192) | 1066(173.5) | 914(121)
670 | 1230 | LNR | LAXMI NAGAR | LGR004 | TG-LGR004A-3 | DT-3 | KISHAN KUNJ:K | 3 | 990 | 19506173 | 1313 | 2019-06-30 00:30 | 476 | 2043 | 448 | 1904 | 389 | 1642 | 353 | 394.5 | 177 | 67 | 80 | 324 | 133% | 89% | 91% | 126% | 8.7407 | Loss 5-10% |  | 1109(126.5) | 1146(282.5) | 1128(220.5) | 978(168) | 828(28)
671 | 1230 | LNR | LAXMI NAGAR | LGR007 | TG-LGR007A-2 | DT-2 | WALIA NURSHING HOME:PL | 2 | 630 | 19505459 | 631 | 2019-06-08 15:00 | 208 | 906 | 207 | 912 | 215 | 940 | 32 | 543 | 168.5 | 7 | 0.5 | 176 | 73% | 54% | 100% | 73% | 4.4856 | Loss 0-5% |  |  | 521(62.5) | 590(114) | 617(116.5) | 518(39.5)
672 | 1230 | LNR | LAXMI NAGAR | LGR008 | TG-LGR008A-1 | DT-1 | LALITA PARK:K | 3 | 990 | 19506683 | 825 | 2019-06-28 23:30 | 272 | 1230 | 232 | 1033 | 320 | 1432 | 346 | 665 | 54.5 |  |  | 54.5 | 79% | 55% | 57% | 83% | 5.1258 | Loss 5-10% |  |  | 789(57)
673 | 1230 | LNR | LAXMI NAGAR | LGR008 | TG-LGR008A-3 | DT-3 | LALITA PARK:K | 3 | 990 | 19506761 | 785 | 2019-06-28 23:30 | 308 | 1371 | 191 | 842 | 286 | 1287 | 493 | 682.5 | 37 |  |  | 37 | 77% | 51% | 59% | 79% | 5.1258 | Loss 5-10%
674 | 1230 | LNR | LAXMI NAGAR | LGR009 | TG-LGR009A-1 | DT-1 | RAMESH PARK AKHARA:PL | 2 | 990 | 19503006 | 855 | 2019-06-01 04:30 | 273 | 1139 | 251 | 1040 | 332 | 1403 | 324 | 680 | 39.5 |  |  | 39.5 | 86% | 76% | 73% | 73% | 5.077 | Loss 5-10% |  | 929(187.5) | 1023(390.5) | 989(232) | 843(132.5)
675 | 1230 | LNR | LAXMI NAGAR | LGR009 | TG-LGR009A-2 | DT-2 | RAMESH PARK AKHARA:PL | 2 | 990 | 19506036 | 917 | 2019-06-01 19:00 | 363 | 1740 | 396 | 1763 | 158 | 673 | 1078 | 661.5 | 56 | 0.5 |  | 56.5 | 49% | 38% | 93% | 51% | 5.077 | Loss 5-10%
676 | 1230 | LNR | LAXMI NAGAR | LGR011 | TG-LGR011A-1 | DT-1 | JAGAT RAM PARK:K | 5 | 990 | 19502822 | 934 | 2019-06-30 00:30 | 359 | 1503 | 283 | 1197 | 292 | 1219 | 296 | 584.5 | 128.5 | 7 |  | 135.5 | 94% | 67% | 64% | 92% | 8.6892 | Loss 5-10% | 931(27) | 1098(197.5) | 1130(219) | 912(104) | 803(51.5)
677 | 1230 | LNR | LAXMI NAGAR | LGR011 | TG-LGR011A-2 | DT-2 | JAGAT RAM PARK:K | 5 | 990 | 19502825 | 906 | 2019-06-06 03:30 | 312 | 1349 | 302 | 1296 | 292 | 1269 | 70 | 606.5 | 112 | 0.5 |  | 112.5 | 91% | 63% | 65% | 89% | 8.6892 | Loss 5-10% |  |  | 870(78) | 870(70)
678 | 1230 | LNR | LAXMI NAGAR | LGR011 | TG-LGR011A-3 | DT-3 | JAGAT RAM PARK:K | 5 | 990 | 19506037 | 928 | 2019-06-03 23:00 | 365 | 1607 | 355 | 1510 | 207 | 885 | 679 | 620.5 | 99 | 0.5 |  | 99.5 | 85% | 60% | 66% | 94% | 8.6892 | Loss 5-10% |  | 1034(30) | 1005(96.5) | 844(48.5)
679 | 1230 | LNR | LAXMI NAGAR | LGR012 | TG-LGR012A-1 | DT-1 | GURU RAM DASS NAGAR:PL | 3 | 990 | 19502826 | 891 | 2019-06-30 23:30 | 298 | 1285 | 318 | 1368 | 276 | 1181 | 162 | 615.5 | 104.5 |  |  | 104.5 | 90% | 60% | 66% | 90% | 5.962 | Loss 5-10% |  | 1158(174.5) | 1085(216) | 1148(156) | 884(113)
680 | 1230 | LNR | LAXMI NAGAR | LGR012 | TG-LGR012A-2 | DT-2 | GURU RAM DASS NAGAR:PL | 3 | 990 | 19502829 | 1153.7459 | 2019-06-12 | 364.1066 | 1501.9659 | 377.1575 | 1548.4561 | 412.4819 | 1714.531 | 193.5538 | 296.5 | 101.5 | 43.5 | 48.5 | 193.5 | 117% | 78% | 84% | 116% | 5.962 | Loss 5-10% | 843(49) | 1058(104.5) | 1125(276.5) | 1075(205) | 974(181) | 840(35)
681 | 1230 | LNR | LAXMI NAGAR | LGR012 | TG-LGR012A-3 | DT-3 | GURU RAM DASS NAGAR:PL | 3 | 990 | 19505569 | 1059 | 2019-06-30 01:30 | 395 | 1655 | 367 | 1557 | 297 | 1238 | 378 | 555.5 | 141 | 18.5 | 3 | 162.5 | 107% | 72% | 69% | 96% | 5.962 | Loss 5-10% |  | 1014(190) | 775(345) | 808(271)
682 | 1230 | LNR | LAXMI NAGAR | LGR014 | TG-LGR014A-1 | DT-1 | TIKONA PARK:ID | 4 | 990 | 19502942 | 1007 | 2019-06-11 23:30 | 257 | 1050 | 366 | 1516 | 384 | 1597 | 511 | 504 | 192 | 21 | 0.5 | 213.5 | 100% | 70% | 86% | 102% | 8.6616 | Loss 5-10% |  | 1032(141.5) | 1130(358) | 1116(194) | 794(41)
683 | 1230 | LNR | LAXMI NAGAR | LGR014 | TG-LGR014A-2 | DT-2 | TIKONA PARK:ID | 4 | 990 | 19505669 | 865 | 2019-06-30 23:30 | 241 | 1049 | 362 | 1591 | 262 | 1145 | 501 | 685.5 | 34.5 |  |  | 34.5 | 84% | 59% | 81% | 87% | 8.6616 | Loss 5-10% |  | 1167(197) | 1244(305.5)
684 | 1230 | LNR | LAXMI NAGAR | LGR014 | TG-LGR014A-3 | DT-3 | TIKONA PARK:ID | 4 | 630 | 19505467 | 727 | 2019-06-11 23:30 | 295 | 1191 | 198 | 794 | 234 | 935 | 349 | 468.5 | 161.5 | 53 | 37 | 251.5 | 115% | 75% | 81% | 115% | 8.6616 | Loss 5-10% |  |  | 669(120.5) | 750(310.5) | 658(237) | 567(47.5)
685 | 1230 | LNR | LAXMI NAGAR | LGR016 | TG-LGR016A-1 | DT-1 | WEST GURU ANGAD NAGAR, SCHOOL WALA | 1 | 990 | 19502944 | 755 | 2019-06-10 00:30 | 224 | 938 | 265 | 1126 | 265 | 1117 | 184 | 693 | 27 |  |  | 27 | 76% | 56% | 69% | 76% | 3.1758 | Loss 0-5% |  |  | 788(39.5)
686 | 1230 | LNR | LAXMI NAGAR | LGR017 | TG-LGR017A-2 | DT-2 | POLICE QTR SHAKARPUR:ID | 2 | 990 | 19503391 | 784 | 2019-06-30 00:30 | 283 | 1252 | 237 | 1049 | 264 | 1170 | 177 | 664.5 | 31.5 |  |  | 31.5 | 79% | 64% | 60% | 76% | 9.1818 | Loss 5-10% |  |  | 804(100.5) | 840(57.5)
687 | 1230 | LNR | LAXMI NAGAR | LGR018 | TG-LGR018A-2 | DT-2 | D BLOCK KHATTA VIKAS MARG:PL | 3 | 990 | 19504830 | 830 | 2019-06-11 22:30 | 312 | 1363 | 283 | 1239 | 235 | 1038 | 284 | 545.5 | 174.5 |  |  | 174.5 | 82% | 64% | 79% | 84% | 9.5255 | Loss 5-10% |  | 871(173.5) | 987(469.5) | 1121(385) | 989(346) | 766(71.5)
688 | 1230 | LNR | LAXMI NAGAR | LGR019 | TG-LGR019A-1 | DT-1 | RAMESH PARK J & K BLOCK:PL | 1 | 1600 | 19502336 | 1286 | 2019-06-01 | 421 | 1847 | 471 | 2103 | 393 | 1728 | 332 | 672 | 48 |  |  | 48 | 80% | 53% | 58% | 79% | 8.5694 | Loss 5-10% |  | 1183(199.5)
689 | 1230 | LNR | LAXMI NAGAR | LGR020 | TG-LGR020A-2 | DT-2 | MASTER BLOCK SHAKARPUR:PL | 2 | 630 | 19505481 | 546 | 2019-06-28 23:00 | 158 | 698 | 154 | 673 | 234 | 1044 | 359 | 650 | 70 |  |  | 70 | 86% | 57% | 62% | 87% | 3.0777 | Loss 0-5%
690 | 1230 | LNR | LAXMI NAGAR | LGR021 | TG-LGR021A-1 | DT-1 | G-BLOCK SHAKARPUR:K | 2 | 990 | 19504461 | 1055 | 2019-06-12 | 367 | 1564 | 359 | 1533 | 330 | 1417 | 134 | 493 | 131.5 | 56 | 14.5 | 202 | 107% | 83% | 76% | 105% | 9.4444 | Loss 5-10%
691 | 1230 | LNR | LAXMI NAGAR | LGR021 | TG-LGR021A-2 | DT-2 | G-BLOCK SHAKARPUR:K | 2 | 990 | 19502945 | 1186 | 2019-06-30 01:00 | 406 | 1720 | 384 | 1638 | 396 | 1690 | 72 | 512.5 | 130.5 | 57.5 | 16.5 | 204.5 | 120% | 77% | 77% | 108% | 9.4444 | Loss 5-10% |  | 975(98.5) | 1121(203.5) | 1090(141) | 1038(93)
692 | 1230 | LNR | LAXMI NAGAR | LGR022 | TG-LGR022A-1 | DT-1 | WB BLOCK SHAKARPUR:K | 4 | 990 | 19506691 | 1031 | 2019-06-30 23:00 | 336 | 1432 | 331 | 1384 | 363 | 1540 | 139 | 543.5 | 137 | 35.5 | 4 | 176.5 | 101% | 66% | 74% | 104% | 4.679 | Loss 0-5% |  |  | 846(64.5) | 866(51.5) | 855(30)
693 | 1230 | LNR | LAXMI NAGAR | LGR022 | TG-LGR022A-2 | DT-2 | WB BLOCK SHAKARPUR:K | 4 | 990 | 19502950 | 984 | 2019-06-30 23:30 | 348 | 1486 | 361 | 1563 | 274 | 1157 | 373 | 546 | 149.5 | 23.5 |  | 173 | 98% | 65% | 72% | 99% | 4.679 | Loss 0-5% |  | 871(55) | 1089(196) | 1096(182.5) | 956(68)
694 | 1230 | LNR | LAXMI NAGAR | LGR022 | TG-LGR022A-3 | DT-3 | WB BLOCK SHAKARPUR:K | 4 | 990 | 19504770 | 870 | 2019-06-29 23:30 | 258 | 1073 | 315 | 1320 | 298 | 1258 | 223 | 632.5 | 62.5 |  |  | 62.5 | 87% | 57% | 64% | 88% | 4.679 | Loss 0-5% |  | 886(70) | 1009(96.5)
695 | 1230 | LNR | LAXMI NAGAR | LGR022 | TG-LGR022A-4 | DT-4 | WB BLOCK SHAKARPUR:K | 4 | 630 | 19506276 | 639 | 2019-06-03 00:30 | 187 | 800 | 213 | 908 | 240 | 1040 | 209 | 589.5 | 124.5 | 3.5 | 0.5 | 128.5 | 101% | 65% | 67% | 93% | 4.679 | Loss 0-5% |  | 541(39) | 548(103) | 530(45)
696 | 1230 | LNR | LAXMI NAGAR | LGR024 | TG-LGR024A-1 | DT-1 | SHAKARPUR SANJAY PARK | 2 | 990 | 19505154 | 1211 | 2019-06-02 00:30 | 417 | 1835 | 489 | 2257 | 305 | 1329 | 804 | 438 | 174 | 69 | 37 | 280 | 122% | 81% | 87% | 110% | 12.3224 | Loss 10-20% | 958(55.5) |  | 1086(271.5) | 1066(202.5) | 965(171)
697 | 1230 | LNR | LAXMI NAGAR | LGR024 | TG-LGR024A-2 | DT-2 | SHAKARPUR SANJAY PARK | 2 | 990 | 19502827 | 1061 | 2019-06-11 23:30 | 345 | 1568 | 374 | 1705 | 342 | 1563 | 139 | 511.5 | 152.5 | 41 | 14 | 207.5 | 107% | 86% | 79% | 107% | 12.3224 | Loss 10-20% |  | 967(66.5) | 1141(229) | 1089(184.5) | 908(130)
698 | 1230 | LNR | LAXMI NAGAR | LGR025 | TG-LGR025A-1 | DT-1 | DALL MILL SHAKARPUR:PM | 1 | 990 | 19502941 | 892 | 2019-06-29 23:30 | 316 | 1331 | 264 | 1098 | 313 | 1310 | 223 | 581 | 138.5 | 0.5 |  | 139 | 90% | 68% | 69% | 90% | 13.3322 | Loss 10-20% |  | 773(29) | 836(122.5) | 852(88.5) | 791(36.5)
699 | 1230 | LNR | LAXMI NAGAR | LGR026 | TG-LGR026A-1 | DT-1 | POLICE BOOTH S. PUR, V. MARG:PL | 1 | 990 | 19506000 | 843 | 2019-06-10 23:30 | 263 | 1204 | 209 | 939 | 371 | 1723 | 691 | 590.5 | 128 |  |  | 128 | 84% | 70% | 82% | 85% | 8.6678 | Loss 5-10% |  |  | 907(123) | 1226(32)
700 | 1230 | LNR | LAXMI NAGAR | LGR027 | TG-LGR027A-2 | DT-2 | U BLOCK SHAKARPUR, V. MARG:PL | 2 | 990 | 19504762 | 840 | 2019-06-29 16:00 | 310 | 1318 | 257 | 1111 | 273 | 1159 | 187 | 605.5 | 114 |  |  | 114 | 53% | 43% | 85% | 53% | 4.8678 | Loss 0-5%
701 | 1230 | LNR | LAXMI NAGAR | LGR030 | TG-LGR030A-1 | DT-1 | BODH VIHAR LAXMI NAGAR:K | 2 | 990 | 19503402 | 815 | 2019-06-01 | 229 | 1030 | 308 | 1413 | 278 | 1260 | 333 | 647.5 | 72 |  |  | 72 | 82% | 58% | 59% | 82% | 6.2016 | Loss 5-10% |  | 960(45.5) | 909(134.5) | 1063(81.5) | 818(29.5)
702 | 1230 | LNR | LAXMI NAGAR | LGR030 | TG-LGR030A-2 | DT-2 | BODH VIHAR LAXMI NAGAR:K | 2 | 630 | 19504644 | 580 | 2019-06-05 03:30 | 189 | 766 | 215 | 884 | 175 | 719 | 148 | 589 | 129.5 | 1 |  | 130.5 | 92% | 62% | 66% | 91% | 6.2016 | Loss 5-10% |  |  |  |  | 545(29.5)
703 | 1230 | LNR | LAXMI NAGAR | LGR031 | TG-LGR031A-1 | DT-1 | MANGAL BAZAR LAXMI NAGAR:PL | 3 | 990 | 19504511 | 1213 | 2019-06-12 00:30 | 387 | 1620 | 461 | 1944 | 364 | 1536 | 373 | 389 | 239.5 | 64 | 26 | 329.5 | 122% | 77% | 94% | 108% | 7.6228 | Loss 5-10% |  | 1261(224) | 1290(322.5) |  |  | 783(26.5)
704 | 1230 | LNR | LAXMI NAGAR | LGR031 | TG-LGR031A-3 | DT-3 | MANGAL BAZAR LAXMI NAGAR:PL | 3 | 990 | 19506025 | 830 | 2019-06-10 23:30 | 319 | 1367 | 256 | 1094 | 255 | 1098 | 271 | 658 | 61.5 |  |  | 61.5 | 84% | 54% | 64% | 84% | 7.6228 | Loss 5-10% |  |  | 906(33)
705 | 1230 | LNR | LAXMI NAGAR | LGR032 | TG-LGR032A-1 | DT-1 | KULDEEP NURSING HOME LNG:K | 3 | 990 | 19502461 | 902 | 2019-06-11 21:30 | 287 | 1171 | 298 | 1227 | 318 | 1304 | 116 | 588 | 127.5 | 1 |  | 128.5 | 85% | 59% | 85% | 91% | 5.4971 | Loss 5-10% |  | 846(72) | 897(153) | 881(76) | 782(28.5)
706 | 1230 | LNR | LAXMI NAGAR | LGR032 | TG-LGR032A-2 | DT-2 | KULDEEP NURSING HOME LNG:K | 3 | 990 | 19502463 | 917 | 2019-06-12 00:30 | 310 | 1253 | 284 | 1148 | 323 | 1315 | 146 | 600 | 118.5 | 1.5 |  | 120 | 93% | 60% | 62% | 91% | 5.4971 | Loss 5-10% |  | 1126(160.5) | 1153(208.5) | 862(47)
707 | 1230 | LNR | LAXMI NAGAR | LGR034 | TG-LGR034A-1 | DT-1 | MOHAN PARK LAXMI NAGAR:K | 1 | 990 | 19502470 | 910 | 2019-06-11 19:30 | 305 | 1298 | 293 | 1254 | 312 | 1330 | 66 | 532.5 | 186.5 | 0.5 |  | 187 | 72% | 80% | 92% | 85% | 6.3201 | Loss 5-10% |  | 822(55.5) | 896(130) | 854(47.5)
708 | 1230 | LNR | LAXMI NAGAR | LGR035 | TG-LGR035A-1 | DT-1 | N.GANESH NAGAR SHAKARPUR:PL | 1 | 630 | 19502820 | 563 | 2019-06-30 | 151 | 668 | 205 | 922 | 208 | 917 | 251 | 601.5 | 118.5 |  |  | 118.5 | 89% | 59% | 66% | 88% | 3.915 | Loss 0-5% |  | 650(127.5) | 771(93.5) | 716(202.5) | 749(157.5)
709 | 1230 | LNR | LAXMI NAGAR | LGR036 | TG-LGR036A-1 | DT-1 | SHIROMANI SCHOOL, SHAKARPUR:PL | 2 | 990 | 19506252 | 1033 | 2019-06-30 23:30 | 357 | 1551 | 242 | 1048 | 433 | 1908 | 748 | 569 | 132.5 | 18 | 0.5 | 151 | 99% | 64% | 71% | 104% | 5.0908 | Loss 5-10%
710 | 1230 | LNR | LAXMI NAGAR | LGR040 | TG-LGR040A-1 | DT-1 | J EXTN. LAXMI NAGAR:PM | 1 | 990 | 19503409 | 1156 | 2019-06-30 01:30 | 351 | 1489 | 365 | 1626 | 440 | 1926 | 387 | 468 | 186.5 | 54 | 6.5 | 247 | 117% | 87% | 77% | 97% | 3.6605 | Loss 0-5% |  | 884(119.5) | 999(251) | 996(188.5) | 1106(157) | 929(77.5)
711 | 1230 | LNR | LAXMI NAGAR | LGR041 | TG-LGR041A-1 | DT-1 | KUNDAN NAGAR, LAXMI NAGAR:K | 1 | 990 | 19505457 | 1052 | 2019-06-11 01:00 | 348 | 1512 | 313 | 1354 | 391 | 1710 | 308 | 506.5 | 126 | 11.5 | 0.5 | 138 | 106% | 62% | 75% | 99% | 3.336 | Loss 0-5% |  | 920(74) | 928(59.5)
712 | 1230 | LNR | LAXMI NAGAR | LGR042 | TG-LGR042A-1 | DT-1 | V. SAVARKAR BLOCK, SHAKARPUR:PL | 1 | 990 | 19506382 | 975 | 2019-06-10 15:00 | 304 | 1266 | 339 | 1415 | 332 | 1401 | 143 | 586.5 | 132 | 0.5 |  | 132.5 | 15% | 15% | 98% | 23% | 3.9973 | Loss 0-5% |  | 970(80) | 938(139) |  | 766(36.5)
713 | 1230 | LNR | LAXMI NAGAR | LGR043 | TG-LGR043A-1 | DT-1 | SUNDER BLOCK, SHAKARPUR:PL | 1 | 1600 | 19502815 | 1768.3862 | 2019-06-30 01:30 | 380.2798 | 1630.5626 | 397.481 | 1707.686 | 990.6254 | 4230.9105 | 2562.6567 | 483.5 | 137 | 30 | 16.5 | 183.5 | 111% | 96% | 98% | 110% | 4.4588 | Loss 0-5% |  | 992(116) | 1203(217.5)
714 | 1230 | LNR | LAXMI NAGAR | LGR049 | TG-LGR049A-2 | DT-2 | R BLOCK SHAKARPUR:PL | 2 | 630 | 19504448 | 544 | 2019-06-29 23:30 | 205 | 896 | 205 | 891 | 134 | 578 | 315 | 593.5 | 126.5 |  |  | 126.5 | 84% | 57% | 82% | 86% | 9.7215 | Loss 5-10% |  | 508(31.5) | 546(94)
715 | 1230 | LNR | LAXMI NAGAR | LGR051 | TG-LGR051A-2 | DT-2 | H BLOCK LAXMI NAGAR:PL | 2 | 630 | 19504765 | 696 | 2019-06-26 14:30 | 206 | 893 | 280 | 1226 | 210 | 904 | 327 | 417.5 | 190.5 | 76.5 | 34.5 | 301.5 | 63% | 51% | 110% | 78% | 5.4756 | Loss 5-10% |  | 500(35.5) | 551(80) | 529(56.5) | 522(34.5)
716 | 1230 | LNR | LAXMI NAGAR | LGR052 | TG-LGR052A-1 | DT-1 | RAMESH PARK, G NO.12, LN:PL | 2 | 990 | 19504589 | 903 | 2019-06-30 00:30 | 283 | 1203 | 368 | 1576 | 253 | 1085 | 444 | 559 | 158 | 3 |  | 161 | 91% | 72% | 70% | 90% | 3.6871 | Loss 0-5% |  | 844(100.5) | 923(211) | 927(121.5) | 785(50.5)
717 | 1230 | LNR | LAXMI NAGAR | LGR052 | TG-LGR052A-2 | DT-2 | RAMESH PARK, G NO.12, LN:PL | 2 | 990 | 19506150 | 799 | 2019-06-03 01:00 | 270 | 1183 | 262 | 1134 | 267 | 1165 | 43 | 674.5 | 45.5 |  |  | 45.5 | 81% | 62% | 61% | 77% | 3.6871 | Loss 0-5% |  |  | 820(39.5) | 880(35)
718 | 1230 | LNR | LAXMI NAGAR | LGR054 | TG-LGR054A-1 | DT-1 | KISHAN KUNJ ENTN.:PL | 2 | 990 | 19503404 | 793 | 2019-06-02 23:30 | 251 | 1013 | 238 | 969 | 304 | 1237 | 249 | 652.5 | 67.5 |  |  | 67.5 | 79% | 62% | 64% | 80% | 3.9884 | Loss 0-5%
719 | 1230 | LNR | LAXMI NAGAR | LGR054 | TG-LGR054A-2 | DT-2 | KISHAN KUNJ ENTN.:PL | 2 | 630 | 19506147 | 579 | 2019-06-11 01:00 | 164 | 710 | 208 | 987 | 208 | 949 | 260 | 606 | 113.5 | 0.5 |  | 114 | 92% | 60% | 67% | 87% | 3.9884 | Loss 0-5% | 639(37) | 727(227.5) | 747(275.5) | 523(25.5)
720 | 1230 | LNR | LAXMI NAGAR | LGR080 | TG-LGR080A-1 | DT-1 | GALI MASJID ANAR WALI | 1 | 990 | 19506548 | 1118 | 2019-06-30 01:00 | 370 | 1595 | 396 | 1704 | 352 | 1499 | 178 | 347 | 221.5 | 89.5 | 59.5 | 370.5 | 113% | 91% | 88% | 111% | 7.2213 | Loss 5-10% | 917(41.5) |  |  |  | 1225(76.5)
721 | 1230 | LNR | LAXMI NAGAR | LGR082 | TG-LGR082A-1 | DT-1 | E BLOCK ,VIKAS MARG | 3 | 990 | 19506667 | 1152 | 2019-06-08 16:00 | 389 | 1684 | 407 | 1762 | 356 | 1539 | 196 | 419.5 | 146.5 | 75 | 78 | 299.5 | 67% | 53% | 116% | 78% | 5.5722 | Loss 5-10% |  | 1031(193) | 1178(261) | 1107(261) | 1083(173.5)
722 | 1230 | LNR | LAXMI NAGAR | LGR083 | TG-LGR083A-1 | DT-1 | EK MINAR MASID | 2 | 990 | 19506852 | 1349 | 2019-06-08 | 452 | 1858 | 431 | 1757 | 467 | 1921 | 144 | 270 | 249 | 71 | 126 | 446 | 136% | 107% | 92% | 131% | 10.4517 | Loss 10-20% |  | 896(74.5) |  | 1010(180) | 870(134) | 867(66.5)
723 | 1230 | LNR | LAXMI NAGAR | LGR084 | TG-LGR084A-1 | DT-1 | WEST GURU ANGAD NAGER GALI NO-2 | 1 | 990 | 19502464 | 904 | 2019-06-12 | 329 | 1359 | 268 | 1114 | 307 | 1271 | 215 | 611.5 | 108 | 0.5 |  | 108.5 | 91% | 63% | 61% | 88% | 10.0308 | Loss 10-20% |  |  | 836(77.5) | 823(38)
724 | 1230 | LNR | LAXMI NAGAR | LGR090 | TG-LGR090A-1 | DT-1 | SCHOOL BLOCK,PARK WALA S/S NEAR MANDIR | 2 | 990 | 19504463 | 968 | 2019-06-10 13:00 | 321 | 1329 | 295 | 1221 | 353 | 1462 | 209 | 545 | 148.5 | 26.5 |  | 175 | 58% | 48% | 98% | 59% | 3.7364 | Loss 0-5% |  | 833(71.5) | 953(180) | 928(116.5) | 826(48)
725 | 1230 | LNR | LAXMI NAGAR | LGR090 | TG-LGR090A-2 | DT-2 | SCHOOL BLOCK,PARK WALA S/S NEAR MANDIR | 2 | 630 | 19503652 | 617 | 2019-06-03 | 188 | 769 | 186 | 755 | 244 | 996 | 234 | 489.5 | 223 | 7.5 |  | 230.5 | 98% | 67% | 82% | 94% | 3.7364 | Loss 0-5% |  | 566(50.5) | 566(205) | 605(173.5) | 508(51)
726 | 1230 | LNR | LAXMI NAGAR | LGR093 | TG-LGR093A-2 | DT-2 | SURANA DHARAMSHALA S/S | 2 | 990 | 19506459 | 828 | 2019-06-30 23:30 | 249 | 1062 | 271 | 1161 | 308 | 1347 | 251 | 664.5 | 55.5 |  |  | 55.5 | 78% | 55% | 63% | 84% | 8.151 | Loss 5-10% |  | 854(42.5) | 879(68.5)
727 | 1230 | LNR | LAXMI NAGAR | LGR097 | TG-LGR097A-1 | DT-1 | A BLK P,D.VIHAR PARK NR. O/H WATER TANK | 1 | 630 | 19505222 | 550 | 2019-06-11 23:30 | 205 | 833 | 135 | 544 | 211 | 857 | 302 | 552.5 | 167 |  |  | 167 | 87% | 65% | 86% | 87% | 3.7314 | Loss 0-5% |  | 608(65.5) | 589(154) | 557(72)
728 | 1230 | LNR | LAXMI NAGAR | LGR100 | TG-LGR100A-1 | DT-1 | GYAN KUNJ | 1 | 990 | 19505137 | 1052.5105 | 2019-06-11 01:30 | 352.113 | 1413.0869 | 315.8192 | 1266.8241 | 384.5782 | 1544.4289 | 240.5285 | 672 | 40 | 4.5 | 1 | 45.5 | 106% | 97% | 72% | 92% | 2.9002 | Loss 0-5% |  |  | 756(26)
729 | 1230 | LNR | LAXMI NAGAR | LGR101 | TG-LGR101A-1 | DT-1 | VEER SAVARKAR BLOCK VIKAS MARG | 1 | 990 | 19504960 | 907 | 2019-06-27 14:00 | 235 | 1071 | 328 | 1506 | 344 | 1597 | 487 | 586.5 | 131.5 | 0.5 |  | 132 | 14% | 19% | 92% | 24% | 6.6538 | Loss 5-10% |  |  | 895(129) | 881(102) | 761(40)
730 | 1230 | LNR | LAXMI NAGAR | LGR103 | TG-LGR103A-1 | DT-1 | NEW WB BLOCK (NEAR AGGARWAL SWEETS) | 1 | 990 | 19505891 | 910 | 2019-06-30 | 281 | 1163 | 314 | 1318 | 314 | 1307 | 150 | 522.5 | 194 | 3.5 |  | 197.5 | 92% | 63% | 79% | 92% | 7.7886 | Loss 5-10% |  | 892(90.5) | 982(289) | 887(138) | 928(60)
731 | 1230 | LNR | LAXMI NAGAR | LGR104 | TG-LGR104A-1 | DT-1 | NARAIN NAGAR (NEAR GARHWALI MOHALLA) | 1 | 630 | 19505680 | 521 | 2019-06-29 23:30 | 188 | 773 | 154 | 639 | 178 | 741 | 121 | 655.5 | 61.5 |  |  | 61.5 | 81% | 67% | 65% | 83% | 9.6686 | Loss 5-10% |  |  | 517(77.5) | 521(47)
732 | 1230 | LNR | LAXMI NAGAR | LGR108 | TG-LGR108A-1 | DT-1 | COMMUNITY CENTER SHAKARPUR | 1 | 630 | 19505626 | 533 | 2019-06-30 23:30 | 185 | 781 | 190 | 801 | 158 | 659 | 133 | 635.5 | 84.5 |  |  | 84.5 | 82% | 57% | 70% | 85% | 5.6641 | Loss 5-10%
733 | 1230 | LNR | LAXMI NAGAR | PVR008 | TG-PVR008A-1 | DT-1 | DDA FLAT NIRMAN VIHAR:ID | 2 | 990 | 19501093 | 805.617 | 2019-06-01 | 228.2324 | 1003.3517 | 244.8038 | 1087.1956 | 332.5808 | 1474.0097 | 434.8413 | 667.5 | 52.5 |  |  | 52.5 | 81% | 55% | 60% | 81% | 13.5333 | Loss 10-20% |  | 698(207.5) | 774(265.5) | 732(103.5) | 664(182) | 589(81.5)
734 | 1230 | LNR | LAXMI NAGAR | PVR008 | TG-PVR008A-2 | DT-2 | DDA FLAT NIRMAN VIHAR:ID | 2 | 990 | 19504486 | 857 | 2019-06-11 23:30 | 282 | 1257 | 270 | 1195 | 305 | 1356 | 141 | 610.5 | 109.5 |  |  | 109.5 | 86% | 59% | 63% | 87% | 13.5333 | Loss 10-20% |  |  | 834(66.5)
735 | 1230 | LNR | MANDAWALI | MAN003 | TG-MAN003A-1 | DT-1 | SOUTH GANESH NAGAR:PM | 1 | 400 | 19505687 | 588 | 2019-06-30 | 183 | 823 | 190 | 864 | 216 | 982 | 143 | 250.5 | 230.5 | 78.5 | 160 | 469 | 147% | 89% | 99% | 135% | 4.4307 | Loss 0-5% | 408(71) | 472(260.5) | 560(467.5) | 557(417.5) |  | 432(150.5)
736 | 1230 | LNR | MANDAWALI | MAN004 | TG-MAN004A-2 | DT-2 | SOUTH GANESH NAGAR EXTN.:ID | 2 | 630 | 19506133 | 711 | 2019-06-30 | 231 | 1065 | 223 | 1024 | 258 | 1201 | 160 | 523.5 | 131.5 | 54 | 11 | 196.5 | 113% | 67% | 76% | 104% | 4.2275 | Loss 0-5% |  |  | 990(205.5) | 547(61) | 487(28.5)
737 | 1230 | LNR | MANDAWALI | MAN006 | TG-MAN006A-1 | DT-1 | PANDAV NAGAR D PARK:K | 5 | 990 | 19505744 | 1034 | 2019-06-05 01:00 | 340 | 1441 | 383 | 1639 | 312 | 1335 | 267 | 525.5 | 133 | 50.5 | 10 | 193.5 | 104% | 70% | 74% | 104% | 5.5812 | Loss 5-10% |  | 830(45.5) | 981(129.5) | 923(94) | 779(39.5)
738 | 1230 | LNR | MANDAWALI | MAN006 | TG-MAN006A-2 | DT-2 | PANDAV NAGAR D PARK:K | 5 | 990 | 19501944 | 965 | 2019-06-05 00:30 | 324 | 1357 | 345 | 1439 | 296 | 1224 | 188 | 538 | 165 | 16 |  | 181 | 97% | 64% | 78% | 97% | 5.5812 | Loss 5-10% | 892(30) |  | 834(68) | 816(44.5) | 809(56.5)
739 | 1230 | LNR | MANDAWALI | MAN006 | TG-MAN006A-3 | DT-3 | PANDAV NAGAR D PARK:K | 5 | 990 | 19505981 | 917 | 2019-06-07 23:30 | 297 | 1366 | 349 | 1604 | 271 | 1250 | 312 | 594 | 118.5 | 6 |  | 124.5 | 92% | 63% | 73% | 93% | 5.5812 | Loss 5-10% |  | 1210(232.5) | 1299(394.5) | 1213(176) | 1007(175)
740 | 1230 | LNR | MANDAWALI | MAN007 | TG-MAN007A-1 | DT-1 | PANDAV NAGAR S BLOCK:ID | 1 | 990 | 19501803 | 874 | 2019-06-06 03:00 | 274 | 1152 | 287 | 1212 | 314 | 1319 | 146 | 615 | 104.5 |  |  | 104.5 | 88% | 60% | 64% | 88% | 5.4968 | Loss 5-10% |  | 873(42.5) | 902(127) | 892(99) | 784(43)
741 | 1230 | LNR | MANDAWALI | MAN008 | TG-MAN008A-1 | DT-1 | PANDAV NAGAR S BLOCK NEAR PETROL PUMP:PM | 2 | 990 | 19506364 | 791 | 2019-06-30 23:00 | 256 | 1172 | 287 | 1314 | 249 | 1137 | 162 | 683.5 | 36 |  |  | 36 | 80% | 51% | 61% | 80% | 3.8894 | Loss 0-5% |  |  | 799(50.5)
742 | 1230 | LNR | MANDAWALI | MAN009 | TG-MAN009A-1 | DT-1 | J PARK PANDAV NAGAR:K | 1 | 990 | 19502964 | 1094 | 2019-06-29 23:00 | 368 | 1588 | 397 | 1713 | 330 | 1407 | 266 | 489.5 | 139 | 54.5 | 23.5 | 217 | 109% | 68% | 81% | 111% | 3.4241 | Loss 0-5% |  | 1030(97) | 1027(402.5) | 1005(140.5) | 880(87.5)
743 | 1230 | LNR | MANDAWALI | MAN010 | TG-MAN010A-1 | DT-1 | GANESH NAGAR COM. E BLCK.:PL | 2 | 990 | 19506916 | 1131 | 2019-06-30 | 341 | 1514 | 427 | 1915 | 362 | 1608 | 364 | 338.5 | 101.5 | 40 | 22 | 163.5 | 114% | 71% | 89% | 111% | 4.5931 | Loss 0-5% |  |  |  |  | 1108(177.5) | 951(57)
744 | 1230 | LNR | MANDAWALI | MAN010 | TG-MAN010A-2 | DT-2 | GANESH NAGAR COM. E BLCK.:PL | 2 | 990 | 19500753 | 1023.2342 | 2019-06-30 00:30 | 334.4389 | 1395.4724 | 352.5955 | 1523.8805 | 336.1998 | 1447.2655 | 111.8951 | 493.5 | 163.5 | 55 | 6 | 224.5 | 103% | 73% | 77% | 102% | 4.5931 | Loss 0-5% | 887(32) | 1214(209) | 1091(203) | 887(109) | 788(61.5)
745 | 1230 | LNR | MANDAWALI | MAN011 | TG-MAN011A-1 | DT-1 | GANESH NAGAR COM. C BLCK.:PL | 2 | 1600 | 19500759 | 1503.0792 | 2019-06-30 23:30 | 476.6178 | 2165.3617 | 576.61 | 2608.7411 | 449.8514 | 2026.8143 | 526.5071 | 573 | 137.5 | 9 |  | 146.5 | 91% | 62% | 69% | 94% | 3.7274 | Loss 0-5% |  | 1083(97.5) | 1333(413.5) | 1133(273) | 1034(218) | 929(47)
746 | 1230 | LNR | MANDAWALI | MAN013 | TG-MAN013A-1 | DT-1 | MANDAWALI A BLOCK SHIV MANDIR MARG:PL | 2 | 990 | 19506457 | 1135 | 2019-06-30 23:30 | 413 | 1753 | 358 | 1510 | 364 | 1524 | 236 | 465.5 | 164 | 65.5 | 23 | 252.5 | 110% | 77% | 82% | 115% | 5.4843 | Loss 5-10% |  |  |  |  | 958(132) | 925(31.5)
747 | 1230 | LNR | MANDAWALI | MAN013 | TG-MAN013A-2 | DT-2 | MANDAWALI A BLOCK SHIV MANDIR MARG:PL | 2 | 990 | 19502779 | 1242 | 2019-06-29 23:30 | 438 | 1889 | 398 | 1731 | 405 | 1772 | 142 | 426.5 | 168.5 | 44 | 80.5 | 293 | 124% | 85% | 99% | 125% | 5.4843 | Loss 5-10% |  |  |  |  | 991(133.5) | 897(26.5)
748 | 1230 | LNR | MANDAWALI | MAN016 | TG-MAN016A-1 | DT-1 | MANDAWALI PRIMARY SCHOOL:PL | 3 | 990 | 19506407 | 1132 | 2019-06-29 23:30 | 393 | 1678 | 339 | 1439 | 400 | 1714 | 259 | 405 | 213.5 | 66.5 | 34.5 | 314.5 | 112% | 81% | 92% | 114% | 8.0713 | Loss 5-10% | 799(34.5) | 1143(282.5) | 1290(477)
749 | 1230 | LNR | MANDAWALI | MAN016 | TG-MAN016A-3 | DT-3 | MANDAWALI PRIMARY SCHOOL:PL | 3 | 630 | 19506597 | 670 | 2019-06-11 | 209 | 913 | 201 | 881 | 260 | 1143 | 247 | 493 | 180 | 43.5 | 3.5 | 227 | 106% | 84% | 78% | 105% | 8.0713 | Loss 5-10%
750 | 1230 | LNR | MANDAWALI | MAN017 | TG-MAN017A-1 | DT-1 | SCHOOL KHATTA-1, MANDAWALI:PL | 2 | 990 | 19500781 | 1141.9346 | 2019-06-29 23:30 | 355.0863 | 1542.3112 | 385.3779 | 1680.5981 | 401.4703 | 1750.7756 | 183.7192 | 387.5 | 209 | 78 | 44 | 331 | 114% | 80% | 88% | 115% | 11.9836 | Loss 10-20% |  | 950(107.5) | 1056(224.5) | 1064(221.5) | 992(195.5) | 899(56)
751 | 1230 | LNR | MANDAWALI | MAN017 | TG-MAN017A-2 | DT-2 | SCHOOL KHATTA-1, MANDAWALI:PL | 2 | 630 | 19505686 | 540 | 2019-06-30 23:30 | 174 | 770 | 179 | 795 | 187 | 825 | 48 | 685 | 33.5 |  |  | 33.5 | 82% | 56% | 58% | 86% | 11.9836 | Loss 10-20% |  | 552(35) | 598(123) | 602(72)
752 | 1230 | LNR | MANDAWALI | MAN018 | TG-MAN018A-1 | DT-1 | SCHOOL KHATTA-II,MANDAWALI:PM | 1 | 990 | 19500784 | 945.2505 | 2019-06-30 23:30 | 322.5007 | 1399.3783 | 347.5744 | 1529.5476 | 275.1754 | 1197.6125 | 289.6846 | 563.5 | 145 | 10 |  | 155 | 92% | 69% | 76% | 95% | 6.1722 | Loss 5-10% |  |  | 914(105)
753 | 1230 | LNR | MANDAWALI | MAN019 | TG-MAN019A-1 | DT-1 | MANDAWALI UNCHEPAR;PL | 2 | 990 | 19501990 | 1093 | 2019-06-29 23:30 | 353 | 1547 | 387 | 1699 | 353 | 1528 | 162 | 522.5 | 147 | 38 | 12.5 | 197.5 | 110% | 72% | 76% | 110% | 3.0626 | Loss 0-5% |  | 889(59) | 981(164) | 1032(123.5) | 845(76.5)
754 | 1230 | LNR | MANDAWALI | MAN021 | TG-MAN021A-1 | DT-1 | MANDAWALI SUBJI MANDI:PL | 2 | 990 | 19504821 | 939 | 2019-06-30 23:00 | 324 | 1402 | 301 | 1309 | 315 | 1369 | 81 | 580 | 133.5 | 6.5 |  | 140 | 91% | 63% | 78% | 95% | 3.9525 | Loss 0-5% |  | 894(80.5) | 1025(221) | 1004(172.5) | 910(124)
755 | 1230 | LNR | MANDAWALI | MAN021 | TG-MAN021A-2 | DT-2 | MANDAWALI SUBJI MANDI:PL | 2 | 990 | 19504828 | 1069 | 2019-06-29 23:00 | 345 | 1485 | 370 | 1589 | 354 | 1523 | 91 | 426.5 | 253 | 36 | 4 | 293 | 101% | 77% | 90% | 108% | 3.9525 | Loss 0-5%
756 | 1230 | LNR | MANDAWALI | MAN023 | TG-MAN023A-1 | DT-1 | UTTARY SCHOOL BLOCK:K | 3 | 990 | 19502766 | 1159 | 2019-06-30 23:30 | 407 | 1693 | 384 | 1608 | 368 | 1538 | 134 | 428.5 | 161 | 72.5 | 58 | 291.5 | 112% | 79% | 88% | 117% | 3.8539 | Loss 0-5% |  | 1016(133) | 1056(271) | 1084(244.5) | 1000(220.5) | 838(33)
757 | 1230 | LNR | MANDAWALI | MAN023 | TG-MAN023A-2 | DT-2 | UTTARY SCHOOL BLOCK:K | 3 | 630 | 19502768 | 720 | 2019-06-29 23:00 | 283 | 1170 | 218 | 911 | 220 | 911 | 259 | 486.5 | 141.5 | 63.5 | 28 | 233 | 102% | 61% | 114% | 114% | 3.8539 | Loss 0-5% |  | 677(200.5) | 758(278.5) | 669(194) | 588(120.5) | 567(75)
758 | 1230 | LNR | MANDAWALI | MAN023 | TG-MAN023A-3 | DT-3 | UTTARY SCHOOL BLOCK:K | 3 | 630 | 19504321 | 609 | 2019-06-30 23:00 | 222 | 965 | 215 | 937 | 171 | 742 | 210 | 570.5 | 138.5 | 10 |  | 148.5 | 96% | 67% | 79% | 97% | 3.8539 | Loss 0-5%
759 | 1230 | LNR | MANDAWALI | MAN024 | TG-MAN024A-2 | DT-2 | CHANDERVIHAR SS-1:ID | 2 | 990 | 19500076 | 1018 | 2019-06-29 23:00 | 354 | 1525 | 325 | 1403 | 339 | 1461 | 105 | 560.5 | 139.5 | 18 | 2 | 159.5 | 95% | 63% | 74% | 103% | 5.4734 | Loss 5-10% |  | 888(44.5) | 1000(156) | 988(111.5) | 1009(141.5) | 828(25)
760 | 1230 | LNR | MANDAWALI | MAN025 | TG-MAN025A-1 | DT-1 | CHANDERVIHAR SS-II:ID | 2 | 630 | 19500845 | 751 | 2019-06-15 23:00 | 254 | 1085 | 250 | 1063 | 247 | 1057 | 25 | 436 | 183.5 | 63 | 37.5 | 284 | 108% | 79% | 89% | 119% | 4.2908 | Loss 0-5% |  | 662(104) | 723(146.5) | 694(198) | 642(173.5) | 547(33.5)
761 | 1230 | LNR | MANDAWALI | MAN025 | TG-MAN025A-2 | DT-2 | CHANDERVIHAR SS-II:ID | 2 | 630 | 19504725 | 675 | 2019-06-29 23:00 | 245 | 1072 | 231 | 1004 | 199 | 861 | 186 | 540 | 137 | 35 | 8 | 180 | 102% | 70% | 78% | 107% | 4.2908 | Loss 0-5% |  | 617(51) | 664(106) | 614(130) | 570(91)
762 | 1230 | LNR | MANDAWALI | MAN026 | TG-MAN026A-1 | DT-1 | WESTVINOD NAGAR NEAR MANGLAM:PL | 3 | 990 | 19506612 | 943 | 2019-06-02 23:30 | 293 | 1232 | 330 | 1392 | 319 | 1345 | 142 | 637 | 75 | 7.5 |  | 82.5 | 92% | 53% | 68% | 95% | 8.8027 | Loss 5-10% |  | 1068(64.5) | 998(103) | 1047(115)
763 | 1230 | LNR | MANDAWALI | MAN026 | TG-MAN026A-2 | DT-2 | WESTVINOD NAGAR NEAR MANGLAM:PL | 3 | 990 | 19506134 | 1698.2957 | 2019-06-27 00:30 | 553.9903 | 2289.3109 | 568.7532 | 2360.4614 | 575.5522 | 2381.6609 | 83.7865 | 154.5 | 226.5 | 76 | 241 | 543.5 | 172% | 109% | 136% | 165% | 8.8027 | Loss 5-10% | 1119(144) |  | 1573(452.5) |  |  | 1265(295.5)
764 | 1230 | LNR | MANDAWALI | MAN026 | TG-MAN026A-3 | DT-3 | WESTVINOD NAGAR NEAR MANGLAM:PL | 3 | 990 | 19505743 | 1060 | 2019-06-26 23:00 | 331 | 1380 | 333 | 1382 | 396 | 1650 | 269 | 545.5 | 133 | 33.5 | 7.5 | 174 | 103% | 64% | 100% | 107% | 8.8027 | Loss 5-10% |  | 587(59.5) | 645(116) | 685(131) | 587(67.5)
765 | 1230 | LNR | MANDAWALI | MAN027 | TG-MAN027A-2 | DT-2 | WESTVINOD NAGAR D BLOCK:ID | 2 | 990 | 19505858 | 1271 | 2019-06-30 23:30 | 421 | 1841 | 446 | 1954 | 404 | 1758 | 170 | 350 | 215 | 74.5 | 80.5 | 370 | 124% | 104% | 98% | 128% | 6.5012 | Loss 5-10% |  | 1055(190) | 1169(257.5) | 1222(337.5) |  | 897(64.5)
766 | 1230 | LNR | MANDAWALI | MAN029 | TG-MAN029A-1 | DT-1 | A BLOCK WESTVINOD NAGAR | 2 | 990 | 19504659 | 1213 | 2019-06-30 23:30 | 384 | 1682 | 446 | 1966 | 383 | 1685 | 282 | 464.5 | 166 | 55.5 | 33.5 | 255 | 110% | 80% | 85% | 122% | 7.0759 | Loss 5-10% |  | 898(80.5) | 987(154) | 1045(143.5) | 979(84)
767 | 1230 | LNR | MANDAWALI | MAN029 | TG-MAN029A-2 | DT-2 | A BLOCK WESTVINOD NAGAR | 2 | 990 | 19501888 | 1185 | 2019-06-30 23:30 | 360 | 1530 | 401 | 1700 | 424 | 1813 | 246 | 406.5 | 196.5 | 64.5 | 52 | 313 | 116% | 82% | 92% | 120% | 7.0759 | Loss 5-10% |  | 1159(173) | 1325(252) | 1311(325.5) | 1283(252.5) | 1010(63)
768 | 1230 | LNR | MANDAWALI | MAN030 | TG-MAN030A-1 | DT-1 | E BLOCK WESTVINOD NAGAR:ID | 2 | 990 | 19505814 | 826.9265 | 2019-06-30 23:00 | 269.7131 | 1166.1252 | 334.0345 | 1470.8048 | 223.1789 | 965.4321 | 440.7431 | 684.5 | 34 |  |  | 34 | 79% | 58% | 66% | 84% | 4.004 | Loss 0-5% |  |  |  | 878(33.5)
769 | 1230 | LNR | MANDAWALI | MAN030 | TG-MAN030A-2 | DT-2 | E BLOCK WESTVINOD NAGAR:ID | 2 | 990 | 19505463 | 927 | 2019-06-26 23:00 | 272 | 1197 | 353 | 1559 | 301 | 1321 | 319 | 554 | 162 | 2.5 |  | 164.5 | 89% | 68% | 81% | 94% | 4.004 | Loss 0-5% |  | 992(149) | 1106(295.5) | 1183(143) | 882(55.5)
770 | 1230 | LNR | MANDAWALI | MAN031 | TG-MAN031A-1 | DT-1 | MOHAN BABA MANDIR MANDAWALI:PL | 2 | 990 | 19506135 | 1290 | 2019-06-30 23:30 | 448 | 1956 | 447 | 1951 | 395 | 1723 | 231 | 159 | 257.5 | 114.5 | 188 | 560 | 129% | 103% | 126% | 130% | 9.39 | Loss 5-10% | 862(96) | 976(141) |  |  |  | 950(40)
771 | 1230 | LNR | MANDAWALI | MAN032 | TG-MAN032A-1 | DT-1 | SONIYA VIHAR MANDAWALI:PL | 1 | 400 | 19505665 | 430 | 2019-06-11 23:00 | 151 | 683 | 136 | 612 | 143 | 641 | 62 | 329.5 | 273.5 | 101.5 | 15.5 | 390.5 | 106% | 84% | 89% | 107% | 6.2177 | Loss 5-10% |  | 372(187) | 418(338.5) | 433(77) | 412(245.5) | 538(157.5)
772 | 1230 | LNR | MANDAWALI | MAN033 | TG-MAN033A-1 | DT-1 | B BLOCK MANDAWALI:ID | 3 | 990 | 19506545 | 1105 | 2019-06-30 23:30 | 394 | 1767 | 366 | 1644 | 344 | 1544 | 194 | 479 | 179 | 48 | 13.5 | 240.5 | 104% | 93% | 85% | 112% | 3.6324 | Loss 0-5% |  |  |  |  | 1104(164.5) | 911(46.5)
773 | 1230 | LNR | MANDAWALI | MAN034 | TG-MAN034A-1 | DT-1 | C BLOCK WESTVINOD NAGAR:PL | 2 | 990 | 19505260 | 1068 | 2019-06-26 23:30 | 368 | 1536 | 326 | 1358 | 374 | 1573 | 200 | 526.5 | 152 | 37 | 4.5 | 193.5 | 106% | 71% | 86% | 108% | 4.471 | Loss 0-5% |  |  | 967(73) | 1011(137.5) | 898(96)
774 | 1230 | LNR | MANDAWALI | MAN037 | TG-MAN037A-1 | DT-1 | SHANKAR MARG MANDAWALI:PL | 1 | 990 | 19506836 | 1290 | 2019-06-30 23:30 | 420 | 1822 | 386 | 1678 | 484 | 2131 | 400 | 395.5 | 159.5 | 60 | 105 | 324.5 | 128% | 85% | 93% | 130% | 4.9787 | Loss 0-5% |  |  | 1277(117) | 1294(179) | 1136(134.5) | 994(52)
775 | 1230 | LNR | MANDAWALI | MAN038 | TG-MAN038A-1 | DT-1 | KRISHNA PURI MANDAWALI:PL | 1 | 630 | 19504301 | 589 | 2019-06-30 23:30 | 208 | 954 | 192 | 865 | 189 | 855 | 94 | 563.5 | 154.5 | 2 |  | 156.5 | 91% | 68% | 68% | 93% | 10.5314 | Loss 10-20% |  | 563(109.5) | 668(259.5) | 635(212) | 565(147)
776 | 1230 | LNR | MANDAWALI | MAN039 | TG-MAN039A-1 | DT-1 | ALLAH COLONY MANDAWALI:PL | 1 | 630 | 19506415 | 616 | 2019-06-29 23:30 | 194 | 840 | 212 | 923 | 210 | 913 | 78 | 618.5 | 96 | 5.5 |  | 101.5 | 92% | 87% | 77% | 98% | 9.998 | Loss 5-10% |  |  | 559(61) | 589(69) | 542(43.5)
777 | 1230 | LNR | MANDAWALI | MAN059 | TG-MAN059A-1 | DT-1 | S/STN.NO-2, PPG CGHS:ID | 1 | 630 | 19501860 | 635 | 2019-06-30 23:00 | 225 | 1040 | 202 | 918 | 208 | 947 | 110 | 503 | 200.5 | 13.5 | 0.5 | 214.5 | 93% | 66% | 83% | 101% | 3.0581 | Loss 0-5% |  |  | 555(94) | 567(71) | 515(33)
778 | 1230 | LNR | MANDAWALI | MAN212 | TG-MAN212A-1 | DT-1 | RAILWAY COLONY GALI NO. 2:PL | 2 | 990 | 19505555 | 1063 | 2019-06-01 23:00 | 381 | 1715 | 374 | 1681 | 307 | 1386 | 313 | 589 | 91.5 | 28 | 10.5 | 130 | 105% | 84% | 92% | 107% | 6.5533 | Loss 5-10% | 850(68.5) | 1045(285) | 1155(502) |  | 1122(468) | 1007(244.5)
779 | 1230 | LNR | MANDAWALI | MAN247 | TG-MAN247A-1 | DT-1 | Budha marg Mandawali | 1 | 990 | 19504474 | 951 | 2019-06-30 23:30 | 348 | 1536 | 321 | 1422 | 282 | 1250 | 250 | 683.5 | 31 | 4 |  | 35 | 94% | 73% | 74% | 96% | 3.3098 | Loss 0-5% |  | 829(43) | 982(167) | 927(131) | 843(68.5)
780 | 1230 | LNR | MANDAWALI | MAN273 | TG-MAN273A-1 | DT-1 | Ew S/S D-Blk Ramleela Ground Pandav Ngr | 2 | 990 | 19504634 | 904 | 2019-06-30 23:30 | 321 | 1476 | 262 | 1200 | 321 | 1461 | 269 | 604 | 115 | 0.5 |  | 115.5 | 88% | 57% | 70% | 91% | 6.1473 | Loss 5-10% |  | 778(27.5) | 834(87.5) | 823(28.5)
781 | 1230 | LNR | MANDAWALI | MAN274 | TG-MAN274A-1 | DT-1 | Gnpn Complex, Rob-36 Pandav Nagar | 1 | 630 | 19504788 | 652 | 2019-06-07 23:00 | 225 | 1017 | 211 | 947 | 217 | 973 | 61 | 520 | 153 | 42.5 | 4 | 199.5 | 99% | 67% | 74% | 104% | 4.425 | Loss 0-5% |  | 605(119) | 658(48) | 596(36) | 605(186) | 516(28)
782 | 1230 | LNR | MANDAWALI | MAN296 | TG-MAN296A-1 | DT-1 | SOUTH GANESH NAGAR (NEAR RAILWAY LINE) | 1 | 630 | 19505316 | 628 | 2019-06-29 23:30 | 211 | 935 | 205 | 915 | 211 | 936 | 21 | 464.5 | 132 | 3 |  | 135 | 98% | 67% | 71% | 100% | 4.8418 | Loss 0-5% |  | 550(74) | 588(168) | 585(84) | 506(61)
783 | 1230 | LNR | PREET VIHAR | PVR001 | TG-PVR001A-1 | DT-1 | G-II, PREET VIHAR:ID | 2 | 630 | 19503221 | 738 | 2019-06-06 00:30 | 228 | 945 | 275 | 1145 | 235 | 975 | 187 | 534 | 126.5 | 26 | 8.5 | 161 | 117% | 76% | 85% | 109% | 2.6245 | Loss 0-5% |  |  | 565(85.5) | 518(24.5) | 581(25.5)
784 | 1230 | LNR | PREET VIHAR | PVR006 | TG-PVR006A-2 | DT-2 | B BLOCK, PREET VIHAR:ID | 2 | 630 | 19501150 | 487 | 2019-06-10 23:30 | 172 | 769 | 118 | 519 | 197 | 882 | 322 | 670.5 | 49.5 |  |  | 49.5 | 77% | 58% | 71% | 77% | 3.186 | Loss 0-5%
785 | 1230 | LNR | PREET VIHAR | PVR009 | TG-PVR009A-1 | DT-1 | EAST GURU ANGAD NAGAR:K | 3 | 630 | 19504643 | 669 | 2019-06-30 23:30 | 211 | 892 | 193 | 833 | 265 | 1134 | 276 | 486 | 148.5 | 32 | 4.5 | 185 | 101% | 70% | 79% | 106% | 4.5107 | Loss 0-5% |  | 660(85.5) | 638(85) | 609(89)
786 | 1230 | LNR | PREET VIHAR | PVR009 | TG-PVR009A-2 | DT-2 | EAST GURU ANGAD NAGAR:K | 3 | 990 | 19504514 | 1253.9548 | 2019-06-11 22:00 | 325.802 | 1325.0987 | 572.0406 | 2396.0819 | 356.1122 | 1451.0909 | 1013.8755 | 402.5 | 128.5 | 48 | 43.5 | 220 | 107% | 63% | 108% | 127% | 4.5107 | Loss 0-5% |  | 1054(144) |  | 969(29.5) | 980(169)
787 | 1230 | LNR | PREET VIHAR | PVR009 | TG-PVR009A-3 | DT-3 | EAST GURU ANGAD NAGAR:K | 3 | 990 | 19504811 | 1096 | 2019-06-03 | 325 | 1429 | 401 | 1769 | 370 | 1623 | 295 | 517.5 | 160 | 39.5 | 3 | 202.5 | 111% | 68% | 78% | 102% | 4.5107 | Loss 0-5% |  | 969(52) | 1022(152) | 955(114.5) | 862(80)
788 | 1230 | LNR | PREET VIHAR | PVR015 | TG-PVR015A-1 | DT-1 | G-I, PREET VIHAR:ID | 2 | 990 | 19501193 | 1017 | 2019-06-10 13:00 | 343 | 1462 | 362 | 1548 | 312 | 1328 | 192 | 423 | 210.5 | 79 | 7.5 | 297 | 62% | 66% | 103% | 73% | 3.7925 | Loss 0-5% |  | 890(96.5) | 976(191) | 967(153.5) | 822(78.5)
789 | 1230 | LNR | PREET VIHAR | PVR015 | TG-PVR015A-2 | DT-2 | G-I, PREET VIHAR:ID | 2 | 990 | 19506821 | 884 | 2019-06-01 15:30 | 301 | 1289 | 296 | 1277 | 287 | 1224 | 60 | 529.5 | 190 |  |  | 190 | 73% | 52% | 89% | 77% | 3.7925 | Loss 0-5% |  | 812(25) | 919(116) | 851(55)
790 | 1230 | LNR | PREET VIHAR | PVR018 | TG-PVR018A-1 | DT-1 | C-BLOCK, PREET VIHAR:ID | 3 | 630 | 19501148 | 618 | 2019-06-02 14:00 | 194 | 838 | 236 | 1029 | 188 | 811 | 206 | 583.5 | 134 | 2 |  | 136 | 88% | 70% | 98% | 90% | 7.8937 | Loss 5-10% |  | 504(34) | 499(30.5) | 530(44.5)
791 | 1230 | LNR | PREET VIHAR | PVR019 | TG-PVR019A-1 | DT-1 | NIRMAN VIHAR (NEAR MKT.):ID | 3 | 990 | 19504881 | 802 | 2019-06-11 23:30 | 225 | 970 | 272 | 1150 | 306 | 1342 | 322 | 669.5 | 50 |  |  | 50 | 78% | 49% | 63% | 81% | 5.0685 | Loss 5-10%
792 | 1230 | LNR | PREET VIHAR | PVR021 | TG-PVR021A-1 | DT-1 | BHARATI ARTIST COLONY:K | 1 | 990 | 19506726 | 1232 | 2019-06-29 14:30 | 430 | 1911 | 426 | 1894 | 376 | 1671 | 232 | 409.5 | 116 | 70 | 122 | 308 | 45% | 48% | 124% | 67% | 4.0596 | Loss 0-5% | 799(44) | 989(176.5) | 1097(237.5) | 1006(178.5)
793 | 1230 | LNR | PREET VIHAR | PVR026 | TG-PVR026A-1 | DT-1 | B-BLOCK, PREET VIHAR, NEAR MKT.:ID | 1 | 630 | 19503229 | 523 | 2019-06-30 23:00 | 180 | 774 | 191 | 823 | 152 | 646 | 158 | 664 | 56 |  |  | 56 | 81% | 51% | 69% | 83% | 3.9249 | Loss 0-5% |  | 586(99) | 606(179.5) | 571(113)
794 | 1230 | LNR | PREET VIHAR | PVR067 | TG-PVR067A-1 | DT-1 | Swasthya vihar kiosk Vikas Marg | 2 | 630 | 19502956 | 689 | 2019-06-29 12:30 | 234 | 941 | 241 | 1003 | 213 | 880 | 107 | 476 | 130.5 | 72.5 | 15.5 | 218.5 | 26% | 43% | 109% | 43% | 4.5634 | Loss 0-5% | 511(57) | 636(178) | 695(238.5) | 635(177.5) | 538(61.5) | 537(100.5)
795 | 1230 | LNR | PREET VIHAR | PVR067 | TG-PVR067A-2 | DT-2 | Swasthya vihar kiosk Vikas Marg | 2 | 630 | 19504801 | 499 | 2019-06-12 17:00 | 198 | 783 | 124 | 485 | 177 | 683 | 263 | 642.5 | 77.5 |  |  | 77.5 | 29% | 32% | 79% | 42% | 4.5634 | Loss 0-5%
796 | 1230 | LNR | PREET VIHAR | PVR068 | TG-PVR068A-1 | DT-1 | CHITRA VIHAR:ID | 3 | 630 | 19506666 | 528 | 2019-06-30 01:00 | 199 | 814 | 174 | 716 | 155 | 634 | 156 | 692.5 | 26 |  |  | 26 | 84% | 59% | 62% | 76% | 5.0892 | Loss 5-10% |  |  | 511(49.5)
797 | 1230 | LNR | PREET VIHAR | PVR068 | TG-PVR068A-2 | DT-2 | CHITRA VIHAR:ID | 3 | 630 | 19503203 | 567 | 2019-06-02 22:30 | 238 | 1081 | 199 | 884 | 130 | 573 | 444 | 615.5 | 104 |  |  | 104 | 88% | 56% | 63% | 90% | 5.0892 | Loss 5-10% |  | 552(46) | 564(111) | 535(28.5)
798 | 1230 | LNR | PREET VIHAR | PVR082 | TG-PVR082A-1 | DT-1 | E-BLK PREET VIHAR(NEAR E-95 PREET VIHAR) | 1 | 630 | 19503740 | 583 | 2019-06-12 | 159 | 690 | 180 | 783 | 244 | 1070 | 343 | 579 | 115.5 | 1.5 |  | 117 | 93% | 58% | 67% | 91% | 3.243 | Loss 0-5% |  | 584(75.5) | 605(154) | 546(61)
799 | 1240 | MVR | S/STN 8 POCKET C | MV2002 | TG-MV2002A-2 | DT-2 | 15 BLCOK KALYAN PURI:K | 2 | 630 | 19505816 | 558 | 2019-06-30 23:00 | 171 | 705 | 137 | 559 | 250 | 1031 | 419 | 640 | 79 |  |  | 79 | 84% | 66% | 78% | 89% | 9.0896 | Loss 5-10% |  |  | 545(63) | 533(40)
800 | 1240 | MVR | S/STN 8 POCKET C | MV2004 | TG-MV2004A-1 | DT-1 | 13 & 18 BLK,KALYANPURI | 2 | 990 | 19505817 | 956 | 2019-06-09 06:00 | 334 | 1439 | 291 | 1254 | 331 | 1424 | 178 | 420.5 | 290.5 | 7 |  | 297.5 | 93% | 97% | 91% | 92% | 7.936 | Loss 5-10%
801 | 1240 | MVR | S/STN 8 POCKET C | MV2005 | TG-MV2005A-2 | DT-2 | 17 BLOCK KLP:PL | 3 | 990 | 19502773 | 815 | 2019-06-11 23:30 | 278 | 1252 | 266 | 1196 | 270 | 1215 | 50 | 601 | 119 |  |  | 119 | 80% | 68% | 68% | 82% | 18.9815 | Loss 10-20% |  | 760(32.5) | 823(153.5) | 853(135.5) | 780(70)
802 | 1240 | MVR | S/STN 8 POCKET C | MV2005 | TG-MV2005A-3 | DT-3 | 17 BLOCK KLP:PL | 3 | 630 | 19505914 | 495 | 2019-06-29 23:30 | 175 | 787 | 169 | 762 | 151 | 676 | 100 | 690.5 | 29.5 |  |  | 29.5 | 76% | 61% | 64% | 79% | 18.9815 | Loss 10-20% |  | 740(165.5) | 715(349.5) | 660(242.5) | 727(153.5)
803 | 1240 | MVR | S/STN 8 POCKET C | MV2007 | TG-MV2007A-1 | DT-1 | KHP VILLAGE MAIN ROAD:PL | 2 | 630 | 19506237 | 555 | 2019-06-11 23:30 | 152 | 661 | 191 | 818 | 212 | 917 | 224 | 499.5 | 220.5 |  |  | 220.5 | 87% | 69% | 82% | 88% | 19.5724 | Loss 10-20% |  |  | 494(77.5)
804 | 1240 | MVR | S/STN 8 POCKET C | MV2009 | TG-MV2009A-1 | DT-1 | A BLOCK V. NAGAR:PL | 1 | 990 | 19502531 | 934 | 2019-06-30 23:00 | 347 | 1658 | 287 | 1363 | 301 | 1433 | 266 | 587.5 | 128 | 4 |  | 132 | 89% | 57% | 72% | 94% | 3.0145 | Loss 0-5% |  |  | 806(66.5) | 894(76.5) | 778(32.5)
805 | 1240 | MVR | S/STN 8 POCKET C | MV2010 | TG-MV2010A-1 | DT-1 | E BLOCK V. NAGAR:PL | 3 | 630 | 19503465 | 656 | 2019-06-30 02:00 | 181 | 777 | 205 | 889 | 271 | 1187 | 367 | 573 | 125 | 20.5 | 1.5 | 147 | 104% | 82% | 69% | 73% | 9.1771 | Loss 5-10% |  |  | 654(89.5) |  | 520(48)
806 | 1240 | MVR | S/STN 8 POCKET C | MV2010 | TG-MV2010A-2 | DT-2 | E BLOCK V. NAGAR:PL | 3 | 990 | 19502553 | 1099 | 2019-06-30 23:00 | 336 | 1513 | 406 | 1836 | 357 | 1596 | 290 | 592 | 86 | 28 | 14 | 128 | 107% | 72% | 82% | 111% | 9.1771 | Loss 5-10% | 1118(91) | 1552(370.5) | 1447(478) | 1344(126) |  | 1109(178)
807 | 1240 | MVR | S/STN 8 POCKET C | MV2018 | TG-MV2018A-1 | DT-1 | S/S NO. 5 PKT. B :ID | 2 | 630 | 19500735 | 508.838 | 2019-06-30 | 190.6848 | 869.0404 | 155.94 | 715.1899 | 162.2131 | 736.9639 | 144.2018 | 666 | 54 |  |  | 54 | 81% | 51% | 63% | 81% | 9.0414 | Loss 5-10% |  |  | 536(67)
808 | 1240 | MVR | S/STN 8 POCKET C | MV2025 | TG-MV2025A-2 | DT-2 | S/S NO. 4 PKT-E MVR II:ID | 2 | 630 | 19502109 | 533 | 2019-06-26 23:30 | 153 | 730 | 173 | 823 | 207 | 990 | 229 | 679 | 41 |  |  | 41 | 81% | 50% | 57% | 85% | 9.4297 | Loss 5-10% |  |  | 510(29)
809 | 1240 | MVR | S/STN 8 POCKET C | MV2034 | TG-MV2034A-2 | DT-2 | D BLOCK GAZIPUR:ID | 2 | 400 | 19506238 | 332 | 2019-06-25 17:30 | 137 | 556 | 90 | 365 | 105 | 425 | 169 | 661 | 59 |  |  | 59 | 74% | 74% | 83% | 64% | 28.8864 | Loss 20-30% | 393(168.5) | 387(257) | 457(330) | 375(150) | 382(81) | 522(134)
810 | 1240 | MVR | S/STN 8 POCKET C | MV2036 | TG-MV2036A-2 | DT-2 | DDA JANTA FLAT GAZIPUR:ID | 2 | 990 | 19502496 | 906 | 2019-06-30 | 244 | 1036 | 330 | 1392 | 332 | 1411 | 366 | 555 | 163 | 2 |  | 165 | 91% | 64% | 73% | 91% | 9.0693 | Loss 5-10% |  | 821(55) | 895(159) | 915(126.5) | 813(71)
811 | 1240 | MVR | S/STN 8 POCKET C | MV2037 | TG-MV2037A-1 | DT-1 | S/S NO. 1 PKT A MVR-II:ID | 1 | 630 | 19502073 | 606 | 2019-06-11 23:30 | 211 | 886 | 202 | 842 | 193 | 807 | 69 | 599.5 | 114 | 6.5 |  | 120.5 | 96% | 61% | 72% | 96% | 4.3259 | Loss 0-5% |  | 538(40) | 576(99.5) | 561(54)
812 | 1240 | MVR | S/STN 8 POCKET C | MV2041 | TG-MV2041A-1 | DT-1 | S/S NO. 1 KHR COLONY:ID | 2 | 990 | 19502491 | 786 | 2019-06-26 22:30 | 263 | 1082 | 212 | 868 | 310 | 1269 | 347 | 687.5 | 31.5 |  |  | 31.5 | 76% | 67% | 64% | 79% | 3.4545 | Loss 0-5%
813 | 1240 | MVR | S/STN 8 POCKET C | MV2041 | TG-MV2041A-2 | DT-2 | S/S NO. 1 KHR COLONY:ID | 2 | 400 | 19504469 | 343 | 2019-06-11 03:00 | 84 | 332 | 166 | 659 | 93 | 389 | 302 | 680.5 | 38.5 |  |  | 38.5 | 86% | 71% | 63% | 85% | 3.4545 | Loss 0-5% |  |  | 300(29)
814 | 1240 | MVR | S/STN 8 POCKET C | MV2043 | TG-MV2043A-2 | DT-2 | S/S -10 BLK KHP. COROM:PL | 2 | 630 | 19505915 | 691 | 2019-06-29 23:30 | 221 | 940 | 248 | 1055 | 222 | 933 | 118 | 288.5 | 302 | 101.5 | 27 | 430.5 | 108% | 93% | 108% | 110% | 14.1884 | Loss 10-20% | 581(100) | 752(399) | 722(476.5) | 727(450.5) |  | 657(139)
815 | 1240 | MVR | S/STN 8 POCKET C | MV2045 | TG-MV2045A-1 | DT-1 | S/S 8 BLK KHP COLONY:PL | 2 | 630 | 19505911 | 619 | 2019-06-10 10:30 | 226 | 988 | 218 | 950 | 175 | 761 | 211 | 494.5 | 204 | 21.5 |  | 225.5 | 93% | 81% | 98% | 96% | 10.6083 | Loss 10-20% | 770(307) | 827(545) | 853(652) | 1068(686.5)
816 | 1240 | MVR | S/STN 8 POCKET C | MV2046 | TG-MV2046A-1 | DT-1 | S/S 10 BLK KHP COLONY (OLD):PL | 1 | 990 | 19502572 | 876 | 2019-06-30 23:30 | 253 | 1031 | 303 | 1253 | 319 | 1324 | 264 | 585 | 134.5 |  |  | 134.5 | 85% | 66% | 73% | 88% | 12.1003 | Loss 10-20% |  |  | 767(41) | 798(35.5)
817 | 1240 | MVR | S/STN 8 POCKET C | MV2047 | TG-MV2047A-1 | DT-1 | S/S 2 BLK KHP COLONY:ID | 2 | 630 | 19506725 | 750 | 2019-06-06 | 230 | 942 | 258 | 1066 | 262 | 1089 | 137 | 404.5 | 263.5 | 48.5 | 3.5 | 315.5 | 119% | 81% | 87% | 101% | 3.3797 | Loss 0-5% |  | 579(96) | 668(301.5) | 666(298.5) | 603(239) | 593(36.5)
818 | 1240 | MVR | S/STN 8 POCKET C | MV2062 | TG-MV2062A-1 | DT-1 | D BLK EAST VINOD NAGAR | 1 | 630 | 19505701 | 620 | 2019-06-30 23:30 | 248 | 1094 | 186 | 813 | 186 | 817 | 279 | 631.5 | 83 | 5.5 |  | 88.5 | 96% | 52% | 75% | 98% | 3.8374 | Loss 0-5%
819 | 1240 | MVR | S/STN 8 POCKET C | MV2064 | TG-MV2064A-1 | DT-1 | R BLOCK EAST VINOD NGR SPER SHINE | 1 | 990 | 19505715 | 806 | 2019-06-06 | 267 | 1115 | 267 | 1116 | 272 | 1138 | 23 | 663.5 | 56.5 |  |  | 56.5 | 81% | 53% | 69% | 80% | 11.8147 | Loss 10-20% |  |  | 792(25) | 794(25.5)
820 | 1240 | MVR | SADAR APPARTMENTS | MV1007 | TG-MV1007A-1 | DT-1 | ACHARYA NIKETAN PL/M:PL | 1 | 990 | 19502065 | 754 | 2019-06-13 16:00 | 286 | 1266 | 254 | 1115 | 214 | 940 | 282 | 688 | 32 |  |  | 32 | 25% | 20% | 76% | 54% | 6.4824 | Loss 5-10%
821 | 1240 | MVR | SADAR APPARTMENTS | MV1008 | TG-MV1008A-2 | DT-2 | ACHARYA NIKETAN:ID | 3 | 990 | 19504284 | 855 | 2019-06-13 17:30 | 297 | 1268 | 308 | 1321 | 249 | 1063 | 237 | 513.5 | 206 |  |  | 206 | 77% | 56% | 86% | 76% | 4.5642 | Loss 0-5% |  | 925(126) | 971(324.5) | 990(242.5) | 865(172)
822 | 1240 | MVR | SADAR APPARTMENTS | MV1008 | TG-MV1008A-3 | DT-3 | ACHARYA NIKETAN:ID | 3 | 630 | 19505647 | 627 | 2019-06-30 14:30 | 127 | 540 | 348 | 1581 | 152 | 681 | 977 | 439 | 276 | 4.5 |  | 280.5 | 96% | 68% | 100% | 91% | 4.5642 | Loss 0-5% |  |  | 581(107) | 527(53) |  | 595(91.5)
823 | 1240 | MVR | SADAR APPARTMENTS | MV1009 | TG-MV1009A-1 | DT-1 | SHASHI GARDEN PLM:PL | 2 | 990 | 19502111 | 1297 | 2019-06-30 01:00 | 363 | 1522 | 473 | 2002 | 460 | 1939 | 452 | 373.5 | 184.5 | 63.5 | 98.5 | 346.5 | 131% | 79% | 90% | 131% | 5.7344 | Loss 5-10% |  | 1217(153.5) | 1353(460) |  | 1132(288) | 952(72.5)
824 | 1240 | MVR | SADAR APPARTMENTS | MV1018 | TG-MV1018A-1 | DT-1 | S/S-2 PKT-I MVR PH-I:ID | 3 | 630 | 19502099 | 540 | 2019-06-30 23:30 | 158 | 669 | 218 | 923 | 164 | 685 | 247 | 638 | 82 |  |  | 82 | 83% | 74% | 79% | 86% | 6.6913 | Loss 5-10% |  | 569(34) | 541(113.5) | 540(46)
825 | 1240 | MVR | SADAR APPARTMENTS | MV1023 | TG-MV1023A-1 | DT-1 | S/S-B PKT-2 MVR PH-I:ID | 2 | 630 | 19502096 | 536 | 2019-06-10 23:30 | 206 | 911 | 141 | 628 | 188 | 821 | 250 | 658 | 62 |  |  | 62 | 83% | 49% | 62% | 85% | 6.2483 | Loss 5-10% |  | 521(28.5) | 552(80.5)
826 | 1240 | MVR | SADAR APPARTMENTS | MV1024 | TG-MV1024A-1 | DT-1 | PARTAP NAGAR PLM:PL | 1 | 990 | 19500719 | 1051 | 2019-06-06 17:30 | 438 | 1804 | 302 | 1229 | 311 | 1268 | 557 | 495.5 | 197 | 24.5 | 1.5 | 223 | 99% | 71% | 106% | 98% | 3.7964 | Loss 0-5% |  |  | 821(72) | 809(30.5)
827 | 1240 | MVR | SADAR APPARTMENTS | MV1028 | TG-MV1028A-2 | DT-2 | S/S-2 PKT IV MVR PH-1:ID | 2 | 630 | 19502067 | 569 | 2019-06-02 23:30 | 182 | 772 | 206 | 877 | 182 | 776 | 103 | 672.5 | 46.5 | 0.5 |  | 47 | 89% | 50% | 69% | 90% | 5.6935 | Loss 5-10% |  | 553(48.5) | 609(105.5)
828 | 1240 | MVR | SADAR APPARTMENTS | MV1046 | TG-MV1046A-1 | DT-1 | STN-8 PKT-1 MVR-1(SWITCHING STN) | 2 | 630 | 19500700 | 587.8158 | 2019-06-30 23:00 | 249.0262 | 1124.3224 | 168.7015 | 749.9845 | 170.0881 | 743.2295 | 377.7607 | 617.5 | 99 | 2 |  | 101 | 89% | 57% | 68% | 93% | 4.9963 | Loss 0-5% |  | 527(31.5) | 580(104) | 548(47.5)
829 | 1240 | MVR | SADAR APPARTMENTS | MV1058 | TG-MV1058A-1 | DT-1 | CHILLA VILLAGE (OLD):PL | 1 | 990 | 19505242 | 869 | 2019-06-29 00:30 | 324 | 1356 | 220 | 915 | 326 | 1395 | 461 | 635.5 | 83 |  |  | 83 | 88% | 76% | 67% | 78% | 38.5453 | Loss >30% |  |  | 768(70.5) | 790(93.5)
830 | 1240 | MVR | SADAR APPARTMENTS | MV1074 | TG-MV1074A-1 | DT-1 | ADRESH MOHALLA:PL | 2 | 990 | 19502118 | 827 | 2019-06-02 | 332 | 1370 | 279 | 1136 | 216 | 886 | 419 | 647 | 71.5 |  |  | 71.5 | 83% | 59% | 64% | 80% | 3.6182 | Loss 0-5% |  | 992(154) | 953(212) | 895(102.5) | 793(53.5)
831 | 1240 | MVR | SADAR APPARTMENTS | MV1074 | TG-MV1074A-2 | DT-2 | ADRESH MOHALLA:PL | 2 | 630 | 19504290 | 602 | 2019-06-30 00:30 | 184 | 823 | 184 | 827 | 234 | 1061 | 237 | 569.5 | 147 | 2.5 |  | 149.5 | 96% | 72% | 69% | 91% | 3.6182 | Loss 0-5% |  |  | 566(120) | 547(73.5) | 486(30.5)
832 | 1240 | MVR | SADAR APPARTMENTS | MV1075 | TG-MV1075A-2 | DT-2 | SAMASPUR VILLAGE:PL | 3 | 990 | 19504676 | 830 | 2019-06-30 00:30 | 299 | 1254 | 236 | 986 | 295 | 1238 | 261 | 687 | 33 |  |  | 33 | 84% | 58% | 63% | 82% | 4.9383 | Loss 0-5% |  | 1014(43) | 878(46.5)
833 | 1240 | MVR | SADAR APPARTMENTS | MV1077 | TG-MV1077A-1 | DT-1 | PATPAR GANJ VILLAGE:ID | 2 | 990 | 19504556 | 974 | 2019-06-30 | 361 | 1576 | 308 | 1334 | 305 | 1330 | 244 | 330.5 | 361.5 | 26.5 |  | 388 | 98% | 73% | 95% | 95% | 3.5524 | Loss 0-5% |  | 933(222) | 986(439.5) | 979(304.5) | 871(172)
834 | 1240 | MVR | SADAR APPARTMENTS | MV1092 | TG-MV1092A-1 | DT-1 | S.S 1 CGHS MVR PH 1:ID | 3 | 990 | 19502958 | 1000 | 2019-06-11 23:30 | 398 | 1667 | 287 | 1192 | 315 | 1315 | 427 | 548 | 147.5 | 22.5 | 1.5 | 171.5 | 99% | 66% | 74% | 101% | 9.7717 | Loss 5-10% |  | 1065(125.5) | 1157(259) | 1160(267.5) | 912(136.5)
835 | 1240 | MVR | SADAR APPARTMENTS | MV1092 | TG-MV1092A-3 | DT-3 | S.S 1 CGHS MVR PH 1:ID | 3 | 630 | 19506267 | 741 | 2019-06-26 23:00 | 319 | 1549 | 213 | 1000 | 209 | 995 | 551 | 527.5 | 133.5 | 49 | 10 | 192.5 | 108% | 66% | 90% | 118% | 9.7717 | Loss 5-10%
836 | 1240 | MVR | SADAR APPARTMENTS | MV1106 | TG-MV1106A-1 | DT-1 | S/S-4 PKT-5 PH-1:ID | 1 | 400 | 19502538 | 385 | 2019-06-26 22:30 | 156 | 678 | 124 | 535 | 105 | 446 | 203 | 663 | 51.5 | 3 |  | 54.5 | 92% | 64% | 64% | 96% | 13.2304 | Loss 10-20% |  | 342(43) | 373(41) | 383(58)
837 | 1240 | MVR | SADAR APPARTMENTS | MV1107 | TG-MV1107A-2 | DT-2 | NEW S/S SHASHIGARDEN:PLM | 3 | 630 | 19502512 | 685 | 2019-06-26 23:30 | 213 | 881 | 265 | 1101 | 207 | 856 | 233 | 183 | 342.5 | 162.5 | 30 | 535 | 108% | 95% | 89% | 109% | 16.6018 | Loss 10-20% |  | 629(57.5) | 665(492) | 677(228) | 616(59) | 614(280.5)
838 | 1240 | MVR | SADAR APPARTMENTS | MV1107 | TG-MV1107A-3 | DT-3 | NEW S/S SHASHIGARDEN:PLM | 3 | 630 | 19505731 | 569 | 2019-06-26 23:30 | 186 | 776 | 177 | 748 | 206 | 868 | 108 | 550 | 169 | 1 |  | 170 | 87% | 70% | 77% | 90% | 16.6018 | Loss 10-20% |  | 554(39.5) | 521(111) | 525(89.5) | 503(36)
839 | 1240 | MVR | SADAR APPARTMENTS | MV1117 | TG-MV1117A-1 | DT-1 | STN-4 CHILLA VIL NR DDA FLAT | 1 | 630 | 19505536 | 531 | 2019-06-10 02:00 | 175 | 761 | 153 | 649 | 204 | 883 | 202 | 556 | 164 |  |  | 164 | 84% | 84% | 77% | 82% | 46.7507 | Loss >30% |  | 1043(39) | 532(162.5) | 545(175) | 542(125.5)
840 | 1240 | MVR | TRILOKPURI | TKP003 | TG-TKP003A-1 | DT-1 | 7 BLOCK TKP:K | 2 | 990 | 19505097 | 873 | 2019-06-26 23:00 | 304 | 1292 | 262 | 1116 | 306 | 1311 | 186 | 589 | 130.5 |  |  | 130.5 | 88% | 69% | 73% | 88% | 3.1243 | Loss 0-5% |  |  | 790(52.5) | 1125(179)
841 | 1240 | MVR | TRILOKPURI | TKP003 | TG-TKP003A-2 | DT-2 | 7 BLOCK TKP:K | 2 | 630 | 19505810 | 535 | 2019-06-07 19:00 | 190 | 797 | 166 | 691 | 179 | 749 | 91 | 668 | 51.5 |  |  | 51.5 | 65% | 72% | 85% | 66% | 3.1243 | Loss 0-5% |  |  | 498(32) |  | 500(26)
842 | 1240 | MVR | TRILOKPURI | TKP005 | TG-TKP005A-1 | DT-1 | 10 BLOCK TKP:PL | 2 | 400 | 19505993 | 360 | 2019-06-22 20:00 | 141 | 591 | 111 | 463 | 108 | 446 | 138 | 608.5 | 111 | 0.5 |  | 111.5 | 80% | 72% | 90% | 85% | 9.7355 | Loss 5-10% |  |  | 347(35.5) | 363(26.5)
843 | 1240 | MVR | TRILOKPURI | TKP006 | TG-TKP006A-1 | DT-1 | 18 BLOCK TKP:PL:ID | 2 | 630 | 19505763 | 567 | 2019-06-30 23:30 | 182 | 818 | 186 | 827 | 198 | 898 | 77 | 528.5 | 191 | 0.5 |  | 191.5 | 89% | 73% | 80% | 90% | 8.5464 | Loss 5-10% |  | 528(35) | 616(177) | 589(155) | 542(95)
844 | 1240 | MVR | TRILOKPURI | TKP007 | TG-TKP007A-1 | DT-1 | 13 BLOCK TKP:ID | 2 | 630 | 19500453 | 647 | 2019-06-30 01:00 | 221 | 960 | 194 | 839 | 233 | 1018 | 158 | 560 | 156.5 | 2.5 | 1 | 160 | 103% | 78% | 76% | 93% | 9.5923 | Loss 5-10% |  | 507(34) | 544(130) | 551(141.5) | 503(86.5)
845 | 1240 | MVR | TRILOKPURI | TKP007 | TG-TKP007A-2 | DT-2 | 13 BLOCK TKP:ID | 2 | 990 | 19506208 | 916 | 2019-06-30 01:00 | 395 | 1711 | 258 | 1122 | 263 | 1125 | 587 | 642.5 | 77 | 0.5 |  | 77.5 | 93% | 72% | 72% | 85% | 9.5923 | Loss 5-10% |  | 985(90.5) | 911(181.5) | 933(177.5) | 841(117.5)
846 | 1240 | MVR | TRILOKPURI | TKP008 | TG-TKP008A-1 | DT-1 | 23 BLOCK TKP:PL | 2 | 990 | 19504151 | 944 | 2019-06-26 23:00 | 326 | 1360 | 310 | 1301 | 308 | 1280 | 72 | 540 | 172 | 8 |  | 180 | 91% | 74% | 72% | 95% | 4.5654 | Loss 0-5% |  | 853(34) | 908(145.5) | 905(154.5) | 822(79.5)
847 | 1240 | MVR | TRILOKPURI | TKP008 | TG-TKP008A-2 | DT-2 | 23 BLOCK TKP:PL | 2 | 630 | 19504155 | 709 | 2019-06-12 06:00 | 246 | 1012 | 206 | 850 | 257 | 1069 | 197 | 437 | 271.5 | 10.5 | 1 | 283 | 95% | 112% | 92% | 94% | 4.5654 | Loss 0-5% |  | 513(60) | 590(218) | 578(202.5) | 521(142)
848 | 1240 | MVR | TRILOKPURI | TKP012 | TG-TKP012A-1 | DT-1 | 26 BLOCK TKP:ID | 2 | 990 | 19506805 | 889 | 2019-06-27 06:00 | 295 | 1295 | 302 | 1308 | 292 | 1258 | 45 | 659.5 | 60.5 |  |  | 60.5 | 83% | 90% | 75% | 85% | 11.9696 | Loss 10-20% |  |  | 791(33)
849 | 1240 | MVR | TRILOKPURI | TKP013 | TG-TKP013A-1 | DT-1 | 134 WORK CENTER:ID | 2 | 630 | 19505258 | 535 | 2019-06-26 00:30 | 217 | 899 | 144 | 590 | 174 | 725 | 268 | 672 | 48 |  |  | 48 | 85% | 81% | 70% | 78% | 11.2278 | Loss 10-20% |  |  | 504(43) | 508(30)
850 | 1240 | MVR | TRILOKPURI | TKP014 | TG-TKP014A-1 | DT-1 | 320 EWS CHILLA DDA FLAT,TKP | 1 | 630 | 19506913 | 516.4526 | 2019-06-30 23:30 | 168.6874 | 735.47 | 166.1172 | 732.1808 | 181.648 | 797.5063 | 63.7446 | 681 | 39 |  |  | 39 | 78% | 63% | 60% | 82% | 2.6459 | Loss 0-5%
851 | 1240 | MVR | TRILOKPURI | TKP016 | TG-TKP016A-1 | DT-1 | 31 BLOCK TKP:K | 2 | 630 | 19504812 | 784 | 2019-06-30 23:00 | 229 | 1007 | 287 | 1293 | 269 | 1214 | 255 | 180.5 | 282 | 101 | 156.5 | 539.5 | 124% | 104% | 99% | 124% | 6.4787 | Loss 5-10% |  |  | 515(108) | 531(81)
852 | 1240 | MVR | TRILOKPURI | TKP018 | TG-TKP018A-1 | DT-1 | 28 BLOCK TKP:PL | 2 | 990 | 19506682 | 837 | 2019-06-27 06:00 | 301 | 1283 | 259 | 1118 | 278 | 1186 | 144 | 694 | 25 |  |  | 25 | 78% | 85% | 72% | 76% | 3.5227 | Loss 0-5%
853 | 1240 | MVR | TRILOKPURI | TKP020 | TG-TKP020A-2 | DT-2 | KOTLA VILLAGE:PL | 2 | 630 | 19505256 | 651 | 2019-06-12 00:30 | 191 | 819 | 244 | 1050 | 215 | 918 | 201 | 385 | 311.5 | 18 | 0.5 | 330 | 103% | 79% | 89% | 98% | 25.8551 | Loss 20-30% |  | 582(147) | 681(344) | 615(309.5) | 584(212)
854 | 1240 | MVR | TRILOKPURI | TKP023 | TG-TKP023A-1 | DT-1 | 17 BLOCK TKP:PL | 2 | 990 | 19502505 | 1079 | 2019-06-03 02:00 | 343 | 1449 | 333 | 1410 | 402 | 1694 | 266 | 447 | 187.5 | 67 | 15.5 | 270 | 109% | 77% | 81% | 104% | 6.449 | Loss 5-10% |  | 907(109.5) | 1049(168) | 1086(271) | 949(83.5) | 795(30)
855 | 1240 | MVR | TRILOKPURI | TKP023 | TG-TKP023A-2 | DT-2 | 17 BLOCK TKP:PL | 2 | 630 | 19505648 | 722 | 2019-06-03 | 274 | 1235 | 261 | 1183 | 187 | 840 | 372 | 538 | 134 | 35.5 | 9.5 | 179 | 115% | 75% | 73% | 104% | 6.449 | Loss 5-10% |  | 587(80) | 692(199.5) | 629(150.5) | 614(104.5)
856 | 1240 | MVR | TRILOKPURI | TKP024 | TG-TKP024A-1 | DT-1 | 2 BLOCK TKP:PL | 2 | 630 | 19505548 | 764 | 2019-06-09 | 245 | 1182 | 239 | 1145 | 281 | 1361 | 200 | 603.5 | 75.5 | 33.5 | 5 | 114 | 121% | 80% | 87% | 101% | 4.7514 | Loss 0-5% |  | 739(160.5) | 707(320) | 665(306) | 640(281) | 556(59)
857 | 1240 | MVR | TRILOKPURI | TKP025 | TG-TKP025A-1 | DT-1 | 15 BLOCK TKP:PL | 1 | 630 | 19502486 | 562 | 2019-06-26 23:30 | 208 | 882 | 165 | 701 | 189 | 799 | 157 | 554 | 166 |  |  | 166 | 89% | 77% | 65% | 89% | 9.822 | Loss 5-10% |  | 486(32) | 524(173) | 522(120.5) | 503(51)
858 | 1240 | MVR | TRILOKPURI | TKP027 | TG-TKP027A-1 | DT-1 | 11&12 BLOCK TRILOK TRILOK PURI | 2 | 630 | 19505745 | 597 | 2019-06-22 20:00 | 175 | 750 | 219 | 935 | 203 | 871 | 163 | 568.5 | 150.5 | 0.5 |  | 151 | 87% | 75% | 95% | 87% | 3.4944 | Loss 0-5% |  |  | 621(64.5) | 636(48)
859 | 1240 | MVR | TRILOKPURI | TKP030 | TG-TKP030A-1 | DT-1 | KOTLA VILLAGE NEW | 1 | 630 | 19504357 | 675 | 2019-06-13 23:30 | 226 | 962 | 223 | 946 | 226 | 965 | 17 | 224 | 153.5 | 43 | 21.5 | 218 | 107% | 85% | 89% | 107% | 6.3206 | Loss 5-10%
860 | 1240 | MVR | TRILOKPURI | TKP032 | TG-TKP032A-1 | DT-1 | NEW 28 BLOCK TRILOKPURI | 1 | 630 | 19506216 | 647 | 2019-06-27 06:00 | 203 | 828 | 220 | 891 | 224 | 927 | 86 | 538 | 176.5 | 4.5 | 1 | 182 | 102% | 103% | 88% | 99% | 5.5413 | Loss 5-10% |  | 555(68) | 759(176) | 578(128)
861 | 1241 | MV3 | MVR-III | VSE004 | TG-VSE004A-2 | DT-2 | S/STN 5 A2 PKT MVR-III:ID | 2 | 400 | 19503533 | 440 | 2019-06-03 01:00 | 172 | 781 | 165 | 744 | 103 | 455 | 309 | 587 | 109 | 21 | 2 | 132 | 110% | 53% | 70% | 102% | 3.0953 | Loss 0-5% |  | 345(30) | 387(98) | 403(72)
862 | 1241 | MV3 | MVR-III | VSE008 | TG-VSE008A-2 | DT-2 | S/STN 9 A2 PKT MVR - III:ID | 2 | 630 | 19502404 | 550 | 2019-06-29 23:30 | 175 | 728 | 215 | 908 | 160 | 666 | 218 | 676 | 43 |  |  | 43 | 87% | 47% | 62% | 87% | 4.1941 | Loss 0-5% |  |  | 546(49)
863 | 1241 | MV3 | MVR-III | VSE011 | TG-VSE011A-1 | DT-1 | S/STN B5 DDA JANTA FLATE:ID | 1 | 400 | 19506212 | 369 | 2019-06-30 23:00 | 109 | 442 | 142 | 578 | 119 | 486 | 120 | 622.5 | 95 | 2.5 |  | 97.5 | 92% | 48% | 72% | 92% | 2.8602 | Loss 0-5% |  |  | 348(68) | 378(76.5)
864 | 1241 | MV3 | MVR-III | VSE012 | TG-VSE012A-1 | DT-1 | S/STN 3 B-7 DDA JANTA FLAT:ID | 2 | 400 | 19502420 | 477 | 2019-06-30 22:30 | 197 | 833 | 104 | 433 | 176 | 751 | 366 | 517.5 | 131 | 48.5 | 23 | 202.5 | 109% | 56% | 89% | 119% | 4.3101 | Loss 0-5% |  | 385(87) |  |  | 385(123.5)
865 | 1241 | MV3 | MVR-III | VSE014 | TG-VSE014A-1 | DT-1 | S/STN C-1 PKT DDA JANTA FLAT:ID | 1 | 630 | 19506899 | 527 | 2019-06-02 | 211 | 873 | 143 | 593 | 173 | 718 | 243 | 642.5 | 76.5 |  |  | 76.5 | 84% | 57% | 72% | 83% | 7.006 | Loss 5-10% |  |  | 506(49.5)
866 | 1241 | MV3 | MVR-III | VSE015 | TG-VSE015A-1 | DT-1 | S/STN C-2 PKT DDA JANTA FLAT:ID | 1 | 630 | 19502405 | 661 | 2019-06-30 23:00 | 226 | 949 | 242 | 1025 | 193 | 819 | 181 | 496 | 177.5 | 40.5 | 6 | 224 | 102% | 70% | 87% | 105% | 6.3715 | Loss 5-10% |  | 595(83) | 607(208) | 681(155) | 549(86)
867 | 1241 | MV3 | MVR-III | VSE036 | TG-VSE036A-1 | DT-1 | SUBJI MANDI HARIJAN BASTI KNODLI:K | 2 | 990 | 19506914 | 1208 | 2019-06-02 23:30 | 358 | 1615 | 453 | 2059 | 396 | 1770 | 390 | 373.5 | 286 | 46.5 | 5.5 | 338 | 100% | 81% | 89% | 122% | 12.9457 | Loss 10-20% | 788(26.5) | 1093(311.5) | 1216(577.5) | 1225(524) | 1071(328.5) | 768(25)
868 | 1241 | MV3 | MVR-III | VSE037 | TG-VSE037A-1 | DT-1 | KNODLI VILL. PANCHYAT GHAR:PL | 1 | 990 | 19502838 | 794 | 2019-06-29 22:30 | 199 | 859 | 357 | 1550 | 238 | 1010 | 630 | 655 | 63 |  |  | 63 | 77% | 69% | 72% | 80% | 16.0114 | Loss 10-20% |  |  | 876(197.5) | 886(54.5) | 866(92)
869 | 1241 | MV3 | MVR-III | VSE039 | TG-VSE039A-1 | DT-1 | KNODLI INDAL PUBLIC SCHOOL:PM | 1 | 400 | 19506640 | 433 | 2019-06-30 22:30 | 152 | 632 | 163 | 676 | 118 | 483 | 175 | 205.5 | 387 | 114.5 | 12.5 | 514 | 102% | 93% | 93% | 108% | 20.3023 | Loss 20-30% | 334(42.5) | 420(376.5) | 386(447) | 378(286)
870 | 1241 | MV3 | MVR-III | VSE042 | TG-VSE042A-1 | DT-1 | B-BLK RAJBIR COLONY:PL | 2 | 990 | 19502732 | 763 | 2019-06-11 23:00 | 212 | 912 | 286 | 1256 | 265 | 1160 | 307 | 688 | 31.5 |  |  | 31.5 | 76% | 67% | 65% | 77% | 11.3691 | Loss 10-20%
871 | 1241 | MV3 | MVR-III | VSE045 | TG-VSE045A-1 | DT-1 | GHARAOLI VILL. OLD:PL | 1 | 630 | 19502849 | 504 | 2019-06-13 23:00 | 175 | 731 | 151 | 624 | 177 | 724 | 104 | 606.5 | 112.5 |  |  | 112.5 | 79% | 71% | 70% | 80% | 17.1142 | Loss 10-20%
872 | 1241 | MV3 | MVR-III | VSE046 | TG-VSE046A-1 | DT-1 | GHARAOLI VILL. NEW:PL | 1 | 990 | 19502842 | 785 | 2019-06-13 23:00 | 270 | 1108 | 241 | 998 | 274 | 1146 | 133 | 632 | 87.5 |  |  | 87.5 | 77% | 69% | 72% | 79% | 11.469 | Loss 10-20% |  | 858(111) | 893(270.5) | 827(53.5) | 760(26.5)
873 | 1241 | MV3 | MVR-III | VSE142 | TG-VSE142A-1 | DT-1 | STN 3 GHAROLI DAIRY CL MVR PH-3:ID | 2 | 990 | 19504841 | 1052 | 2019-06-30 23:30 | 333 | 1416 | 334 | 1440 | 385 | 1680 | 253 | 463.5 | 194 | 55 | 7.5 | 256.5 | 104% | 66% | 89% | 106% | 4.8702 | Loss 0-5% |  | 958(116.5) | 1033(287) | 1020(207) | 1010(161)
874 | 1241 | MV3 | MVR-III | VSE142 | TG-VSE142A-2 | DT-2 | STN 3 GHAROLI DAIRY CL MVR PH-3:ID | 2 | 630 | 19502831 | 522 | 2019-06-11 23:30 | 189 | 764 | 158 | 636 | 175 | 713 | 111 | 645 | 75 |  |  | 75 | 82% | 56% | 77% | 83% | 4.8702 | Loss 0-5%
875 | 1241 | MV3 | MVR-III | VSE143 | TG-VSE143A-1 | DT-1 | STN 4 GHAROLI DAIRY CL MVR PH-3:ID | 2 | 990 | 19503159 | 1001 | 2019-06-02 23:00 | 425 | 1830 | 273 | 1147 | 303 | 1298 | 621 | 533.5 | 154 | 29.5 | 1 | 184.5 | 99% | 72% | 87% | 101% | 6.3496 | Loss 5-10% |  |  | 975(172.5) | 966(198) | 1000(142)
876 | 1241 | MV3 | MVR-III | VSE143 | TG-VSE143A-2 | DT-2 | STN 4 GHAROLI DAIRY CL MVR PH-3:ID | 2 | 630 | 19502843 | 666 | 2019-06-30 23:00 | 231 | 1013 | 213 | 934 | 222 | 974 | 68 | 535 | 136.5 | 39.5 | 7.5 | 183.5 | 103% | 72% | 95% | 106% | 6.3496 | Loss 5-10%
877 | 1241 | MV3 | MVR-III | VSE163 | TG-VSE163A-1 | DT-1 | S/S-2 C-BLK HARIZAN BASTI,MULLA CLY:PL | 1 | 630 | 19506207 | 719 | 2019-06-02 23:30 | 250 | 1121 | 232 | 1049 | 238 | 1067 | 65 | 292 | 344 | 80 | 4 | 428 | 101% | 91% | 106% | 114% | 7.6876 | Loss 5-10% |  |  |  |  | 612(302)
878 | 1241 | MV3 | NEW ASHOK NAGAR | VSE103 | TG-VSE103A-1 | DT-1 | ABLK NEW ASHOK NAGAR:ID | 2 | 990 | 19500836 | 1020.3621 | 2019-06-30 23:30 | 341.4279 | 1514.7642 | 311.9477 | 1378.3478 | 366.9866 | 1631.4866 | 219.4457 | 390.5 | 267.5 | 59.5 | 2.5 | 329.5 | 99% | 78% | 84% | 103% | 5.0648 | Loss 5-10% |  | 936(103) | 1055(285.5) | 982(253.5) | 928(161)
879 | 1241 | MV3 | NEW ASHOK NAGAR | VSE103 | TG-VSE103A-2 | DT-2 | ABLK NEW ASHOK NAGAR:ID | 2 | 630 | 19500873 | 506.9606 | 2019-06-02 22:30 | 154.4813 | 704.7824 | 191.0069 | 876.9429 | 161.4724 | 730.5454 | 160.8341 | 619.5 | 100.5 |  |  | 100.5 | 80% | 63% | 74% | 80% | 5.0648 | Loss 5-10% |  |  | 528(61) | 500(71)
880 | 1241 | MV3 | NEW ASHOK NAGAR | VSE104 | TG-VSE104A-1 | DT-1 | ABLK (LOOP) NEW ASHOK NAGAR:ID | 2 | 990 | 19505992 | 1143 | 2019-06-26 22:30 | 361 | 1633 | 395 | 1757 | 387 | 1730 | 113 | 159 | 374 | 123 | 64 | 561 | 111% | 88% | 103% | 115% | 3.9427 | Loss 0-5% | 816(33) | 1106(321) | 1149(635) | 1124(598) | 1081(517.5) | 955(192)
881 | 1241 | MV3 | NEW ASHOK NAGAR | VSE105 | TG-VSE105A-1 | DT-1 | B BLK NEW ASHOK NAGAR:ID | 2 | 990 | 19506128 | 948 | 2019-06-09 23:30 | 289 | 1315 | 375 | 1707 | 284 | 1288 | 406 | 635.5 | 81 | 3.5 |  | 84.5 | 94% | 71% | 86% | 96% | 5.5377 | Loss 5-10% |  |  | 776(47) | 778(35)
882 | 1241 | MV3 | NEW ASHOK NAGAR | VSE105 | TG-VSE105A-2 | DT-2 | B BLK NEW ASHOK NAGAR:ID | 2 | 990 | 19505427 | 765 | 2019-06-30 | 243 | 1078 | 264 | 1176 | 258 | 1167 | 94 | 689 | 31 |  |  | 31 | 77% | 58% | 68% | 77% | 5.5377 | Loss 5-10% |  |  | 751(28)
883 | 1241 | MV3 | NEW ASHOK NAGAR | VSE106 | TG-VSE106A-2 | DT-2 | B1 BLK NEW ASHOK NAGAR:ID | 2 | 990 | 19505221 | 900 | 2019-06-30 | 266 | 1222 | 310 | 1420 | 323 | 1479 | 233 | 535 | 184 | 0.5 |  | 184.5 | 91% | 80% | 75% | 89% | 5.5782 | Loss 5-10%
884 | 1241 | MV3 | NEW ASHOK NAGAR | VSE107 | TG-VSE107A-1 | DT-1 | B2 BLK NEW ASHOK NAGAR:ID | 2 | 990 | 19500797 | 1222.6722 | 2019-06-30 | 383.9311 | 1699.8631 | 426.4464 | 1913.4313 | 412.2947 | 1871.175 | 195.8887 | 250 | 325.5 | 95.5 | 48.5 | 469.5 | 124% | 88% | 92% | 110% | 3.7303 | Loss 0-5% | 846(35) | 1275(315.5) | 1015(339.5) | 1073(282.5) | 1024(224) | 823(30)
885 | 1241 | MV3 | NEW ASHOK NAGAR | VSE107 | TG-VSE107A-2 | DT-2 | B2 BLK NEW ASHOK NAGAR:ID | 2 | 990 | 19500303 | 1005 | 2019-06-30 01:30 | 336 | 1477 | 292 | 1291 | 377 | 1681 | 338 | 531.5 | 185 | 1 | 1 | 187 | 101% | 71% | 76% | 88% | 3.7303 | Loss 0-5% |  |  | 859(188.5) | 868(103.5) | 824(53)
886 | 1241 | MV3 | NEW ASHOK NAGAR | VSE108 | TG-VSE108A-2 | DT-2 | C2 BLK NEW ASHOK NAGAR:ID | 2 | 630 | 19506902 | 708 | 2019-06-29 23:30 | 234 | 1037 | 222 | 968 | 252 | 1101 | 115 | 376 | 227.5 | 81.5 | 34.5 | 343.5 | 112% | 82% | 84% | 112% | 4.6568 | Loss 0-5% |  | 562(59.5) | 518(112.5) | 552(116) | 488(39)
887 | 1241 | MV3 | NEW ASHOK NAGAR | VSE109 | TG-VSE109A-1 | DT-1 | C3 BLK NEW ASHOK NAGAR:ID | 2 | 630 | 19506026 | 916 | 2019-06-13 23:00 | 307 | 1330 | 329 | 1439 | 280 | 1206 | 202 | 417.5 | 159 | 37.5 | 98 | 294.5 | 141% | 139% | 131% | 145% | 3.8299 | Loss 0-5% |  |  | 541(139.5) | 556(105.5) | 521(46)
888 | 1241 | MV3 | NEW ASHOK NAGAR | VSE109 | TG-VSE109A-2 | DT-2 | C3 BLK NEW ASHOK NAGAR:ID | 2 | 990 | 19506757 | 842 | 2019-06-29 23:30 | 284 | 1244 | 233 | 1017 | 325 | 1444 | 370 | 687 | 31.5 |  |  | 31.5 | 82% | 59% | 63% | 85% | 3.8299 | Loss 0-5%
889 | 1241 | MV3 | NEW ASHOK NAGAR | VSE110 | TG-VSE110A-1 | DT-1 | C4 BLK NEW ASHOK NAGAR:ID | 2 | 630 | 19505530 | 728 | 2019-06-12 | 233 | 1013 | 259 | 1141 | 237 | 1032 | 119 | 437 | 220 | 36 | 27 | 283 | 116% | 85% | 91% | 115% | 4.6547 | Loss 0-5% |  | 518(44.5) | 561(79)
890 | 1241 | MV3 | NEW ASHOK NAGAR | VSE111 | TG-VSE111A-1 | DT-1 | C5 BLK NEW ASHOK NAGAR:ID | 2 | 990 | 19500846 | 927.2653 | 2019-06-26 23:00 | 285.326 | 1230.7024 | 284.4857 | 1215.0237 | 357.4536 | 1543.3427 | 320.7672 | 650.5 | 63.5 | 2 |  | 65.5 | 87% | 73% | 75% | 94% | 5.6564 | Loss 5-10% | 531(35.5)
891 | 1241 | MV3 | NEW ASHOK NAGAR | VSE111 | TG-VSE111A-2 | DT-2 | C5 BLK NEW ASHOK NAGAR:ID | 2 | 630 | 19500850 | 688.7085 | 2019-06-13 23:30 | 219.9498 | 920.4074 | 231.2776 | 977.2153 | 237.4812 | 1000.5107 | 71.3665 | 352.5 | 253.5 | 77 | 36.5 | 367 | 108% | 89% | 88% | 109% | 5.6564 | Loss 5-10% |  | 642(259.5) | 650(531) | 616(46) | 635(480) | 553(34)
892 | 1241 | MV3 | NEW ASHOK NAGAR | VSE112 | TG-VSE112A-2 | DT-2 | D BLK NEW ASHOK NAGAR:ID | 2 | 990 | 19505544 | 937 | 2019-06-30 23:00 | 283 | 1312 | 353 | 1651 | 301 | 1418 | 301 | 508.5 | 207 | 4.5 |  | 211.5 | 89% | 74% | 78% | 95% | 6.5989 | Loss 5-10% |  |  |  |  | 819(38.5)
893 | 1241 | MV3 | NEW ASHOK NAGAR | VSE113 | TG-VSE113A-1 | DT-1 | E1 BLK NEW ASHOK NAGAR:ID | 2 | 990 | 19505322 | 774 | 2019-06-02 23:30 | 269 | 1142 | 290 | 1214 | 215 | 901 | 284 | 677 | 41.5 |  |  | 41.5 | 77% | 66% | 66% | 78% | 4.4917 | Loss 0-5% |  | 1028(313) | 1048(398)
894 | 1241 | MV3 | NEW ASHOK NAGAR | VSE114 | TG-VSE114A-1 | DT-1 | E2 BLK NEW ASHOK NAGAR:ID | 2 | 630 | 19505994 | 1034.8665 | 2019-06-27 21:30 | 327.6259 | 1390.3664 | 380.7403 | 1656.5451 | 326.5002 | 1425.5784 | 250.4362 | 375 | 288 | 41.5 | 14.5 | 344 | 118% | 88% | 116% | 164% | 7.4756 | Loss 5-10% |  | 597(160.5) | 681(529) | 711(565) | 754(525.5) | 606(155)
895 | 1241 | MV3 | NEW ASHOK NAGAR | VSE114 | TG-VSE114A-2 | DT-2 | E2 BLK NEW ASHOK NAGAR:ID | 2 | 400 | 19505522 | 513 | 2019-06-30 23:00 | 170 | 769 | 181 | 822 | 162 | 733 | 78 | 251 | 307.5 | 66.5 | 94.5 | 468.5 | 124% | 100% | 104% | 128% | 7.4756 | Loss 5-10%
896 | 1241 | MV3 | VASUNDHARA ENCLAVE | VSE031 | TG-VSE031A-2 | DT-2 | S/STN 9 MIXED HOUSING MVR III:ID | 2 | 630 | 19506129 | 629 | 2019-06-30 03:00 | 260 | 1119 | 179 | 750 | 190 | 801 | 347 | 628 | 90.5 | 1.5 |  | 92 | 100% | 57% | 66% | 92% | 3.926 | Loss 0-5% |  | 517(33) | 535(88) | 565(36)
897 | 1241 | MV3 | VASUNDHARA ENCLAVE | VSE035 | TG-VSE035A-2 | DT-2 | S/STN D-BLK NEW KNODLI:ID | 2 | 400 | 19505985 | 377 | 2019-06-13 22:30 | 111 | 442 | 142 | 564 | 124 | 491 | 107 | 356.5 | 361 | 2 |  | 363 | 91% | 68% | 89% | 94% | 5.4137 | Loss 5-10%
898 | 1241 | MV3 | VASUNDHARA ENCLAVE | VSE048 | TG-VSE048A-1 | DT-1 | DALLUPURA VILL. DURGA PARK:ID | 2 | 990 | 19505213 | 800 | 2019-06-14 00:30 | 227 | 953 | 211 | 895 | 363 | 1558 | 636 | 679 | 40 |  |  | 40 | 81% | 67% | 73% | 76% | 30.429 | Loss >30% |  | 1025(98.5) | 949(228) | 1038(251.5) | 1005(63.5)
899 | 1241 | MV3 | VASUNDHARA ENCLAVE | VSE048 | TG-VSE048A-2 | DT-2 | DALLUPURA VILL. DURGA PARK:ID | 2 | 630 | 19505346 | 856 | 2019-06-30 12:30 | 248 | 1012 | 296 | 1222 | 312 | 1287 | 249 | 519 | 198.5 |  | 1.5 | 200 | 81% | 75% | 136% | 102% | 30.429 | Loss >30% |  | 701(237) | 586(82) | 675(62.5)
900 | 1241 | MV3 | VASUNDHARA ENCLAVE | VSE172 | TG-VSE172A-1 | DT-1 | DALLUPURA HARIZAN BASTI SUB STN. | 3 | 630 | 19500842 | 618.4301 | 2019-06-30 22:30 | 236.7289 | 1032.3531 | 198.3688 | 869.4286 | 183.3324 | 789.2052 | 214.5939 | 377.5 | 325 | 17 |  | 342 | 90% | 86% | 92% | 98% | 38.9217 | Loss >30% |  |  | 500(38.5) | 489(59.5) |  | 571(57)
901 | 1241 | MV3 | VASUNDHARA ENCLAVE | VSE172 | TG-VSE172A-2 | DT-2 | DALLUPURA HARIZAN BASTI SUB STN. | 3 | 630 | 19505698 | 570 | 2019-06-21 23:00 | 164 | 670 | 164 | 663 | 242 | 997 | 331 | 570.5 | 148.5 | 0.5 |  | 149 | 84% | 71% | 87% | 91% | 38.9217 | Loss >30% |  | 608(227.5) | 653(453) | 581(167)
902 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM001 | TG-YAM001A-1 | DT-1 | C-4 YAMUNA VIHAR:PL | 1 | 990 | 19506333 | 1005 | 2019-06-11 23:30 | 316 | 1339 | 264 | 1112 | 425 | 1825 | 632 | 635 | 80 | 3 | 0.5 | 83.5 | 86% | 62% | 63% | 101% | 5.6558 | Loss 5-10% |  | 949(69) | 1031(172) | 814(36)
903 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM003 | TG-YAM003A-1 | DT-1 | C-6, YAMUNA VIHAR:PG | 2 | 990 | 19503253 | 1093 | 2019-06-12 | 341 | 1454 | 360 | 1518 | 393 | 1663 | 186 | 565.5 | 91.5 | 40.5 | 21.5 | 153.5 | 110% | 58% | 74% | 109% | 6.5689 | Loss 5-10% |  | 1057(96) | 1125(186) | 1016(122) | 891(89)
904 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM003 | TG-YAM003A-2 | DT-2 | C-6, YAMUNA VIHAR:PG | 2 | 990 | 19503252 | 967 | 2019-06-29 23:30 | 396 | 1691 | 314 | 1325 | 257 | 1088 | 526 | 687.5 | 28 | 4.5 |  | 32.5 | 97% | 58% | 64% | 98% | 6.5689 | Loss 5-10%
905 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM005 | TG-YAM005A-2 | DT-2 | C-7, YAMUNA VIHAR:ID | 2 | 990 | 19506506 | 1024.4402 | 2019-06-12 | 382.7983 | 1627.2672 | 301.5334 | 1259.7486 | 340.1085 | 1429.748 | 318.5777 | 580.5 | 127 | 10.5 | 1.5 | 139 | 103% | 88% | 94% | 103% | 6.986 | Loss 5-10%
906 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM006 | TG-YAM006A-2 | DT-2 | C-7/2, YAMUNA VIHAR:ID | 2 | 630 | 19502948 | 552 | 2019-06-12 00:30 | 213 | 908 | 156 | 672 | 183 | 750 | 208 | 628 | 90 |  |  | 90 | 88% | 53% | 70% | 87% | 6.986 | Loss 5-10% |  | 628(55.5) | 706(162) | 589(100.5)
907 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM007 | TG-YAM007A-1 | DT-1 | C-8 YAMUNA VIHAR:ID | 3 | 990 | 19503237 | 960 | 2019-06-30 23:30 | 313 | 1287 | 336 | 1392 | 311 | 1285 | 106 | 663 | 51.5 | 5 |  | 56.5 | 94% | 56% | 67% | 97% | 10.0918 | Loss 10-20% |  | 1501(165.5) | 910(79.5) | 870(49)
908 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM008 | TG-YAM008A-1 | DT-1 | C-11 YAMUNA VIHAR:ID | 2 | 630 | 19500554 | 525 | 2019-06-30 00:30 | 180 | 704 | 209 | 830 | 135 | 529 | 262 | 694.5 | 25 |  |  | 25 | 83% | 56% | 58% | 80% | 9.1291 | Loss 5-10%
909 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM009 | TG-YAM009A-2 | DT-2 | C-12, YAMUNA VIHAR:ID | 2 | 400 | 19505309 | 368 | 2019-06-12 | 167 | 749 | 104 | 453 | 97 | 428 | 309 | 613.5 | 104.5 | 1 |  | 105.5 | 92% | 84% | 78% | 92% | 7.1641 | Loss 5-10% |  | 322(36.5) | 420(127.5) | 347(65.5)
910 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM011 | TG-YAM011A-1 | DT-1 | B-2 YAMUNA VIHAR:PL | 1 | 990 | 19503247 | 918 | 2019-06-29 23:00 | 370 | 1608 | 304 | 1309 | 244 | 1055 | 479 | 573 | 139 | 8 |  | 147 | 92% | 57% | 73% | 93% | 3.668 | Loss 0-5% |  | 842(34.5) | 949(114.5) | 899(59.5)
911 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM012 | TG-YAM012A-2 | DT-2 | B-4 YAMUNA VIHAR:ID | 2 | 990 | 19503453 | 1044 | 2019-06-10 01:30 | 348 | 1376 | 386 | 1548 | 310 | 1235 | 272 | 523.5 | 160 | 31 | 2 | 193 | 105% | 61% | 76% | 99% | 7.6872 | Loss 5-10% |  | 957(36.5) |  | 968(46.5) | 889(95)
912 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM015 | TG-YAM015A-1 | DT-1 | PUMPING STATION BHAJAN PURA :ID | 1 | 990 | 19504082 | 1166 | 2019-06-01 22:30 | 412 | 1677 | 386 | 1565 | 368 | 1501 | 155 | 282.5 | 294 | 105.5 | 36.5 | 436 | 113% | 73% | 106% | 118% | 6.4079 | Loss 5-10% |  | 1209(310.5) | 1280(303) | 848(114.5) | 809(31.5)
913 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM017 | TG-YAM017A-1 | DT-1 | C-BLOCK GALI NO7 BHAJAN PURA:PL | 1 | 1600 | 19502144 | 1608 | 2019-06-01 00:30 | 495 | 2096 | 452 | 1919 | 661 | 2819 | 826 | 609.5 | 99 | 6 | 0.5 | 105.5 | 100% | 69% | 67% | 91% | 15.1465 | Loss 10-20% |  |  |  | 1179(168) | 1173(317.5) | 993(76)
914 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM018 | TG-YAM018A-2 | DT-2 | K-BLOCK GHONDA:ID | 3 | 630 | 19506573 | 607 | 2019-06-16 03:00 | 233 | 937 | 213 | 856 | 161 | 647 | 259 | 684 | 24 | 3.5 |  | 27.5 | 96% | 77% | 70% | 94% | 7.067 | Loss 5-10% |  |  |  |  | 666(202) | 593(146.5)
915 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM018 | TG-YAM018A-3 | DT-3 | K-BLOCK GHONDA:ID | 3 | 630 | 19506826 | 1148.6508 | 2019-06-10 00:30 | 422.1685 | 1785.5963 | 415.9515 | 1762.1332 | 310.5307 | 1283.8744 | 490.4115 | 344.5 | 93 | 28 | 221.5 | 342.5 | 182% | 175% | 130% | 177% | 7.067 | Loss 5-10%
916 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM019 | TG-YAM019A-1 | DT-1 | DISPENSERY BHAJAN PURA:PL | 2 | 990 | 19502203 | 1465 | 2019-06-01 01:00 | 446 | 1860 | 480 | 2000 | 538 | 2239 | 332 | 188 | 265.5 | 77.5 | 174 | 517 | 148% | 114% | 116% | 139% | 7.0042 | Loss 5-10% |  |  | 1381(471) | 1346(398) | 1150(228.5) | 977(94)
917 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM019 | TG-YAM019A-2 | DT-2 | DISPENSERY BHAJAN PURA:PL | 2 | 990 | 19506331 | 1158 | 2019-06-01 01:00 | 372 | 1426 | 388 | 1499 | 398 | 1528 | 91 | 436.5 | 171.5 | 54.5 | 42.5 | 268.5 | 117% | 103% | 95% | 115% | 7.0042 | Loss 5-10% | 679(49.5) |  |  |  | 803(28)
918 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM020 | TG-YAM020A-1 | DT-1 | D-BLOCK, SANJAY MOHALLA:K | 2 | 990 | 19505851 | 908 | 2019-06-30 00:30 | 289 | 1147 | 304 | 1199 | 314 | 1251 | 90 | 559.5 | 156.5 | 1.5 |  | 158 | 92% | 72% | 80% | 90% | 6.2749 | Loss 5-10%
919 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM021 | TG-YAM021A-2 | DT-2 | NOOR-E-ILLAHI:K | 3 | 990 | 19500192 | 1344 | 2019-06-11 01:30 | 450 | 1882 | 428 | 1773 | 466 | 1943 | 149 | 22.5 | 249.5 | 187 | 259 | 695.5 | 136% | 118% | 127% | 130% | 13.0353 | Loss 10-20% | 852(148) | 1104(559.5) | 1016(485.5) | 923(381.5) | 845(221.5)
920 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM021 | TG-YAM021A-3 | DT-3 | NOOR-E-ILLAHI:K | 3 | 990 | 19502220 | 890 | 2019-06-11 02:00 | 323 | 1360 | 250 | 1033 | 317 | 1327 | 312 | 579.5 | 137 |  |  | 137 | 90% | 74% | 84% | 84% | 13.0353 | Loss 10-20% |  | 985(189.5) | 1059(606.5) | 1099(537) | 912(391) | 806(69.5)
921 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM025 | TG-YAM025A-1 | DT-1 | GHONDA CHOWK:K | 4 | 630 | 19505509 | 535 | 2019-06-29 12:00 | 173 | 703 | 184 | 753 | 178 | 731 | 43 | 686.5 | 31.5 |  |  | 31.5 | 56% | 50% | 85% | 59% | 8.7219 | Loss 5-10% | 571(164.5) | 605(210.5) | 586(161) | 612(224) | 642(109.5) | 522(28)
922 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM025 | TG-YAM025A-2 | DT-2 | GHONDA CHOWK:K | 4 | 990 | 19504714 | 865 | 2019-06-29 16:00 | 294 | 1222 | 315 | 1294 | 257 | 1060 | 208 | 566.5 | 151.5 |  |  | 151.5 | 85% | 67% | 87% | 86% | 8.7219 | Loss 5-10% |  | 957(225.5) | 930(262.5) | 911(208) | 859(130)
923 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM025 | TG-YAM025A-3 | DT-3 | GHONDA CHOWK:K | 4 | 990 | 19503250 | 983 | 2019-06-01 23:30 | 353 | 1488 | 348 | 1501 | 282 | 1187 | 308 | 364 | 331.5 | 23 |  | 354.5 | 96% | 90% | 99% | 99% | 8.7219 | Loss 5-10% |  | 934(238.5) | 966(437) | 988(386) | 893(275.5) | 810(122.5)
924 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM027 | TG-YAM027A-1 | DT-1 | CHET RAM MAUJ PUR:PL | 3 | 990 | 19502189 | 1340 | 2019-06-30 03:00 | 495 | 2107 | 382 | 1612 | 463 | 1956 | 439 | 174.5 | 297.5 | 100.5 | 137 | 535 | 135% | 119% | 118% | 133% | 13.3986 | Loss 10-20% | 906(45) |  |  |  | 1193(436) | 937(72.5)
925 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM027 | TG-YAM027A-2 | DT-2 | CHET RAM MAUJ PUR:PL | 3 | 990 | 19502235 | 1332 | 2019-06-30 03:30 | 391 | 1649 | 491 | 2100 | 451 | 1907 | 392 | 168.5 | 324.5 | 101 | 115 | 540.5 | 135% | 112% | 116% | 129% | 13.3986 | Loss 10-20% | 873(29.5) | 1108(355.5) | 1251(537.5) | 1034(39)
926 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM027 | TG-YAM027A-3 | DT-3 | CHET RAM MAUJ PUR:PL | 3 | 630 | 19505259 | 672 | 2019-06-11 01:00 | 221 | 988 | 219 | 957 | 232 | 1022 | 57 | 515 | 168.5 | 23 | 2.5 | 194 | 107% | 88% | 81% | 101% | 13.3986 | Loss 10-20%
927 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM028 | TG-YAM028A-1 | DT-1 | SUBJI MANDI-1 MAUJ PUR | 1 | 1600 | 19506745 | 1717 | 2019-06-30 01:30 | 582 | 2515 | 607 | 2592 | 528 | 2265 | 296 | 528.5 | 149 | 31.5 | 5 | 185.5 | 107% | 72% | 88% | 102% | 18.449 | Loss 10-20% | 795(31.5) | 1083(396.5) | 1349(612) |  | 1309(666.5) | 1006(392.5)
928 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM030 | TG-YAM030A-2 | DT-2 | BABU RAM CHOWK MAUJ PUR:PL | 2 | 990 | 19503728 | 761 | 2019-06-29 23:30 | 261 | 1091 | 239 | 1005 | 260 | 1099 | 91 | 679.5 | 37 |  |  | 37 | 75% | 57% | 76% | 77% | 14.7313 | Loss 10-20% |  | 752(24.5) | 804(62) | 796(45) | 791(55.5)
929 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM031 | TG-YAM031A-1 | DT-1 | SANDHYA PUBLIC SCHOOL:PL | 2 | 990 | 19504743 | 1043 | 2019-06-29 17:30 | 366 | 1657 | 347 | 1573 | 330 | 1497 | 139 | 344 | 333 | 32 | 8 | 373 | 91% | 77% | 105% | 96% | 15.8772 | Loss 10-20% |  |  |  | 995(157.5) | 866(214.5) | 768(55)
930 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM031 | TG-YAM031A-2 | DT-2 | SANDHYA PUBLIC SCHOOL:PL | 2 | 400 | 19505485 | 375 | 2019-06-03 15:00 | 79 | 326 | 128 | 536 | 167 | 701 | 326 | 584.5 | 132.5 | 1 |  | 133.5 | 90% | 79% | 94% | 92% | 15.8772 | Loss 10-20% | 489(545) | 654(738.5) | 717(669.5) | 746(547) | 361(234.5)
931 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM033 | TG-YAM033A-1 | DT-1 | SUBHASH MOHALLA NO-1:PL | 1 | 990 | 19506704 | 1213 | 2019-06-05 23:30 | 441 | 1818 | 405 | 1653 | 367 | 1495 | 280 | 261 | 304.5 | 72 | 81.5 | 458 | 120% | 86% | 99% | 123% | 9.9227 | Loss 5-10% |  |  | 986(91.5) | 1001(143.5)
932 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM034 | TG-YAM034A-1 | DT-1 | SUBHASH MOHALLA NO.-2:PL | 3 | 990 | 19500611 | 935.594 | 2019-06-01 23:00 | 311.6341 | 1272.2355 | 299.8014 | 1215.9371 | 324.1585 | 1308.621 | 80.8817 | 493 | 218 | 7 |  | 225 | 94% | 83% | 81% | 95% | 8.7048 | Loss 5-10% |  | 786(41.5) | 813(113.5) | 818(103.5)
933 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM034 | TG-YAM034A-2 | DT-2 | SUBHASH MOHALLA NO.-2:PL | 3 | 990 | 19502153 | 1036 | 2019-06-11 00:30 | 355 | 1397 | 306 | 1195 | 375 | 1484 | 257 | 382.5 | 279 | 52.5 | 4.5 | 336 | 105% | 86% | 83% | 104% | 8.7048 | Loss 5-10% |  |  | 784(75) | 769(46)
934 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM036 | TG-YAM036A-1 | DT-1 | VIJAY PARK KIOSK:K | 2 | 630 | 19505577 | 670 | 2019-06-27 00:30 | 132 | 555 | 201 | 868 | 337 | 1426 | 764 | 450.5 | 217 | 42.5 | 5.5 | 265 | 106% | 92% | 98% | 100% | 11.7499 | Loss 10-20% |  | 577(151) | 746(350) | 673(222.5) | 577(136.5)
935 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM036 | TG-YAM036A-2 | DT-2 | VIJAY PARK KIOSK:K | 2 | 990 | 19505778 | 1279 | 2019-06-30 00:30 | 498 | 2000 | 450 | 1787 | 331 | 1301 | 620 | 100 | 254 | 59.5 | 28 | 341.5 | 129% | 87% | 101% | 114% | 11.7499 | Loss 10-20% |  | 987(292.5) | 1205(507) | 1032(437) | 942(334) | 765(58)
936 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM038 | TG-YAM038A-1 | DT-1 | VIJAY PARK SHIV SADHAN MANDIR:PL | 1 | 990 | 19505446 | 1068 | 2019-06-12 | 456 | 1773 | 255 | 1014 | 356 | 1409 | 657 | 370.5 | 274 | 61 | 13.5 | 348.5 | 108% | 88% | 96% | 105% | 5.102 | Loss 5-10% |  |  | 962(137) | 1034(175) | 885(121.5)
937 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM039 | TG-YAM039A-1 | DT-1 | VIJAY PARK NEAR NURSARY:PL | 2 | 630 | 19505323 | 806 | 2019-06-29 01:30 | 278 | 1180 | 276 | 1165 | 253 | 1058 | 115 | 345.5 | 220 | 69.5 | 80.5 | 370 | 128% | 85% | 95% | 118% | 15.164 | Loss 10-20% |  | 687(153.5) | 890(293.5) | 701(247.5) | 653(212) | 517(29)
938 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM039 | TG-YAM039A-2 | DT-2 | VIJAY PARK NEAR NURSARY:PL | 2 | 400 | 19505873 | 459 | 2019-06-01 01:00 | 141 | 568 | 171 | 701 | 147 | 597 | 121 | 624.5 | 69.5 | 9 | 12.5 | 91 | 115% | 82% | 89% | 111% | 15.164 | Loss 10-20% | 389(51) | 430(161.5) | 456(286.5) | 438(367.5) | 399(292.5) | 358(44)
939 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM041 | TG-YAM041A-1 | DT-1 | NALA NO.4 MAUJPUR:PL | 2 | 990 | 19503438 | 1171 | 2019-06-12 | 376 | 1502 | 423 | 1668 | 373 | 1481 | 177 | 376 | 248.5 | 60.5 | 33.5 | 342.5 | 118% | 68% | 93% | 115% | 16.8893 | Loss 10-20% |  | 926(96.5) | 1398(406) |  | 793(50.5) | 799(26.5)
940 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM041 | TG-YAM041A-2 | DT-2 | NALA NO.4 MAUJPUR:PL | 2 | 630 | 19505866 | 719 | 2019-06-12 | 304 | 1228 | 192 | 748 | 223 | 890 | 426 | 531 | 144 | 38 | 4.5 | 186.5 | 114% | 64% | 89% | 102% | 16.8893 | Loss 10-20% |  |  |  |  | 551(36.5)
941 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM042 | TG-YAM042A-1 | DT-1 | SETH BHAGWAN DAS MAUJ PUR:PL | 1 | 990 | 19506033 | 937 | 2019-06-12 00:30 | 255 | 1028 | 396 | 1625 | 286 | 1148 | 546 | 569.5 | 146 | 3.5 |  | 149.5 | 95% | 67% | 80% | 92% | 8.6529 | Loss 5-10% |  | 906(59.5) | 1127(159.5) | 1032(100.5)
942 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM043 | TG-YAM043A-1 | DT-1 | CRESENT PUBLIC SCHOOL MAUJ PUR:PL | 2 | 990 | 19503717 | 1026 | 2019-06-30 03:30 | 336 | 1358 | 390 | 1578 | 300 | 1200 | 329 | 598.5 | 106.5 | 10.5 | 0.5 | 117.5 | 104% | 86% | 83% | 95% | 15.0808 | Loss 10-20% |  | 901(47)
943 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM043 | TG-YAM043A-2 | DT-2 | CRESENT PUBLIC SCHOOL MAUJ PUR:PL | 2 | 630 | 19506512 | 704 | 2019-06-03 | 251 | 1142 | 223 | 994 | 229 | 1041 | 132 | 393 | 241.5 | 68.5 | 13 | 323 | 112% | 96% | 93% | 109% | 15.0808 | Loss 10-20%
944 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM044 | TG-YAM044A-2 | DT-2 | ZAMALO KA BAGH MAUJ PUR:PL | 2 | 990 | 19505170 | 988 | 2019-06-02 02:00 | 322 | 1365 | 401 | 1699 | 265 | 1097 | 522 | 459 | 230 | 30 |  | 260 | 100% | 86% | 90% | 96% | 9.7778 | Loss 5-10% |  |  | 1067(380.5) | 913(326) | 858(202.5)
945 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM045 | TG-YAM045A-1 | DT-1 | VIJAY MOHALLA GALI NO 11:PL | 1 | 990 | 19503437 | 1061 | 2019-06-03 03:00 | 356 | 1487 | 347 | 1456 | 358 | 1519 | 55 | 316.5 | 336.5 | 47.5 | 18 | 402 | 107% | 96% | 88% | 93% | 8.6791 | Loss 5-10% | 913(118.5) | 1233(635) | 1357(524) | 1045(542) | 975(378.5) | 870(60)
946 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM048 | TG-YAM048A-1 | DT-1 | C- 9 YAMUNA VIHAR:PG | 1 | 990 | 19504378 | 1178 | 2019-06-11 03:30 | 351 | 1375 | 509 | 2016 | 318 | 1263 | 704 | 455.5 | 152 | 62.5 | 49 | 263.5 | 119% | 86% | 81% | 115% | 6.4358 | Loss 5-10% | 854(28.5) | 1086(162.5) | 962(148) | 959(86) | 819(63.5)
947 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM053 | TG-YAM053A-1 | DT-1 | MOHANPURI NO-2 OUTSIDE SCHOOL | 2 | 630 | 19504374 | 773 | 2019-06-11 | 254 | 1115 | 289 | 1276 | 231 | 1020 | 225 | 246 | 358 | 64.5 | 51 | 473.5 | 123% | 83% | 97% | 114% | 9.2308 | Loss 5-10% |  | 622(299.5) | 661(294.5) | 632(163) | 611(262) | 513(37.5)
948 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM054 | TG-YAM054A-1 | DT-1 | SUBHASH MOHALLA NO.-3:PL | 2 | 990 | 19502226 | 871 | 2019-06-30 23:00 | 308 | 1241 | 297 | 1199 | 266 | 1076 | 149 | 595 | 123 |  |  | 123 | 88% | 71% | 73% | 88% | 9.0717 | Loss 5-10% |  |  | 776(55.5) | 792(29.5)
949 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM060 | TG-YAM060A-1 | DT-1 | C-1, YVR NEAR ANAND SAGAR | 1 | 630 | 19506311 | 710 | 2019-06-14 11:30 | 237 | 972 | 227 | 928 | 246 | 1002 | 64 | 467.5 | 127 | 91.5 | 34 | 252.5 | 73% | 63% | 113% | 76% | 4.5252 | Loss 0-5% |  | 540(54) | 683(249) | 649(212.5) | 591(89)
950 | 1250 | YVR | GHONDA | GHO001 | TG-GHO001A-1 | DT-1 | A BLOCK BHAJANPURA GALI NO. -3:PL | 1 | 990 | 19504886 | 898 | 2019-06-30 00:30 | 287 | 1205 | 356 | 1499 | 254 | 1059 | 388 | 609 | 110 | 0.5 |  | 110.5 | 91% | 53% | 61% | 90% | 6.372 | Loss 5-10% |  | 896(80.5) | 987(180.5) | 948(111.5) | 823(69.5)
951 | 1250 | YVR | GHONDA | GHO002 | TG-GHO002A-1 | DT-1 | B BLOCK BHAJANPURA:K | 3 | 990 | 19501767 | 1101 | 2019-06-08 14:00 | 356 | 1492 | 372 | 1589 | 373 | 1583 | 94 | 405 | 149 | 44 | 12.5 | 205.5 | 106% | 81% | 111% | 111% | 11.4238 | Loss 10-20% | 823(24) | 1133(194.5) | 1202(426.5) | 964(216.5) | 902(111)
952 | 1250 | YVR | GHONDA | GHO002 | TG-GHO002A-2 | DT-2 | B BLOCK BHAJANPURA:K | 3 | 990 | 19506334 | 1265.9065 | 2019-06-29 23:00 | 445.525 | 1989.6617 | 405.0761 | 1791.5796 | 415.3053 | 1848.2655 | 176.6956 | 372 | 236 | 54 | 42 | 332 | 120% | 99% | 122% | 128% | 11.4238 | Loss 10-20% |  |  |  | 868(34) | 956(45.5)
953 | 1250 | YVR | GHONDA | GHO002 | TG-GHO002A-3 | DT-3 | B BLOCK BHAJANPURA:K | 3 | 990 | 19504179 | 1251 | 2019-06-02 23:30 | 421 | 1821 | 413 | 1779 | 417 | 1802 | 36 | 515.5 | 152.5 | 18.5 | 18.5 | 189.5 | 126% | 81% | 98% | 126% | 11.4238 | Loss 10-20% |  | 1010(163) | 1242(403.5) | 1059(237.5) | 1019(187)
954 | 1250 | YVR | GHONDA | GHO003 | TG-GHO003A-1 | DT-1 | D BLOCK BHAJANPURA:K | 3 | 990 | 19503712 | 1020 | 2019-06-29 23:30 | 360 | 1530 | 318 | 1355 | 343 | 1447 | 152 | 531.5 | 144.5 | 39.5 | 4.5 | 188.5 | 102% | 73% | 74% | 103% | 19.5469 | Loss 10-20% |  |  | 1439(632.5) | 1431(434.5)
955 | 1250 | YVR | GHONDA | GHO003 | TG-GHO003A-2 | DT-2 | D BLOCK BHAJANPURA:K | 3 | 990 | 19504884 | 1023 | 2019-06-29 23:30 | 328 | 1397 | 382 | 1640 | 313 | 1321 | 289 | 525 | 183 | 10.5 | 1 | 194.5 | 102% | 72% | 79% | 103% | 19.5469 | Loss 10-20% |  |  |  |  | 878(85.5) | 843(102.5)
956 | 1250 | YVR | GHONDA | GHO003 | TG-GHO003A-3 | DT-3 | D BLOCK BHAJANPURA:K | 3 | 990 | 19501785 | 1020 | 2019-06-30 02:00 | 324 | 1366 | 342 | 1443 | 354 | 1492 | 110 | 562.5 | 151.5 | 5 | 0.5 | 157 | 103% | 85% | 74% | 78% | 19.5469 | Loss 10-20% | 819(84.5) | 960(339) | 813(51) | 794(34.5) | 896(128.5) | 874(67.5)
957 | 1250 | YVR | GHONDA | GHO006 | TG-GHO006A-2 | DT-2 | SOUTH GAMRI KIOSK:K | 2 | 990 | 19505655 | 898 | 2019-06-29 23:00 | 291 | 1259 | 270 | 1175 | 337 | 1474 | 267 | 576.5 | 142 | 1.5 |  | 143.5 | 88% | 71% | 88% | 91% | 11.8158 | Loss 10-20% |  |  | 910(58) | 1140(173.5) | 880(134)
958 | 1250 | YVR | GHONDA | GHO007 | TG-GHO007A-1 | DT-1 | GAMRHI VILLAGE:PL | 2 | 630 | 19502639 | 599 | 2019-06-30 00:30 | 196 | 830 | 176 | 747 | 228 | 965 | 191 | 639 | 70.5 | 5.5 |  | 76 | 95% | 75% | 73% | 93% | 33.7815 | Loss >30% |  | 533(59) | 598(128.5) | 517(39.5)
959 | 1250 | YVR | GHONDA | GHO007 | TG-GHO007A-2 | DT-2 | GAMRHI VILLAGE:PL | 2 | 990 | 19506047 | 922 | 2019-06-01 | 296 | 1295 | 306 | 1331 | 320 | 1390 | 83 | 471.5 | 242.5 | 4 |  | 246.5 | 93% | 77% | 86% | 94% | 33.7815 | Loss >30% | 760(33) | 918(225) | 978(483) | 960(434.5) | 921(309.5) | 851(142.5)
960 | 1250 | YVR | GHONDA | GHO008 | TG-GHO008A-1 | DT-1 | GAMRI KIOSK:K | 1 | 1600 | 19506830 | 1217 | 2019-06-11 23:30 | 362 | 1489 | 394 | 1645 | 462 | 1918 | 376 | 687.5 | 31.5 |  |  | 31.5 | 76% | 72% | 67% | 76% | 23.4899 | Loss 20-30% | 974(430.5) | 1253(694) | 1367(645)
961 | 1250 | YVR | GHONDA | GHO009 | TG-GHO009A-1 | DT-1 | ARVIND NAGAR PRIMARY SCHOOL GAUTAM VIHAR:PL | 3 | 990 | 19506005 | 969 | 2019-06-12 | 366 | 1489 | 289 | 1173 | 314 | 1268 | 281 | 551.5 | 154.5 | 11 |  | 165.5 | 98% | 75% | 74% | 97% | 24.6905 | Loss 20-30%
962 | 1250 | YVR | GHONDA | GHO010 | TG-GHO010A-1 | DT-1 | GAUTAM VIHAR KIOSK:K | 2 | 990 | 19501769 | 1072 | 2019-06-10 23:30 | 305 | 1214 | 350 | 1412 | 417 | 1680 | 405 | 130 | 444.5 | 113.5 | 30.5 | 588.5 | 107% | 92% | 97% | 108% | 13.4553 | Loss 10-20% | 825(58) | 1060(480) | 1163(620) | 1033(575.5) | 975(325) | 838(131.5)
963 | 1250 | YVR | GHONDA | GHO010 | TG-GHO010A-2 | DT-2 | GAUTAM VIHAR KIOSK:K | 2 | 990 | 19505118 | 871 | 2019-06-09 23:30 | 289 | 1172 | 292 | 1181 | 289 | 1169 | 11 | 558.5 | 160 |  |  | 160 | 87% | 78% | 74% | 88% | 13.4553 | Loss 10-20% | 820(51) | 1079(371.5) | 1100(414.5) | 804(100.5) | 752(36)
964 | 1250 | YVR | GHONDA | GHO011 | TG-GHO011A-1 | DT-1 | JAI PRAKASH NO-1:PL | 1 | 990 | 19501819 | 957 | 2019-06-29 23:30 | 326 | 1438 | 332 | 1478 | 299 | 1325 | 137 | 572.5 | 140.5 | 5 |  | 145.5 | 92% | 69% | 75% | 97% | 6.0258 | Loss 5-10% |  | 978(213.5) | 1101(574.5) | 1023(540.5) | 1045(422) | 810(99)
965 | 1250 | YVR | GHONDA | GHO012 | TG-GHO012A-1 | DT-1 | JAI PRAKASH NO-2:PL | 1 | 990 | 19506116 | 1043 | 2019-06-29 23:30 | 283 | 1262 | 389 | 1749 | 371 | 1671 | 452 | 293 | 366.5 | 51.5 | 7 | 425 | 102% | 80% | 84% | 105% | 12.1486 | Loss 10-20% |  |  | 767(25) | 788(41.5)
966 | 1250 | YVR | GHONDA | GHO013 | TG-GHO013A-1 | DT-1 | KARTAR NAGAR HOTEL WALA:PL | 1 | 990 | 19501723 | 1116 | 2019-06-10 23:30 | 378 | 1634 | 344 | 1471 | 394 | 1711 | 213 | 211 | 384.5 | 73 | 51 | 508.5 | 109% | 83% | 93% | 113% | 20.0801 | Loss 20-30% |  |  | 1266(665) | 1335(665) | 1229(598.5) | 1056(412)
967 | 1250 | YVR | GHONDA | GHO014 | TG-GHO014A-1 | DT-1 | 3.5 PUSTA KARTAR NAGAR:K | 2 | 630 | 19505486 | 700 | 2019-06-29 23:30 | 219 | 922 | 230 | 968 | 251 | 1063 | 125 | 124 | 91.5 | 19.5 | 12.5 | 123.5 | 109% | 81% | 92% | 111% | 5.3389 | Loss 5-10% | [5 empty] | 612(62.5)
968 | 1250 | YVR | GHONDA | GHO014 | TG-GHO014A-2 | DT-2 | 3.5 PUSTA KARTAR NAGAR:K | 2 | 630 | 19504173 | 555 | 2019-06-29 23:30 | 175 | 737 | 206 | 878 | 174 | 734 | 142 | 651.5 | 63 |  |  | 63 | 85% | 68% | 75% | 88% | 5.3389 | Loss 5-10%
969 | 1250 | YVR | GHONDA | GHO015 | TG-GHO015A-1 | DT-1 | JAGJEET NAGAR KIOSK:K | 3 | 990 | 19506721 | 1021 | 2019-06-29 23:30 | 360 | 1465 | 312 | 1264 | 349 | 1420 | 183 | 412 | 259 | 40.5 | 4 | 303.5 | 103% | 96% | 94% | 103% | 5.4038 | Loss 5-10% | 1077(496) | 1358(566.5) | 1480(654) | 1111(542.5) | 1027(446) | 1069(118)
970 | 1250 | YVR | GHONDA | GHO015 | TG-GHO015A-2 | DT-2 | JAGJEET NAGAR KIOSK:K | 3 | 990 | 19506046 | 1237 | 2019-06-01 07:30 | 368 | 1510 | 414 | 1693 | 456 | 1879 | 320 | 159 | 390 | 110 | 59.5 | 559.5 | 120% | 125% | 108% | 120% | 5.4038 | Loss 5-10% | 853(80.5) | 1168(215.5)
971 | 1250 | YVR | GHONDA | GHO015 | TG-GHO015A-3 | DT-3 | JAGJEET NAGAR KIOSK:K | 3 | 990 | 19506495 | 927 | 2019-06-06 00:30 | 316 | 1396 | 289 | 1283 | 322 | 1437 | 138 | 579 | 135 | 1.5 |  | 136.5 | 94% | 68% | 79% | 91% | 5.4038 | Loss 5-10%
972 | 1250 | YVR | GHONDA | GHO016 | TG-GHO016A-1 | DT-1 | 3 RD JAGJEET NAGAR :PL | 1 | 990 | 19506707 | 904 | 2019-06-25 18:30 | 290 | 1222 | 248 | 1029 | 365 | 1554 | 460 | 614 | 100.5 | 0.5 |  | 101 | 88% | 77% | 91% | 87% | 7.2109 | Loss 5-10%
973 | 1250 | YVR | GHONDA | GHO017 | TG-GHO017A-1 | DT-1 | VIJAY COLONY:PL | 1 | 990 | 19505799 | 1398 | 2019-06-30 | 511 | 2325 | 481 | 2251 | 406 | 1841 | 452 | 549 | 163 | 5 | 2 | 170 | 141% | 83% | 83% | 101% | 7.8147 | Loss 5-10%
974 | 1250 | YVR | GHONDA | GHO018 | TG-GHO018A-1 | DT-1 | USMANPUR PUSTA NO-2:PL | 2 | 630 | 19506644 | 544 | 2019-06-15 16:00 | 127 | 535 | 291 | 1198 | 126 | 524 | 669 | 563.5 | 153 |  |  | 153 | 83% | 65% | 86% | 85% | 24.4679 | Loss 20-30% |  | 546(151) | 538(89.5) | 541(268.5)
975 | 1250 | YVR | GHONDA | GHO018 | TG-GHO018A-2 | DT-2 | USMANPUR PUSTA NO-2:PL | 2 | 630 | 19504176 | 546 | 2019-06-27 23:30 | 153 | 668 | 138 | 605 | 255 | 1121 | 488 | 604 | 113.5 |  |  | 113.5 | 84% | 68% | 75% | 87% | 24.4679 | Loss 20-30% |  |  | 484(27)
976 | 1250 | YVR | GHONDA | GHO019 | TG-GHO019A-1 | DT-1 | KHADDEY WALI MASJID:PM | 1 | 630 | 19506336 | 935 | 2019-06-22 01:30 | 315 | 1341 | 340 | 1456 | 279 | 1189 | 233 | 20.5 | 197 | 166 | 335 | 698 | 148% | 120% | 144% | 147% | 10.1807 | Loss 10-20% | [5 empty] | 792(363)
977 | 1250 | YVR | GHONDA | GHO020 | TG-GHO020A-1 | DT-1 | MONI BABA MANDIR:K | 3 | 990 | 19504129 | 1086 | 2019-06-30 23:30 | 419 | 1906 | 309 | 1379 | 358 | 1613 | 457 | 354 | 258 | 80 | 27.5 | 365.5 | 107% | 89% | 91% | 110% | 7.6924 | Loss 5-10% |  |  |  |  | 1044(49) | 941(70)
978 | 1250 | YVR | GHONDA | GHO020 | TG-GHO020A-2 | DT-2 | MONI BABA MANDIR:K | 3 | 630 | 19500582 | 836.1671 | 2019-06-29 23:30 | 213.0083 | 893.0792 | 318.2256 | 1360.4617 | 304.9332 | 1288.4318 | 435.8546 | 183.5 | 310.5 | 84 | 140.5 | 535 | 133% | 94% | 99% | 133% | 7.6924 | Loss 5-10% |  | 929(125.5) | 1450(458) | 897(706) | 822(691.5) | 729(367)
979 | 1250 | YVR | GHONDA | GHO020 | TG-GHO020A-3 | DT-3 | MONI BABA MANDIR:K | 3 | 990 | 19506337 | 1022.5369 | 2019-06-29 23:00 | 311.7354 | 1382.0507 | 393.8928 | 1799.9124 | 316.9087 | 1422.8382 | 399.0345 | 516 | 159.5 | 41 | 2.5 | 203 | 100% | 75% | 81% | 103% | 7.6924 | Loss 5-10% |  | 590(36) | 527(26.5)
980 | 1250 | YVR | GHONDA | GHO021 | TG-GHO021A-1 | DT-1 | R BLOCK BRAHAMPURI:PL | 1 | 990 | 19505894 | 861 | 2019-06-11 00:30 | 217 | 924 | 372 | 1619 | 272 | 1153 | 614 | 562.5 | 155.5 |  |  | 155.5 | 87% | 85% | 86% | 85% | 10.9312 | Loss 10-20%
981 | 1250 | YVR | GHONDA | GHO023 | TG-GHO023A-1 | DT-1 | BRAMPURI NO-6 NEAR MANDIR:PL | 1 | 990 | 19502174 | 942 | 2019-06-03 | 314 | 1328 | 302 | 1270 | 327 | 1367 | 84 | 337 | 368.5 | 14.5 |  | 383 | 95% | 80% | 88% | 95% | 26.7926 | Loss 20-30% | 910(355) | 924(350) | 983(500.5) | 947(471) | 902(392) | 846(148)
982 | 1250 | YVR | GHONDA | GHO024 | TG-GHO024A-1 | DT-1 | X BL BRAHAMPURI RAMNIWAS WALA:PL | 3 | 990 | 19506904 | 943 | 2019-06-09 23:30 | 383 | 1674 | 291 | 1269 | 268 | 1149 | 476 | 478.5 | 230.5 | 9.5 |  | 240 | 92% | 89% | 83% | 95% | 10.1778 | Loss 10-20% |  | 821(53) | 1021(158) | 856(95.5) | 821(84)
983 | 1250 | YVR | GHONDA | GHO025 | TG-GHO025A-1 | DT-1 | X BL BRAHAMPURI KHATTEY WALA:PL | 2 | 990 | 19503713 | 896 | 2019-06-29 22:30 | 330 | 1467 | 269 | 1198 | 297 | 1304 | 234 | 482 | 79 | 0.5 |  | 79.5 | 85% | 64% | 79% | 90% | 16.5691 | Loss 10-20%
984 | 1250 | YVR | GHONDA | GHO026 | TG-GHO026A-1 | DT-1 | X BL BRAHAMPURI BHISHAM WALA:PL | 1 | 990 | 19504986 | 963 | 2019-06-29 23:00 | 299 | 1198 | 324 | 1352 | 340 | 1412 | 191 | 531 | 177 | 10.5 |  | 187.5 | 94% | 71% | 76% | 97% | 4.6979 | Loss 0-5% |  | 818(50) | 893(153.5) | 884(130) | 875(68)
985 | 1250 | YVR | GHONDA | GHO035 | TG-GHO035A-1 | DT-1 | BALLU KA TUBEWELL | 1 | 990 | 19504732 | 875 | 2019-06-29 23:00 | 269 | 1179 | 332 | 1465 | 274 | 1212 | 272 | 595 | 123.5 |  |  | 123.5 | 87% | 73% | 72% | 88% | 15.9877 | Loss 10-20% |  |  | 854(96) | 791(55) | 777(32)
986 | 1250 | YVR | GHONDA | GHO038 | TG-GHO038A-1 | DT-1 | MAIN BRAHMPURI RD GALI NO.7:PM | 1 | 990 | 19504532 | 932 | 2019-06-03 00:30 | 208 | 870 | 367 | 1549 | 357 | 1522 | 666 | 515 | 191 | 12.5 |  | 203.5 | 94% | 77% | 80% | 92% | 15.0867 | Loss 10-20% |  | 1010(219) | 1003(389) | 987(391.5) | 987(221.5) | 812(89)
987 | 1250 | YVR | GHONDA | GHO040 | TG-GHO040A-1 | DT-1 | MAIN BRAHMPURI RD GALI NO.19:PM | 1 | 630 | 19506050 | 774 | 2019-06-30 01:30 | 239 | 1016 | 244 | 1032 | 291 | 1243 | 219 | 151 | 409 | 111 | 48 | 568 | 123% | 103% | 108% | 112% | 5.9512 | Loss 5-10% | 680(349.5) | 834(706) | 887(713.5) | 817(732.5) | 777(741)
988 | 1250 | YVR | GHONDA | GHO041 | TG-GHO041A-1 | DT-1 | MAIN BRAHMPURI RD GALI NO. 24 | 1 | 400 | 19505946 | 317 | 2019-06-01 17:00 | 125 | 516 | 93 | 403 | 99 | 428 | 103 | 682 | 37.5 |  |  | 37.5 | 74% | 72% | 79% | 70% | 6.1509 | Loss 5-10% |  | 315(25.5) | 339(64.5) | 320(89.5)
989 | 1250 | YVR | GHONDA | GHO042 | TG-GHO042A-1 | DT-1 | MAIN BRAHMPURI RD GALI NO. 23:PM | 1 | 990 | 19505995 | 1071 | 2019-06-26 02:00 | 362 | 1477 | 390 | 1583 | 320 | 1304 | 244 | 239 | 372 | 85.5 | 16 | 473.5 | 108% | 100% | 104% | 104% | 16.1339 | Loss 10-20% | 604(92) | 916(353.5) | 932(326.5) | 930(406)
990 | 1250 | YVR | GHONDA | GHO054 | TG-GHO054A-2 | DT-2 | D-BLOCK GAMRI EXTR S/ST | 2 | 630 | 19505777 | 642 | 2019-06-30 06:30 | 130 | 517 | 274 | 1104 | 237 | 979 | 536 | 493.5 | 212 | 10 | 1 | 223 | 101% | 102% | 91% | 98% | 39.99 | Loss >30% | [5 empty] | 504(30)
991 | 1250 | YVR | GHONDA | GHO056 | TG-GHO056A-1 | DT-1 | A BLOCK BHAJANPURA GALI NO. -2:P/M | 1 | 630 | 19506048 | 662 | 2019-06-30 14:30 | 306 | 1429 | 136 | 611 | 220 | 971 | 710 | 593.5 | 119 | 4.5 | 2.5 | 126 | 102% | 62% | 105% | 103% | 10.8644 | Loss 10-20% |  |  | 681(100.5) | 716(36)
992 | 1250 | YVR | GHONDA | YAM032 | TG-YAM032A-2 | DT-2 | GAMRI ROAD PUMP HOUSE:PL | 2 | 990 | 19505820 | 949 | 2019-06-12 12:00 | 361 | 1458 | 347 | 1419 | 242 | 958 | 482 | 611 | 108 | 1 |  | 109 | 74% | 74% | 96% | 80% | 44.8804 | Loss >30%
993 | 1250 | YVR | NEW SEELAMPUR | SLM010 | TG-SLM010A-1 | DT-1 | RISHI KARDOM MARG:PL | 1 | 990 | 19503434 | 778 | 2019-06-30 | 188 | 803 | 361 | 1561 | 229 | 962 | 692 | 691 | 28 |  |  | 28 | 79% | 69% | 72% | 78% | 18.7756 | Loss 10-20% |  | 843(91.5) | 861(207.5)
994 | 1250 | YVR | NEW SEELAMPUR | SLM011 | TG-SLM011A-1 | DT-1 | BRAHMPURI NO-I:PL | 2 | 990 | 19506454 | 881 | 2019-06-26 18:00 | 332 | 1363 | 298 | 1203 | 251 | 1024 | 293 | 448.5 | 148.5 |  |  | 148.5 | 82% | 73% | 89% | 80% | 31.8886 | Loss >30% |  |  |  | 1184(169) | 991(220) | 827(62.5)
995 | 1250 | YVR | NEW SEELAMPUR | SLM013 | TG-SLM013A-1 | DT-1 | OUTSIDE KOTHI ZAFRABAD:PL | 2 | 990 | 19502308 | 821 | 2019-06-30 03:00 | 213 | 852 | 307 | 1229 | 301 | 1194 | 361 | 681.5 | 37 |  |  | 37 | 83% | 72% | 74% | 80% | 16.6384 | Loss 10-20% |  | 836(115.5) | 883(218) | 839(195) | 831(131.5)
996 | 1250 | YVR | NEW SEELAMPUR | SLM014 | TG-SLM014A-2 | DT-2 | INSIDE KOTHI ZAFRABAD:PL | 2 | 990 | 19503729 | 882 | 2019-06-30 00:30 | 320 | 1321 | 246 | 1009 | 316 | 1310 | 307 | 606 | 114 |  |  | 114 | 89% | 76% | 79% | 86% | 33.7557 | Loss >30% |  | 871(152.5) | 921(311.5) | 848(209) | 801(141.5)
997 | 1250 | YVR | NEW SEELAMPUR | SLM015 | TG-SLM015A-1 | DT-1 | KHATTA ROAD NO 66 ZAFRABAD:PL | 2 | 990 | 19505169 | 847 | 2019-06-30 | 249 | 1004 | 299 | 1191 | 299 | 1194 | 188 | 265 | 59.5 |  |  | 59.5 | 86% | 78% | 78% | 84% | 49.9148 | Loss >30% |  |  | 1137(46.5) | 884(215.5) | 892(168) | 767(37)
998 | 1250 | YVR | NEW SEELAMPUR | SLM015 | TG-SLM015A-2 | DT-2 | KHATTA ROAD NO 66 ZAFRABAD:PL | 2 | 990 | 19506711 | 983 | 2019-06-29 23:30 | 335 | 1329 | 323 | 1282 | 325 | 1315 | 42 | 495.5 | 208 | 15.5 |  | 223.5 | 98% | 87% | 92% | 99% | 49.9148 | Loss >30% | 988(254.5) | 1027(165.5) | 895(32.5) | 1033(394) | 1165(484.5) | 1023(325)
999 | 1250 | YVR | NEW SEELAMPUR | SLM016 | TG-SLM016A-1 | DT-1 | OUTSIDE SCHOOL ZAFRABAD:PL | 2 | 990 | 19505290 | 775 | 2019-06-03 01:00 | 254 | 1081 | 221 | 931 | 301 | 1306 | 327 | 683 | 36 |  |  | 36 | 78% | 67% | 75% | 75% | 27.0774 | Loss 20-30% |  |  |  |  | 901(192.5) | 928(189)
1000 | 1250 | YVR | NEW SEELAMPUR | SLM017 | TG-SLM017A-2 | DT-2 | NALA NO 1 SEELAMPUR:PL | 3 | 990 | 19505652 | 787 | 2019-06-29 23:30 | 285 | 1279 | 229 | 1019 | 273 | 1219 | 236 | 665 | 52 |  |  | 52 | 79% | 68% | 76% | 80% | 38.2424 | Loss >30% |  | 940(226.5) | 981(309) | 819(201) | 812(157)
1001 | 1250 | YVR | NEW SEELAMPUR | SLM018 | TG-SLM018A-1 | DT-1 | SBI WELCOME:ID | 3 | 990 | 19506718 | 917 | 2019-06-01 23:00 | 310 | 1253 | 291 | 1167 | 316 | 1257 | 88 | 507.5 | 205.5 | 3 |  | 208.5 | 90% | 86% | 92% | 93% | 12.0079 | Loss 10-20% |  |  |  |  | 963(103) | 919(34)
1002 | 1250 | YVR | NEW SEELAMPUR | SLM019 | TG-SLM019A-2 | DT-2 | PHOTO CHOCK WELCOME:PL | 3 | 990 | 19505086 | 1005 | 2019-06-30 00:30 | 327 | 1403 | 319 | 1359 | 360 | 1532 | 156 | 600 | 113 | 2 | 0.5 | 115.5 | 102% | 78% | 81% | 89% | 32.3349 | Loss >30% |  | 880(186.5) | 947(181.5) | 885(147.5) | 851(86.5)
1003 | 1250 | YVR | NEW SEELAMPUR | SLM020 | TG-SLM020A-2 | DT-2 | Z-2 BLOCK WELCOME:PL | 2 | 990 | 19500583 | 916 | 2019-06-01 00:30 | 298 | 1284 | 276 | 1184 | 342 | 1476 | 257 | 649 | 69.5 | 1 |  | 70.5 | 93% | 76% | 76% | 84% | 12.6212 | Loss 10-20% |  | 823(76) | 849(123.5) | 820(94) | 812(33.5)
1004 | 1250 | YVR | NEW SEELAMPUR | SLM021 | TG-SLM021A-2 | DT-2 | KABOOTER MARKET WELCOME:ID | 3 | 990 | 19500609 | 1084 | 2019-06-03 01:30 | 397 | 1701 | 272 | 1148 | 415 | 1797 | 607 | 370.5 | 300.5 | 37 | 12 | 349.5 | 109% | 98% | 100% | 104% | 21.5762 | Loss 20-30% |  |  |  |  | 931(31.5)
1005 | 1250 | YVR | NEW SEELAMPUR | SLM044 | TG-SLM044A-3 | DT-3 | CHAUHAN BANGAR GALI NO 10:PL | 5 | 990 | 19502234 | 864 | 2019-06-02 00:30 | 314 | 1401 | 233 | 1019 | 317 | 1351 | 360 | 388.5 | 78 |  |  | 78 | 87% | 77% | 80% | 86% | 33.6837 | Loss >30% |  | 880(231.5) | 948(289) | 847(253) | 889(193) | 784(55.5)
1006 | 1250 | YVR | NEW SEELAMPUR | SLM056 | TG-SLM056A-1 | DT-1 | OPP MAZAR BRAHMPURI ROAD:PM | 1 | 400 | 19506254 | 409 | 2019-06-30 03:30 | 128 | 546 | 146 | 629 | 135 | 585 | 72 | 450 | 258.5 | 10 | 1 | 269.5 | 102% | 84% | 91% | 98% | 34.6216 | Loss >30%
1007 | 1250 | YVR | NEW SEELAMPUR | SLM057 | TG-SLM057A-1 | DT-1 | CHAUHAN BANGAR GALI NO 5:PL | 2 | 990 | 19505374 | 967 | 2019-06-01 00:30 | 283 | 1193 | 352 | 1517 | 332 | 1429 | 290 | 508 | 202.5 | 7 |  | 209.5 | 98% | 81% | 85% | 94% | 28.7906 | Loss 20-30% |  | 951(229.5) | 1140(349) | 1078(297.5) | 834(213) | 816(46)
1008 | 1250 | YVR | NEW SEELAMPUR | SLM060 | TG-SLM060A-1 | DT-1 | JANTA COLONY NO-2 | 1 | 400 | 19506052 | 342 | 2019-06-01 03:00 | 104 | 416 | 99 | 405 | 139 | 555 | 144 | 659.5 | 60.5 |  |  | 60.5 | 86% | 74% | 85% | 80% | 35.0115 | Loss >30% | 384(59) | 354(78) |  |  |  | 381(117.5)
1009 | 1250 | YVR | NEW SEELAMPUR | SLM061 | TG-SLM061A-1 | DT-1 | JANTA COLONY NO-3 | 1 | 630 | 19505809 | 591 | 2019-06-02 18:30 | 225 | 912 | 185 | 759 | 181 | 743 | 162 | 688 | 28.5 | 0.5 |  | 29 | 76% | 70% | 94% | 77% | 38.4575 | Loss >30%
1010 | 1250 | YVR | NEW SEELAMPUR | SLM073 | TG-SLM073A-1 | DT-1 | ARORA BLDG GALI-24 CHAUHAN | 1 | 630 | 19506061 | 534 | 2019-06-30 03:30 | 169 | 660 | 197 | 780 | 168 | 665 | 117 | 666 | 53 |  |  | 53 | 85% | 71% | 74% | 78% | 35.7816 | Loss >30% |  | 546(156) | 769(310.5) | 547(202) | 549(116)
1011 | 1250 | YVR | SHASTRI PARK | SLM001 | TG-SLM001A-1 | DT-1 | USMAN PUR KIOSK:K | 2 | 990 | 19502886 | 935 | 2019-06-27 23:00 | 314 | 1340 | 293 | 1248 | 327 | 1402 | 134 | 482.5 | 232.5 | 1.5 |  | 234 | 88% | 72% | 81% | 94% | 15.2261 | Loss 10-20% |  | 748(25.5) | 785(68) | 790(60.5) | 787(46)
1012 | 1250 | YVR | SHASTRI PARK | SLM001 | TG-SLM001A-2 | DT-2 | USMAN PUR KIOSK:K | 2 | 630 | 19506418 | 751 | 2019-06-14 | 209 | 911 | 269 | 1189 | 272 | 1188 | 277 | 420.5 | 197 | 53.5 | 45.5 | 296 | 119% | 80% | 94% | 116% | 15.2261 | Loss 10-20% | 638(65.5) | 823(448) | 853(659.5) | 822(667) | 767(631.5) | 635(247)
1013 | 1250 | YVR | SHASTRI PARK | SLM005 | TG-SLM005A-1 | DT-1 | GAUTAM PURI NO.1:PL | 1 | 990 | 19506608 | 1018 | 2019-06-03 14:30 | 309 | 1299 | 353 | 1465 | 356 | 1501 | 186 | 359 | 326 | 32 | 3 | 361 | 101% | 87% | 103% | 101% | 5.1853 | Loss 5-10% |  | 918(210.5) | 960(439.5) |  |  | 968(37.5)
1014 | 1250 | YVR | SHASTRI PARK | SLM007 | TG-SLM007A-1 | DT-1 | BHAGAT SINGH MOHALLA:PL | 1 | 990 | 19504172 | 858 | 2019-06-30 23:00 | 281 | 1231 | 282 | 1241 | 295 | 1294 | 59 | 614 | 103 |  |  | 103 | 85% | 58% | 70% | 87% | 5.5783 | Loss 5-10% |  | 811(34.5) | 856(100.5) | 832(48.5)
1015 | 1250 | YVR | SHASTRI PARK | SLM027 | TG-SLM027A-1 | DT-1 | H BLOCK SEELAMPUR:PL | 2 | 990 | 19505107 | 764 | 2019-06-29 23:30 | 278 | 1160 | 229 | 948 | 258 | 1089 | 187 | 686.5 | 33.5 |  |  | 33.5 | 77% | 65% | 66% | 77% | 17.9051 | Loss 10-20% |  |  | 849(43.5)
1016 | 1250 | YVR | SHASTRI PARK | SLM034 | TG-SLM034A-1 | DT-1 | RAJU WALA SHASTRI PARK:PL | 1 | 990 | 19505879 | 803 | 2019-06-29 23:30 | 260 | 1123 | 304 | 1294 | 239 | 1033 | 230 | 666 | 53 |  |  | 53 | 79% | 70% | 69% | 81% | 7.9029 | Loss 5-10% |  |  | 1062(48) | 784(29)
1017 | 1250 | YVR | SHASTRI PARK | SLM086 | TG-SLM086A-2 | DT-2 | ENGG COLL GAUTAM PUR NO-3:PL | 2 | 630 | 19505880 | 487 | 2019-06-29 23:30 | 165 | 713 | 160 | 689 | 162 | 693 | 22 | 679 | 41 |  |  | 41 | 77% | 59% | 72% | 77% | 4.4451 | Loss 0-5%
1018 | 1251 | KWR | GOKUL PURI | KWL001 | TG-KWL001A-1 | DT-1 | RAJEEV GANDHI NAGAR GALI NO.-3:ID | 2 | 630 | 19506907 | 664 | 2019-06-10 21:30 | 206 | 824 | 234 | 963 | 224 | 916 | 122 | 591 | 118.5 | 6 | 2 | 126.5 | 104% | 83% | 103% | 105% | 11.8949 | Loss 10-20%
1019 | 1251 | KWR | GOKUL PURI | KWL003 | TG-KWL003A-2 | DT-2 | RAJEEV GANDHI NAGAR GALI NO.-15:ID | 2 | 990 | 19504934 | 882.7997 | 2019-06-01 23:30 | 329.2282 | 1360.672 | 235.1079 | 956.2287 | 318.4636 | 1317.435 | 384.6517 | 37 | 107 |  |  | 107 | 88% | 79% | 85% | 89% | 7.8682 | Loss 5-10% |  | 833(125.5) | 872(325) | 849(190.5) | 801(92.5)
1020 | 1251 | KWR | GOKUL PURI | KWL004 | TG-KWL004A-1 | DT-1 | RAJEEV GANDHI NAGAR GALI NO.-21:ID | 2 | 990 | 19504064 | 784 | 2019-06-30 | 243 | 969 | 240 | 956 | 300 | 1208 | 245 | 655 | 64.5 |  |  | 64.5 | 79% | 74% | 74% | 79% | 6.7925 | Loss 5-10%
1021 | 1251 | KWR | GOKUL PURI | KWL005 | TG-KWL005A-1 | DT-1 | D BLOCK BHAGRATHI VIHAR:PL | 2 | 630 | 19500546 | 545 | 2019-06-02 08:00 | 154 | 628 | 203 | 823 | 188 | 768 | 174 | 619.5 | 99.5 |  |  | 99.5 | 84% | 87% | 71% | 82% | 7.9448 | Loss 5-10% |  | 538(24.5) | 613(56.5) | 498(42.5) | 493(25.5)
1022 | 1251 | KWR | GOKUL PURI | KWL014 | TG-KWL014A-1 | DT-1 | D BL BRIJPURI GALI NO. 10:ID | 1 | 630 | 19500566 | 529 | 2019-06-29 23:00 | 211 | 852 | 188 | 738 | 131 | 525 | 288 | 670 | 50 |  |  | 50 | 83% | 70% | 70% | 84% | 5.751 | Loss 5-10% |  |  | 500(48.5) | 495(37.5)
1023 | 1251 | KWR | GOKUL PURI | KWL019 | TG-KWL019A-1 | DT-1 | A BLK G N 2 BHAGIRATHI VIHAR NO-II :ID | 2 | 630 | 19506448 | 515 | 2019-06-30 | 184 | 720 | 177 | 684 | 154 | 592 | 115 | 665 | 54.5 |  |  | 54.5 | 82% | 76% | 77% | 80% | 5.4688 | Loss 5-10%
1024 | 1251 | KWR | GOKUL PURI | KWL019 | TG-KWL019A-2 | DT-2 | A BLK G N 2 BHAGIRATHI VIHAR NO-II :ID | 2 | 630 | 19505765 | 558 | 2019-06-29 23:30 | 184 | 738 | 228 | 925 | 146 | 580 | 299 | 582 | 137 |  |  | 137 | 88% | 86% | 87% | 89% | 5.4688 | Loss 5-10% |  |  | 523(41) | 549(47.5)
1025 | 1251 | KWR | GOKUL PURI | KWL027 | TG-KWL027A-1 | DT-1 | A BLOCK BRIJ PURI:ID | 2 | 630 | 19500627 | 643 | 2019-06-10 23:30 | 298 | 1293 | 228 | 992 | 116 | 486 | 706 | 577.5 | 127 | 13 | 1 | 141 | 100% | 71% | 86% | 102% | 6.2381 | Loss 5-10% | 518(36.5) | 686(389) | 650(104.5) | 764(495.5) |  | 554(96)
1026 | 1251 | KWR | GOKUL PURI | KWL028 | TG-KWL028A-1 | DT-1 | B BLOCK BRIJ PURI:ID | 1 | 990 | 19505234 | 925 | 2019-06-10 01:00 | 259 | 1110 | 279 | 1194 | 388 | 1688 | 541 | 554 | 159.5 | 6.5 |  | 166 | 93% | 83% | 88% | 92% | 5.6254 | Loss 5-10% |  | 872(30.5) | 875(104.5) | 890(79.5) | 825(31.5)
1027 | 1251 | KWR | GOKUL PURI | KWL039 | TG-KWL039A-2 | DT-2 | GANGA VIHAR NO-1:ID | 2 | 990 | 19500982 | 956 | 2019-06-25 23:30 | 412 | 1691 | 272 | 1098 | 272 | 1115 | 585 | 561.5 | 146 | 12.5 |  | 158.5 | 96% | 83% | 71% | 97% | 5.791 | Loss 5-10% |  | 671(156.5) | 717(372) | 704(276) | 701(181.5)
1028 | 1251 | KWR | GOKUL PURI | KWL040 | TG-KWL040A-1 | DT-1 | GANGA VIHAR NO-2:ID | 2 | 990 | 19501736 | 1126 | 2019-06-30 07:30 | 398 | 1520 | 377 | 1378 | 351 | 1337 | 166 | 378.5 | 244.5 | 68.5 | 25.5 | 338.5 | 106% | 114% | 96% | 108% | 7.2668 | Loss 5-10% | 914(38.5) | 1229(373.5) | 1410(150.5) | 952(48) | 1148(131)
1029 | 1251 | KWR | GOKUL PURI | KWL040 | TG-KWL040A-2 | DT-2 | GANGA VIHAR NO-2:ID | 2 | 990 | 19503794 | 1153 | 2019-06-08 23:30 | 282 | 1139 | 457 | 1903 | 414 | 1699 | 685 | 306 | 319 | 65.5 | 26.5 | 411 | 109% | 73% | 105% | 116% | 7.2668 | Loss 5-10% |  | 949(188) |  | 1027(99.5) | 1187(419.5) | 917(92.5)
1030 | 1251 | KWR | GOKUL PURI | KWL044 | TG-KWL044A-1 | DT-1 | GALI NO.3 OLD MUSTAFABAD:ID | 2 | 990 | 19502319 | 866 | 2019-06-02 07:00 | 334 | 1409 | 240 | 1006 | 292 | 1221 | 349 | 543.5 | 172 |  |  | 172 | 82% | 88% | 81% | 83% | 14.4156 | Loss 10-20% |  |  | 774(88.5) | 794(50.5)
1031 | 1251 | KWR | GOKUL PURI | KWL044 | TG-KWL044A-2 | DT-2 | GALI NO.3 OLD MUSTAFABAD:ID | 2 | 400 | 19501040 | 373 | 2019-06-29 23:30 | 136 | 566 | 119 | 496 | 117 | 481 | 79 | 320.5 | 393.5 | 2 |  | 395.5 | 91% | 93% | 90% | 93% | 14.4156 | Loss 10-20% |  | 354(144) | 357(420.5) | 389(394.5) | 334(127.5)
1032 | 1251 | KWR | GOKUL PURI | KWL052 | TG-KWL052A-1 | DT-1 | B BLOCK GOKUL PURI:PL | 1 | 630 | 19503799 | 538 | 2019-06-02 23:00 | 214 | 942 | 139 | 598 | 185 | 804 | 299 | 599 | 121 |  |  | 121 | 84% | 65% | 67% | 85% | 6.3099 | Loss 5-10%
1033 | 1251 | KWR | GOKUL PURI | KWL053 | TG-KWL053A-2 | DT-2 | JAWHAR NAGAR NO.-1:PL | 2 | 990 | 19504953 | 1037 | 2019-06-24 12:00 | 346 | 1461 | 338 | 1428 | 354 | 1488 | 52 | 535.5 | 134.5 | 47.5 | 2 | 184 | 31% | 57% | 105% | 31% | 6.6515 | Loss 5-10% | 910(136.5) | 962(167) | 1010(173.5) | 1051(188.5) | 1083(221.5) | 1185(251)
1034 | 1251 | KWR | GOKUL PURI | KWL077 | TG-KWL077A-2 | DT-2 | SAMPAT NAGAR 1:ID | 2 | 400 | 19505301 | 413 | 2019-06-30 | 156 | 655 | 130 | 547 | 126 | 528 | 118 | 238.5 | 389 | 87.5 | 4.5 | 481 | 103% | 97% | 100% | 102% | 8.972 | Loss 5-10% | 379(156) | 525(552) |  | 383(179) | 371(92)
1035 | 1251 | KWR | GOKUL PURI | KWL101 | TG-KWL101A-1 | DT-1 | MANSINGH NAGAR GALI NO. 16:ID | 2 | 630 | 19503017 | 500 | 2019-06-29 23:00 | 159 | 644 | 132 | 532 | 209 | 844 | 274 | 687.5 | 30.5 |  |  | 30.5 | 78% | 71% | 77% | 79% | 5.6675 | Loss 5-10% |  | 638(427)
1036 | 1251 | KWR | GOKUL PURI | KWL103 | TG-KWL103A-1 | DT-1 | MAJOR MALHOTRA FARM HOUSE:PM | 1 | 100 | 19506634 | 85 | 2019-06-28 12:00 | 11 | 44 | 30 | 122 | 44 | 182 | 120 | 649.5 | 70.5 |  |  | 70.5 | 55% | 55% | 85% | 59% | 2.6432 | Loss 0-5%
1037 | 1251 | KWR | GOKUL PURI | KWL107 | TG-KWL107A-1 | DT-1 | JOHRIPUR GUJARMAL MOHALLA:PL | 1 | 990 | 19506817 | 934 | 2019-06-27 15:30 | 325 | 1503 | 305 | 1368 | 304 | 1391 | 125 | 668.5 | 49.5 | 0.5 |  | 50 | 39% | 45% | 94% | 40% | 7.491 | Loss 5-10% | 843(33.5) | 853(51) |  | 902(80.5) | 851(44.5) | 875(59.5)
1038 | 1251 | KWR | GOKUL PURI | KWL162 | TG-KWL162A-1 | DT-1 | JAIN COMPLEX JOHIRIPUR:PM | 1 | 100 | 19506636 | 87 | 2019-06-12 03:30 | 33 | 135 | 26 | 105 | 28 | 111 | 28 | 666.5 | 49.5 |  |  | 49.5 | 87% | 59% | 77% | 82% | 2.1297 | Loss 0-5% |  |  | 79(31.5)
1039 | 1251 | KWR | GOKUL PURI | KWL237 | TG-KWL237A-1 | DT-1 | SHANI BAZAR ROAD JOHRI PUR :PM | 1 | 630 | 19505924 | 905 | 2019-06-29 12:00 | 289 | 1325 | 292 | 1356 | 324 | 1488 | 150 | 551.5 | 150.5 | 14 | 1.5 | 166 | 63% | 68% | 144% | 67% | 5.8425 | Loss 5-10% | 681(197) | 701(200) | 826(195) | 727(190.5) | 769(221.5) | 748(228.5)
1040 | 1251 | KWR | GOKUL PURI | KWL243 | TG-KWL243A-1 | DT-1 | G & H BLK MUSTAFABAD GALI NO. 18:ID | 2 | 990 | 19505960 | 1101 | 2019-06-02 05:30 | 392 | 1669 | 396 | 1692 | 314 | 1323 | 359 | 293.5 | 395 | 29.5 | 2 | 426.5 | 111% | 86% | 107% | 103% | 6.5849 | Loss 5-10% |  | 1062(132.5) | 1046(384.5) | 1094(256.5) | 1042(135.5)
1041 | 1251 | KWR | GOKUL PURI | KWL246 | TG-KWL246A-1 | DT-1 | C BLOCK BRIJ PURI:ID | 1 | 990 | 19505514 | 985 | 2019-06-03 14:00 | 326 | 1578 | 344 | 1617 | 315 | 1491 | 111 | 478.5 | 220.5 | 21 |  | 241.5 | 95% | 95% | 99% | 97% | 4.6852 | Loss 0-5% |  | 1020(54) | 998(168) | 1221(140) | 1028(69.5)
1042 | 1251 | KWR | GOKUL PURI | KWL331 | TG-KWL331A-1 | DT-1 | GALI NO.5 JAWAHAR NAGAR P/M | 1 | 990 | 19504775 | 935 | 2019-06-22 16:00 | 310 | 1350 | 309 | 1332 | 315 | 1363 | 27 | 583.5 | 128 | 3 |  | 131 | 44% | 57% | 94% | 40% | 12.9229 | Loss 10-20% | 883(123.5) | 842(82.5) |  | 906(87) | 802(43.5) | 886(96)
1043 | 1251 | KWR | GOKUL PURI | KWL344 | TG-KWL344A-1 | DT-1 | MAIN ROAD MCD SCHOOL JOHRI PUR | 1 | 990 | 19505304 | 1164 | 2019-06-29 15:00 | 405 | 1827 | 384 | 1720 | 375 | 1689 | 125 | 509.5 | 153 | 38.5 | 16.5 | 208 | 42% | 52% | 118% | 46% | 10.2229 | Loss 10-20% | 997(170.5) | 1114(214) |  | 1171(241) | 1199(214) | 1128(167)
1044 | 1251 | KWR | GOKUL PURI | KWL349 | TG-KWL349A-1 | DT-1 | G BLK GANGA VIHAR(SHAMSHAAN GHAT) | 2 | 630 | 19506686 | 566 | 2019-06-11 23:00 | 191 | 795 | 181 | 750 | 194 | 803 | 50 | 608 | 112 |  |  | 112 | 88% | 74% | 76% | 90% | 3.8389 | Loss 0-5%
1045 | 1251 | KWR | KARAWAL NAGAR | KWL010 | TG-KWL010A-1 | DT-1 | MUKUND VIHAR "A" BLK:ID | 1 | 630 | 19500537 | 598 | 2019-06-12 17:00 | 194 | 868 | 207 | 923 | 198 | 884 | 49 | 513.5 | 199.5 | 2 |  | 201.5 | 86% | 71% | 95% | 85% | 6.9589 | Loss 5-10% |  | 635(157.5) | 620(278) | 604(152.5) | 593(221.5) | 557(88)
1046 | 1251 | KWR | KARAWAL NAGAR | KWL013 | TG-KWL013A-1 | DT-1 | C BLK MUKUND VIHAR GALI NO. 9:ID | 1 | 1600 | 19505641 | 1944 | 2019-06-02 05:30 | 665 | 2676 | 591 | 2390 | 689 | 2810 | 371 | 483 | 205 | 21.5 | 2 | 228.5 | 122% | 82% | 103% | 101% | 13.461 | Loss 10-20% |  | 1037(233) | 1103(509) | 1284(434.5) | 1096(403.5) | 824(174.5)
1047 | 1251 | KWR | KARAWAL NAGAR | KWL031 | TG-KWL031A-1 | DT-1 | PREM NAGAR S/STN :ID | 2 | 630 | 19505231 | 637 | 2019-06-12 00:30 | 219 | 959 | 208 | 915 | 211 | 912 | 46 | 609 | 102 | 1.5 | 0.5 | 104 | 101% | 81% | 85% | 90% | 4.424 | Loss 0-5%
1048 | 1251 | KWR | KARAWAL NAGAR | KWL033 | TG-KWL033A-1 | DT-1 | MAHALAXMI ENCLAVE:ID | 2 | 990 | 19506283 | 880 | 2019-06-11 22:00 | 330 | 1431 | 272 | 1190 | 279 | 1219 | 227 | 657.5 | 61.5 |  |  | 61.5 | 81% | 75% | 75% | 89% | 10.4578 | Loss 10-20% |  | 901(81) | 956(243.5) | 1119(172.5) | 905(97.5)
1049 | 1251 | KWR | KARAWAL NAGAR | KWL033 | TG-KWL033A-2 | DT-2 | MAHALAXMI ENCLAVE:ID | 2 | 630 | 19500685 | 567.545 | 2019-06-12 | 192.0934 | 822.8459 | 196.3834 | 835.4606 | 179.0683 | 765.5434 | 64.5412 | 664.5 | 53.5 | 0.5 |  | 54 | 90% | 77% | 71% | 87% | 10.4578 | Loss 10-20%
1050 | 1251 | KWR | KARAWAL NAGAR | KWL046 | TG-KWL046A-1 | DT-1 | C C KARAWAL NAGAR S/STN. NO. 2:I/D | 2 | 990 | 19500592 | 933 | 2019-06-26 15:30 | 334 | 1431 | 304 | 1317 | 295 | 1269 | 143 | 602.5 | 113 | 3 |  | 116 | 46% | 40% | 94% | 47% | 14.591 | Loss 10-20% | 778(35) | 894(121.5) |  | 784(39) | 813(84) | 824(28.5)
1051 | 1251 | KWR | KARAWAL NAGAR | KWL056 | TG-KWL056A-1 | DT-1 | KARWAL NAGAR NO.-1 DAL MILL:PL | 2 | 990 | 19505998 | 867 | 2019-06-28 16:00 | 291 | 1329 | 275 | 1250 | 300 | 1364 | 102 | 673.5 | 46 |  |  | 46 | 47% | 46% | 88% | 50% | 10.2339 | Loss 10-20%
1052 | 1251 | KWR | KARAWAL NAGAR | KWL056 | TG-KWL056A-2 | DT-2 | KARWAL NAGAR NO.-1 DAL MILL:PL | 2 | 990 | 19506728 | 929.3679 | 2019-06-01 12:00 | 293.9679 | 1276.2345 | 296.9879 | 1298.7053 | 338.4121 | 1485.3058 | 198.7907 | 585.5 | 133 | 1 |  | 134 | 53% | 54% | 94% | 55% | 10.2339 | Loss 10-20% | 1017(165) | 1106(187.5) | 975(152.5) | 986(168.5) | 968(148.5) | 1004(172)
1053 | 1251 | KWR | KARAWAL NAGAR | KWL058 | TG-KWL058A-1 | DT-1 | KARWAL NAGAR NO.-4:PL | 2 | 990 | 19504901 | 775 | 2019-06-27 15:00 | 264 | 1127 | 266 | 1137 | 245 | 1042 | 91 | 681.5 | 38 |  |  | 38 | 26% | 40% | 78% | 31% | 14.8878 | Loss 10-20% | 1028(163) | 1119(203.5) |  |  | 988(182)
1054 | 1251 | KWR | KARAWAL NAGAR | KWL058 | TG-KWL058A-2 | DT-2 | KARWAL NAGAR NO.-4:PL | 2 | 990 | 19503507 | 850 | 2019-06-28 16:00 | 278 | 1180 | 272 | 1151 | 300 | 1277 | 114 | 616.5 | 102.5 |  |  | 102.5 | 35% | 41% | 86% | 43% | 14.8878 | Loss 10-20% |  |  |  | 807(33.5) | 910(75.5) | 896(119)
1055 | 1251 | KWR | KARAWAL NAGAR | KWL059 | TG-KWL059A-1 | DT-1 | KARWAL NAGAR NO.-5 SBI KWR:PL | 3 | 990 | 19500596 | 1087.1146 | 2019-06-27 16:30 | 431.2797 | 1884.5518 | 337.7799 | 1492.4881 | 318.0551 | 1387.0091 | 454.0861 | 570.5 | 129 | 16.5 | 2 | 147.5 | 30% | 51% | 110% | 32% | 14.3272 | Loss 10-20% | 1042(173) | 1158(213.5) | 1129(183.5) | 1250(228.5) | 1212(177) | 984(154)
1056 | 1251 | KWR | KARAWAL NAGAR | KWL059 | TG-KWL059A-2 | DT-2 | KARWAL NAGAR NO.-5 SBI KWR:PL | 3 | 990 | 19502963 | 823 | 2019-06-03 14:30 | 262 | 1162 | 269 | 1202 | 292 | 1310 | 133 | 625.5 | 93.5 |  |  | 93.5 | 54% | 68% | 83% | 52% | 14.3272 | Loss 10-20% | 865(80) | 942(112) | 1053(211.5) | 1015(153.5) | 1120(232.5) | 1158(294)
1057 | 1251 | KWR | KARAWAL NAGAR | KWL059 | TG-KWL059A-3 | DT-3 | KARWAL NAGAR NO.-5 SBI KWR:PL | 3 | 990 | 19505348 | 823 | 2019-06-29 11:00 | 285 | 1232 | 275 | 1183 | 262 | 1132 | 87 | 672 | 47 |  |  | 47 | 33% | 43% | 83% | 38% | 14.3272 | Loss 10-20%
1058 | 1251 | KWR | KARAWAL NAGAR | KWL100 | TG-KWL100A-1 | DT-1 | SAHID BHAGAT SINGH CLY GALI NO 16:ID | 1 | 630 | 19506759 | 616 | 2019-06-02 07:00 | 194 | 840 | 187 | 811 | 236 | 1022 | 198 | 538.5 | 172.5 | 7 |  | 179.5 | 97% | 98% | 96% | 92% | 6.9448 | Loss 5-10% |  |  | 518(27)
1059 | 1251 | KWR | KARAWAL NAGAR | KWL264 | TG-KWL264A-1 | DT-1 | WEST KAMAL VIHAR (HVDS) INDUT. AREA:PM | 1 | 400 | 19505888 | 393 | 2019-06-30 14:30 | 148 | 669 | 112 | 508 | 134 | 605 | 140 | 638.5 | 73.5 | 3.5 |  | 77 | 57% | 44% | 98% | 55% | 2.9268 | Loss 0-5% | [5 empty] | 415(47.5)
1060 | 1251 | KWR | KARAWAL NAGAR | KWL287 | TG-KWL287A-1 | DT-1 | BABU NAGAR 1 GALI NO. 5:ID | 1 | 630 | 19506284 | 575 | 2019-06-14 11:00 | 181 | 795 | 200 | 878 | 194 | 849 | 73 | 613 | 104.5 | 0.5 |  | 105 | 83% | 88% | 91% | 79% | 8.2377 | Loss 5-10% |  |  |  | 585(32.5)
1061 | 1251 | KWR | KARAWAL NAGAR | KWL296 | TG-KWL296A-1 | DT-1 | SAHID BHAGAT SINGH CLY GALI NO 6:ID | 1 | 990 | 19500671 | 863.5283 | 2019-06-30 23:30 | 291.338 | 1285.9764 | 295.9745 | 1301.1584 | 276.2158 | 1219.2267 | 75.4945 | 621.5 | 97 |  |  | 97 | 83% | 72% | 74% | 87% | 6.3234 | Loss 5-10% |  |  | 991(43) | 833(37)
1062 | 1251 | KWR | SONIA VIHAR | KWL016 | TG-KWL016A-2 | DT-2 | CHANDU NAGAR:ID | 2 | 400 | 19505302 | 422 | 2019-06-10 22:00 | 143 | 580 | 131 | 538 | 148 | 615 | 67 | 570.5 | 144 | 1.5 | 1 | 146.5 | 95% | 80% | 87% | 106% | 3.6533 | Loss 0-5%
1063 | 1251 | KWR | SONIA VIHAR | KWL017 | TG-KWL017A-2 | DT-2 | E BLOCK KHAJOORI GALI NO. 3:ID | 2 | 990 | 19505644 | 892 | 2019-06-30 23:00 | 305 | 1346 | 282 | 1226 | 304 | 1342 | 118 | 635.5 | 84 | 0.5 |  | 84.5 | 81% | 61% | 76% | 90% | 5.4279 | Loss 5-10% |  |  | 951(46.5) | 827(36.5)
1064 | 1251 | KWR | SONIA VIHAR | KWL018 | TG-KWL018A-1 | DT-1 | F BLOCK KHAJOORI GALI NO. 11&13:ID | 2 | 990 | 19504694 | 973 | 2019-06-02 22:30 | 319 | 1353 | 341 | 1463 | 313 | 1317 | 131 | 387.5 | 321 | 10.5 |  | 331.5 | 92% | 76% | 89% | 98% | 6.2874 | Loss 5-10% | 763(44.5) | 798(27.5) | 839(78.5) | 927(224.5) | 878(150)
1065 | 1251 | KWR | SONIA VIHAR | KWL018 | TG-KWL018A-2 | DT-2 | F BLOCK KHAJOORI GALI NO. 11&13:ID | 2 | 630 | 19502248 | 544 | 2019-06-03 15:30 | 155 | 677 | 224 | 988 | 166 | 724 | 290 | 549.5 | 169.5 |  |  | 169.5 | 80% | 62% | 86% | 80% | 6.2874 | Loss 5-10% |  | 656(434.5) | 697(468) | 577(190.5)
1066 | 1251 | KWR | SONIA VIHAR | KWL022 | TG-KWL022A-1 | DT-1 | B-II BLOCK NEHRU VIHAR GALI NO. 6:ID | 1 | 630 | 19506820 | 933 | 2019-06-28 14:30 | 336 | 1412 | 305 | 1272 | 292 | 1217 | 174 | 17 | 319 | 217 | 167 | 703 | 119% | 110% | 148% | 120% | 8.5328 | Loss 5-10% |  | 504(59.5) | 494(29) | 529(112) | 502(58.5)
1067 | 1251 | KWR | SONIA VIHAR | KWL026 | TG-KWL026A-1 | DT-1 | E-1, NEHRU VIHAR:ID | 1 | 990 | 19505257 | 891 | 2019-06-11 22:30 | 270 | 1221 | 308 | 1399 | 312 | 1414 | 186 | 647 | 73 |  |  | 73 | 89% | 82% | 82% | 90% | 3.4253 | Loss 0-5% |  |  | 873(27.5)
1068 | 1251 | KWR | SONIA VIHAR | KWL060 | TG-KWL060A-1 | DT-1 | C BLOCK KHAJORI MAIN MARKET | 3 | 990 | 19506447 | 869.5479 | 2019-06-13 23:00 | 236.4072 | 974.5939 | 367.6768 | 1527.8487 | 265.4639 | 1115.7695 | 497.911 | 650.5 | 67 |  |  | 67 | 87% | 61% | 73% | 88% | 4.7355 | Loss 0-5% |  | 923(87.5) | 1020(218.5) | 1086(169) | 920(125)
1069 | 1251 | KWR | SONIA VIHAR | KWL060 | TG-KWL060A-3 | DT-3 | C BLOCK KHAJORI MAIN MARKET | 3 | 630 | 19506413 | 647 | 2019-06-12 | 199 | 825 | 261 | 1079 | 187 | 769 | 286 | 505.5 | 164 | 47 | 1.5 | 212.5 | 103% | 75% | 98% | 102% | 4.7355 | Loss 0-5%
1070 | 1251 | KWR | SONIA VIHAR | KWL061 | TG-KWL061A-1 | DT-1 | FATMA NURSARY CHAND BAGH MRD WZB ROAD:PL | 1 | 990 | 19502590 | 875 | 2019-06-30 23:30 | 299 | 1223 | 282 | 1151 | 294 | 1203 | 64 | 496 | 222.5 |  |  | 222.5 | 88% | 77% | 82% | 88% | 8.5864 | Loss 5-10% |  | 784(33.5) | 790(99) | 846(100.5) | 783(50)
1071 | 1251 | KWR | SONIA VIHAR | KWL063 | TG-KWL063A-1 | DT-1 | VILLAGE SABHAPUR:PM | 1 | 630 | 19502302 | 758 | 2019-06-09 23:00 | 293 | 1297 | 211 | 918 | 255 | 1125 | 329 | 304 | 266 | 95.5 | 48 | 409.5 | 115% | 86% | 95% | 120% | 10.8069 | Loss 10-20% |  |  |  | 738(119) | 735(442) | 674(192)
1072 | 1251 | KWR | SONIA VIHAR | KWL064 | TG-KWL064A-2 | DT-2 | SHERPUR CHOWK:PL | 2 | 630 | 19506395 | 624 | 2019-06-24 15:30 | 200 | 841 | 223 | 946 | 201 | 852 | 100 | 583 | 117 | 20 |  | 137 | 58% | 82% | 99% | 58% | 14.5623 | Loss 10-20% |  |  | 665(167.5) | 671(130.5) | 665(206.5)
1073 | 1251 | KWR | SONIA VIHAR | KWL069 | TG-KWL069A-2 | DT-2 | DAYAL PUR 1 TANKI MAIN ROAD DAYAL PUR:PL | 3 | 630 | 19506601 | 564 | 2019-06-11 22:30 | 154 | 651 | 165 | 695 | 246 | 1089 | 418 | 641 | 79 |  |  | 79 | 80% | 65% | 80% | 90% | 10.9717 | Loss 10-20% |  |  | 475(32.5)
1074 | 1251 | KWR | SONIA VIHAR | KWL070 | TG-KWL070A-1 | DT-1 | B BLK GALI NO. 9, CHAND BAGH:ID | 2 | 630 | 19500570 | 584 | 2019-06-02 23:30 | 196 | 859 | 225 | 994 | 164 | 715 | 242 | 476 | 238.5 | 4.5 |  | 243 | 93% | 76% | 87% | 93% | 11.9171 | Loss 10-20% |  | 533(70) | 549(206) | 535(91.5) | 539(49.5)
1075 | 1251 | KWR | SONIA VIHAR | KWL072 | TG-KWL072A-1 | DT-1 | VILLAGE KHAJOORI NR.SCHOOL:PL | 1 | 630 | 19504805 | 601 | 2019-06-12 15:00 | 253 | 1061 | 174 | 721 | 174 | 720 | 340 | 466.5 | 251 | 1.5 |  | 252.5 | 86% | 64% | 95% | 86% | 18.023 | Loss 10-20% |  | 517(74.5) |  | 579(165) | 538(79)
1076 | 1251 | KWR | SONIA VIHAR | KWL076 | TG-KWL076A-1 | DT-1 | A BL MAIN ROAD DAYALPUR:PL | 1 | 990 | 19506896 | 988 | 2019-06-16 02:00 | 353 | 1486 | 286 | 1185 | 349 | 1457 | 287 | 540.5 | 168.5 | 7 |  | 175.5 | 100% | 69% | 88% | 94% | 13.0986 | Loss 10-20% |  | 838(24) | 822(83) | 897(86) | 886(63)
1077 | 1251 | KWR | SONIA VIHAR | KWL079 | TG-KWL079A-1 | DT-1 | B BLK SADAT PUR GALI NO. 8:ID | 1 | 400 | 19504409 | 369 | 2019-06-29 23:00 | 141 | 631 | 112 | 491 | 115 | 508 | 132 | 578 | 139.5 | 2.5 |  | 142 | 91% | 59% | 72% | 92% | 2.9931 | Loss 0-5%
1078 | 1251 | KWR | SONIA VIHAR | KWL080 | TG-KWL080A-1 | DT-1 | BIHARI PUR VILLNR. NLA KHJURI PUST RD:PL | 1 | 990 | 19506903 | 842 | 2019-06-30 14:30 | 309 | 1384 | 257 | 1170 | 276 | 1266 | 186 | 663.5 | 56 |  |  | 56 | 78% | 64% | 85% | 78% | 20.6627 | Loss 20-30% |  |  | 784(24)
1079 | 1251 | KWR | SONIA VIHAR | KWL083 | TG-KWL083A-1 | DT-1 | L BLK SADAT PUR:ID | 1 | 990 | 19500560 | 893.8565 | 2019-06-30 | 286.146 | 1304.1016 | 295.6431 | 1344.5655 | 312.0675 | 1416.2997 | 98.4163 | 661.5 | 58 | 0.5 |  | 58.5 | 90% | 70% | 68% | 90% | 6.5996 | Loss 5-10%
1080 | 1251 | KWR | SONIA VIHAR | KWL085 | TG-KWL085A-1 | DT-1 | B BLK PUSTA 1 SONIA VIHAR GALI NO 1 | 1 | 630 | 19506042 | 589 | 2019-06-08 09:30 | 176 | 745 | 202 | 854 | 210 | 883 | 126 | 616 | 89.5 | 1 |  | 90.5 | 90% | 92% | 93% | 90% | 7.1229 | Loss 5-10% |  |  |  | 611(728)
1081 | 1251 | KWR | SONIA VIHAR | KWL093 | TG-KWL093A-1 | DT-1 | CHAUHAN PATTI PUSTA VILL SONIA VIHAR:PL | 1 | 630 | 19506301 | 714 | 2019-06-29 22:30 | 218 | 952 | 262 | 1154 | 234 | 1025 | 177 | 347 | 328 | 33.5 | 3.5 | 365 | 100% | 99% | 103% | 113% | 7.2728 | Loss 5-10% |  | 652(76) | 722(256.5) | 726(276.5) |  | 592(31.5)
1082 | 1251 | KWR | SONIA VIHAR | KWL096 | TG-KWL096A-1 | DT-1 | B-I, NEHRU VIHAR:ID | 1 | 990 | 19500614 | 1166 | 2019-06-29 23:00 | 389 | 1610 | 380 | 1576 | 397 | 1648 | 62 | 313.5 | 268 | 78 | 60 | 406 | 116% | 86% | 89% | 118% | 7.9336 | Loss 5-10% |  | 969(168.5) | 1043(328) | 1098(285)
1083 | 1251 | KWR | SONIA VIHAR | KWL113 | TG-KWL113A-1 | DT-1 | SONIA VIHAR "B" BLK GALI NO-27 | 1 | 400 | 19506291 | 524 | 2019-06-10 05:00 | 193 | 808 | 181 | 756 | 150 | 616 | 172 | 128 | 519.5 | 58.5 | 6.5 | 584.5 | 131% | 95% | 102% | 113% | 7.5588 | Loss 5-10%
1084 | 1251 | KWR | SONIA VIHAR | KWL115 | TG-KWL115A-1 | DT-1 | C 1 KHAJOORI GALI NO. 24:PM | 1 | 400 | 19502314 | 439 | 2019-06-02 23:00 | 152 | 636 | 89 | 365 | 198 | 832 | 406 | 299.5 | 307.5 | 84 | 29 | 420.5 | 107% | 86% | 94% | 110% | 4.8874 | Loss 0-5%
1085 | 1251 | KWR | SONIA VIHAR | KWL119 | TG-KWL119A-1 | DT-1 | F BLK DAYAL PUR : ID | 1 | 630 | 19503341 | 500 | 2019-06-29 23:30 | 213 | 952 | 139 | 614 | 148 | 664 | 316 | 674 | 46 |  |  | 46 | 79% | 61% | 69% | 79% | 11.7189 | Loss 10-20%
1086 | 1251 | KWR | SONIA VIHAR | KWL121 | TG-KWL121A-2 | DT-2 | JEEVAN JYOTI SCHOOL SADAT PUR : ID | 2 | 990 | 19500551 | 1161.4047 | 2019-06-27 | 414.5778 | 1811.5699 | 392.1803 | 1725.8417 | 354.6466 | 1563.8355 | 217.9078 | 383.5 | 192.5 | 64.5 | 79.5 | 336.5 | 117% | 79% | 92% | 117% | 5.9491 | Loss 5-10% |  | 895(96.5) | 1061(200) | 980(141)
1087 | 1251 | KWR | SONIA VIHAR | KWL127 | TG-KWL127A-1 | DT-1 | NIKKA PLASTIC TUKMEERPUR VILLAGE:PM | 1 | 400 | 19505123 | 501 | 2019-06-17 20:00 | 165 | 662 | 166 | 674 | 169 | 683 | 18 | 487 | 130.5 | 32 | 67.5 | 230 | 117% | 117% | 125% | 116% | 29.45 | Loss 20-30% | 446(400.5) | 564(513.5) | 716(242) | 374(116.5) | 397(256.5) | 415(414)
1088 | 1251 | KWR | SONIA VIHAR | KWL145 | TG-KWL145A-1 | DT-1 | SHRI RAM COLONY B BLK RAMLILA GROUND | 1 | 400 | 19506532 | 487.9528 | 2019-06-30 14:30 | 196.3645 | 800.2791 | 110.7378 | 443.377 | 180.8505 | 734.5673 | 329.0053 | 439.5 | 266.5 | 9.5 | 2.5 | 278.5 | 120% | 103% | 122% | 98% | 10.6186 | Loss 10-20% |  |  |  | 490(132.5) | 414(155.5)
1089 | 1251 | KWR | SONIA VIHAR | KWL146 | TG-KWL146A-1 | DT-1 | C BLK SHRI RAM COLONY :PLM | 1 | 630 | 19506504 | 697.4431 | 2019-06-14 06:00 | 155.4979 | 636.4779 | 299.0081 | 1262.3832 | 242.9371 | 1014.5206 | 545.944 | 286.5 | 417.5 | 11.5 | 1.5 | 430.5 | 93% | 111% | 103% | 98% | 10.0862 | Loss 10-20% |  |  |  | 640(422) | 694(258)
1090 | 1251 | KWR | SONIA VIHAR | KWL147 | TG-KWL147A-1 | DT-1 | SHRI RAM COLONY D BLK:PLM | 1 | 630 | 19506716 | 788 | 2019-06-30 01:30 | 259 | 1094 | 301 | 1302 | 228 | 968 | 292 | 554.5 | 162.5 | 0.5 | 1.5 | 164.5 | 125% | 111% | 120% | 86% | 3.6386 | Loss 0-5% |  | 468(26) |  | 524(78.5) | 477(53)
1091 | 1251 | KWR | SONIA VIHAR | KWL154 | TG-KWL154A-1 | DT-1 | SHRI RAM CLY E BLK GN 3 NR MASJID :PM | 1 | 400 | 19504596 | 388 | 2019-06-02 15:00 | 124 | 530 | 122 | 519 | 143 | 614 | 89 | 296.5 | 385 | 37 |  | 422 | 94% | 85% | 97% | 95% | 13.0373 | Loss 10-20% |  | 355(287.5) | 376(229.5) | 396(477) | 401(315) | 351(129.5)
1092 | 1251 | KWR | SONIA VIHAR | KWL157 | TG-KWL157A-1 | DT-1 | D BLOCK GALI NO 2 DAYAL PUR | 2 | 990 | 19504362 | 972 | 2019-06-28 23:00 | 292 | 1180 | 341 | 1386 | 339 | 1374 | 200 | 526 | 180 | 13 |  | 193 | 98% | 81% | 90% | 98% | 7.3168 | Loss 5-10% |  |  | 861(91) | 852(59)
1093 | 1251 | KWR | SONIA VIHAR | KWL157 | TG-KWL157A-2 | DT-2 | D BLOCK GALI NO 2 DAYAL PUR | 2 | 630 | 19505019 | 639 | 2019-06-11 23:00 | 191 | 819 | 214 | 917 | 235 | 1004 | 160 | 614 | 96 | 6.5 | 0.5 | 103 | 97% | 68% | 73% | 101% | 7.3168 | Loss 5-10%
1094 | 1251 | KWR | SONIA VIHAR | KWL158 | TG-KWL158A-1 | DT-1 | D-3 NEHRU VIHAR : ID | 2 | 990 | 19500584 | 874 | 2019-06-10 23:00 | 250 | 1056 | 339 | 1438 | 285 | 1192 | 336 | 504 | 215.5 |  |  | 215.5 | 88% | 73% | 79% | 88% | 7.1995 | Loss 5-10% | 758(28.5) | 1035(361.5) | 927(255.5) | 1021(479.5) | 911(324) | 767(42.5)
1095 | 1251 | KWR | SONIA VIHAR | KWL234 | TG-KWL234A-1 | DT-1 | B BLK SHRI RAM COLONY :PL | 1 | 990 | 19506536 | 1156 | 2019-06-30 01:30 | 424 | 1808 | 445 | 1885 | 287 | 1202 | 648 | 533 | 184 | 1 | 1 | 186 | 117% | 100% | 114% | 87% | 14.3165 | Loss 10-20% |  | 829(104) |  | 927(52) | 916(110.5)
1096 | 1251 | KWR | SONIA VIHAR | KWL235 | TG-KWL235A-1 | DT-1 | A BLK SHRI RAM CLY NEAR GALI 26:PL | 1 | 630 | 19505324 | 755 | 2019-06-30 01:30 | 277 | 1189 | 210 | 887 | 268 | 1146 | 283 | 638 | 78.5 |  | 1.5 | 80 | 120% | 103% | 116% | 82% | 7.6651 | Loss 5-10% |  | 545(62) |  | 594(105) | 715(42.5)
1097 | 1251 | KWR | SONIA VIHAR | KWL249 | TG-KWL249A-1 | DT-1 | A BLOCK SHRI RAM CLY. NEAR SERVICE RD:PL | 1 | 630 | 19506533 | 739 | 2019-06-30 | 207 | 870 | 304 | 1307 | 228 | 964 | 398 | 465.5 | 252.5 | 0.5 | 0.5 | 253.5 | 117% | 83% | 91% | 90% | 10.0142 | Loss 10-20% |  | 513(79) |  | 623(53) | 515(95.5)
1098 | 1251 | KWR | SONIA VIHAR | KWL251 | TG-KWL251A-1 | DT-1 | A BLK KHAJOORI:PL | 1 | 630 | 19505294 | 747 | 2019-06-01 05:00 | 227 | 923 | 284 | 1159 | 236 | 968 | 217 | 669.5 | 49.5 |  | 0.5 | 50 | 119% | 60% | 80% | 81% | 12.4516 | Loss 10-20%
1099 | 1251 | KWR | SONIA VIHAR | KWL292 | TG-KWL292A-1 | DT-1 | E BLOCK CHAND BAGH:PL | 1 | 630 | 19506537 | 810 | 2019-06-30 01:30 | 242 | 1030 | 280 | 1194 | 289 | 1244 | 194 | 109 | 410.5 | 112.5 | 87.5 | 610.5 | 129% | 118% | 125% | 118% | 11.2623 | Loss 10-20% | 488(26) | 616(358) |  | 683(179)
1100 | 1251 | KWR | SONIA VIHAR | KWL295 | TG-KWL295A-1 | DT-1 | K BLK SADAT PUR EXT. GALI NO. 51:ID | 1 | 990 | 19500647 | 876 | 2019-06-09 23:00 | 265 | 1156 | 302 | 1322 | 308 | 1366 | 192 | 581.5 | 138.5 |  |  | 138.5 | 85% | 62% | 73% | 88% | 5.0709 | Loss 5-10% |  | 886(98) |  | 988(254) | 946(188.5) | 752(29.5)
1101 | 1251 | KWR | SONIA VIHAR | KWL297 | TG-KWL297A-1 | DT-1 | B BLK SHRI RAM COLONY SAITAN CHOWK:PL | 1 | 990 | 19506034 | 1222 | 2019-06-15 07:30 | 493 | 2032 | 393 | 1595 | 337 | 1358 | 592 | 169.5 | 463.5 | 74 | 11 | 548.5 | 106% | 123% | 115% | 106% | 8.4841 | Loss 5-10% | 694(165.5) |  |  |  | 901(30)
1102 | 1251 | KWR | SONIA VIHAR | KWL298 | TG-KWL298A-1 | DT-1 | Delhi Police Training Center:PM | 1 | 400 | 19506396 | 460 | 2019-06-18 04:00 | 162 | 623 | 151 | 576 | 147 | 567 | 53 | 382 | 307.5 | 26.5 | 3 | 337 | 115% | 80% | 114% | 91% | 2.5361 | Loss 0-5% |  |  |  | 384(108.5) | 363(140)
1103 | 1260 | NNG | C-4 NANDNAGRI | NGR006 | TG-NGR006A-1 | DT-1 | JANTA FLAT S/S NO.1 GTB ENCLAVE:ID | 3 | 990 | 19505505 | 956.1592 | 2019-06-30 23:30 | 314.798 | 1386.409 | 276.0916 | 1206.6412 | 365.2696 | 1618.9593 | 358.0519 | 609.5 | 105.5 | 3.5 |  | 109 | 93% | 55% | 63% | 97% | 6.4544 | Loss 5-10% |  | 917(71) | 926(101.5) | 958(55)
1104 | 1260 | NNG | C-4 NANDNAGRI | NGR007 | TG-NGR007A-1 | DT-1 | JANTA FLAT S/S NO.2 GTB ENCLAVE:ID | 3 | 630 | 19505795 | 525 | 2019-06-30 23:30 | 174 | 736 | 217 | 939 | 134 | 570 | 321 | 658 | 61.5 |  |  | 61.5 | 83% | 51% | 58% | 83% | 5.62 | Loss 5-10% |  |  | 493(25.5)
1105 | 1260 | NNG | C-4 NANDNAGRI | NGR007 | TG-NGR007A-2 | DT-2 | JANTA FLAT S/S NO.2 GTB ENCLAVE:ID | 3 | 630 | 19505794 | 593 | 2019-06-03 | 164 | 687 | 186 | 786 | 244 | 1049 | 324 | 616 | 102.5 | 1.5 |  | 104 | 94% | 53% | 64% | 94% | 5.62 | Loss 5-10% |  | 528(30.5) | 602(109) | 602(65) | 506(28)
1106 | 1260 | NNG | C-4 NANDNAGRI | NGR007 | TG-NGR007A-3 | DT-3 | JANTA FLAT S/S NO.2 GTB ENCLAVE:ID | 3 | 630 | 19505801 | 518 | 2019-06-12 00:30 | 218 | 944 | 114 | 480 | 186 | 788 | 409 | 681 | 38.5 |  |  | 38.5 | 82% | 48% | 61% | 82% | 5.62 | Loss 5-10% |  |  | 535(44.5)
1107 | 1260 | NNG | C-4 NANDNAGRI | NGR008 | TG-NGR008A-1 | DT-1 | JANTA FLAT S/S NO.3 GTB ENCLAVE:ID | 2 | 990 | 19505360 | 752 | 2019-06-30 23:30 | 202 | 849 | 267 | 1140 | 283 | 1193 | 321 | 688.5 | 31 |  |  | 31 | 76% | 52% | 55% | 76% | 8.9519 | Loss 5-10%
1108 | 1260 | NNG | C-4 NANDNAGRI | NGR008 | TG-NGR008A-2 | DT-2 | JANTA FLAT S/S NO.3 GTB ENCLAVE:ID | 2 | 990 | 19505177 | 926 | 2019-06-30 00:30 | 222 | 910 | 303 | 1264 | 401 | 1678 | 666 | 634 | 84.5 | 1 |  | 85.5 | 94% | 56% | 63% | 88% | 8.9519 | Loss 5-10% |  |  | 990(79.5) | 823(34)
1109 | 1260 | NNG | C-4 NANDNAGRI | NGR014 | TG-NGR014A-1 | DT-1 | I.J K BLOCK SUNDER NAGARI:K | 2 | 990 | 19502680 | 876 | 2019-06-11 23:00 | 267 | 1129 | 303 | 1289 | 306 | 1293 | 162 | 503.5 | 215.5 |  |  | 215.5 | 88% | 81% | 76% | 88% | 5.7344 | Loss 5-10% |  | 791(55.5) | 834(171.5) | 877(134.5) | 757(51)
1110 | 1260 | NNG | C-4 NANDNAGRI | NGR015 | TG-NGR015A-2 | DT-2 | MN BLOCK SUNDER NAGARI:K | 3 | 630 | 19506466 | 555 | 2019-06-11 | 176 | 740 | 169 | 708 | 209 | 880 | 158 | 547 | 172.5 |  |  | 172.5 | 88% | 74% | 77% | 87% | 15.9324 | Loss 10-20% |  |  |  | 515(31)
1111 | 1260 | NNG | C-4 NANDNAGRI | NGR016 | TG-NGR016A-1 | DT-1 | E-1 NAND NAGARI PK WALA GAGAN CINEMA:PL | 1 | 630 | 19505497 | 553 | 2019-06-14 16:00 | 142 | 595 | 199 | 849 | 211 | 913 | 291 | 634.5 | 85.5 |  |  | 85.5 | 84% | 70% | 88% | 83% | 3.5431 | Loss 0-5% |  |  | 673(37) | 529(81)
1112 | 1260 | NNG | C-4 NANDNAGRI | NGR018 | TG-NGR018A-1 | DT-1 | E-4 NAND NAGARI:ID | 3 | 630 | 19506221 | 635 | 2019-06-08 00:30 | 234 | 1020 | 226 | 980 | 175 | 748 | 254 | 502 | 195.5 | 20 | 0.5 | 216 | 101% | 82% | 93% | 99% | 5.9363 | Loss 5-10% | 510(33) | 616(213) | 697(250) | 677(208.5) | 532(130.5)
1113 | 1260 | NNG | C-4 NANDNAGRI | NGR018 | TG-NGR018A-2 | DT-2 | E-4 NAND NAGARI:ID | 3 | 630 | 19506220 | 631 | 2019-06-29 23:00 | 206 | 865 | 250 | 1067 | 175 | 740 | 285 | 681.5 | 36 |  | 0.5 | 36.5 | 82% | 75% | 80% | 100% | 5.9363 | Loss 5-10% |  |  |  | 580(29)
1114 | 1260 | NNG | C-4 NANDNAGRI | NGR018 | TG-NGR018A-3 | DT-3 | E-4 NAND NAGARI:ID | 3 | 630 | 19506699 | 631 | 2019-06-08 21:00 | 193 | 846 | 223 | 985 | 215 | 938 | 122 | 537.5 | 178 | 2 | 0.5 | 180.5 | 91% | 84% | 92% | 100% | 5.9363 | Loss 5-10% |  | 575(97.5) | 588(276) | 526(127) | 489(48)
1115 | 1260 | NNG | C-4 NANDNAGRI | NGR019 | TG-NGR019A-1 | DT-1 | JAGAT PURI EXT.NO.1:ID | 1 | 990 | 19505917 | 883 | 2019-06-11 23:30 | 293 | 1205 | 340 | 1390 | 250 | 1017 | 323 | 583.5 | 136.5 |  |  | 136.5 | 89% | 65% | 69% | 89% | 5.6822 | Loss 5-10% |  | 984(39) | 836(111.5) | 865(72)
1116 | 1260 | NNG | C-4 NANDNAGRI | NGR020 | TG-NGR020A-1 | DT-1 | JAGAT PURI EXT.NO.2:ID | 1 | 990 | 19502686 | 755 | 2019-06-11 23:00 | 313 | 1292 | 265 | 1085 | 176 | 723 | 498 | 695 | 25 |  |  | 25 | 76% | 54% | 56% | 76% | 4.9826 | Loss 0-5%
1117 | 1260 | NNG | C-4 NANDNAGRI | NGR021 | TG-NGR021A-2 | DT-2 | A-4 NAND NAGARI:ID | 3 | 990 | 19505803 | 789 | 2019-06-30 00:30 | 315 | 1331 | 214 | 890 | 259 | 1077 | 384 | 642.5 | 75 |  |  | 75 | 80% | 70% | 79% | 79% | 8.6786 | Loss 5-10%
1118 | 1260 | NNG | C-4 NANDNAGRI | NGR021 | TG-NGR021A-3 | DT-3 | A-4 NAND NAGARI:ID | 3 | 990 | 19505342 | 805 | 2019-06-14 15:00 | 313 | 1442 | 167 | 758 | 325 | 1463 | 695 | 683.5 | 34.5 |  |  | 34.5 | 75% | 65% | 81% | 75% | 8.6786 | Loss 5-10%
1119 | 1260 | NNG | C-4 NANDNAGRI | NGR022 | TG-NGR022A-3 | DT-3 | B-4 NAND NAGARI AKHADA WALA :ID | 4 | 630 | 19505435 | 526 | 2019-06-01 23:00 | 168 | 704 | 216 | 913 | 142 | 586 | 287 | 693 | 27 |  |  | 27 | 76% | 66% | 67% | 84% | 4.4724 | Loss 0-5%
1120 | 1260 | NNG | C-4 NANDNAGRI | NGR022 | TG-NGR022A-4 | DT-4 | B-4 NAND NAGARI AKHADA WALA :ID | 4 | 630 | 19506004 | 501 | 2019-06-29 23:30 | 170 | 725 | 194 | 839 | 137 | 598 | 209 | 671.5 | 48 |  |  | 48 | 78% | 64% | 71% | 80% | 4.4724 | Loss 0-5% |  |  | 525(40)
1121 | 1260 | NNG | C-4 NANDNAGRI | NGR023 | TG-NGR023A-2 | DT-2 | C BLOCK COMPLAINT CENTRE NNG:ID | 4 | 990 | 19505918 | 869 | 2019-06-30 | 296 | 1316 | 280 | 1250 | 294 | 1294 | 59 | 643.5 | 76 |  |  | 76 | 88% | 68% | 76% | 81% | 8.2969 | Loss 5-10% |  |  | 879(38)
1122 | 1260 | NNG | C-4 NANDNAGRI | NGR023 | TG-NGR023A-3 | DT-3 | C BLOCK COMPLAINT CENTRE NNG:ID | 4 | 630 | 19502635 | 585 | 2019-06-29 23:30 | 203 | 838 | 197 | 805 | 185 | 766 | 63 | 532.5 | 183.5 | 3 |  | 186.5 | 92% | 73% | 73% | 93% | 8.2969 | Loss 5-10% |  | 519(51.5) | 595(186.5) | 556(143.5) | 544(77.5)
1123 | 1260 | NNG | C-4 NANDNAGRI | NGR030 | TG-NGR030A-1 | DT-1 | MANDOLI S/S-4 (PANI KI TANKI) :PL | 2 | 990 | 19506090 | 838 | 2019-06-12 01:00 | 282 | 1137 | 252 | 1014 | 305 | 1235 | 192 | 665.5 | 49.5 |  |  | 49.5 | 85% | 60% | 73% | 80% | 10.2836 | Loss 10-20%
1124 | 1260 | NNG | C-4 NANDNAGRI | NGR035 | TG-NGR035A-1 | DT-1 | MANDOLI EXTN.NO.1,GALI NO.-9:ID | 2 | 400 | 19502142 | 388 | 2019-06-02 21:30 | 155 | 702 | 116 | 521 | 117 | 524 | 179 | 614 | 96 | 9 |  | 105 | 94% | 75% | 86% | 97% | 8.9484 | Loss 5-10% |  | 403(157) | 419(287) | 410(147) |  | 318(27)
1125 | 1260 | NNG | C-4 NANDNAGRI | NGR035 | TG-NGR035A-2 | DT-2 | MANDOLI EXTN.NO.1,GALI NO.-9:ID | 2 | 990 | 19506611 | 874 | 2019-06-10 22:00 | 307 | 1305 | 236 | 996 | 331 | 1418 | 378 | 621 | 97.5 |  |  | 97.5 | 83% | 80% | 88% | 88% | 8.9484 | Loss 5-10%
1126 | 1260 | NNG | C-4 NANDNAGRI | NGR044 | TG-NGR044A-1 | DT-1 | SAFAI KARAMCHARI NAND NAGARI-E BLK:ID | 1 | 400 | 19503383 | 336 | 2019-06-09 23:00 | 112 | 500 | 124 | 549 | 100 | 445 | 90 | 592.5 | 127.5 |  |  | 127.5 | 83% | 60% | 62% | 84% | 5.4694 | Loss 5-10% |  |  | 327(69) | 310(24)
1127 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1002 | TG-LO1002A-1 | DT-1 | B-BLOCK MEET NAGAR:ID | 2 | 990 | 19505636 | 968.3635 | 2019-06-11 01:00 | 239.9317 | 1005.9609 | 421.3517 | 1775.2335 | 307.0801 | 1288.0338 | 674.0583 | 621 | 82 | 2.5 |  | 84.5 | 98% | 73% | 82% | 89% | 8.8071 | Loss 5-10% |  | 498(42) | 645(180) | 606(80.5) | 519(37.5)
1128 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1009 | TG-LO1009A-1 | DT-1 | GOKUL PUR VILL NO.KAPOOR WALA PETROL:PL | 3 | 990 | 19506309 | 770 | 2019-06-26 15:30 | 234 | 1015 | 265 | 1151 | 271 | 1170 | 146 | 683 | 35 |  |  | 35 | 43% | 37% | 78% | 45% | 7.8914 | Loss 5-10% |  | 884(79) | 914(132.5) | 957(170.5) | 958(148.5) | 891(145.5)
1129 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1017 | TG-LO1017A-1 | DT-1 | E JYOTI NAGAR BEHAIND JOYATI NURSING:ID | 4 | 630 | 19502178 | 578 | 2019-06-30 01:30 | 143 | 624 | 209 | 923 | 226 | 1002 | 345 | 580.5 | 48 | 0.5 |  | 48.5 | 92% | 66% | 61% | 84% | 7.002 | Loss 5-10% |  | 716(130) | 797(236) | 706(156) | 581(107)
1130 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1017 | TG-LO1017A-2 | DT-2 | E JYOTI NAGAR BEHAIND JOYATI NURSING:ID | 4 | 990 | 19504503 | 1223 | 2019-06-11 23:30 | 299 | 1281 | 407 | 1753 | 517 | 2254 | 843 | 409 | 108.5 | 28 | 29 | 165.5 | 120% | 73% | 95% | 124% | 7.002 | Loss 5-10%
1131 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1017 | TG-LO1017A-3 | DT-3 | E JYOTI NAGAR BEHAIND JOYATI NURSING:ID | 4 | 990 | 19502206 | 1003 | 2019-06-30 01:30 | 394 | 1696 | 354 | 1507 | 255 | 1076 | 551 | 590 | 113 | 9.5 | 0.5 | 123 | 101% | 71% | 67% | 97% | 7.002 | Loss 5-10%
1132 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1017 | TG-LO1017A-4 | DT-4 | E JYOTI NAGAR BEHAIND JOYATI NURSING:ID | 4 | 630 | 19506358 | 587 | 2019-06-30 01:00 | 166 | 690 | 219 | 922 | 202 | 850 | 206 | 661.5 | 53.5 | 1 |  | 54.5 | 93% | 63% | 80% | 84% | 7.002 | Loss 5-10%
1133 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1024 | TG-LO1024A-1 | DT-1 | EAST OF LONI ROAD,MIG,S/STN-7:ID | 2 | 400 | 19502176 | 365 | 2019-06-03 02:30 | 112 | 481 | 114 | 485 | 139 | 598 | 115 | 650 | 69 | 0.5 |  | 69.5 | 91% | 46% | 61% | 89% | 4.112 | Loss 0-5% |  |  |  | 327(26.5)
1134 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1024 | TG-LO1024A-2 | DT-2 | EAST OF LONI ROAD,MIG,S/STN-7:ID | 2 | 400 | 19502202 | 335 | 2019-06-11 23:30 | 146 | 617 | 95 | 404 | 93 | 401 | 215 | 652 | 68 |  |  | 68 | 83% | 45% | 67% | 84% | 4.112 | Loss 0-5% |  | 395(76) | 465(149) | 332(25.5)
1135 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1028 | TG-LO1028A-1 | DT-1 | D-BLOCK ASHOK NAGAR GALI NO-3:ID | 3 | 990 | 19503018 | 950 | 2019-06-30 | 381 | 1641 | 319 | 1392 | 250 | 1096 | 472 | 682.5 | 29.5 | 4.5 |  | 34 | 96% | 65% | 70% | 96% | 5.9352 | Loss 5-10%
1136 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1028 | TG-LO1028A-2 | DT-2 | D-BLOCK ASHOK NAGAR GALI NO-3:ID | 3 | 630 | 19503472 | 549 | 2019-06-10 23:30 | 170 | 759 | 178 | 800 | 201 | 892 | 118 | 619 | 97.5 |  |  | 97.5 | 85% | 61% | 69% | 87% | 5.9352 | Loss 5-10%
1137 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1028 | TG-LO1028A-3 | DT-3 | D-BLOCK ASHOK NAGAR GALI NO-3:ID | 3 | 990 | 19504095 | 941 | 2019-06-10 23:30 | 334 | 1502 | 324 | 1446 | 283 | 1246 | 233 | 617 | 94 | 5.5 |  | 99.5 | 93% | 65% | 71% | 95% | 5.9352 | Loss 5-10% |  | 804(32.5)
1138 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1029 | TG-LO1029A-1 | DT-1 | B-BLOCK ASHOK NAGAR SCHOOL WALA:K | 3 | 990 | 19506195 | 1128.7818 | 2019-06-01 01:30 | 384.6673 | 1712.1435 | 386.7725 | 1691.1785 | 357.342 | 1571.0103 | 131.9062 | 556 | 135.5 | 19 | 3.5 | 158 | 114% | 82% | 79% | 99% | 4.1572 | Loss 0-5% |  | 931(47) | 1067(122.5) | 897(54)
1139 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1029 | TG-LO1029A-2 | DT-2 | B-BLOCK ASHOK NAGAR SCHOOL WALA:K | 3 | 630 | 19502179 | 595 | 2019-06-30 02:00 | 144 | 616 | 245 | 1057 | 207 | 890 | 386 | 437 | 60 | 2.5 |  | 62.5 | 94% | 72% | 68% | 88% | 4.1572 | Loss 0-5% |  | 775(217) | 822(230) | 742(220.5) | 651(179) | 642(50)
1140 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1029 | TG-LO1029A-3 | DT-3 | B-BLOCK ASHOK NAGAR SCHOOL WALA:K | 3 | 990 | 19502205 | 1145 | 2019-06-12 00:30 | 408 | 1689 | 281 | 1157 | 455 | 1898 | 662 | 544.5 | 120 | 34.5 | 14.5 | 169 | 116% | 102% | 76% | 107% | 4.1572 | Loss 0-5% |  |  | 836(24) | 915(26)
1141 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1031 | TG-LO1031A-1 | DT-1 | HARDEV PURI NO.1:ID | 1 | 990 | 19502158 | 805 | 2019-06-11 | 198 | 857 | 356 | 1584 | 251 | 1124 | 637 | 642.5 | 52 |  |  | 52 | 81% | 54% | 70% | 81% | 14.1886 | Loss 10-20%
1142 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1032 | TG-LO1032A-1 | DT-1 | HARDEVPURI NO.2 ( JOSHI WALA):PL | 1 | 990 | 19506310 | 1146 | 2019-06-29 23:00 | 375 | 1697 | 464 | 2148 | 306 | 1378 | 670 | 470 | 142.5 | 43 | 35 | 220.5 | 114% | 78% | 89% | 116% | 5.6375 | Loss 5-10% |  |  | 1301(238) | 1366(245) | 1037(153)
1143 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1033 | TG-LO1033A-1 | DT-1 | E-1 BLK ASHOK NAGAR.KANCH WALA NR S BHAWAN:K | 2 | 630 | 19504098 | 587 | 2019-06-03 01:30 | 223 | 879 | 235 | 948 | 130 | 515 | 403 | 606.5 | 111 | 2.5 |  | 113.5 | 93% | 69% | 72% | 91% | 12.964 | Loss 10-20% |  |  |  |  | 489(26)
1144 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1033 | TG-LO1033A-2 | DT-2 | E-1 BLK ASHOK NAGAR.KANCH WALA NR S BHAWAN:K | 2 | 630 | 19505663 | 490 | 2019-06-02 23:00 | 160 | 676 | 175 | 736 | 155 | 640 | 84 | 685.5 | 33 |  |  | 33 | 76% | 54% | 55% | 78% | 12.964 | Loss 10-20%
1145 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1034 | TG-LO1034A-2 | DT-2 | ASHOK NAGAR NO EXTN NO 1 KACHCHI CLY:PL | 2 | 630 | 19505269 | 711 | 2019-06-10 23:30 | 186 | 850 | 201 | 900 | 324 | 1534 | 660 | 488 | 174.5 | 35.5 | 18 | 228 | 113% | 77% | 100% | 113% | 3.8141 | Loss 0-5% |  | 569(70) | 624(185) | 627(62.5) | 519(47.5)
1146 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1035 | TG-LO1035A-1 | DT-1 | NATHU COLONY:K | 2 | 990 | 19506177 | 912 | 2019-06-11 23:30 | 248 | 1090 | 324 | 1443 | 340 | 1541 | 411 | 621 | 94 | 0.5 |  | 94.5 | 87% | 69% | 72% | 92% | 5.0527 | Loss 5-10%
1147 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1043 | TG-LO1043A-1 | DT-1 | LALITA MANDIR ASHOK NAGAR D BLK:PL | 1 | 990 | 19502640 | 907 | 2019-06-26 23:30 | 319 | 1378 | 324 | 1408 | 264 | 1144 | 250 | 588.5 | 125 | 1 |  | 126 | 90% | 68% | 69% | 92% | 5.4957 | Loss 5-10% |  |  | 865(80) | 855(47.5)
1148 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1045 | TG-LO1045A-1 | DT-1 | HARIJAN BASTI, AKHADA EAST GOKAL PUR:PL | 2 | 990 | 19505674 | 879 | 2019-06-01 10:30 | 297 | 1284 | 292 | 1257 | 290 | 1252 | 30 | 650 | 69 |  |  | 69 | 51% | 62% | 89% | 49% | 25.1555 | Loss 20-30%
1149 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1047 | TG-LO1047A-1 | DT-1 | D-1 ASHOK NAGAR WAZIRA BAD ROAD:PL | 1 | 630 | 19505923 | 725 | 2019-06-02 18:30 | 206 | 895 | 283 | 1219 | 237 | 1051 | 281 | 498 | 163 | 32.5 | 19.5 | 215 | 111% | 93% | 115% | 115% | 4.363 | Loss 0-5% | 660(33) | 747(291.5) | 764(470) | 728(198.5) | 597(129)
1150 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1053 | TG-LO1053A-1 | DT-1 | D 1/1 BLK ASHOK NAGAR DP :PL | 1 | 990 | 19505926 | 928 | 2019-06-29 23:30 | 394 | 1684 | 302 | 1281 | 232 | 981 | 611 | 660.5 | 54.5 | 1 |  | 55.5 | 91% | 74% | 79% | 94% | 6.744 | Loss 5-10%
1151 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1055 | TG-LO1055A-1 | DT-1 | LONI BORDER S/S NO-1 | 1 | 630 | 19505051 | 653 | 2019-06-10 22:30 | 272 | 1185 | 206 | 871 | 175 | 755 | 385 | 535 | 166 | 5 | 0.5 | 171.5 | 92% | 85% | 98% | 104% | 25.6375 | Loss 20-30% |  |  | 625(72.5) | 594(44)
1152 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1056 | TG-LO1056A-1 | DT-1 | LONI BORDER S/S NO-2 | 1 | 630 | 19503678 | 875 | 2019-06-18 17:30 | 357 | 1543 | 240 | 1023 | 279 | 1166 | 466 | 174.5 | 451.5 | 46.5 | 13.5 | 511.5 | 101% | 114% | 139% | 117% | 36.826 | Loss >30% | 615(43) | 589(164.5) | 793(390) | 770(334.5) | 847(279) | 816(112.5)
1153 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1060 | TG-LO1060A-1 | DT-1 | DURGA PURI MAIN GALI - 10:ID | 3 | 630 | 19505223 | 897.5917 | 2019-06-08 02:00 | 336.1458 | 1603.2901 | 265.3966 | 1236.1852 | 296.0493 | 1392.649 | 319.0741 | 450.5 | 130.5 | 45.5 | 42.5 | 218.5 | 142% | 84% | 93% | 114% | 5.8835 | Loss 5-10% |  | 666(129.5) | 712(229) | 673(168.5) | 630(127)
1154 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1060 | TG-LO1060A-2 | DT-2 | DURGA PURI MAIN GALI - 10:ID | 3 | 990 | 19506308 | 1286 | 2019-06-08 01:30 | 307 | 1392 | 465 | 2154 | 514 | 2263 | 822 | 324.5 | 293.5 | 62 | 37 | 392.5 | 130% | 70% | 101% | 117% | 5.8835 | Loss 5-10%
1155 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1061 | TG-LO1061A-1 | DT-1 | JAGAT PURI MAIN:PL | 2 | 630 | 19503373 | 603 | 2019-06-11 23:00 | 174 | 741 | 225 | 964 | 204 | 873 | 194 | 605 | 110.5 | 2.5 |  | 113 | 89% | 62% | 69% | 96% | 4.2091 | Loss 0-5% | 584(54.5) | 762(340) | 608(90) | 529(41.5)
1156 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1061 | TG-LO1061A-2 | DT-2 | JAGAT PURI MAIN:PL | 2 | 630 | 19506558 | 936.9566 | 2019-06-11 19:30 | 336.9131 | 1386.8161 | 248.7815 | 1032.8027 | 351.262 | 1486.6975 | 413.1115 | 556 | 154 | 3.5 | 1 | 158.5 | 119% | 71% | 149% | 99% | 4.2091 | Loss 0-5%
1157 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1063 | TG-LO1063A-1 | DT-1 | JAG JIVAN NAGAR:PL | 1 | 990 | 19506222 | 1078 | 2019-06-06 00:30 | 322 | 1419 | 418 | 1857 | 338 | 1510 | 400 | 577 | 128.5 | 8.5 | 2 | 139 | 109% | 75% | 74% | 94% | 10.0496 | Loss 10-20% |  | 863(41) | 970(91.5) | 801(28)
1158 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1066 | TG-LO1066A-1 | DT-1 | CHANDER LOK:PL | 1 | 990 | 19505936 | 1182.4515 | 2019-06-30 01:00 | 360.6617 | 1579.0102 | 475.0448 | 2102.8987 | 346.7449 | 1504.8386 | 564.6399 | 431.5 | 192.5 | 49 | 44.5 | 286 | 119% | 73% | 94% | 117% | 11.0792 | Loss 10-20% |  | 987(88.5) | 1090(205) | 998(134.5) | 979(99.5)
1159 | 1260 | NNG | SUDAMA PURI | LO2004 | TG-LO2004A-1 | DT-1 | JYOTI COLONY NO.1:K | 2 | 630 | 19506079 | 874 | 2019-06-11 00:30 | 295 | 1306 | 249 | 1085 | 330 | 1457 | 324 | 386 | 192.5 | 51.5 | 89 | 333 | 139% | 79% | 101% | 130% | 9.3425 | Loss 5-10% | 666(46.5) | 1028(330.5) | 933(546) |  | 625(95)
1160 | 1260 | NNG | SUDAMA PURI | LO2004 | TG-LO2004A-2 | DT-2 | JYOTI COLONY NO.1:K | 2 | 400 | 19505874 | 402 | 2019-06-11 01:00 | 186 | 802 | 94 | 395 | 122 | 515 | 362 | 603 | 111.5 | 4 | 0.5 | 116 | 100% | 62% | 61% | 97% | 9.3425 | Loss 5-10% |  | 400(80.5) | 426(165)
1161 | 1260 | NNG | SUDAMA PURI | LO2006 | TG-LO2006A-2 | DT-2 | JYOTI COLONY NO.3:K | 2 | 630 | 19506078 | 689 | 2019-06-12 00:30 | 283 | 1176 | 199 | 814 | 207 | 854 | 344 | 632 | 69 | 15 | 3 | 87 | 109% | 69% | 83% | 102% | 7.8995 | Loss 5-10%
1162 | 1260 | NNG | SUDAMA PURI | LO2007 | TG-LO2007A-1 | DT-1 | AMBEDKAR PARK:PL | 2 | 990 | 19506615 | 974 | 2019-06-10 23:00 | 344 | 1494 | 437 | 1859 | 193 | 819 | 914 | 585.5 | 121 | 10.5 |  | 131.5 | 95% | 66% | 76% | 98% | 7.6514 | Loss 5-10% | 913(24.5) |  | 1386(102) | 1073(104.5)
1163 | 1260 | NNG | SUDAMA PURI | LO2007 | TG-LO2007A-2 | DT-2 | AMBEDKAR PARK:PL | 2 | 630 | 19506514 | 774 | 2019-06-11 01:00 | 262 | 1120 | 293 | 1233 | 218 | 916 | 279 | 489 | 135 | 50.5 | 42.5 | 228 | 123% | 71% | 87% | 113% | 7.6514 | Loss 5-10%
1164 | 1260 | NNG | SUDAMA PURI | LO2009 | TG-LO2009A-2 | DT-2 | SHIV MANDIR 100 FT. RD:PL | 2 | 400 | 19506549 | 405 | 2019-06-10 23:00 | 167 | 721 | 123 | 519 | 116 | 496 | 215 | 566.5 | 130.5 | 21 | 0.5 | 152 | 95% | 69% | 77% | 101% | 7.0932 | Loss 5-10%
1165 | 1260 | NNG | SUDAMA PURI | LO2012 | TG-LO2012A-1 | DT-1 | BABAR PUR VILLAGE:PL | 2 | 630 | 19502729 | 525 | 2019-06-11 23:30 | 140 | 589 | 181 | 772 | 203 | 869 | 246 | 641 | 78 |  |  | 78 | 82% | 65% | 69% | 83% | 21.0092 | Loss 20-30% | 636(147) | 638(264.5)
1166 | 1260 | NNG | SUDAMA PURI | LO2013 | TG-LO2013A-1 | DT-1 | MAHA DEVI SCHOOL:PL | 2 | 630 | 19502715 | 716 | 2019-06-03 | 263 | 1160 | 217 | 961 | 236 | 1053 | 172 | 549 | 121.5 | 37 | 11 | 169.5 | 114% | 76% | 74% | 108% | 6.8494 | Loss 5-10% |  | 628(85.5) | 670(211.5) | 672(150) | 585(108)
1167 | 1260 | NNG | SUDAMA PURI | LO2013 | TG-LO2013A-2 | DT-2 | MAHA DEVI SCHOOL:PL | 2 | 630 | 19502722 | 550 | 2019-06-29 00:30 | 131 | 562 | 207 | 905 | 212 | 928 | 355 | 683.5 | 33 |  |  | 33 | 87% | 62% | 72% | 82% | 6.8494 | Loss 5-10%
1168 | 1260 | NNG | SUDAMA PURI | LO2016 | TG-LO2016A-1 | DT-1 | SUDAMA PURI NO.3:PL | 1 | 990 | 19506468 | 992.4833 | 2019-06-27 00:30 | 275.2841 | 1161.2912 | 279.1033 | 1187.7747 | 438.0959 | 1848.194 | 674.0513 | 511.5 | 187 | 19 | 0.5 | 206.5 | 100% | 69% | 84% | 96% | 8.2144 | Loss 5-10% |  |  | 871(98.5) | 877(76.5) | 851(99)
1169 | 1260 | NNG | SUDAMA PURI | LO2018 | TG-LO2018A-1 | DT-1 | SUDAMAPURI NO. 4:PL | 1 | 400 | 19506829 | 481 | 2019-06-09 23:30 | 178 | 755 | 130 | 552 | 174 | 735 | 194 | 360.5 | 209.5 | 65 | 84 | 358.5 | 119% | 86% | 89% | 120% | 6.1208 | Loss 5-10% |  | 314(28) |  | 399(38) |  | 349(36)
1170 | 1260 | NNG | SUDAMA PURI | LO2020 | TG-LO2020A-1 | DT-1 | BALBIR NAGAR EXT.:PL | 2 | 990 | 19504551 | 1475 | 2019-06-11 00:30 | 451 | 1824 | 478 | 1967 | 546 | 2289 | 412 | 236.5 | 217 | 96 | 165.5 | 478.5 | 149% | 87% | 131% | 145% | 5.8898 | Loss 5-10% |  | 1201(203) | 1199(417.5) | 1239(291) | 1014(214) | 862(34)
1171 | 1260 | NNG | SUDAMA PURI | LO2021 | TG-LO2021A-1 | DT-1 | D BLOCK KABIR NAGAR(SHAMSHAN GHAT) | 3 | 990 | 19505805 | 972 | 2019-06-01 23:30 | 368 | 1557 | 310 | 1294 | 294 | 1235 | 296 | 628.5 | 82.5 | 7.5 |  | 90 | 98% | 79% | 89% | 98% | 11.5993 | Loss 10-20% |  |  | 799(30.5)
1172 | 1260 | NNG | SUDAMA PURI | LO2023 | TG-LO2023A-1 | DT-1 | A BLOCK KABIR NAGAR:ID | 3 | 990 | 19502671 | 975 | 2019-06-01 | 331 | 1301 | 356 | 1417 | 288 | 1144 | 237 | 506.5 | 200.5 | 12.5 |  | 213 | 98% | 84% | 82% | 96% | 13.2709 | Loss 10-20% |  | 950(173.5) | 1019(210) | 827(41.5) | 864(82)
1173 | 1260 | NNG | SUDAMA PURI | LO2025 | TG-LO2025A-1 | DT-1 | B-BLOCK KABIR NAGAR:ID | 2 | 990 | 19506075 | 816 | 2019-06-01 | 300 | 1291 | 242 | 1037 | 274 | 1174 | 220 | 692 | 27 |  |  | 27 | 82% | 71% | 78% | 79% | 13.3839 | Loss 10-20% |  | 879(116.5) | 908(131.5) | 788(36.5)
1174 | 1260 | NNG | SUDAMA PURI | LO2026 | TG-LO2026A-1 | DT-1 | C BLOCK KABIR NAGAR | 2 | 990 | 19502709 | 960 | 2019-06-01 01:00 | 351 | 1503 | 292 | 1308 | 317 | 1355 | 176 | 558 | 150 | 9.5 |  | 159.5 | 97% | 81% | 95% | 95% | 12.6474 | Loss 10-20% | 808(37) | 1128(202) | 1185(401) | 1091(419) | 1047(310) | 842(92)
1175 | 1260 | NNG | SUDAMA PURI | LO2028 | TG-LO2028A-1 | DT-1 | HARIJAN BASTI WEST JYOTI NARAR:ID | 2 | 630 | 19502724 | 622 | 2019-06-29 23:30 | 234 | 985 | 190 | 795 | 197 | 822 | 178 | 543 | 153 | 24 |  | 177 | 97% | 68% | 71% | 99% | 6.1603 | Loss 5-10% |  |  | 599(53) | 639(100) | 510(47.5)
1176 | 1260 | NNG | SUDAMA PURI | LO2028 | TG-LO2028A-2 | DT-2 | HARIJAN BASTI WEST JYOTI NARAR:ID | 2 | 400 | 19502719 | 467 | 2019-06-11 00:30 | 95 | 398 | 187 | 817 | 186 | 807 | 414 | 469 | 131 | 56.5 | 63.5 | 251 | 117% | 78% | 81% | 116% | 6.1603 | Loss 5-10% | 405(39) | 613(310) | 543(186) | 452(140.5) | 354(88.5)
1177 | 1260 | NNG | SUDAMA PURI | LO2029 | TG-LO2029A-2 | DT-2 | KARDAM MARG KHET WALA:-PL | 2 | 990 | 19506895 | 1018 | 2019-06-11 23:00 | 291 | 1264 | 425 | 1883 | 302 | 1302 | 601 | 567.5 | 126.5 | 23 | 1 | 150.5 | 98% | 57% | 78% | 103% | 7.7449 | Loss 5-10% |  |  | 1041(111) | 937(55.5)
1178 | 1260 | NNG | SUDAMA PURI | LO2030 | TG-LO2030A-1 | DT-1 | KARDAM PURI AZAD CHOWK:-ID | 2 | 990 | 19506684 | 892 | 2019-06-01 | 253 | 1062 | 343 | 1453 | 296 | 1236 | 339 | 615.5 | 104 | 0.5 |  | 104.5 | 90% | 73% | 82% | 87% | 13.4219 | Loss 10-20% |  | 782(36) | 804(27.5) | 932(53) | 790(33.5)
1179 | 1260 | NNG | SUDAMA PURI | LO2031 | TG-LO2031A-1 | DT-1 | NEW KARDAMPURI NO 1 GALI NO -4:PL | 1 | 630 | 19506465 | 603 | 2019-06-29 23:30 | 176 | 784 | 259 | 1183 | 168 | 699 | 448 | 501.5 | 193 | 14.5 |  | 207.5 | 96% | 82% | 91% | 96% | 9.041 | Loss 5-10% |  |  |  |  | 595(67)
1180 | 1260 | NNG | SUDAMA PURI | LO2032 | TG-LO2032A-1 | DT-1 | NORTH CHAJJUPUR:ID | 2 | 990 | 19502700 | 1029 | 2019-06-11 02:00 | 337 | 1402 | 310 | 1286 | 382 | 1599 | 275 | 559.5 | 132 | 23 | 3.5 | 158.5 | 104% | 63% | 72% | 101% | 7.9983 | Loss 5-10% |  | 1002(82.5) | 983(149.5) | 989(105) | 830(64.5)
1181 | 1260 | NNG | SUDAMA PURI | LO2041 | TG-LO2041A-1 | DT-1 | West Jyoti Ngr(Beh. Gopal Nur Home):-PL | 2 | 990 | 19506073 | 900 | 2019-06-11 00:30 | 354 | 1474 | 295 | 1232 | 251 | 1046 | 372 | 649 | 70.5 | 0.5 |  | 71 | 91% | 50% | 70% | 89% | 5.5294 | Loss 5-10% |  | 1177(29.5) | 983(91.5) | 1045(34.5)
1182 | 1260 | NNG | SUDAMA PURI | LO2044 | TG-LO2044A-2 | DT-2 | CNG STATION LONI ROAD:PM | 2 | 400 | 19506633 | 355 | 2019-06-04 06:00 | 118 | 481 | 118 | 482 | 119 | 489 | 8 | 666.5 | 52.5 |  |  | 52.5 | 87% | 89% | 87% | 83% | 5.4597 | Loss 5-10%
1183 | 1260 | NNG | SUDAMA PURI | LO2046 | TG-LO2046A-1 | DT-1 | SUDAMAPURI S/S- 5 Nr. BABARPUR BUS TERM. | 1 | 630 | 19505667 | 886 | 2019-06-08 01:30 | 312 | 1364 | 250 | 1077 | 324 | 1419 | 319 | 425.5 | 209.5 | 67.5 | 14.5 | 291.5 | 141% | 82% | 87% | 107% | 17.3868 | Loss 10-20% | 611(31.5) | 769(276) | 836(451.5) | 725(219.5) | 567(130.5)

## Complete SSTn Loading Details
Overloaded DT in the SSTN
Not Overloaded DTs in the SSTn
Overloaded DTs June2019(Loading>70% for >24 Hrs in the month)
[11 empty] | Peak KVA Condition | [8 empty] | Load Category Wise Duration (Hours) |  |  |  |  | Peak Load % Across Time-Slots | [5 empty] | Last Summer Peak Loading KVA (>70% Overloading Hrs)
Sr.No. | SDO | DIVISION | ZONE | SSTN SAP CODE | DT CODE | DT | SSTN NAME | Total DTs In Sstn | KVA RATING | DT METER NO. | Peak KVA | Peak KVA Date and Time | KVA_R | I (AMP)_R | KVA_Y | I (AMP)_Y | KVA_B | I (AMP)_B | Neutral Current | Loading<70% | 70%Loading90% | 90%Loading100% | Loading>100% | > 70% Total Overloading Hours | 00:00 to 06:00 | 06:00 to 09:00 | 09:00 to 21:00 | 21:00 to 00:00 | Rolling T&D Loss May 2019 | Loss Band | 2018-04-01 | 2018-05-01 | 2018-06-01 | 2018-07-01 | 2018-08-01 | 2018-09-01 | PF June2019
1 | 1110 | CCK | HAMILTON ROAD | HAM003 | TG-HAM003A-1 | DT-1 | HAMILTON ROAD STN:ID | 2 | 990 | 19500270 | 467 | 2019-06-15 15:00 | 166 | 729 | 139 | 607 | 162 | 703 | 111 | 719.5 |  |  |  | 0 | 6% | 5% | 47% | 9% | 9.7403 | Loss 5-10%
2 | 1110 | CCK | HAMILTON ROAD | HAM003 | TG-HAM003A-2 | DT-2 | HAMILTON ROAD STN:ID | 2 | 990 | 19500269 | 809 | 2019-06-13 15:30 | 297 | 1288 | 271 | 1177 | 242 | 1028 | 226 | 647 | 72 |  |  | 72 | 38% | 28% | 82% | 38% | 9.7403 | Loss 5-10% |  |  | 827(90.5) | 850(58.5)
3 | 1110 | CCK | HAMILTON ROAD | HAM009 | TG-HAM009A-1 | DT-1 | CHABBI GANJ:PL | 1 | 990 | 19503476 | 970 | 2019-06-13 15:00 | 333 | 1326 | 335 | 1393 | 302 | 1238 | 134 | 648.5 | 66 | 4 |  | 70 | 19% | 17% | 98% | 21% | 5.4569 | Loss 5-10% |  |  | 733(28.5)
4 | 1110 | CCK | HAMILTON ROAD | HAM017 | TG-HAM017A-1 | DT-1 | KASHMERE GATE POLICE THANA:PL | 1 | 990 | 19500234 | 763 | 2019-06-15 16:00 | 213 | 871 | 269 | 1110 | 281 | 1145 | 258 | 638.5 | 57.5 |  |  | 57.5 | 15% | 13% | 77% | 16% | 10.6668 | Loss 10-20% |  |  | 787(82) | 810(48)
5 | 1110 | CCK | HAMILTON ROAD | HAM034 | TG-HAM034A-1 | DT-1 | YAMUNA BAZAR GHAT DELHI 6 | 1 | 630 | 19505145 | 928.7217 | 2019-06-15 13:00 | 326.9159 | 1458.3392 | 334.054 | 1525.2215 | 267.7518 | 1168.0488 | 328.8724 | 672 | 47 |  | 0.5 | 47.5 | 74% | 59% | 147% | 75% | 12.3222 | Loss 10-20%
6 | 1110 | CCK | LAHORI GATE | LHR001 | TG-LHR001A-1 | DT-1 | MOHALLA NIHARIYAN:K | 2 | 990 | 19505697 | 996 | 2019-06-11 01:30 | 333 | 1383 | 328 | 1371 | 335 | 1408 | 32 | 312.5 | 377.5 | 27.5 | 0.5 | 405.5 | 101% | 89% | 97% | 90% | 27.2996 | Loss 20-30% |  |  |  |  | 965(264.5) | 1330(127)
7 | 1110 | CCK | LAHORI GATE | LHR001 | TG-LHR001A-2 | DT-2 | MOHALLA NIHARIYAN:K | 2 | 990 | 19501527 | 527 | 2019-06-29 17:00 | 156 | 642 | 192 | 783 | 179 | 730 | 124 | 718 |  |  |  | 0 | 43% | 39% | 53% | 40% | 27.2996 | Loss 20-30%
8 | 1110 | CCK | LAHORI GATE | LHR003 | TG-LHR003A-1 | DT-1 | MOHALLA SHAHGANJ:K | 2 | 990 | 19505363 | 878 | 2019-06-17 23:00 | 377 | 1612 | 172 | 713 | 329 | 1478 | 840 | 617.5 | 99 |  |  | 99 | 77% | 70% | 83% | 89% | 17.3245 | Loss 10-20% |  | 1075(132) | 981(295) | 898(208) | 917(75)
9 | 1110 | CCK | LAHORI GATE | LHR003 | TG-LHR003A-2 | DT-2 | MOHALLA SHAHGANJ:K | 2 | 990 | 19501626 | 761 | 2019-06-28 17:00 | 260 | 1101 | 253 | 1074 | 249 | 1055 | 40 | 707 | 9.5 |  |  | 9.5 | 64% | 58% | 77% | 65% | 17.3245 | Loss 10-20%
10 | 1110 | CCK | LAHORI GATE | LHR015 | TG-LHR015A-1 | DT-1 | ZEENAT MAHAL:K | 2 | 990 | 19501530 | 879 | 2019-06-03 04:00 | 304 | 1254 | 280 | 1148 | 295 | 1212 | 93 | 587.5 | 132 |  |  | 132 | 89% | 77% | 73% | 77% | 21.8345 | Loss 20-30% |  |  | 805(113.5) | 834(75.5)
11 | 1110 | CCK | LAHORI GATE | LHR015 | TG-LHR015A-2 | DT-2 | ZEENAT MAHAL:K | 2 | 630 | 19505377 | 204 | 2019-06-02 01:30 | 73 | 299 | 35 | 143 | 95 | 387 | 213 | 720 |  |  |  | 0 | 32% | 28% | 31% | 32% | 21.8345 | Loss 20-30%
12 | 1110 | CCK | LAHORI GATE | LHR017 | TG-LHR017A-1 | DT-1 | LAL QUAN:PL | 1 | 990 | 19506435 | 1085 | 2019-06-05 02:30 | 324 | 1380 | 244 | 1043 | 517 | 2313 | 1140 | 641.5 | 75.5 | 1 | 0.5 | 77 | 110% | 67% | 96% | 78% | 27.2272 | Loss 20-30% |  |  | 894(38.5)
13 | 1110 | CCK | LAHORI GATE | LHR018 | TG-LHR018A-1 | DT-1 | BARSHABULLA:ID | 2 | 990 | 19501501 | 842 | 2019-06-12 16:30 | 245 | 1096 | 286 | 1296 | 311 | 1422 | 285 | 622.5 | 97.5 |  |  | 97.5 | 36% | 29% | 85% | 34% | 7.0473 | Loss 5-10% |  | 891(73) | 934(79) | 911(83.5) | 797(66.5)
14 | 1110 | CCK | LAHORI GATE | LHR018 | TG-LHR018A-2 | DT-2 | BARSHABULLA:ID | 2 | 990 | 19505696 | 1156 | 2019-06-26 17:30 | 408 | 1794 | 396 | 1739 | 352 | 1518 | 253 | 540 | 130.5 | 49 | 0.5 | 180 | 19% | 12% | 117% | 16% | 7.0473 | Loss 5-10% |  | 1081(149.5) | 1050(203.5) | 1336(182) |  | 893(143)
15 | 1110 | CCK | LAHORI GATE | LHR019 | TG-LHR019A-1 | DT-1 | CHARKHE WALAN:PL | 2 | 630 | 19501607 | 439 | 2019-06-29 17:30 | 140 | 624 | 137 | 619 | 161 | 729 | 108 | 696 |  |  |  | 0 | 37% | 30% | 70% | 37% | 10.896 | Loss 10-20%
16 | 1110 | CCK | LAHORI GATE | LHR019 | TG-LHR019A-2 | DT-2 | CHARKHE WALAN:PL | 2 | 990 | 19504961 | 817 | 2019-06-11 01:30 | 269 | 1147 | 265 | 1116 | 283 | 1208 | 81 | 598 | 120.5 |  |  | 120.5 | 83% | 69% | 76% | 80% | 10.896 | Loss 10-20% | 791(25) | 902(204) | 993(465) | 1032(378) | 880(273)
17 | 1110 | CCK | LAHORI GATE | LHR023 | TG-LHR023A-1 | DT-1 | JOGIWARA:ID | 3 | 990 | 19501520 | 990 | 2019-06-11 17:00 | 340 | 1468 | 343 | 1478 | 306 | 1323 | 150 | 462 | 132 | 54 |  | 186 | 55% | 46% | 100% | 57% | 15.2846 | Loss 10-20% | 1068(204.5) | 1173(133.5) | 1272(221.5) | 831(63.5) | 888(78)
18 | 1110 | CCK | LAHORI GATE | LHR023 | TG-LHR023A-2 | DT-2 | JOGIWARA:ID | 3 | 990 | 19505551 | 904 | 2019-06-01 13:00 | 324 | 1439 | 293 | 1294 | 287 | 1277 | 154 | 644 | 73 | 1 |  | 74 | 8% | 7% | 91% | 24% | 15.2846 | Loss 10-20% | 925(176) | 1050(216) | 1119(212) | 1316(147.5) | 929(111.5) | 837(99.5)
19 | 1110 | CCK | LAHORI GATE | LHR023 | TG-LHR023A-3 | DT-3 | JOGIWARA:ID | 3 | 630 | 19506567 | 442 | 2019-06-05 12:00 | 138 | 621 | 146 | 650 | 158 | 708 | 76 | 718.5 | 1 |  |  | 1 | 68% | 56% | 70% | 60% | 15.2846 | Loss 10-20%
20 | 1110 | CCK | LAHORI GATE | LHR024 | TG-LHR024A-1 | DT-1 | PANDIT BROS:K | 2 | 990 | 19503227 | 814 | 2019-06-15 17:00 | 255 | 1022 | 304 | 1223 | 255 | 1028 | 198 | 613 | 105 |  |  | 105 | 5% | 6% | 82% | 13% | 3.7151 | Loss 0-5% |  | 852(104) | 914(190.5) | 904(126.5) | 931(111) | 775(57.5)
21 | 1110 | CCK | LAHORI GATE | LHR024 | TG-LHR024A-2 | DT-2 | PANDIT BROS:K | 2 | 990 | 19503236 | 871 | 2019-06-01 14:30 | 260 | 1162 | 339 | 1505 | 272 | 1222 | 317 | 663.5 | 53.5 |  |  | 53.5 | 9% | 15% | 88% | 13% | 3.7151 | Loss 0-5% |  |  | 731(32)
22 | 1110 | CCK | LAHORI GATE | LHR025 | TG-LHR025A-1 | DT-1 | CYCLE STAND:ID | 2 | 990 | 19501167 | 735 | 2019-06-03 14:00 | 257 | 1161 | 246 | 1098 | 232 | 1046 | 100 | 687 | 32 |  |  | 32 | 4% | 6% | 74% | 16% | 28.3054 | Loss 20-30%
23 | 1110 | CCK | LAHORI GATE | LHR025 | TG-LHR025A-2 | DT-2 | CYCLE STAND:ID | 2 | 990 | 19501166 | 911 | 2019-06-29 18:00 | 302 | 1302 | 332 | 1459 | 277 | 1207 | 221 | 480.5 | 234 | 1 |  | 235 | 90% | 81% | 92% | 82% | 28.3054 | Loss 20-30% |  | 849(88.5) | 992(433) | 930(240) | 791(87)
24 | 1110 | CCK | LAHORI GATE | LHR026 | TG-LHR026A-1 | DT-1 | OLD KRISHNA MARKET:ID | 1 | 990 | 19501852 | 815 | 2019-06-03 17:00 | 284 | 1202 | 221 | 922 | 310 | 1316 | 352 | 557.5 | 162.5 |  |  | 162.5 | 8% | 8% | 82% | 14% | 14.7889 | Loss 10-20% |  | 790(96) | 844(158.5) | 839(138.5) | 831(147) | 741(30.5)
25 | 1110 | CCK | LAHORI GATE | LHR027 | TG-LHR027A-1 | DT-1 | NEW KRISHNA MKT:ID | 2 | 990 | 19504835 | 939 | 2019-06-07 15:00 | 292 | 1316 | 315 | 1429 | 332 | 1483 | 148 | 539.5 | 167.5 | 13 |  | 180.5 | 8% | 11% | 95% | 16% | 14.7252 | Loss 10-20%
26 | 1110 | CCK | LAHORI GATE | LHR032 | TG-LHR032A-1 | DT-1 | HAVELI HYDERQULI:PM | 1 | 630 | 19506524 | 524.6712 | 2019-06-13 14:00 | 264.1057 | 1178.6225 | 136.5367 | 595.684 | 124.0287 | 540.8779 | 612.1843 | 641 | 77.5 |  |  | 77.5 | 74% | 45% | 83% | 76% | 5.9911 | Loss 5-10% |  |  |  | 525(47.5)
27 | 1110 | CCK | LAHORI GATE | LHR034 | TG-LHR034A-1 | DT-1 | KATRA BARYIAN PLINTH:PL | 1 | 630 | 19501572 | 599 | 2019-06-12 16:00 | 218 | 900 | 210 | 873 | 171 | 718 | 170 | 324.5 | 111.5 | 6.5 |  | 118 | 57% | 48% | 95% | 59% | 14.0195 | Loss 10-20% |  | 481(27.5) | 555(154.5) | 584(150) | 539(96.5)
28 | 1110 | CCK | LAHORI GATE | LHR043 | TG-LHR043A-1 | DT-1 | GADODIA KIOSK:K | 1 | 990 | 19506662 | 947.8727 | 2019-06-06 16:00 | 347.9285 | 1554.2928 | 285.6446 | 1246.5942 | 314.2996 | 1399.7489 | 266.4758 | 580.5 | 124.5 | 8.5 |  | 133 | 15% | 15% | 96% | 17% | 12.0706 | Loss 10-20% |  | 924(29.5) | 988(163.5) | 945(63) | 955(134)
29 | 1110 | CCK | LAHORI GATE | LHR046 | TG-LHR046A-1 | DT-1 | LAL DARWAZA:PM | 2 | 400 | 19506181 | 333.0715 | 2019-06-02 10:00 | 188.3708 | 758.3976 | 82.5021 | 323.3727 | 62.1987 | 243.6202 | 479.8973 | 686.5 | 33 |  |  | 33 | 69% | 59% | 83% | 76% | 31.4545 | Loss >30% | 474(194) |  | 367(46)
30 | 1110 | CCK | LAHORI GATE | LHR046 | TG-LHR046A-2 | DT-2 | LAL DARWAZA:PM | 2 | 400 | 19504892 | 260 | 2019-06-12 00:30 | 67 | 271 | 67 | 276 | 126 | 523 | 249 | 720 |  |  |  | 0 | 65% | 56% | 57% | 59% | 31.4545 | Loss >30%
31 | 1110 | CCK | LAHORI GATE | LHR047 | TG-LHR047A-1 | DT-1 | LAMBI GALI:PL | 1 | 990 | 19501516 | 884 | 2019-06-03 04:30 | 287 | 1183 | 317 | 1314 | 280 | 1148 | 152 | 493.5 | 226 |  |  | 226 | 89% | 83% | 81% | 83% | 18.9247 | Loss 10-20% |  | 853(150.5) | 921(289.5) | 914(209.5) | 795(93)
32 | 1110 | CCK | LAHORI GATE | LHR048 | TG-LHR048A-1 | DT-1 | P.S HAUZ QUAZI:PL | 3 | 990 | 19501649 | 535 | 2019-06-29 17:00 | 181 | 753 | 211 | 883 | 143 | 592 | 252 | 720 |  |  |  | 0 | 19% | 16% | 54% | 19% | 25.5668 | Loss 20-30% |  |  | 970(154.5) | 968(140) | 910(109.5)
33 | 1110 | CCK | LAHORI GATE | LHR048 | TG-LHR048A-2 | DT-2 | P.S HAUZ QUAZI:PL | 3 | 990 | 19501648 | 892 | 2019-06-02 04:00 | 357 | 1590 | 262 | 1168 | 273 | 1211 | 402 | 504 | 215 | 0.5 |  | 215.5 | 90% | 82% | 82% | 83% | 25.5668 | Loss 20-30% | 846(115) | 1027(391) | 1099(444) | 929(289.5) | 846(201)
34 | 1110 | CCK | LAHORI GATE | LHR048 | TG-LHR048A-3 | DT-3 | P.S HAUZ QUAZI:PL | 3 | 990 | 19506502 | 746 | 2019-06-28 14:30 | 192 | 829 | 216 | 966 | 338 | 1512 | 625 | 717.5 | 0.5 |  |  | 0.5 | 39% | 36% | 75% | 37% | 25.5668 | Loss 20-30%
35 | 1110 | CCK | LAHORI GATE | LHR051 | TG-LHR051A-1 | DT-1 | NEW HAUZ QUAZI:ID | 3 | 990 | 19501494 | 460 | 2019-06-29 16:00 | 145 | 570 | 167 | 655 | 148 | 580 | 81 | 719 |  |  |  | 0 | 5% | 5% | 46% | 6% | 17.62 | Loss 10-20%
36 | 1110 | CCK | LAHORI GATE | LHR051 | TG-LHR051A-2 | DT-2 | NEW HAUZ QUAZI:ID | 3 | 990 | 19501627 | 626 | 2019-06-05 14:30 | 207 | 891 | 206 | 891 | 214 | 927 | 36 | 719 |  |  |  | 0 | 29% | 25% | 63% | 29% | 17.62 | Loss 10-20%
37 | 1110 | CCK | LAHORI GATE | LHR051 | TG-LHR051A-3 | DT-3 | NEW HAUZ QUAZI:ID | 3 | 630 | 19505507 | 693 | 2019-06-28 15:00 | 223 | 1044 | 218 | 1040 | 252 | 1236 | 194 | 485.5 | 233.5 |  | 0.5 | 234 | 86% | 77% | 110% | 80% | 17.62 | Loss 10-20% |  | 765(179) | 760(340) | 627(245.5) | 564(105.5)
38 | 1110 | CCK | LAHORI GATE | LHR054 | TG-LHR054A-1 | DT-1 | HAMDARD:ID | 1 | 400 | 19501504 | 337 | 2019-06-11 05:00 | 178 | 782 | 78 | 319 | 80 | 337 | 454 | 682 | 37.5 |  |  | 37.5 | 84% | 68% | 73% | 69% | 23.5342 | Loss 20-30% |  |  | 341(88.5)
39 | 1110 | CCK | LAHORI GATE | LHR055 | TG-LHR055A-1 | DT-1 | GALI KASIM JAAN:ID | 2 | 990 | 19501574 | 966.7434 | 2019-06-02 04:30 | 345.9584 | 1528.6248 | 308.2865 | 1358.0305 | 312.4985 | 1369.6464 | 165.0931 | 470 | 152.5 | 17.5 |  | 170 | 98% | 91% | 88% | 89% | 20.2202 | Loss 20-30%
40 | 1110 | CCK | LAHORI GATE | LHR055 | TG-LHR055A-2 | DT-2 | GALI KASIM JAAN:ID | 2 | 990 | 19501573 | 934 | 2019-06-02 04:00 | 308 | 1387 | 336 | 1522 | 290 | 1285 | 206 | 435.5 | 278.5 | 4.5 |  | 283 | 94% | 81% | 86% | 87% | 20.2202 | Loss 20-30% |  | 904(249) | 1012(448) | 955(301) | 870(182)
41 | 1110 | CCK | LAHORI GATE | LHR056 | TG-LHR056A-1 | DT-1 | GALI HASHMUDDIN:PKG | 1 | 990 | 19500694 | 1138.5187 | 2019-06-30 01:00 | 395.903 | 1664.7171 | 413.7793 | 1782.9935 | 328.8364 | 1333.6971 | 403.3799 | 282 | 239 | 97 | 99 | 435 | 115% | 101% | 92% | 113% | 22.505 | Loss 20-30% | 933(66) | 1053(233.5) | 1151(507) | 1127(173) | 1039(336) | 993(123.5)
42 | 1110 | CCK | TOWN HALL | THL004 | TG-THL004A-1 | DT-1 | KATRA KUSHAL RAI:ID | 3 | 990 | 19500224 | 728 | 2019-06-02 23:30 | 234 | 1028 | 303 | 1347 | 192 | 840 | 444 | 715 | 3.5 |  |  | 3.5 | 73% | 51% | 69% | 74% | 14.747 | Loss 10-20% |  |  | 748(34.5)
43 | 1110 | CCK | TOWN HALL | THL004 | TG-THL004A-2 | DT-2 | KATRA KUSHAL RAI:ID | 3 | 990 | 19500225 | 877 | 2019-06-08 17:00 | 287 | 1242 | 310 | 1355 | 280 | 1223 | 123 | 608.5 | 108.5 |  |  | 108.5 | 34% | 30% | 89% | 34% | 14.747 | Loss 10-20% |  | 801(25.5) |  | 882(105.5) | 862(108) | 805(58.5)
44 | 1110 | CCK | TOWN HALL | THL004 | TG-THL004A-3 | DT-3 | KATRA KUSHAL RAI:ID | 3 | 990 | 19503562 | 699 | 2019-06-12 15:30 | 270 | 1204 | 226 | 1009 | 204 | 912 | 257 | 718 | 0.5 |  |  | 0.5 | 36% | 28% | 71% | 36% | 14.747 | Loss 10-20% |  |  | 773(47.5) | 763(24.5)
45 | 1110 | CCK | TOWN HALL | THL006 | TG-THL006A-1 | DT-1 | NEW LAJPAT RAI MKT:ID | 1 | 990 | 19500223 | 866 | 2019-06-03 16:00 | 395 | 1692 | 200 | 843 | 271 | 1161 | 744 | 650.5 | 67.5 |  |  | 67.5 | 18% | 15% | 87% | 30% | 11.7994 | Loss 10-20% |  |  |  | 780(42)
46 | 1110 | CCK | TOWN HALL | THL007 | TG-THL007A-1 | DT-1 | MALIWARA : PKG | 1 | 990 | 19505462 | 819 | 2019-06-29 17:00 | 294 | 1256 | 266 | 1143 | 259 | 1108 | 134 | 634.5 | 85.5 |  |  | 85.5 | 15% | 10% | 83% | 16% | 5.2475 | Loss 5-10% |  |  | 785(77.5)
47 | 1110 | CCK | TOWN HALL | THL010 | TG-THL010A-1 | DT-1 | KUCHHA NALWA:PKG | 1 | 990 | 19506919 | 941.4822 | 2019-06-27 14:30 | 381.6131 | 1681.3372 | 286.9879 | 1267.5585 | 272.8812 | 1200.8502 | 450.8496 | 330.5 | 101.5 | 7.5 |  | 109 | 9% | 7% | 95% | 11% | 4.2988 | Loss 0-5% | 853(116.5) | 987(178.5) | 963(44) | 939(159) | 925(168.5)
48 | 1110 | CCK | TOWN HALL | THL014 | TG-THL014A-1 | DT-1 | KUMAR CINEMA:PKG | 1 | 990 | 19500231 | 840 | 2019-06-25 16:00 | 285 | 1226 | 265 | 1150 | 290 | 1240 | 84 | 580 | 115 |  |  | 115 | 12% | 21% | 85% | 18% | 8.9216 | Loss 5-10% |  |  | 797(108) | 821(79) | 781(61.5)
49 | 1110 | CCK | TOWN HALL | THL015 | TG-THL015A-1 | DT-1 | MAHARASHTRA BANK:PKG | 1 | 990 | 19500561 | 887.9624 | 2019-06-12 16:00 | 292.7948 | 1245.6174 | 303.7032 | 1306.082 | 291.4644 | 1220.8443 | 75.9445 | 606 | 112 |  |  | 112 | 34% | 26% | 90% | 41% | 4.4886 | Loss 0-5% |  | 808(51.5) | 862(147.5) | 874(111.5) | 825(92.5)
50 | 1110 | CCK | TOWN HALL | THL019 | TG-THL019A-1 | DT-1 | KINARI BAZAR:PM | 2 | 400 | 19503057 | 384 | 2019-06-21 17:00 | 118 | 520 | 118 | 518 | 148 | 664 | 145 | 603.5 | 104.5 | 11.5 |  | 116 | 46% | 34% | 96% | 46% | 4.6231 | Loss 0-5% |  | 354(47.5)
51 | 1110 | CCK | TOWN HALL | THL019 | TG-THL019A-2 | DT-2 | KINARI BAZAR:PM | 2 | 400 | 19503058 | 371 | 2019-06-14 15:30 | 116 | 511 | 149 | 662 | 106 | 463 | 180 | 537.5 | 165.5 | 16 |  | 181.5 | 19% | 15% | 93% | 44% | 4.6231 | Loss 0-5% |  | 336(70) | 354(157.5) | 365(175) | 346(138.5)
52 | 1110 | CCK | TOWN HALL | THL020 | TG-THL020A-1 | DT-1 | DIWAN HALL:PM | 3 | 400 | 19501226 | 344 | 2019-06-29 16:00 | 121 | 536 | 94 | 417 | 129 | 576 | 143 | 598.5 | 113 |  |  | 113 | 8% | 7% | 86% | 12% | 4.212 | Loss 0-5% |  | 339(60) | 408(142.5) | 371(122) | 337(108.5)
53 | 1110 | CCK | TOWN HALL | THL020 | TG-THL020A-2 | DT-2 | DIWAN HALL:PM | 3 | 400 | 19503325 | 138 | 2019-06-03 14:30 | 46 | 210 | 49 | 225 | 42 | 192 | 28 | 669 |  |  |  | 0 | 2% | 3% | 34% | 5% | 4.212 | Loss 0-5%
54 | 1110 | CCK | TOWN HALL | THL020 | TG-THL020A-3 | DT-3 | DIWAN HALL:PM | 3 | 400 | 19505844 | 372 | 2019-06-12 15:00 | 105 | 468 | 121 | 539 | 146 | 653 | 161 | 687 | 20 | 2.5 |  | 22.5 | 7% | 4% | 93% | 14% | 4.212 | Loss 0-5% |  | 324(45) |  | 424(160) |  | 357(65.5)
55 | 1110 | CCK | TOWN HALL | THL021 | TG-THL021A-1 | DT-1 | TIKONA PARK:PL | 2 | 990 | 19501180 | 702 | 2019-06-29 17:00 | 197 | 859 | 228 | 986 | 278 | 1215 | 312 | 716 | 1.5 |  |  | 1.5 | 4% | 3% | 71% | 9% | 6.9356 | Loss 5-10% |  |  | 812(93) | 814(67)
56 | 1110 | CCK | TOWN HALL | THL021 | TG-THL021A-2 | DT-2 | TIKONA PARK:PL | 2 | 630 | 19501176 | 497 | 2019-06-14 15:30 | 136 | 595 | 150 | 653 | 211 | 931 | 311 | 634.5 | 82.5 |  |  | 82.5 | 6% | 4% | 79% | 10% | 6.9356 | Loss 5-10% |  |  | 483(46.5) | 484(30.5)
57 | 1110 | CCK | TOWN HALL | THL025 | TG-THL025A-1 | DT-1 | SHRI RAM:PL | 1 | 990 | 19501100 | 843 | 2019-06-29 13:30 | 243 | 1071 | 321 | 1435 | 278 | 1244 | 315 | 687.5 | 30.5 |  |  | 30.5 | 5% | 5% | 85% | 11% | 4.255 | Loss 0-5%
58 | 1110 | CCK | TOWN HALL | THL028 | TG-THL028A-1 | DT-1 | MOTI BAZAR:PKG | 1 | 990 | 19506477 | 772 | 2019-06-29 16:00 | 247 | 1063 | 257 | 1107 | 268 | 1162 | 86 | 613 | 104.5 |  |  | 104.5 | 8% | 7% | 78% | 10% | 7.7219 | Loss 5-10% |  |  | 899(79.5)
59 | 1110 | CCK | TOWN HALL | THL029 | TG-THL029A-1 | DT-1 | GALI PARATHE:PKG | 1 | 990 | 19501182 | 769 | 2019-06-06 15:30 | 288 | 1302 | 258 | 1175 | 223 | 1017 | 247 | 684 | 32.5 |  |  | 32.5 | 13% | 10% | 78% | 28% | 5.2131 | Loss 5-10% |  |  | 809(77.5) | 777(26.5)
60 | 1110 | CCK | TOWN HALL | THL035 | TG-THL035A-1 | DT-1 | CHARHAT:PKG | 1 | 990 | 19501855 | 875.7033 | 2019-06-11 23:30 | 281.4418 | 1193.8147 | 289.1169 | 1223.9824 | 305.1446 | 1304.5384 | 99.144 | 554 | 165.5 |  |  | 165.5 | 87% | 62% | 88% | 88% | 5.83 | Loss 5-10% |  | 864(96.5) | 943(289) | 934(166) | 891(69.5)
61 | 1120 | DRG | DARYAGANJ | DRY007 | TG-DRY007A-1 | DT-1 | BACHHO KA GHAR:PKG | 2 | 990 | 19500132 | 457 | 2019-06-10 16:00 | 150 | 639 | 143 | 617 | 165 | 704 | 79 | 719 |  |  |  | 0 | 13% | 28% | 46% | 15% | 4.7658 | Loss 0-5%
62 | 1120 | DRG | DARYAGANJ | DRY007 | TG-DRY007A-2 | DT-2 | BACHHO KA GHAR:PKG | 2 | 630 | 19504372 | 582 | 2019-06-10 15:00 | 219 | 943 | 191 | 822 | 171 | 740 | 177 | 566 | 150.5 | 3.5 |  | 154 | 18% | 20% | 92% | 27% | 4.7658 | Loss 0-5%
63 | 1120 | DRG | DARYAGANJ | DRY011 | TG-DRY011A-1 | DT-1 | DARYA GANJ KOTWALI:PL | 1 | 630 | 19501677 | 581 | 2019-06-12 15:00 | 187 | 780 | 210 | 916 | 184 | 801 | 127 | 561 | 155.5 | 3.5 |  | 159 | 45% | 41% | 92% | 42% | 3.0901 | Loss 0-5% | 504(28.5) | 675(189.5) | 731(218.5) | 676(195) | 607(176.5) | 541(77.5)
64 | 1120 | DRG | DARYAGANJ | DRY035 | TG-DRY035A-1 | DT-1 | VIKRAM NAGAR:PACKAGE S/STN | 2 | 990 | 19506404 | 510 | 2019-06-12 | 125 | 521 | 208 | 881 | 177 | 744 | 315 | 720 |  |  |  | 0 | 52% | 30% | 40% | 51% | 10.0599 | Loss 10-20%
65 | 1120 | DRG | DARYAGANJ | DRY035 | TG-DRY035A-2 | DT-2 | VIKRAM NAGAR:PACKAGE S/STN | 2 | 990 | 19505152 | 806 | 2019-06-12 00:30 | 199 | 834 | 219 | 929 | 388 | 1670 | 793 | 686 | 34 |  |  | 34 | 81% | 52% | 58% | 81% | 10.0599 | Loss 10-20%
66 | 1120 | DRG | DARYAGANJ | DRY089 | TG-DRY089A-1 | DT-1 | GHATA MASJID:PG | 1 | 990 | 19500136 | 948 | 2019-06-03 15:30 | 331 | 1418 | 308 | 1316 | 308 | 1320 | 100 | 538 | 169.5 | 12 |  | 181.5 | 45% | 42% | 96% | 51% | 7.3755 | Loss 5-10% |  | 893(87.5) | 955(201.5) | 916(131.5) | 800(81.5)
67 | 1120 | DRG | JAMA MASJID | HAU001 | TG-HAU001A-1 | DT-1 | 84 GHANTA:K | 3 | 990 | 19500381 | 1063 | 2019-06-11 01:00 | 322 | 1486 | 452 | 1919 | 289 | 1202 | 625 | 514 | 159 | 39.5 | 6.5 | 205 | 107% | 71% | 82% | 102% | 21.4421 | Loss 20-30% | 845(33) | 1160(309) | 1194(409.5) | 1119(298) | 926(175.5)
68 | 1120 | DRG | JAMA MASJID | HAU001 | TG-HAU001A-2 | DT-2 | 84 GHANTA:K | 3 | 990 | 19501686 | 1036 | 2019-06-15 00:30 | 297 | 1348 | 342 | 1556 | 398 | 1833 | 421 | 310 | 311.5 | 82.5 | 16 | 410 | 105% | 81% | 89% | 104% | 21.4421 | Loss 20-30% | 816(24.5) | 971(231) | 1074(408) | 1078(369) | 950(321.5) | 865(76.5)
69 | 1120 | DRG | JAMA MASJID | HAU001 | TG-HAU001A-3 | DT-3 | 84 GHANTA:K | 3 | 990 | 19503790 | 981 | 2019-06-12 02:30 | 394 | 1632 | 250 | 1018 | 337 | 1393 | 536 | 355 | 318 | 45 |  | 363 | 99% | 85% | 83% | 96% | 21.4421 | Loss 20-30% |  |  | 947(354) | 928(293.5) | 810(147.5)
70 | 1120 | DRG | JAMA MASJID | HAU003 | TG-HAU003A-1 | DT-1 | DDA HOUSING COMP.TURKMAN GATE:ID | 4 | 990 | 19501668 | 722 | 2019-06-12 01:30 | 260 | 1096 | 238 | 1008 | 224 | 943 | 133 | 702 | 15 |  |  | 15 | 73% | 67% | 66% | 66% | 61.0258 | Loss >30% |  |  | 877(182.5) | 806(98.5)
71 | 1120 | DRG | JAMA MASJID | HAU003 | TG-HAU003A-2 | DT-2 | DDA HOUSING COMP.TURKMAN GATE:ID | 4 | 990 | 19501667 | 793 | 2019-06-02 04:30 | 209 | 916 | 257 | 1138 | 327 | 1455 | 470 | 610 | 107.5 |  |  | 107.5 | 80% | 80% | 76% | 68% | 61.0258 | Loss >30%
72 | 1120 | DRG | JAMA MASJID | HAU003 | TG-HAU003A-3 | DT-3 | DDA HOUSING COMP.TURKMAN GATE:ID | 4 | 990 | 19505526 | 722 | 2019-06-05 15:00 | 254 | 1111 | 288 | 1274 | 180 | 782 | 434 | 716.5 | 0.5 |  |  | 0.5 | 65% | 62% | 73% | 61% | 61.0258 | Loss >30%
73 | 1120 | DRG | JAMA MASJID | HAU003 | TG-HAU003A-4 | DT-4 | DDA HOUSING COMP.TURKMAN GATE:ID | 4 | 630 | 19505108 | 368 | 2019-06-02 08:30 | 79 | 354 | 150 | 684 | 139 | 640 | 310 | 717 |  |  |  | 0 | 58% | 58% | 45% | 46% | 61.0258 | Loss >30%
74 | 1120 | DRG | JAMA MASJID | HAU006 | TG-HAU006A-1 | DT-1 | GALI DAKOTAN:PM | 1 | 990 | 19500348 | 901 | 2019-06-06 | 304 | 1245 | 286 | 1169 | 311 | 1277 | 96 | 591.5 | 123 | 1.5 |  | 124.5 | 91% | 65% | 70% | 91% | 25.312 | Loss 20-30% |  |  |  | 798(27)
75 | 1120 | DRG | JAMA MASJID | HAU008 | TG-HAU008A-1 | DT-1 | GALI SHANKAR:ID | 2 | 990 | 19506161 | 965 | 2019-06-03 13:00 | 252 | 1194 | 323 | 1522 | 389 | 1739 | 476 | 482 | 221 | 17 |  | 238 | 96% | 93% | 97% | 85% | 31.2111 | Loss >30% |  |  | 1077(303.5) | 900(110) | 1036(33) | 1142(88.5)
76 | 1120 | DRG | JAMA MASJID | HAU008 | TG-HAU008A-2 | DT-2 | GALI SHANKAR:ID | 2 | 990 | 19505535 | 1096 | 2019-06-03 13:30 | 334 | 1516 | 387 | 1782 | 375 | 1722 | 242 | 703 | 16 |  | 0.5 | 16.5 | 77% | 68% | 111% | 70% | 31.2111 | Loss >30% |  |  | 962(107.5) | 929(111) | 1004(29)
77 | 1120 | DRG | JAMA MASJID | HAU010 | TG-HAU010A-1 | DT-1 | HAMMATGARH:K | 2 | 990 | 19500364 | 497 | 2019-06-11 14:00 | 160 | 646 | 145 | 588 | 192 | 777 | 168 | 694 |  |  |  | 0 | 15% | 14% | 50% | 20% | 4.5512 | Loss 0-5%
78 | 1120 | DRG | JAMA MASJID | HAU010 | TG-HAU010A-2 | DT-2 | HAMMATGARH:K | 2 | 990 | 19500332 | 779 | 2019-06-10 23:30 | 197 | 846 | 300 | 1298 | 281 | 1219 | 418 | 638 | 79 |  |  | 79 | 77% | 68% | 66% | 79% | 4.5512 | Loss 0-5% |  |  | 795(90.5) | 806(64.5)
79 | 1120 | DRG | JAMA MASJID | HAU011 | TG-HAU011A-1 | DT-1 | RAJ ENGINEERING:ID | 2 | 990 | 19500218 | 808 | 2019-06-05 15:00 | 266 | 1188 | 254 | 1131 | 288 | 1281 | 131 | 654.5 | 65.5 |  |  | 65.5 | 65% | 49% | 82% | 66% | 9.3831 | Loss 5-10% |  |  | 818(55) | 870(36)
80 | 1120 | DRG | JAMA MASJID | HAU011 | TG-HAU011A-2 | DT-2 | RAJ ENGINEERING:ID | 2 | 990 | 19504377 | 767 | 2019-06-05 15:00 | 215 | 965 | 321 | 1458 | 230 | 1034 | 462 | 675.5 | 44.5 |  |  | 44.5 | 72% | 54% | 77% | 74% | 9.3831 | Loss 5-10% |  |  | 858(59) | 872(42)
81 | 1120 | DRG | JAMA MASJID | HAU012 | TG-HAU012A-1 | DT-1 | SARAK PREM NARAIN:PL | 1 | 990 | 19501687 | 1042 | 2019-06-27 05:30 | 296 | 1219 | 384 | 1543 | 362 | 1504 | 306 | 314.5 | 327.5 | 73 | 3.5 | 404 | 105% | 102% | 85% | 93% | 28.5473 | Loss 20-30% | 793(28) | 979(290.5) | 1055(542.5) | 1060(412) | 920(355.5) | 824(59.5)
82 | 1120 | DRG | JAMA MASJID | HAU014 | TG-HAU014A-1 | DT-1 | BARSHABULLA:ID DRG | 1 | 990 | 19503477 | 968 | 2019-06-13 17:00 | 316 | 1432 | 317 | 1428 | 335 | 1529 | 99 | 549 | 145 | 25.5 |  | 170.5 | 65% | 50% | 98% | 64% | 13.7338 | Loss 10-20% |  | 975(130) | 1055(202) | 998(173) | 930(177.5) | 828(75)
83 | 1120 | DRG | JAMA MASJID | HAU015 | TG-HAU015A-1 | DT-1 | NEW HAUZ QUAZI:ID DRG | 1 | 990 | 19502903 | 945 | 2019-06-01 15:00 | 360 | 1575 | 329 | 1438 | 255 | 1114 | 410 | 482 | 233.5 | 4 |  | 237.5 | 88% | 58% | 95% | 83% | 10.0516 | Loss 10-20% |  |  | 941(116.5)
84 | 1120 | DRG | JAMA MASJID | JMS001 | TG-JMS001A-1 | DT-1 | BULIBULI KHANA:ID | 2 | 990 | 19505784 | 879 | 2019-06-03 13:30 | 483 | 2022 | 12 | 50 | 384 | 1608 | 1801 | 656 | 64 |  |  | 64 | 78% | 76% | 89% | 75% | 44.7575 | Loss >30% | 1068(133.5) | 1506(556) | 1502(689.5) | 1524(636) |  | 1268(353.5)
85 | 1120 | DRG | JAMA MASJID | JMS001 | TG-JMS001A-2 | DT-2 | BULIBULI KHANA:ID | 2 | 990 | 19501700 | 984 | 2019-06-04 04:30 | 351 | 1500 | 327 | 1393 | 306 | 1308 | 167 | 268.5 | 400 | 51.5 |  | 451.5 | 99% | 93% | 87% | 90% | 44.7575 | Loss >30% |  | 1003(335.5) | 1176(622) | 993(475.5) | 933(443) | 875(106.5)
86 | 1120 | DRG | JAMA MASJID | JMS002 | TG-JMS002A-1 | DT-1 | CHANDNI MAHAL:ID | 4 | 990 | 19501664 | 632 | 2019-06-03 | 192 | 834 | 227 | 977 | 213 | 920 | 125 | 719 |  |  |  | 0 | 64% | 47% | 60% | 63% | 60.2944 | Loss >30%
87 | 1120 | DRG | JAMA MASJID | JMS002 | TG-JMS002A-2 | DT-2 | CHANDNI MAHAL:ID | 4 | 990 | 19505094 | 1253 | 2019-06-02 18:00 | 374 | 1718 | 447 | 2153 | 431 | 2127 | 422 | 665 | 42.5 | 1 | 0.5 | 44 | 94% | 77% | 127% | 72% | 60.2944 | Loss >30%
88 | 1120 | DRG | JAMA MASJID | JMS002 | TG-JMS002A-3 | DT-3 | CHANDNI MAHAL:ID | 4 | 990 | 19503569 | 288 | 2019-06-02 20:00 | 93 | 429 | 114 | 525 | 80 | 369 | 137 | 720 |  |  |  | 0 | 28% | 25% | 29% | 27% | 60.2944 | Loss >30%
89 | 1120 | DRG | JAMA MASJID | JMS002 | TG-JMS002A-4 | DT-4 | CHANDNI MAHAL:ID | 4 | 630 | 19505203 | 805 | 2019-06-29 02:30 | 395 | 1790 | 216 | 938 | 193 | 839 | 905 | 137.5 | 346.5 | 154.5 | 80 | 581 | 128% | 116% | 119% | 109% | 60.2944 | Loss >30% | 605(121.5) | 862(505.5) | 775(672.5) | 1078(598)
90 | 1120 | DRG | JAMA MASJID | JMS003 | TG-JMS003A-1 | DT-1 | CHANDNI MAHAL [K]:K | 1 | 990 | 19504749 | 1090 | 2019-06-03 04:00 | 374 | 1564 | 381 | 1596 | 336 | 1391 | 191 | 267 | 292 | 113 | 48 | 453 | 110% | 96% | 93% | 102% | 48.1255 | Loss >30% | 806(30.5) | 1051(351) | 1147(547) | 1124(384) | 986(347) | 884(102)
91 | 1120 | DRG | JAMA MASJID | JMS004 | TG-JMS004A-1 | DT-1 | DELHI GATE TELEPHONE EXCHANGE PM:K | 2 | 990 | 19505683 | 1090 | 2019-06-17 03:00 | 345 | 1448 | 363 | 1506 | 383 | 1617 | 148 | 408 | 281.5 | 16 | 8 | 305.5 | 110% | 105% | 110% | 108% | 12.0291 | Loss 10-20% |  |  | 920(34.5) | 973(135) | 1026(375.5) | 846(76)
92 | 1120 | DRG | JAMA MASJID | JMS004 | TG-JMS004A-2 | DT-2 | DELHI GATE TELEPHONE EXCHANGE PM:K | 2 | 990 | 19505473 | 1451 | 2019-06-16 04:30 | 401 | 1653 | 524 | 2207 | 526 | 2150 | 528 | 707.5 | 8 | 1 | 1 | 10 | 147% | 66% | 92% | 68% | 12.0291 | Loss 10-20%
93 | 1120 | DRG | JAMA MASJID | JMS006 | TG-JMS006A-1 | DT-1 | GANJ MEER KHAN:PM | 1 | 990 | 19505263 | 1234 | 2019-06-12 02:00 | 425 | 1527 | 468 | 1763 | 341 | 1290 | 409 | 58 | 280 | 144 | 238 | 662 | 125% | 122% | 108% | 112% | 50.8784 | Loss >30% | 1187(147) |  | 1161(39) |  | 1225(572.5) | 1068(157)
94 | 1120 | DRG | JAMA MASJID | JMS008 | TG-JMS008A-1 | DT-1 | GIRDHAR PANNA:ID | 3 | 990 | 19505336 | 709 | 2019-06-12 01:30 | 236 | 955 | 258 | 1039 | 216 | 869 | 148 | 719.5 | 0.5 |  |  | 0.5 | 72% | 61% | 57% | 63% | 45.4574 | Loss >30%
95 | 1120 | DRG | JAMA MASJID | JMS008 | TG-JMS008A-2 | DT-2 | GIRDHAR PANNA:ID | 3 | 990 | 19505724 | 787 | 2019-06-05 22:30 | 335 | 1679 | 270 | 1342 | 182 | 872 | 702 | 697.5 | 22.5 |  |  | 22.5 | 76% | 68% | 67% | 80% | 45.4574 | Loss >30% |  |  | 1015(454) |  | 1046(393) | 1013(137.5)
96 | 1120 | DRG | JAMA MASJID | JMS008 | TG-JMS008A-3 | DT-3 | GIRDHAR PANNA:ID | 3 | 630 | 19506160 | 775.4229 | 2019-06-03 04:30 | 247.0648 | 1089.5914 | 297.1256 | 1343.244 | 231.2325 | 1025.0123 | 291.3601 | 186.5 | 318 | 134.5 | 80.5 | 533 | 123% | 103% | 105% | 104% | 45.4574 | Loss >30% |  |  | 787(409.5) | 781(495)
97 | 1120 | DRG | JAMA MASJID | JMS010 | TG-JMS010A-1 | DT-1 | JAMA MASJID:ID | 3 | 990 | 19500209 | 466 | 2019-06-10 05:30 | 161 | 657 | 147 | 600 | 157 | 634 | 50 | 720 |  |  |  | 0 | 47% | 47% | 42% | 44% | 29.402 | Loss 20-30%
98 | 1120 | DRG | JAMA MASJID | JMS010 | TG-JMS010A-2 | DT-2 | JAMA MASJID:ID | 3 | 990 | 19500094 | 574 | 2019-06-30 01:00 | 161 | 717 | 220 | 977 | 192 | 854 | 226 | 720 |  |  |  | 0 | 58% | 52% | 49% | 54% | 29.402 | Loss 20-30%
99 | 1120 | DRG | JAMA MASJID | JMS010 | TG-JMS010A-3 | DT-3 | JAMA MASJID:ID | 3 | 630 | 19505361 | 514 | 2019-06-14 05:30 | 224 | 1001 | 137 | 585 | 152 | 620 | 400 | 694.5 | 25.5 |  |  | 25.5 | 82% | 66% | 75% | 74% | 29.402 | Loss 20-30% | 927(95) | 1065(425.5) | 1094(89.5) | 608(57.5)
100 | 1120 | DRG | JAMA MASJID | JMS013 | TG-JMS013A-1 | DT-1 | KASTURBA P/M:PM | 1 | 990 | 19500206 | 784 | 2019-06-03 04:30 | 287 | 1191 | 238 | 978 | 259 | 1066 | 186 | 635.5 | 84.5 |  |  | 84.5 | 79% | 71% | 67% | 72% | 37.6689 | Loss >30% |  | 846(98.5) | 919(292.5) | 853(122.5) | 781(52)
101 | 1120 | DRG | JAMA MASJID | JMS015 | TG-JMS015A-1 | DT-1 | KUCHA CHELAN-2:PL | 3 | 990 | 19506158 | 1004 | 2019-06-05 04:30 | 329 | 1292 | 339 | 1320 | 335 | 1307 | 24 | 342.5 | 335.5 | 39.5 | 1 | 376 | 101% | 92% | 97% | 92% | 68.3145 | Loss >30% | 808(33.5) | 974(351.5) | 1103(575) | 1027(452) | 972(358.5) | 1087(93)
102 | 1120 | DRG | JAMA MASJID | JMS015 | TG-JMS015A-2 | DT-2 | KUCHA CHELAN-2:PL | 3 | 400 | 19500358 | 429 | 2019-06-01 21:00 | 167 | 721 | 140 | 599 | 122 | 519 | 177 | 346 | 310 | 61.5 | 1.5 | 373 | 89% | 78% | 105% | 107% | 68.3145 | Loss >30% | 330(44.5) | 397(283.5) | 406(170.5) | 430(405) |  | 346(126.5)
103 | 1120 | DRG | JAMA MASJID | JMS015 | TG-JMS015A-3 | DT-3 | KUCHA CHELAN-2:PL | 3 | 990 | 19505512 | 1339 | 2019-06-26 22:30 | 499 | 2126 | 386 | 1633 | 454 | 1920 | 429 | 55 | 342 | 179.5 | 140.5 | 662 | 126% | 122% | 111% | 135% | 68.3145 | Loss >30% | 896(105) |  | 1248(665)
104 | 1120 | DRG | JAMA MASJID | JMS017 | TG-JMS017A-1 | DT-1 | KUCHA DAKHINI RAI:PL | 2 | 990 | 19506016 | 1081 | 2019-06-01 19:00 | 454 | 2200 | 219 | 1004 | 408 | 2140 | 1168 | 418 | 260 | 40.5 | 1 | 301.5 | 101% | 92% | 109% | 92% | 50.4237 | Loss >30% | 977(38) |  | 1341(697.5)
105 | 1120 | DRG | JAMA MASJID | JMS017 | TG-JMS017A-2 | DT-2 | KUCHA DAKHINI RAI:PL | 2 | 990 | 19506022 | 826 | 2019-06-11 05:00 | 234 | 1026 | 391 | 1793 | 201 | 861 | 862 | 672 | 47.5 |  |  | 47.5 | 83% | 67% | 83% | 71% | 50.4237 | Loss >30% |  |  | 1042(253.5) |  | 1150(595) | 1096(262)
106 | 1120 | DRG | JAMA MASJID | JMS018 | TG-JMS018A-1 | DT-1 | MOHALLA QUABRISTAN:PL | 1 | 990 | 19501666 | 909 | 2019-06-05 05:00 | 348 | 1504 | 270 | 1167 | 292 | 1264 | 300 | 330.5 | 388.5 | 1 |  | 389.5 | 92% | 84% | 83% | 88% | 59.2166 | Loss >30% |  | 914(251.5) | 985(522) | 971(360) | 916(336) | 843(84.5)
107 | 1120 | DRG | JAMA MASJID | JMS019 | TG-JMS019A-1 | DT-1 | MOTHER DAIRY:K | 1 | 630 | 19500379 | 635 | 2019-06-05 02:00 | 283 | 1194 | 169 | 704 | 183 | 769 | 461 | 447.5 | 259.5 | 9 | 1 | 269.5 | 101% | 77% | 89% | 96% | 40.1033 | Loss >30% |  | 569(44) | 677(444.5) | 597(321.5) | 558(174) | 486(25.5)
108 | 1120 | DRG | JAMA MASJID | JMS021 | TG-JMS021A-1 | DT-1 | NEW DUJANA HOUSE 8 PANEL:ID | 8 | 990 | 19500204 | 544 | 2019-06-01 20:30 | 181 | 797 | 167 | 737 | 196 | 877 | 121 | 719.5 |  |  |  | 0 | 54% | 38% | 55% | 55% | 50.6818 | Loss >30%
109 | 1120 | DRG | JAMA MASJID | JMS021 | TG-JMS021A-2 | DT-2 | NEW DUJANA HOUSE 8 PANEL:ID | 8 | 990 | 19500205 | 588 | 2019-06-03 04:00 | 179 | 750 | 186 | 780 | 223 | 926 | 163 | 720 |  |  |  | 0 | 59% | 54% | 51% | 51% | 50.6818 | Loss >30%
110 | 1120 | DRG | JAMA MASJID | JMS021 | TG-JMS021A-3 | DT-3 | NEW DUJANA HOUSE 8 PANEL:ID | 8 | 990 | 19503567 | 810 | 2019-06-03 04:00 | 308 | 1352 | 270 | 1160 | 233 | 1005 | 301 | 651 | 68.5 |  |  | 68.5 | 82% | 75% | 74% | 72% | 50.6818 | Loss >30% |  | 792(69) | 858(242) | 821(99)
111 | 1120 | DRG | JAMA MASJID | JMS021 | TG-JMS021A-4 | DT-4 | NEW DUJANA HOUSE 8 PANEL:ID | 8 | 990 | 19500203 | 1022 | 2019-06-02 04:30 | 377 | 1608 | 272 | 1157 | 373 | 1597 | 445 | 266 | 368 | 82 | 3.5 | 453.5 | 103% | 93% | 89% | 95% | 50.6818 | Loss >30% | 808(36) | 977(334) | 1122(578) | 1018(466) | 924(398.5) | 876(84.5)
112 | 1120 | DRG | JAMA MASJID | JMS021 | TG-JMS021A-5 | DT-5 | NEW DUJANA HOUSE 8 PANEL:ID | 8 | 990 | 19500202 | 1084 | 2019-06-11 00:30 | 416 | 1832 | 328 | 1436 | 341 | 1479 | 377 | 152.5 | 378.5 | 138 | 50.5 | 567 | 109% | 100% | 95% | 104% | 50.6818 | Loss >30% |  |  | 1163(463) | 1112(582.5) | 1023(560) | 943(144.5)
113 | 1120 | DRG | JAMA MASJID | JMS021 | TG-JMS021A-6 | DT-6 | NEW DUJANA HOUSE 8 PANEL:ID | 8 | 990 | 19500201 | 830 | 2019-06-10 23:30 | 334 | 1473 | 282 | 1220 | 214 | 930 | 471 | 637.5 | 82.5 |  |  | 82.5 | 82% | 68% | 80% | 84% | 50.6818 | Loss >30% |  | 845(119.5) | 949(349.5) | 933(279)
114 | 1120 | DRG | JAMA MASJID | JMS021 | TG-JMS021A-7 | DT-7 | NEW DUJANA HOUSE 8 PANEL:ID | 8 | 990 | 19505289 | 713 | 2019-06-14 06:00 | 395 | 1942 | 147 | 634 | 171 | 789 | 1238 | 719.5 | 0.5 |  |  | 0.5 | 69% | 72% | 63% | 64% | 50.6818 | Loss >30%
115 | 1120 | DRG | JAMA MASJID | JMS021 | TG-JMS021A-8 | DT-8 | NEW DUJANA HOUSE 8 PANEL:ID | 8 | 990 | 19506157 | 824 | 2019-06-02 03:00 | 299 | 1208 | 189 | 771 | 336 | 1400 | 558 | 649.5 | 68 |  |  | 68 | 83% | 75% | 72% | 72% | 50.6818 | Loss >30% |  |  | 1016(169.5) | 949(97.5) | 873(31)
116 | 1120 | DRG | JAMA MASJID | JMS022 | TG-JMS022A-1 | DT-1 | OLD DUJANA:K | 2 | 990 | 19506594 | 1180 | 2019-06-02 04:00 | 361 | 1524 | 308 | 1305 | 510 | 2227 | 834 | 193.5 | 352 | 144.5 | 29 | 525.5 | 119% | 104% | 114% | 100% | 51.5596 | Loss >30% | 837(42.5) | 900(97.5) |  |  | 902(88.5)
117 | 1120 | DRG | JAMA MASJID | JMS022 | TG-JMS022A-2 | DT-2 | OLD DUJANA:K | 2 | 990 | 19500383 | 1002 | 2019-06-03 | 355 | 1585 | 266 | 1167 | 381 | 1717 | 497 | 269.5 | 393.5 | 53.5 | 3.5 | 450.5 | 101% | 90% | 96% | 101% | 51.5596 | Loss >30% | 875(61) | 1020(371) | 1115(560) | 1069(468.5) | 923(409) | 894(133.5)
118 | 1120 | DRG | JAMA MASJID | JMS023 | TG-JMS023A-1 | DT-1 | SHEESH MAHAL:K | 2 | 990 | 19501661 | 1003 | 2019-06-30 01:30 | 384 | 1613 | 335 | 1410 | 284 | 1187 | 369 | 292.5 | 330 | 93.5 | 3.5 | 427 | 101% | 90% | 88% | 96% | 41.1752 | Loss >30% | 828(32) | 929(298.5) | 1048(506.5) | 999(311.5) | 927(301) | 865(85)
119 | 1120 | DRG | JAMA MASJID | JMS023 | TG-JMS023A-2 | DT-2 | SHEESH MAHAL:K | 2 | 990 | 19506663 | 839 | 2019-06-30 01:30 | 231 | 975 | 296 | 1261 | 312 | 1332 | 327 | 587.5 | 132 |  |  | 132 | 85% | 75% | 71% | 74% | 41.1752 | Loss >30% |  | 905(170.5) | 878(181) | 874(128.5) | 758(29)
120 | 1120 | DRG | JAMA MASJID | JMS024 | TG-JMS024A-1 | DT-1 | SSA ROAD:PL:PG | 2 | 990 | 19503516 | 1035 | 2019-06-30 02:30 | 388 | 1702 | 307 | 1336 | 341 | 1473 | 321 | 517 | 183 | 18 | 1 | 202 | 105% | 96% | 87% | 95% | 25.9097 | Loss 20-30% |  |  | 1091(477) | 1085(496.5) | 949(407)
121 | 1120 | DRG | JAMA MASJID | JMS024 | TG-JMS024A-2 | DT-2 | SSA ROAD:PL:PG | 2 | 990 | 19500074 | 933 | 2019-06-03 | 283 | 1225 | 389 | 1691 | 260 | 1104 | 537 | 672 | 40 | 3.5 |  | 43.5 | 94% | 77% | 84% | 93% | 25.9097 | Loss 20-30% |  | 938(27)
122 | 1120 | DRG | JAMA MASJID | JMS025 | TG-JMS025A-1 | DT-1 | TIRAHA BAIRAM KHAN:ID | 2 | 990 | 19500357 | 810 | 2019-06-30 00:30 | 278 | 1188 | 269 | 1146 | 263 | 1113 | 65 | 630 | 86 |  |  | 86 | 82% | 72% | 71% | 77% | 49.4643 | Loss >30% |  | 766(29.5) | 832(134.5) | 831(80)
123 | 1120 | DRG | JAMA MASJID | JMS025 | TG-JMS025A-2 | DT-2 | TIRAHA BAIRAM KHAN:ID | 2 | 990 | 19500359 | 1407 | 2019-06-01 22:30 | 433 | 1843 | 488 | 2078 | 486 | 2085 | 239 | 33.5 | 194 | 156.5 | 335 | 685.5 | 140% | 116% | 140% | 142% | 49.4643 | Loss >30% | 1180(365.5) | 1501(626) | 1458(579) |  |  | 1108(382)
124 | 1120 | DRG | JAMA MASJID | JMS026 | TG-JMS026A-1 | DT-1 | URDU BAZAR:PG | 3 | 990 | 19506156 | 1074 | 2019-06-11 05:00 | 272 | 1161 | 284 | 1164 | 519 | 2367 | 1205 | 492 | 223.5 | 3.5 | 0.5 | 227.5 | 109% | 81% | 86% | 91% | 36.017 | Loss >30% | 965(113.5) |  | 782(43.5) |  | 1028(78) | 807(37)
125 | 1120 | DRG | JAMA MASJID | JMS026 | TG-JMS026A-2 | DT-2 | URDU BAZAR:PG | 3 | 990 | 19506751 | 979 | 2019-06-29 22:00 | 323 | 1428 | 330 | 1510 | 326 | 1451 | 73 | 719 |  | 0.5 |  | 0.5 | 69% | 54% | 68% | 99% | 36.017 | Loss >30%
126 | 1120 | DRG | JAMA MASJID | JMS026 | TG-JMS026A-3 | DT-3 | URDU BAZAR:PG | 3 | 990 | 19506481 | 542 | 2019-06-26 17:30 | 185 | 743 | 176 | 712 | 182 | 739 | 29 | 719.5 |  |  |  | 0 | 14% | 10% | 55% | 30% | 36.017 | Loss >30%
127 | 1120 | DRG | JAMA MASJID | JMS033 | TG-JMS033A-1 | DT-1 | HOTEL BROADWAY:K | 4 | 990 | 19500330 | 1013 | 2019-06-27 01:30 | 382 | 1671 | 348 | 1533 | 283 | 1218 | 402 | 386.5 | 249 | 83 | 1.5 | 333.5 | 102% | 90% | 82% | 94% | 58.7006 | Loss >30% |  | 891(89.5) | 996(379) | 941(235.5) | 909(228) | 834(71.5)
128 | 1120 | DRG | JAMA MASJID | JMS033 | TG-JMS033A-2 | DT-2 | HOTEL BROADWAY:K | 4 | 990 | 19503512 | 806 | 2019-06-26 17:00 | 256 | 1070 | 277 | 1162 | 273 | 1132 | 81 | 625.5 | 94.5 |  |  | 94.5 | 41% | 57% | 81% | 37% | 58.7006 | Loss >30%
129 | 1120 | DRG | JAMA MASJID | JMS033 | TG-JMS033A-3 | DT-3 | HOTEL BROADWAY:K | 4 | 990 | 19506159 | 1087 | 2019-06-02 03:00 | 471 | 2110 | 322 | 1386 | 294 | 1272 | 787 | 598.5 | 100.5 | 12 | 6 | 118.5 | 110% | 106% | 100% | 99% | 58.7006 | Loss >30% | 965(83) |  | 1155(583.5) | 1180(444.5) | 1032(418.5)
130 | 1120 | DRG | JAMA MASJID | JMS033 | TG-JMS033A-4 | DT-4 | HOTEL BROADWAY:K | 4 | 990 | 19505490 | 510 | 2019-06-25 05:00 | 222 | 954 | 215 | 888 | 74 | 304 | 619 | 718 |  |  |  | 0 | 52% | 43% | 46% | 43% | 58.7006 | Loss >30%
131 | 1120 | DRG | MINTO ROAD | MRD012 | TG-MRD012A-1 | DT-1 | KOTLA RD.:PL | 1 | 630 | 19500331 | 535 | 2019-06-06 14:30 | 173 | 744 | 189 | 819 | 173 | 749 | 72 | 654.5 | 65.5 |  |  | 65.5 | 41% | 55% | 85% | 47% | 4.1506 | Loss 0-5%
132 | 1120 | DRG | MINTO ROAD | MRD073 | TG-MRD073A-1 | DT-1 | SHAKOOR KI DANDI P/M | 1 | 630 | 19506142 | 586 | 2019-06-24 15:00 | 206 | 853 | 198 | 824 | 181 | 754 | 88 | 651 | 68 | 0.5 |  | 68.5 | 76% | 73% | 93% | 77% | 44.3119 | Loss >30% |  | 626(90) | 611(280.5) | 666(206) | 547(38)
133 | 1130 | PHG | B G ROAD | BGR003 | TG-BGR003A-1 | DT-1 | GALI BAHUJI: PL | 1 | 990 | 19506463 | 869 | 2019-06-12 17:30 | 295 | 1212 | 246 | 1006 | 328 | 1340 | 292 | 619.5 | 100.5 |  |  | 100.5 | 69% | 56% | 88% | 71% | 18.2556 | Loss 10-20% |  | 830(41.5) | 880(133) | 866(108.5) | 834(66.5)
134 | 1130 | PHG | B G ROAD | BGR004 | TG-BGR004A-1 | DT-1 | MODEL BASTI:PL | 2 | 400 | 19503551 | 220 | 2019-06-30 01:00 | 46 | 190 | 78 | 326 | 96 | 404 | 187 | 719.5 |  |  |  | 0 | 55% | 44% | 51% | 52% | 23.5321 | Loss 20-30%
135 | 1130 | PHG | B G ROAD | BGR004 | TG-BGR004A-2 | DT-2 | MODEL BASTI:PL | 2 | 990 | 19503047 | 804 | 2019-06-26 16:00 | 287 | 1192 | 245 | 1026 | 272 | 1139 | 146 | 652.5 | 67.5 |  |  | 67.5 | 71% | 57% | 81% | 71% | 23.5321 | Loss 20-30% |  | 825(59.5) | 886(25) | 855(154) | 764(64.5)
136 | 1130 | PHG | B G ROAD | BGR005 | TG-BGR005A-1 | DT-1 | CHIMNI MIL PL/M:PL | 2 | 990 | 19503586 | 861 | 2019-06-25 17:30 | 296 | 1304 | 286 | 1249 | 278 | 1226 | 69 | 512.5 | 206 |  |  | 206 | 64% | 55% | 87% | 66% | 36.0781 | Loss >30% |  |  | 851(87) | 902(176) | 926(169) | 901(112.5)
137 | 1130 | PHG | B G ROAD | BGR005 | TG-BGR005A-2 | DT-2 | CHIMNI MIL PL/M:PL | 2 | 990 | 19500047 | 839 | 2019-06-02 04:30 | 267 | 1199 | 289 | 1291 | 282 | 1269 | 84 | 564 | 155 |  |  | 155 | 85% | 79% | 77% | 77% | 36.0781 | Loss >30% |  | 820(91.5) | 861(287.5) | 818(115.5) | 774(25)
138 | 1130 | PHG | B G ROAD | BGR013 | TG-BGR013A-1 | DT-1 | FOOTA ROAD KIOSK:K | 1 | 990 | 19504867 | 996 | 2019-06-04 15:30 | 313 | 1331 | 405 | 1735 | 278 | 1167 | 506 | 536 | 131.5 | 50 | 0.5 | 182 | 39% | 36% | 101% | 39% | 4.0636 | Loss 0-5% |  | 935(134.5) | 1004(131) | 1026(70) | 951(163) | 839(118)
139 | 1130 | PHG | B G ROAD | BGR016 | TG-BGR016A-1 | DT-1 | GALI NEEM WALI:K | 1 | 990 | 19500079 | 850 | 2019-06-30 18:00 | 291 | 1200 | 267 | 1110 | 292 | 1220 | 101 | 628 | 91.5 |  |  | 91.5 | 66% | 73% | 86% | 78% | 11.0281 | Loss 10-20% |  |  | 798(59) | 797(36.5)
140 | 1130 | PHG | B G ROAD | BGR020 | TG-BGR020A-1 | DT-1 | AHATA KIDARA UNIT I:PM | 1 | 400 | 19506187 | 463 | 2019-06-01 19:00 | 238 | 1022 | 119 | 483 | 105 | 456 | 553 | 26.5 | 376.5 | 191.5 | 125 | 693 | 115% | 112% | 116% | 111% | 14.2431 | Loss 10-20% | 383(194) | 540(534) | 486(684) | 466(659.5) | 453(638.5) | 467(443.5)
141 | 1130 | PHG | B G ROAD | BGR021 | TG-BGR021A-1 | DT-1 | FILMISTAN:ID | 1 | 990 | 19505640 | 767 | 2019-06-29 16:00 | 254 | 1035 | 254 | 1039 | 260 | 1051 | 14 | 693 | 25 |  |  | 25 | 69% | 54% | 78% | 70% | 7.1012 | Loss 5-10% | 870(193) | 948(313.5) | 981(332.5) | 885(222) | 810(163) | 756(48)
142 | 1130 | PHG | B G ROAD | BGR022 | TG-BGR022A-1 | DT-1 | B. G. ROAD COMP CTR:ID | 4 | 990 | 19500084 | 544 | 2019-06-01 17:00 | 194 | 849 | 167 | 738 | 183 | 798 | 96 | 718.5 |  |  |  | 0 | 54% | 36% | 55% | 55% | 26.9675 | Loss 20-30%
143 | 1130 | PHG | B G ROAD | BGR022 | TG-BGR022A-2 | DT-2 | B. G. ROAD COMP CTR:ID | 4 | 990 | 19500091 | 541 | 2019-06-30 01:30 | 148 | 640 | 170 | 729 | 223 | 966 | 292 | 720 |  |  |  | 0 | 55% | 47% | 47% | 51% | 26.9675 | Loss 20-30%
144 | 1130 | PHG | B G ROAD | BGR022 | TG-BGR022A-3 | DT-3 | B. G. ROAD COMP CTR:ID | 4 | 990 | 19500092 | 628 | 2019-06-30 23:30 | 175 | 747 | 182 | 780 | 270 | 1150 | 388 | 719 |  |  |  | 0 | 62% | 45% | 56% | 63% | 26.9675 | Loss 20-30%
145 | 1130 | PHG | B G ROAD | BGR022 | TG-BGR022A-4 | DT-4 | B. G. ROAD COMP CTR:ID | 4 | 630 | 19505002 | 511 | 2019-06-11 03:30 | 181 | 749 | 172 | 707 | 159 | 656 | 80 | 621 | 97 |  |  | 97 | 81% | 72% | 73% | 77% | 26.9675 | Loss 20-30% |  | 507(69) | 564(207.5) | 532(114) | 494(57)
146 | 1130 | PHG | B G ROAD | BGR027 | TG-BGR027A-1 | DT-1 | JHABBAR MAL P/M:PKG | 1 | 990 | 19504832 | 900 | 2019-06-25 15:30 | 309 | 1305 | 285 | 1202 | 306 | 1289 | 96 | 573 | 142 | 3 |  | 145 | 5% | 19% | 91% | 8% | 4.698 | Loss 0-5% |  | 858(81) | 933(173) | 947(154.5) | 905(148.5) | 762(55.5)
147 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN007 | TG-CHN007A-1 | DT-1 | CHUNA MANDI:ID | 5 | 990 | 19505831 | 593 | 2019-06-28 15:00 | 339 | 1646 | 90 | 414 | 164 | 768 | 1099 | 719 |  |  |  | 0 | 39% | 30% | 60% | 40% | 9.8821 | Loss 5-10%
148 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN007 | TG-CHN007A-2 | DT-2 | CHUNA MANDI:ID | 5 | 990 | 19504674 | 668 | 2019-06-12 00:30 | 238 | 1004 | 224 | 947 | 206 | 877 | 110 | 720 |  |  |  | 0 | 67% | 48% | 65% | 66% | 9.8821 | Loss 5-10%
149 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN007 | TG-CHN007A-3 | DT-3 | CHUNA MANDI:ID | 5 | 990 | 19500085 | 912 | 2019-06-11 | 302 | 1302 | 303 | 1303 | 308 | 1321 | 19 | 498.5 | 219 | 2.5 |  | 221.5 | 92% | 71% | 84% | 90% | 9.8821 | Loss 5-10% |  | 924(128) | 990(297.5) | 974(82) | 822(58.5)
150 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN007 | TG-CHN007A-4 | DT-4 | CHUNA MANDI:ID | 5 | 990 | 19502770 | 585 | 2019-06-11 00:30 | 210 | 910 | 175 | 763 | 200 | 860 | 129 | 695 |  |  |  | 0 | 59% | 45% | 58% | 59% | 9.8821 | Loss 5-10% |  | 924(117.5) | 919(134)
151 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN007 | TG-CHN007A-5 | DT-5 | CHUNA MANDI:ID | 5 | 990 | 19505582 | 705 | 2019-06-12 00:30 | 225 | 928 | 170 | 697 | 310 | 1301 | 528 | 717 | 1 |  |  | 1 | 71% | 50% | 64% | 71% | 9.8821 | Loss 5-10%
152 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN008 | TG-CHN008A-1 | DT-1 | GALI NALWA:K | 1 | 990 | 19500138 | 784 | 2019-06-16 | 303 | 1257 | 255 | 1053 | 226 | 925 | 290 | 678.5 | 36 |  |  | 36 | 79% | 58% | 68% | 78% | 7.8738 | Loss 5-10% |  | 818(36) | 838(113.5) | 825(52)
153 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN009 | TG-CHN009A-1 | DT-1 | KRISHNA MKT. (K):K | 1 | 990 | 19506843 | 1032 | 2019-06-29 22:00 | 353 | 1532 | 337 | 1451 | 343 | 1472 | 73 | 335 | 325.5 | 51 | 8.5 | 385 | 101% | 76% | 102% | 104% | 3.9596 | Loss 0-5% |  |  | 797(62)
154 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN015 | TG-CHN015A-1 | DT-1 | LADOO GHATI:PL | 1 | 630 | 19500137 | 663 | 2019-06-11 23:30 | 228 | 1005 | 230 | 1007 | 206 | 896 | 110 | 475.5 | 184 | 54 | 5 | 243 | 105% | 80% | 74% | 105% | 6.5367 | Loss 5-10% |  | 587(93) | 664(213) | 633(172.5) | 547(109.5)
155 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN016 | TG-CHN016A-1 | DT-1 | 6: TOOTI PL/M:PL | 2 | 990 | 19506300 | 774 | 2019-06-06 02:30 | 424 | 2038 | 182 | 758 | 168 | 760 | 1279 | 710.5 | 9.5 |  |  | 9.5 | 78% | 61% | 57% | 75% | 9.4765 | Loss 5-10%
156 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN016 | TG-CHN016A-2 | DT-2 | 6: TOOTI PL/M:PL | 2 | 990 | 19504706 | 818 | 2019-06-30 00:30 | 258 | 1164 | 311 | 1404 | 249 | 1113 | 270 | 668 | 51.5 |  |  | 51.5 | 83% | 70% | 79% | 79% | 9.4765 | Loss 5-10% |  | 849(85) | 897(184.5) | 807(71.5)
157 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN020 | TG-CHN020A-1 | DT-1 | BASANT ROAD:K | 2 | 990 | 19504708 | 872 | 2019-06-05 23:30 | 306 | 1253 | 273 | 1116 | 294 | 1204 | 120 | 614 | 104 |  |  | 104 | 87% | 57% | 65% | 88% | 4.6607 | Loss 0-5% |  |  | 878(92) | 791(35)
158 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN020 | TG-CHN020A-2 | DT-2 | BASANT ROAD:K | 2 | 630 | 19506304 | 285 | 2019-06-11 23:30 | 135 | 534 | 79 | 310 | 71 | 280 | 241 | 718.5 |  |  |  | 0 | 45% | 34% | 34% | 45% | 4.6607 | Loss 0-5%
159 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN022 | TG-CHN022A-1 | DT-1 | GALI MANTOLA:PL | 3 | 630 | 19500029 | 542 | 2019-06-06 01:00 | 219 | 893 | 194 | 791 | 129 | 523 | 331 | 609 | 109 |  |  | 109 | 86% | 72% | 65% | 81% | 8.2009 | Loss 5-10% |  |  | 511(67) | 538(32)
160 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN022 | TG-CHN022A-2 | DT-2 | GALI MANTOLA:PL | 3 | 630 | 19500035 | 454 | 2019-06-06 01:00 | 158 | 661 | 123 | 513 | 174 | 733 | 195 | 717.5 | 1 |  |  | 1 | 72% | 51% | 53% | 66% | 8.2009 | Loss 5-10% |  | 584(88.5) | 585(169.5) | 573(84.5)
161 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN022 | TG-CHN022A-3 | DT-3 | GALI MANTOLA:PL | 3 | 990 | 19504552 | 499 | 2019-06-12 | 192 | 800 | 156 | 652 | 151 | 629 | 161 | 718.5 |  |  |  | 0 | 50% | 36% | 36% | 49% | 8.2009 | Loss 5-10% |  | 338(43) | 348(119) | 330(48.5)
162 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN023 | TG-CHN023A-1 | DT-1 | DARIBA PAN KIOSK:K | 3 | 990 | 19500167 | 723 | 2019-06-10 23:30 | 262 | 1058 | 244 | 979 | 217 | 877 | 157 | 716 | 3.5 |  |  | 3.5 | 72% | 51% | 61% | 73% | 3.1092 | Loss 0-5%
163 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN023 | TG-CHN023A-2 | DT-2 | DARIBA PAN KIOSK:K | 3 | 990 | 19502876 | 587 | 2019-06-30 01:00 | 221 | 923 | 157 | 623 | 209 | 852 | 272 | 719 |  |  |  | 0 | 59% | 42% | 46% | 59% | 3.1092 | Loss 0-5%
164 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN023 | TG-CHN023A-3 | DT-3 | DARIBA PAN KIOSK:K | 3 | 630 | 19506193 | 568 | 2019-06-11 01:00 | 205 | 846 | 201 | 821 | 162 | 658 | 176 | 646.5 | 71.5 | 1 |  | 72.5 | 90% | 71% | 64% | 89% | 3.1092 | Loss 0-5% | 545(61.5) | 733(250.5) | 787(336) | 560(151.5) | 515(68)
165 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN025 | TG-CHN025A-1 | DT-1 | PHG DISP.:ID | 4 | 990 | 19504613 | 497 | 2019-06-03 16:00 | 126 | 552 | 240 | 1062 | 132 | 579 | 497 | 720 |  |  |  | 0 | 45% | 39% | 50% | 45% | 15.5206 | Loss 10-20% |  | 825(79) | 917(103)
166 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN025 | TG-CHN025A-2 | DT-2 | PHG DISP.:ID | 4 | 990 | 19504701 | 450 | 2019-06-13 16:30 | 153 | 652 | 134 | 567 | 164 | 704 | 120 | 671.5 |  |  |  | 0 | 40% | 34% | 45% | 39% | 15.5206 | Loss 10-20%
167 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN025 | TG-CHN025A-3 | DT-3 | PHG DISP.:ID | 4 | 990 | 19504675 | 1066 | 2019-06-10 22:30 | 344 | 1548 | 369 | 1675 | 353 | 1592 | 111 | 366 | 301 | 44 | 8.5 | 353.5 | 105% | 81% | 94% | 108% | 15.5206 | Loss 10-20% |  |  | 890(99) | 911(166) | 790(27)
168 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN025 | TG-CHN025A-4 | DT-4 | PHG DISP.:ID | 4 | 630 | 19506038 | 920 | 2019-06-11 23:30 | 293 | 1287 | 265 | 1163 | 363 | 1655 | 443 | 549 | 148.5 | 9.5 | 13 | 171 | 144% | 114% | 103% | 146% | 15.5206 | Loss 10-20% |  | 534(31.5) | 621(111.5) | 678(85)
169 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN026 | TG-CHN026A-1 | DT-1 | GALI SCHOOL WALI:PL | 2 | 990 | 19504851 | 910 | 2019-06-29 23:00 | 373 | 1578 | 278 | 1164 | 260 | 1087 | 458 | 629 | 85.5 | 2 |  | 87.5 | 91% | 71% | 84% | 92% | 5.4223 | Loss 5-10% |  |  | 812(76)
170 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN026 | TG-CHN026A-2 | DT-2 | GALI SCHOOL WALI:PL | 2 | 990 | 19500026 | 978 | 2019-06-02 23:30 | 300 | 1317 | 297 | 1304 | 382 | 1719 | 409 | 577.5 | 121 | 11 |  | 132 | 95% | 74% | 84% | 99% | 5.4223 | Loss 5-10% |  | 865(63.5) | 914(225.5) | 826(109) | 778(39)
171 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM001 | TG-RAM001A-1 | DT-1 | HANUMAN MANDIR:PL | 2 | 630 | 19502877 | 593 | 2019-06-10 23:30 | 190 | 845 | 199 | 889 | 204 | 905 | 54 | 514.5 | 194 | 9 |  | 203 | 93% | 80% | 88% | 94% | 4.8984 | Loss 0-5% |  | 602(143.5) | 614(323.5) | 583(177.5) | 506(39.5)
172 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM001 | TG-RAM001A-2 | DT-2 | HANUMAN MANDIR:PL | 2 | 990 | 19506112 | 839 | 2019-06-30 00:30 | 247 | 1055 | 329 | 1405 | 264 | 1119 | 323 | 668.5 | 48.5 |  |  | 48.5 | 85% | 70% | 70% | 83% | 4.8984 | Loss 0-5% | 965(209.5) | 1121(355) | 857(63)
173 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM003 | TG-RAM003A-1 | DT-1 | KILA KADAM SHARIF:PG | 1 | 990 | 19500294 | 811 | 2019-06-28 23:30 | 313 | 1342 | 281 | 1258 | 218 | 962 | 345 | 654 | 65.5 |  |  | 65.5 | 81% | 62% | 74% | 82% | 7.2088 | Loss 5-10% |  | 817(44) | 869(129.5) | 846(75) | 767(28.5)
174 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM010 | TG-RAM010A-1 | DT-1 | MCD PARK:PG | 3 | 990 | 19500021 | 789 | 2019-06-26 17:30 | 270 | 1106 | 237 | 969 | 281 | 1153 | 165 | 706.5 | 12.5 |  |  | 12.5 | 72% | 59% | 80% | 68% | 10.7832 | Loss 10-20% |  | 809(27.5) | 829(65.5)
175 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM010 | TG-RAM010A-2 | DT-2 | MCD PARK:PG | 3 | 990 | 19500025 | 669 | 2019-06-11 23:00 | 220 | 904 | 239 | 978 | 210 | 860 | 103 | 702 |  |  |  | 0 | 65% | 63% | 60% | 68% | 10.7832 | Loss 10-20%
176 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM010 | TG-RAM010A-3 | DT-3 | MCD PARK:PG | 3 | 630 | 19504836 | 582 | 2019-06-30 06:30 | 189 | 775 | 181 | 745 | 211 | 870 | 113 | 479 | 238 | 2 |  | 240 | 91% | 92% | 91% | 90% | 10.7832 | Loss 10-20% | [5 empty] | 527(27.5)
177 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM011 | TG-RAM011A-1 | DT-1 | YOG MAYA:PG | 1 | 990 | 19505128 | 864 | 2019-06-27 01:00 | 348 | 1504 | 249 | 1080 | 267 | 1158 | 391 | 191 | 84.5 |  |  | 84.5 | 87% | 78% | 79% | 84% | 14.8706 | Loss 10-20% |  | 806(113) | 851(275.5) | 879(304) | 842(111)
178 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM025 | TG-RAM025A-1 | DT-1 | CHARA MANDI:K | 2 | 990 | 19500107 | 725 | 2019-06-11 | 266 | 1124 | 224 | 951 | 236 | 1008 | 153 | 710 | 10 |  |  | 10 | 73% | 60% | 62% | 73% | 6.2134 | Loss 5-10%
179 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM025 | TG-RAM025A-2 | DT-2 | CHARA MANDI:K | 2 | 630 | 19505958 | 555 | 2019-06-27 23:30 | 206 | 865 | 174 | 737 | 174 | 731 | 132 | 530 | 190 |  |  | 190 | 86% | 72% | 69% | 88% | 6.2134 | Loss 5-10% |  | 524(71) | 1004(151) | 529(117) | 502(89.5) | 484(26.5)
180 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM026 | TG-RAM026A-1 | DT-1 | BAGICHI ALLUDDIN:K | 2 | 990 | 19504530 | 757 | 2019-06-06 04:30 | 222 | 925 | 277 | 1149 | 258 | 1070 | 197 | 687 | 31.5 |  |  | 31.5 | 77% | 74% | 73% | 76% | 6.8634 | Loss 5-10% |  |  | 791(61)
181 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM026 | TG-RAM026A-2 | DT-2 | BAGICHI ALLUDDIN:K | 2 | 990 | 19504529 | 805 | 2019-06-29 23:00 | 317 | 1310 | 249 | 1023 | 238 | 984 | 308 | 556.5 | 67.5 |  |  | 67.5 | 81% | 64% | 78% | 81% | 6.8634 | Loss 5-10% |  |  | 782(45.5) | 791(34)
182 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM027 | TG-RAM027A-1 | DT-1 | ARP QUARTERS.:K | 2 | 990 | 19504722 | 609 | 2019-06-30 | 208 | 889 | 213 | 912 | 188 | 800 | 102 | 719 |  |  |  | 0 | 61% | 48% | 45% | 61% | 14.1865 | Loss 10-20%
183 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM027 | TG-RAM027A-2 | DT-2 | ARP QUARTERS.:K | 2 | 990 | 19504649 | 851 | 2019-06-11 23:30 | 297 | 1276 | 229 | 985 | 325 | 1400 | 370 | 614 | 81.5 |  |  | 81.5 | 83% | 51% | 60% | 86% | 14.1865 | Loss 10-20%
184 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM029 | TG-RAM029A-1 | DT-1 | JHANDEWALAN P/M:PL | 1 | 630 | 19503789 | 524 | 2019-06-03 16:00 | 164 | 698 | 164 | 705 | 196 | 837 | 135 | 673.5 | 46 |  |  | 46 | 45% | 32% | 83% | 47% | 4.3876 | Loss 0-5% |  |  | 499(36.5) | 527(40)
185 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM030 | TG-RAM030A-1 | DT-1 | KABIR BASTI:PL | 1 | 630 | 19504709 | 503 | 2019-06-03 21:30 | 141 | 598 | 202 | 872 | 160 | 689 | 241 | 669.5 | 26 |  |  | 26 | 57% | 37% | 75% | 80% | 6.2921 | Loss 5-10%
186 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM031 | TG-RAM031A-1 | DT-1 | GALI NO. 5 MULTANI DHANDA:PKG | 1 | 990 | 19506192 | 965.3712 | 2019-06-03 02:30 | 429.1978 | 1810.5028 | 257.1789 | 1050.9537 | 278.9945 | 1149.4499 | 715.4045 | 387 | 303.5 | 28 |  | 331.5 | 98% | 78% | 97% | 97% | 11.9669 | Loss 10-20% |  | 944(50.5) | 954(237) | 1143(197.5) | 982(83)
187 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM035 | TG-RAM035A-1 | DT-1 | AARAKASHA ROAD:PKG | 2 | 990 | 19505996 | 1011.4528 | 2019-06-12 01:00 | 398.7016 | 1631.2153 | 306.5522 | 1233.5606 | 306.199 | 1241.3307 | 393.8271 | 481.5 | 178 | 52.5 | 5 | 235.5 | 102% | 92% | 83% | 99% | 4.0248 | Loss 0-5% | 914(32) | 1159(282.5) | 1145(259.5) | 1016(238) | 1060(226) | 860(110)
188 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM035 | TG-RAM035A-2 | DT-2 | AARAKASHA ROAD:PKG | 2 | 990 | 19505638 | 908 | 2019-06-28 23:30 | 105 | 450 | 434 | 1873 | 369 | 1584 | 1303 | 680.5 | 38 | 0.5 |  | 38.5 | 89% | 72% | 75% | 92% | 4.0248 | Loss 0-5% |  |  | 1076(131) | 1229(169)
189 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM044 | TG-RAM044A-1 | DT-1 | DB GUPTA ROAD BUS STOP | 1 | 630 | 19506758 | 757 | 2019-06-06 02:30 | 177 | 724 | 225 | 997 | 355 | 1680 | 852 | 565 | 107.5 | 29 | 18.5 | 155 | 120% | 94% | 91% | 109% | 7.8851 | Loss 5-10%
190 | 1130 | PHG | PP QUARTERS | PPQ001 | TG-PPQ001A-1 | DT-1 | RAILWAY BOOKING P/M:PL | 2 | 990 | 19505722 | 711 | 2019-06-04 14:30 | 227 | 967 | 240 | 1015 | 245 | 1029 | 57 | 715 | 3.5 |  |  | 3.5 | 14% | 14% | 72% | 16% | 9.722 | Loss 5-10%
191 | 1130 | PHG | PP QUARTERS | PPQ001 | TG-PPQ001A-2 | DT-2 | RAILWAY BOOKING P/M:PL | 2 | 400 | 19504817 | 366 | 2019-06-15 16:00 | 114 | 426 | 133 | 489 | 120 | 451 | 55 | 572.5 | 143.5 | 1 |  | 144.5 | 7% | 12% | 92% | 15% | 9.722 | Loss 5-10% |  | 314(47) | 347(144.5) | 355(106.5) | 322(71.5)
192 | 1130 | PHG | PP QUARTERS | PPQ003 | TG-PPQ003A-1 | DT-1 | KHURSHEED MARKET:ID | 3 | 990 | 19500125 | 811 | 2019-06-29 15:00 | 285 | 1228 | 264 | 1129 | 262 | 1126 | 100 | 617 | 103 |  |  | 103 | 3% | 4% | 82% | 9% | 24.4113 | Loss 20-30% |  |  | 802(139.5) | 838(96.5) | 810(63)
193 | 1130 | PHG | PP QUARTERS | PPQ003 | TG-PPQ003A-2 | DT-2 | KHURSHEED MARKET:ID | 3 | 990 | 19500124 | 605 | 2019-06-12 16:30 | 179 | 729 | 227 | 934 | 198 | 821 | 178 | 720 |  |  |  | 0 | 2% | 7% | 61% | 6% | 24.4113 | Loss 20-30%
194 | 1130 | PHG | PP QUARTERS | PPQ003 | TG-PPQ003A-3 | DT-3 | KHURSHEED MARKET:ID | 3 | 400 | 19504631 | 264 | 2019-06-29 17:30 | 97 | 395 | 92 | 371 | 75 | 304 | 82 | 720 |  |  |  | 0 | 3% | 3% | 66% | 7% | 24.4113 | Loss 20-30%
195 | 1130 | PHG | PP QUARTERS | PPQ005 | TG-PPQ005A-1 | DT-1 | 12 TOOTI CHOWK:PKG | 2 | 990 | 19505684 | 975 | 2019-06-29 15:00 | 325 | 1417 | 310 | 1345 | 341 | 1478 | 116 | 565 | 104 | 46.5 |  | 150.5 | 4% | 19% | 99% | 10% | 6.912 | Loss 5-10% |  | 905(98.5) | 1185(197) | 1274(115) |  | 990(130.5)
196 | 1130 | PHG | PP QUARTERS | PPQ005 | TG-PPQ005A-2 | DT-2 | 12 TOOTI CHOWK:PKG | 2 | 990 | 19506191 | 624 | 2019-06-12 17:30 | 170 | 702 | 208 | 858 | 247 | 1027 | 282 | 719.5 |  |  |  | 0 | 43% | 39% | 63% | 40% | 6.912 | Loss 5-10%
197 | 1130 | PHG | PP QUARTERS | PPQ006 | TG-PPQ006A-1 | DT-1 | WEST END CINEMA:ID | 2 | 630 | 19500135 | 512 | 2019-06-29 13:00 | 199 | 843 | 157 | 658 | 157 | 661 | 183 | 642.5 | 77.5 |  |  | 77.5 | 18% | 30% | 81% | 19% | 32.8844 | Loss >30% |  |  | 510(76) | 494(63.5) | 488(37.5)
198 | 1130 | PHG | PP QUARTERS | PPQ006 | TG-PPQ006A-2 | DT-2 | WEST END CINEMA:ID | 2 | 630 | 19506190 | 981 | 2019-06-14 16:30 | 359 | 1521 | 364 | 1549 | 258 | 1079 | 456 | 494 | 24 | 12 | 188.5 | 224.5 | 10% | 33% | 156% | 14% | 32.8844 | Loss >30% | 707(203) | 862(241) | 906(228.5) | 906(239.5)
199 | 1130 | PHG | PP QUARTERS | PPQ012 | TG-PPQ012A-1 | DT-1 | A K TANKI P/M:ID | 4 | 990 | 19500116 | 514 | 2019-06-30 01:00 | 209 | 896 | 165 | 701 | 141 | 602 | 260 | 718.5 |  |  |  | 0 | 52% | 47% | 49% | 47% | 12.954 | Loss 10-20%
200 | 1130 | PHG | PP QUARTERS | PPQ012 | TG-PPQ012A-2 | DT-2 | A K TANKI P/M:ID | 4 | 990 | 19500120 | 503 | 2019-06-30 00:30 | 143 | 610 | 166 | 698 | 195 | 838 | 200 | 718.5 |  |  |  | 0 | 51% | 46% | 47% | 47% | 12.954 | Loss 10-20%
201 | 1130 | PHG | PP QUARTERS | PPQ012 | TG-PPQ012A-3 | DT-3 | A K TANKI P/M:ID | 4 | 990 | 19500117 | 621 | 2019-06-29 17:30 | 200 | 810 | 222 | 898 | 198 | 799 | 94 | 718.5 |  |  |  | 0 | 59% | 54% | 63% | 55% | 12.954 | Loss 10-20%
202 | 1130 | PHG | PP QUARTERS | PPQ012 | TG-PPQ012A-4 | DT-4 | A K TANKI P/M:ID | 4 | 400 | 19504724 | 328 | 2019-06-14 17:30 | 111 | 488 | 106 | 470 | 111 | 490 | 19 | 669 | 49.5 |  |  | 49.5 | 76% | 78% | 82% | 1% | 12.954 | Loss 10-20% |  |  | 290(25) |  | 305(44) | 301(37)
203 | 1130 | PHG | PP QUARTERS | PPQ015 | TG-PPQ015A-1 | DT-1 | OLD QASAB PURA:K | 2 | 990 | 19503520 | 776 | 2019-06-12 02:00 | 283 | 1182 | 224 | 934 | 269 | 1124 | 225 | 678.5 | 39.5 |  |  | 39.5 | 78% | 72% | 68% | 68% | 17.3046 | Loss 10-20% |  |  | 751(55) | 772(27)
204 | 1130 | PHG | PP QUARTERS | PPQ015 | TG-PPQ015A-2 | DT-2 | OLD QASAB PURA:K | 2 | 630 | 19506695 | 340 | 2019-06-30 00:30 | 102 | 433 | 129 | 541 | 110 | 464 | 96 | 718.5 |  |  |  | 0 | 54% | 51% | 46% | 49% | 17.3046 | Loss 10-20%
205 | 1130 | PHG | PP QUARTERS | PPQ023 | TG-PPQ023A-1 | DT-1 | NARIAN MARKET:K | 2 | 990 | 19504809 | 914 | 2019-06-25 16:00 | 277 | 1181 | 265 | 1110 | 371 | 1561 | 420 | 661.5 | 55.5 | 1 |  | 56.5 | 22% | 27% | 92% | 24% | 20.3662 | Loss 20-30%
206 | 1130 | PHG | PP QUARTERS | PPQ023 | TG-PPQ023A-2 | DT-2 | NARIAN MARKET:K | 2 | 990 | 19504968 | 569 | 2019-06-26 18:30 | 176 | 699 | 178 | 699 | 216 | 853 | 154 | 719 |  |  |  | 0 | 46% | 42% | 58% | 47% | 20.3662 | Loss 20-30%
207 | 1140 | SRD | CHHAPARWALAN | CPW032 | TG-CPW032A-1 | DT-1 | JOSHI ROAD KIOSK:K | 2 | 990 | 19506293 | 870 | 2019-06-03 | 287 | 1191 | 257 | 1079 | 326 | 1377 | 261 | 602 | 118 |  |  | 118 | 88% | 59% | 79% | 86% | 3.3209 | Loss 0-5%
208 | 1140 | SRD | CHHAPARWALAN | CPW032 | TG-CPW032A-2 | DT-2 | JOSHI ROAD KIOSK:K | 2 | 630 | 19505957 | 408 | 2019-06-10 23:30 | 116 | 487 | 166 | 709 | 126 | 536 | 202 | 720 |  |  |  | 0 | 64% | 48% | 59% | 65% | 3.3209 | Loss 0-5% |  |  | 589(72)
209 | 1140 | SRD | CHHAPARWALAN | CPW035 | TG-CPW035A-1 | DT-1 | AJMAL KHAN KIOSK | 2 | 990 | 19500400 | 563 | 2019-06-26 14:30 | 232 | 947 | 182 | 757 | 150 | 624 | 282 | 720 |  |  |  | 0 | 26% | 23% | 57% | 33% | 6.1661 | Loss 5-10%
210 | 1140 | SRD | CHHAPARWALAN | CPW035 | TG-CPW035A-2 | DT-2 | AJMAL KHAN KIOSK | 2 | 400 | 19505173 | 314 | 2019-06-03 14:30 | 155 | 685 | 80 | 354 | 78 | 342 | 337 | 693 | 27 |  |  | 27 | 28% | 35% | 78% | 35% | 6.1661 | Loss 5-10% |  | 323(37) | 333(97.5) | 380(48.5)
211 | 1140 | SRD | CHHAPARWALAN | CPW037 | TG-CPW037A-1 | DT-1 | 53 BLOCK RAMJAS ROAD:K | 1 | 990 | 19500315 | 923 | 2019-06-03 02:00 | 248 | 1003 | 268 | 1103 | 407 | 1664 | 617 | 626.5 | 88 | 1 |  | 89 | 93% | 80% | 67% | 82% | 4.1262 | Loss 0-5% |  |  | 804(54)
212 | 1140 | SRD | CHHAPARWALAN | CPW038 | TG-CPW038A-1 | DT-1 | 61 BLOCK RAMJAS ROAD PL/M:PL | 1 | 990 | 19504948 | 799 | 2019-06-03 00:30 | 290 | 1238 | 254 | 1086 | 256 | 1058 | 167 | 667 | 53 |  |  | 53 | 81% | 58% | 72% | 79% | 3.3351 | Loss 0-5% |  |  | 841(67.5)
213 | 1140 | SRD | CHHAPARWALAN | KKW001 | TG-KKW001A-1 | DT-1 | NANAK HOTEL K. BAGH:PL | 1 | 990 | 19503278 | 1029 | 2019-06-04 16:00 | 380 | 1675 | 319 | 1409 | 330 | 1452 | 248 | 528.5 | 121.5 | 40 | 5 | 166.5 | 23% | 51% | 104% | 29% | 2.5526 | Loss 0-5% |  | 911(139) | 941(162.5) | 917(110.5) | 889(77.5)
214 | 1140 | SRD | CHHAPARWALAN | KKW002 | TG-KKW002A-1 | DT-1 | MASJID WALA K. BAGH.:PL | 1 | 990 | 19506653 | 995 | 2019-06-15 16:00 | 328 | 1340 | 318 | 1305 | 349 | 1433 | 114 | 527.5 | 141.5 | 49.5 | 0.5 | 191.5 | 30% | 25% | 101% | 34% | 5.1071 | Loss 5-10% |  | 938(122) | 977(202) | 1037(83.5)
215 | 1140 | SRD | CHHAPARWALAN | KKW003 | TG-KKW003A-1 | DT-1 | ELAHI BUX:PL | 2 | 990 | 19503286 | 831 | 2019-06-29 15:30 | 271 | 1169 | 287 | 1235 | 273 | 1177 | 62 | 330.5 | 72 |  |  | 72 | 43% | 34% | 84% | 42% | 3.4866 | Loss 0-5%
216 | 1140 | SRD | CHHAPARWALAN | KKW003 | TG-KKW003A-2 | DT-2 | ELAHI BUX:PL | 2 | 990 | 19503288 | 630 | 2019-06-12 15:00 | 253 | 1068 | 180 | 757 | 197 | 833 | 281 | 719.5 |  |  |  | 0 | 27% | 22% | 64% | 28% | 3.4866 | Loss 0-5% |  |  | 744(26.5)
217 | 1140 | SRD | CHHAPARWALAN | KKW004 | TG-KKW004A-1 | DT-1 | BIRLA FLATS K. BAGH:PL | 2 | 990 | 19504500 | 842 | 2019-06-29 16:30 | 238 | 1027 | 282 | 1225 | 323 | 1404 | 326 | 641 | 78.5 |  |  | 78.5 | 48% | 41% | 85% | 47% | 7.6676 | Loss 5-10% |  |  | 768(36)
218 | 1140 | SRD | CHHAPARWALAN | KKW004 | TG-KKW004A-2 | DT-2 | BIRLA FLATS K. BAGH:PL | 2 | 990 | 19500429 | 838 | 2019-06-15 15:30 | 247 | 1028 | 296 | 1234 | 294 | 1218 | 199 | 578.5 | 141 |  |  | 141 | 33% | 26% | 85% | 36% | 7.6676 | Loss 5-10% |  | 806(49.5) | 847(153.5) | 890(107) | 784(65)
219 | 1140 | SRD | CHHAPARWALAN | KKW010 | TG-KKW010A-1 | DT-1 | POLICE QTR. K. BAGH:PL | 3 | 990 | 19500312 | 743 | 2019-06-11 16:30 | 216 | 941 | 244 | 1065 | 283 | 1226 | 248 | 683.5 | 35.5 |  |  | 35.5 | 11% | 10% | 75% | 24% | 3.5235 | Loss 0-5% |  |  | 784(88.5) | 777(53) | 783(25.5)
220 | 1140 | SRD | CHHAPARWALAN | KKW010 | TG-KKW010A-2 | DT-2 | POLICE QTR. K. BAGH:PL | 3 | 990 | 19500430 | 352 | 2019-06-26 12:00 | 115 | 488 | 129 | 550 | 108 | 455 | 83 | 719.5 |  |  |  | 0 | 10% | 8% | 36% | 14% | 3.5235 | Loss 0-5%
221 | 1140 | SRD | CHHAPARWALAN | KKW010 | TG-KKW010A-3 | DT-3 | POLICE QTR. K. BAGH:PL | 3 | 630 | 19501358 | 313 | 2019-06-11 14:30 | 113 | 485 | 103 | 439 | 96 | 413 | 63 | 719 |  |  |  | 0 | 10% | 8% | 50% | 16% | 3.5235 | Loss 0-5%
222 | 1140 | SRD | CHHAPARWALAN | KKW013 | TG-KKW013A-1 | DT-1 | PO NO. 1 K. BAGH:PL | 2 | 990 | 19500426 | 817 | 2019-06-11 17:00 | 298 | 1258 | 275 | 1155 | 244 | 1015 | 212 | 704.5 | 13.5 |  |  | 13.5 | 10% | 15% | 83% | 17% | 7.6665 | Loss 5-10%
223 | 1140 | SRD | CHHAPARWALAN | KKW013 | TG-KKW013A-2 | DT-2 | PO NO. 1 K. BAGH:PL | 2 | 990 | 19505447 | 817 | 2019-06-12 14:00 | 258 | 1091 | 300 | 1278 | 259 | 1089 | 188 | 630.5 | 88.5 |  |  | 88.5 | 15% | 15% | 83% | 19% | 7.6665 | Loss 5-10% | 802(27.5) | 1085(129) | 1034(148) | 874(71.5)
224 | 1140 | SRD | CHHAPARWALAN | KKW017 | TG-KKW017A-1 | DT-1 | PO NO. 5 K. BAGH:PG | 1 | 990 | 19503298 | 888 | 2019-06-29 13:00 | 310 | 1352 | 301 | 1308 | 276 | 1196 | 139 | 548 | 171.5 |  |  | 171.5 | 5% | 61% | 90% | 13% | 3.5948 | Loss 0-5% |  | 864(104) | 871(154.5) | 818(90) | 814(50)
225 | 1140 | SRD | CHHAPARWALAN | KKW018 | TG-KKW018A-1 | DT-1 | H S ROAD BASEMENT:ID | 6 | 990 | 19500620 | 949.1251 | 2019-06-04 16:30 | 316.2925 | 1364.2707 | 345.4483 | 1484.1396 | 287.3842 | 1222.5994 | 226.7626 | 515 | 178 | 25.5 |  | 203.5 | 6% | 8% | 96% | 38% | 6.961 | Loss 5-10% |  |  | 760(72) |  | 773(49)
226 | 1140 | SRD | CHHAPARWALAN | KKW018 | TG-KKW018A-2 | DT-2 | H S ROAD BASEMENT:ID | 6 | 990 | 19500417 | 808 | 2019-06-30 14:30 | 279 | 1105 | 260 | 1016 | 269 | 1063 | 77 | 583 | 136.5 |  |  | 136.5 | 5% | 6% | 82% | 37% | 6.961 | Loss 5-10% |  |  | 781(94.5) | 755(46.5)
227 | 1140 | SRD | CHHAPARWALAN | KKW018 | TG-KKW018A-3 | DT-3 | H S ROAD BASEMENT:ID | 6 | 990 | 19500418 | 988 | 2019-06-15 15:30 | 322 | 1341 | 294 | 1221 | 372 | 1543 | 282 | 512 | 148 | 59.5 |  | 207.5 | 9% | 7% | 100% | 29% | 6.961 | Loss 5-10% |  | 794(48) | 854(126.5) | 837(57.5)
228 | 1140 | SRD | CHHAPARWALAN | KKW018 | TG-KKW018A-4 | DT-4 | H S ROAD BASEMENT:ID | 6 | 630 | 19502004 | 234 | 2019-06-02 15:00 | 63 | 253 | 113 | 462 | 58 | 236 | 218 | 720 |  |  |  | 0 | 2% | 2% | 37% | 23% | 6.961 | Loss 5-10%
229 | 1140 | SRD | CHHAPARWALAN | KKW018 | TG-KKW018A-5 | DT-5 | H S ROAD BASEMENT:ID | 6 | 630 | 19502915 | 218 | 2019-06-02 18:30 | 80 | 339 | 75 | 317 | 63 | 266 | 65 | 719 |  |  |  | 0 | 2% | 2% | 35% | 24% | 6.961 | Loss 5-10%
230 | 1140 | SRD | CHHAPARWALAN | RJN030 | TG-RJN030A-1 | DT-1 | SP.MUKERJI MKT. FAIZ RD. P/M NO. 2:PL | 2 | 990 | 19503297 | 675 | 2019-06-30 | 201 | 827 | 262 | 1077 | 213 | 872 | 231 | 717.5 |  |  |  | 0 | 68% | 49% | 67% | 67% | 5.1093 | Loss 5-10%
231 | 1140 | SRD | CHHAPARWALAN | RJN030 | TG-RJN030A-2 | DT-2 | SP.MUKERJI MKT. FAIZ RD. P/M NO. 2:PL | 2 | 400 | 19505972 | 393 | 2019-06-02 02:00 | 76 | 311 | 112 | 458 | 206 | 881 | 513 | 631.5 | 82.5 | 3.5 |  | 86 | 98% | 59% | 90% | 96% | 5.1093 | Loss 5-10% |  | 398(201.5) | 436(404) | 490(260) |  | 357(41)
232 | 1140 | SRD | CHHAPARWALAN | RJN037 | TG-RJN037A-1 | DT-1 | 2E JHANDEWALAN PL/M(PARK):PL | 3 | 990 | 19500714 | 854.6998 | 2019-06-11 15:00 | 308.1731 | 1295.8252 | 263.9132 | 1106.508 | 282.6135 | 1182.6315 | 164.9979 | 684 | 36 |  |  | 36 | 21% | 37% | 86% | 27% | 5.453 | Loss 5-10%
233 | 1140 | SRD | CHHAPARWALAN | RJN037 | TG-RJN037A-2 | DT-2 | 2E JHANDEWALAN PL/M(PARK):PL | 3 | 990 | 19500411 | 401 | 2019-06-03 13:00 | 126 | 510 | 166 | 671 | 109 | 440 | 206 | 720 |  |  |  | 0 | 10% | 16% | 41% | 14% | 5.453 | Loss 5-10%
234 | 1140 | SRD | CHHAPARWALAN | RJN037 | TG-RJN037A-3 | DT-3 | 2E JHANDEWALAN PL/M(PARK):PL | 3 | 990 | 19503558 | 680 | 2019-06-21 12:00 | 218 | 899 | 248 | 1022 | 214 | 874 | 137 | 694 |  |  |  | 0 | 10% | 29% | 69% | 14% | 5.453 | Loss 5-10%
235 | 1140 | SRD | CHHAPARWALAN | RJN041 | TG-RJN041A-1 | DT-1 | JHANDENWALAN NO. 1:ID | 2 | 990 | 19500386 | 812 | 2019-06-14 13:00 | 244 | 1049 | 250 | 1063 | 318 | 1367 | 311 | 679 | 40 |  |  | 40 | 21% | 28% | 82% | 32% | 3.9932 | Loss 0-5%
236 | 1140 | SRD | CHHAPARWALAN | RJN041 | TG-RJN041A-2 | DT-2 | JHANDENWALAN NO. 1:ID | 2 | 990 | 19504595 | 532 | 2019-06-04 14:00 | 155 | 699 | 170 | 769 | 207 | 930 | 205 | 718.5 |  |  |  | 0 | 7% | 17% | 54% | 16% | 3.9932 | Loss 0-5%
237 | 1140 | SRD | PUSA ROAD | KKW006 | TG-KKW006A-1 | DT-1 | SATBHRAWA (K) STN.:ID | 2 | 990 | 19506040 | 611 | 2019-06-03 15:00 | 207 | 866 | 184 | 768 | 220 | 917 | 131 | 720 |  |  |  | 0 | 32% | 30% | 62% | 33% | 7.6136 | Loss 5-10%
238 | 1140 | SRD | PUSA ROAD | KKW006 | TG-KKW006A-2 | DT-2 | SATBHRAWA (K) STN.:ID | 2 | 630 | 19505386 | 507 | 2019-06-11 16:00 | 171 | 717 | 175 | 725 | 162 | 680 | 41 | 693 | 27 |  |  | 27 | 55% | 57% | 80% | 55% | 7.6136 | Loss 5-10% |  | 574(28) | 779(86) | 506(32)
239 | 1140 | SRD | PUSA ROAD | KKW007 | TG-KKW007A-1 | DT-1 | SHASTRI PARK (INDOOR):ID | 3 | 990 | 19503317 | 825 | 2019-06-14 13:30 | 239 | 1019 | 300 | 1284 | 286 | 1216 | 239 | 614.5 | 105.5 |  |  | 105.5 | 19% | 30% | 83% | 33% | 4.4668 | Loss 0-5% |  | 803(53) | 883(128.5) | 861(92.5) | 780(45.5)
240 | 1140 | SRD | PUSA ROAD | KKW007 | TG-KKW007A-2 | DT-2 | SHASTRI PARK (INDOOR):ID | 3 | 990 | 19503312 | 587 | 2019-06-06 15:30 | 194 | 845 | 194 | 853 | 199 | 874 | 26 | 720 |  |  |  | 0 | 32% | 41% | 59% | 38% | 4.4668 | Loss 0-5%
241 | 1140 | SRD | PUSA ROAD | KKW007 | TG-KKW007A-3 | DT-3 | SHASTRI PARK (INDOOR):ID | 3 | 990 | 19500106 | 743 | 2019-06-12 17:00 | 251 | 1053 | 231 | 967 | 260 | 1080 | 102 | 695 | 23 |  |  | 23 | 43% | 33% | 75% | 51% | 4.4668 | Loss 0-5% |  |  | 788(56.5) | 768(26.5)
242 | 1140 | SRD | PUSA ROAD | KKW008 | TG-KKW008A-1 | DT-1 | JESSA RAM HOSPITAL PACKAGE S/STN | 3 | 990 | 19503352 | 160 | 2019-06-14 18:00 | 78 | 322 | 55 | 227 | 27 | 110 | 184 | 696 |  |  |  | 0 | 5% | 5% | 16% | 9% | 4.019 | Loss 0-5%
243 | 1140 | SRD | PUSA ROAD | KKW008 | TG-KKW008A-2 | DT-2 | JESSA RAM HOSPITAL PACKAGE S/STN | 3 | 990 | 19503322 | 156 | 2019-06-29 16:00 | 37 | 155 | 53 | 223 | 66 | 276 | 105 | 696 |  |  |  | 0 | 10% | 10% | 16% | 10% | 4.019 | Loss 0-5%
244 | 1140 | SRD | PUSA ROAD | KKW008 | TG-KKW008A-3 | DT-3 | JESSA RAM HOSPITAL PACKAGE S/STN | 3 | 630 | 19505210 | 731 | 2019-06-08 17:30 | 255 | 1060 | 235 | 987 | 241 | 1015 | 64 | 428.5 | 200.5 | 89.5 | 1.5 | 291.5 | 56% | 44% | 116% | 87% | 4.019 | Loss 0-5% |  |  | 521(120) | 549(102) | 523(63)
245 | 1140 | SRD | PUSA ROAD | KKW020 | TG-KKW020A-1 | DT-1 | 39, BEEDEN PURA (W):PL | 2 | 990 | 19503258 | 637 | 2019-06-12 16:30 | 181 | 752 | 218 | 906 | 237 | 983 | 204 | 720 |  |  |  | 0 | 28% | 21% | 64% | 30% | 4.0132 | Loss 0-5%
246 | 1140 | SRD | PUSA ROAD | KKW020 | TG-KKW020A-2 | DT-2 | 39, BEEDEN PURA (W):PL | 2 | 630 | 19505869 | 513 | 2019-06-29 15:30 | 158 | 678 | 183 | 782 | 172 | 734 | 90 | 622 | 96.5 |  |  | 96.5 | 34% | 29% | 81% | 44% | 4.0132 | Loss 0-5%
247 | 1140 | SRD | PUSA ROAD | KKW025 | TG-KKW025A-1 | DT-1 | 8 C WEA KAROL BAGH JASSA RAM | 2 | 990 | 19506095 | 1011 | 2019-06-11 14:00 | 346 | 1482 | 309 | 1320 | 356 | 1521 | 185 | 557.5 | 122 | 30.5 | 2 | 154.5 | 46% | 70% | 102% | 59% | 6.9893 | Loss 5-10% |  |  | 829(60) | 800(33.5)
248 | 1140 | SRD | PUSA ROAD | KKW025 | TG-KKW025A-2 | DT-2 | 8 C WEA KAROL BAGH JASSA RAM | 2 | 400 | 19506378 | 404 | 2019-06-24 16:00 | 131 | 553 | 145 | 618 | 128 | 536 | 75 | 601.5 | 89 | 27.5 | 1.5 | 118 | 61% | 63% | 101% | 66% | 6.9893 | Loss 5-10%
249 | 1140 | SRD | PUSA ROAD | KKW028 | TG-KKW028A-1 | DT-1 | H.S.RD. KHATTAWAL K. BAGH:PL | 2 | 990 | 19505272 | 959 | 2019-06-01 | 287 | 1205 | 390 | 1653 | 282 | 1188 | 457 | 383.5 | 311 | 25 |  | 336 | 97% | 73% | 95% | 91% | 7.0993 | Loss 5-10% |  | 894(134) | 1114(350.5) | 990(250) | 866(103.5)
250 | 1140 | SRD | PUSA ROAD | KKW028 | TG-KKW028A-2 | DT-2 | H.S.RD. KHATTAWAL K. BAGH:PL | 2 | 990 | 19505496 | 914 | 2019-06-29 16:00 | 296 | 1235 | 352 | 1473 | 265 | 1109 | 320 | 535 | 180 | 4.5 |  | 184.5 | 76% | 60% | 92% | 74% | 7.0993 | Loss 5-10% |  |  |  | 1085(165) | 1044(138) | 753(38)
251 | 1140 | SRD | PUSA ROAD | KKW030 | TG-KKW030A-1 | DT-1 | NALA WALA H. S. RD.:PL | 1 | 990 | 19503266 | 784 | 2019-06-30 14:30 | 228 | 940 | 259 | 1079 | 296 | 1232 | 253 | 656.5 | 39.5 |  |  | 39.5 | 60% | 45% | 79% | 62% | 7.0102 | Loss 5-10% |  | 823(54.5) | 909(170) | 904(140) | 945(113.5) | 751(30.5)
252 | 1140 | SRD | PUSA ROAD | KKW031 | TG-KKW031A-1 | DT-1 | 13 BLK WEA K. BAGH:PACKAGE S/STN | 4 | 990 | 19504622 | 576 | 2019-06-14 12:30 | 181 | 814 | 194 | 873 | 201 | 902 | 78 | 695.5 |  |  |  | 0 | 6% | 9% | 58% | 35% | 4.8654 | Loss 0-5%
253 | 1140 | SRD | PUSA ROAD | KKW031 | TG-KKW031A-2 | DT-2 | 13 BLK WEA K. BAGH:PACKAGE S/STN | 4 | 990 | 19504549 | 862 | 2019-06-26 14:00 | 287 | 1217 | 316 | 1331 | 259 | 1093 | 206 | 537.5 | 182.5 |  |  | 182.5 | 11% | 12% | 87% | 29% | 4.8654 | Loss 0-5% |  | 804(73) | 865(176) | 860(108) | 789(40)
254 | 1140 | SRD | PUSA ROAD | KKW031 | TG-KKW031A-3 | DT-3 | 13 BLK WEA K. BAGH:PACKAGE S/STN | 4 | 990 | 19504607 | 417 | 2019-06-04 14:00 | 127 | 538 | 146 | 622 | 144 | 610 | 78 | 719.5 |  |  |  | 0 | 8% | 7% | 42% | 22% | 4.8654 | Loss 0-5%
255 | 1140 | SRD | PUSA ROAD | KKW031 | TG-KKW031A-4 | DT-4 | 13 BLK WEA K. BAGH:PACKAGE S/STN | 4 | 630 | 19505207 | 491 | 2019-06-12 19:00 | 121 | 477 | 239 | 1025 | 131 | 535 | 522 | 715 | 5 |  |  | 5 | 3% | 3% | 78% | 38% | 4.8654 | Loss 0-5%
256 | 1140 | SRD | PUSA ROAD | KKW032 | TG-KKW032A-1 | DT-1 | 5WEA K BAGH KIOSK:PACKAGE S/STN | 3 | 990 | 19504636 | 696 | 2019-06-15 17:00 | 237 | 1033 | 211 | 916 | 248 | 1084 | 150 | 719 | 0.5 |  |  | 0.5 | 32% | 30% | 70% | 52% | 5.8564 | Loss 5-10% |  | 761(25.5) | 746(54) | 753(25.5)
257 | 1140 | SRD | PUSA ROAD | KKW032 | TG-KKW032A-2 | DT-2 | 5WEA K BAGH KIOSK:PACKAGE S/STN | 3 | 990 | 19504614 | 893 | 2019-06-14 13:00 | 279 | 1135 | 314 | 1293 | 300 | 1228 | 137 | 595 | 124 | 0.5 |  | 124.5 | 35% | 28% | 90% | 55% | 5.8564 | Loss 5-10%
258 | 1140 | SRD | PUSA ROAD | KKW032 | TG-KKW032A-3 | DT-3 | 5WEA K BAGH KIOSK:PACKAGE S/STN | 3 | 630 | 19505867 | 358 | 2019-06-04 15:00 | 122 | 531 | 122 | 534 | 114 | 498 | 34 | 719.5 |  |  |  | 0 | 31% | 28% | 57% | 40% | 5.8564 | Loss 5-10% | 518(95.5) | 571(231.5) | 608(279) | 600(210.5)
259 | 1140 | SRD | PUSA ROAD | KKW037 | TG-KKW037A-1 | DT-1 | 26 BEEDEN PURA P.L RD.:PL | 1 | 990 | 19504238 | 967 | 2019-06-12 16:00 | 356 | 1465 | 272 | 1155 | 339 | 1443 | 300 | 516 | 197 | 7 |  | 204 | 80% | 57% | 98% | 79% | 4.2336 | Loss 0-5% |  | 873(92) | 1052(265.5) | 1134(210) | 914(163.5) | 761(37.5)
260 | 1140 | SRD | PUSA ROAD | KKW039 | TG-KKW039A-1 | DT-1 | 40 REGER PURA P/M:PL | 1 | 990 | 19506093 | 950 | 2019-06-06 02:30 | 295 | 1301 | 231 | 968 | 423 | 1966 | 880 | 478 | 232.5 | 7.5 |  | 240 | 96% | 68% | 86% | 93% | 4.7152 | Loss 0-5% |  | 1143(88.5) | 937(214.5) | 1113(166) | 980(76)
261 | 1140 | SRD | PUSA ROAD | KKW046 | TG-KKW046A-1 | DT-1 | PUSA RD. CAMP CENTRE:ID | 4 | 990 | 19503332 | 875 | 2019-06-30 00:30 | 267 | 1101 | 289 | 1190 | 319 | 1330 | 200 | 600 | 96 |  |  | 96 | 88% | 66% | 68% | 86% | 11.22 | Loss 10-20% |  | 942(225.5) | 953(325) | 1025(293.5) | 873(133) | 818(62.5)
262 | 1140 | SRD | PUSA ROAD | KKW046 | TG-KKW046A-2 | DT-2 | PUSA RD. CAMP CENTRE:ID | 4 | 990 | 19503315 | 957 | 2019-06-11 23:30 | 279 | 1198 | 338 | 1472 | 340 | 1457 | 267 | 450 | 236.5 | 29 |  | 265.5 | 96% | 75% | 80% | 97% | 11.22 | Loss 10-20% |  | 963(154.5) | 1020(335) | 975(151.5)
263 | 1140 | SRD | PUSA ROAD | KKW046 | TG-KKW046A-3 | DT-3 | PUSA RD. CAMP CENTRE:ID | 4 | 990 | 19503546 | 761 | 2019-06-28 23:30 | 262 | 1102 | 248 | 1036 | 251 | 1051 | 60 | 673 | 23 |  |  | 23 | 74% | 53% | 74% | 77% | 11.22 | Loss 10-20% | 811(50.5) | 1109(393) | 1088(574) | 1131(424.5) | 935(295.5) | 808(97.5)
264 | 1140 | SRD | PUSA ROAD | KKW046 | TG-KKW046A-4 | DT-4 | PUSA RD. CAMP CENTRE:ID | 4 | 990 | 19505842 | 1023 | 2019-06-30 15:00 | 353 | 1495 | 327 | 1380 | 343 | 1445 | 100 | 457.5 | 231.5 | 29.5 | 1.5 | 262.5 | 79% | 62% | 103% | 80% | 11.22 | Loss 10-20%
265 | 1140 | SRD | PUSA ROAD | KKW049 | TG-KKW049A-1 | DT-1 | R. K. DASS-1 K. BAGH:K | 2 | 990 | 19504998 | 1175 | 2019-06-30 00:30 | 393 | 1574 | 393 | 1574 | 389 | 1535 | 39 | 271.5 | 293.5 | 90 | 65 | 448.5 | 119% | 96% | 99% | 118% | 5.3418 | Loss 5-10% |  | 945(166) | 1003(330) | 1032(272) | 899(120.5) | 821(25.5)
266 | 1140 | SRD | PUSA ROAD | KKW049 | TG-KKW049A-2 | DT-2 | R. K. DASS-1 K. BAGH:K | 2 | 990 | 19503292 | 810 | 2019-06-30 15:00 | 271 | 1061 | 293 | 1158 | 246 | 970 | 163 | 622.5 | 72.5 |  |  | 72.5 | 72% | 56% | 82% | 71% | 5.3418 | Loss 5-10% |  | 809(30.5) | 860(120) | 858(77.5)
267 | 1140 | SRD | PUSA ROAD | KKW050 | TG-KKW050A-1 | DT-1 | R.K.DASS-1/2 K. BAGH:K | 2 | 990 | 19503319 | 780 | 2019-06-30 00:30 | 296 | 1208 | 240 | 980 | 244 | 986 | 225 | 695 | 25 |  |  | 25 | 79% | 53% | 70% | 76% | 3.7533 | Loss 0-5%
268 | 1140 | SRD | PUSA ROAD | KKW050 | TG-KKW050A-2 | DT-2 | R.K.DASS-1/2 K. BAGH:K | 2 | 990 | 19506694 | 697 | 2019-06-30 | 277 | 1161 | 183 | 759 | 238 | 989 | 349 | 719.5 | 0.5 |  |  | 0.5 | 70% | 54% | 65% | 70% | 3.7533 | Loss 0-5%
269 | 1140 | SRD | PUSA ROAD | KKW059 | TG-KKW059A-1 | DT-1 | BAPU BHAWAN S/ST.:PL | 1 | 990 | 19504541 | 852 | 2019-06-30 00:30 | 306 | 1337 | 279 | 1206 | 267 | 1123 | 187 | 631.5 | 88.5 |  |  | 88.5 | 86% | 61% | 77% | 86% | 3.4863 | Loss 0-5% |  | 844(50.5) | 848(116) | 887(52.5)
270 | 1140 | SRD | PUSA ROAD | KKW067 | TG-KKW067A-1 | DT-1 | 5 BLOCK WEA KAROL BAGH KIOSK | 3 | 990 | 19503314 | 929 | 2019-06-11 15:00 | 287 | 1250 | 289 | 1255 | 353 | 1534 | 281 | 547.5 | 141.5 | 7 |  | 148.5 | 8% | 7% | 94% | 74% | 11.9368 | Loss 10-20% | 852(38) |  | 820(125.5) | 827(96) | 781(33)
271 | 1140 | SRD | PUSA ROAD | KKW067 | TG-KKW067A-2 | DT-2 | 5 BLOCK WEA KAROL BAGH KIOSK | 3 | 990 | 19505495 | 1094 | 2019-06-12 19:00 | 527 | 2312 | 304 | 1252 | 264 | 1050 | 1173 | 517.5 | 175.5 | 26.5 | 0.5 | 202.5 | 57% | 51% | 111% | 62% | 11.9368 | Loss 10-20% | 834(44) | 927(162.5) | 989(223) | 978(168) | 1008(165) | 780(71.5)
272 | 1140 | SRD | PUSA ROAD | KKW067 | TG-KKW067A-3 | DT-3 | 5 BLOCK WEA KAROL BAGH KIOSK | 3 | 630 | 19505709 | 256 | 2019-06-15 17:00 | 82 | 339 | 85 | 352 | 88 | 364 | 22 | 720 |  |  |  | 0 | 9% | 7% | 41% | 25% | 11.9368 | Loss 10-20%
273 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | EPN003 | TG-EPN003A-1 | DT-1 | 21 BLK. O. R. NAGAR:K | 3 | 990 | 19503328 | 923 | 2019-06-30 01:00 | 295 | 1240 | 318 | 1335 | 310 | 1295 | 83 | 610 | 105.5 | 4.5 |  | 110 | 93% | 70% | 75% | 91% | 6.3205 | Loss 5-10% |  | 833(30.5) | 920(94.5) | 890(46.5)
274 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | EPN003 | TG-EPN003A-2 | DT-2 | 21 BLK. O. R. NAGAR:K | 3 | 990 | 19503329 | 500 | 2019-06-30 00:30 | 106 | 438 | 180 | 752 | 213 | 894 | 404 | 720 |  |  |  | 0 | 50% | 38% | 38% | 50% | 6.3205 | Loss 5-10%
275 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | EPN003 | TG-EPN003A-3 | DT-3 | 21 BLK. O. R. NAGAR:K | 3 | 990 | 19504344 | 913 | 2019-06-10 13:00 | 327 | 1493 | 306 | 1402 | 280 | 1270 | 194 | 626.5 | 92.5 | 1 |  | 93.5 | 71% | 67% | 92% | 74% | 6.3205 | Loss 5-10% |  | 960(61.5)
276 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN006 | TG-RJN006A-1 | DT-1 | TIKONA PARK BAZAR MARG:PL | 3 | 990 | 19503361 | 917 | 2019-06-30 23:30 | 365 | 1577 | 256 | 1089 | 296 | 1261 | 429 | 619.5 | 98.5 | 2 |  | 100.5 | 90% | 62% | 75% | 93% | 8.2463 | Loss 5-10% |  | 977(79) | 978(159.5) | 1013(50.5)
277 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN006 | TG-RJN006A-2 | DT-2 | TIKONA PARK BAZAR MARG:PL | 3 | 990 | 19505747 | 791 | 2019-06-01 16:00 | 241 | 1075 | 307 | 1377 | 243 | 1079 | 300 | 685 | 35 |  |  | 35 | 72% | 54% | 80% | 75% | 8.2463 | Loss 5-10%
278 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN006 | TG-RJN006A-3 | DT-3 | TIKONA PARK BAZAR MARG:PL | 3 | 630 | 19505136 | 594 | 2019-06-06 03:00 | 106 | 435 | 288 | 1255 | 199 | 862 | 710 | 638.5 | 81 | 0.5 |  | 81.5 | 94% | 66% | 75% | 89% | 8.2463 | Loss 5-10%
279 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN007 | TG-RJN007A-1 | DT-1 | BAZAR MARG (K):K | 2 | 990 | 19503364 | 589 | 2019-06-30 01:00 | 184 | 760 | 204 | 841 | 201 | 834 | 78 | 696 |  |  |  | 0 | 59% | 41% | 44% | 59% | 4.1771 | Loss 0-5% |  | 863(41) | 826(32.5)
280 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN007 | TG-RJN007A-2 | DT-2 | BAZAR MARG (K):K | 2 | 630 | 19505084 | 702 | 2019-06-30 00:30 | 253 | 1099 | 208 | 889 | 241 | 1032 | 186 | 471.5 | 173.5 | 38 | 13 | 224.5 | 111% | 75% | 83% | 111% | 4.1771 | Loss 0-5% |  |  | 590(36) | 581(48)
281 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN011 | TG-RJN011A-1 | DT-1 | SALWAN SCHOOL OLD:PL | 4 | 990 | 19506581 | 982 | 2019-06-01 12:30 | 321 | 1367 | 320 | 1357 | 341 | 1445 | 83 | 549 | 161 | 9.5 |  | 170.5 | 34% | 68% | 99% | 38% | 6.1005 | Loss 5-10% | 898(126) | 1014(210.5) | 1103(237.5) |  | 872(63) | 879(141.5)
282 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN011 | TG-RJN011A-2 | DT-2 | SALWAN SCHOOL OLD:PL | 4 | 630 | 19504280 | 392 | 2019-06-01 03:00 | 161 | 656 | 113 | 459 | 118 | 482 | 186 | 720 |  |  |  | 0 | 62% | 42% | 43% | 55% | 6.1005 | Loss 5-10%
283 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN011 | TG-RJN011A-3 | DT-3 | SALWAN SCHOOL OLD:PL | 4 | 990 | 19504346 | 650 | 2019-06-01 15:30 | 215 | 907 | 217 | 919 | 217 | 919 | 12 | 719.5 |  |  |  | 0 | 42% | 35% | 66% | 45% | 6.1005 | Loss 5-10%
284 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN011 | TG-RJN011A-4 | DT-4 | SALWAN SCHOOL OLD:PL | 4 | 630 | 19505433 | 366 | 2019-06-03 14:00 | 132 | 550 | 112 | 468 | 122 | 510 | 71 | 718 |  |  |  | 0 | 24% | 42% | 58% | 29% | 6.1005 | Loss 5-10%
285 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN012 | TG-RJN012A-1 | DT-1 | SALWAN SCHOOL NEW:K | 3 | 990 | 19503377 | 931 | 2019-06-30 | 273 | 1149 | 337 | 1426 | 322 | 1370 | 253 | 664.5 | 51 | 3 |  | 54 | 94% | 63% | 69% | 94% | 7.5304 | Loss 5-10%
286 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN012 | TG-RJN012A-2 | DT-2 | SALWAN SCHOOL NEW:K | 3 | 990 | 19504309 | 224 | 2019-06-30 02:00 | 88 | 360 | 95 | 393 | 41 | 166 | 213 | 719 |  |  |  | 0 | 23% | 16% | 20% | 20% | 7.5304 | Loss 5-10% |  |  | 926(48.5)
287 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN012 | TG-RJN012A-3 | DT-3 | SALWAN SCHOOL NEW:K | 3 | 990 | 19506445 | 714 | 2019-06-01 23:30 | 279 | 1288 | 216 | 982 | 219 | 995 | 300 | 717.5 | 1.5 |  |  | 1.5 | 71% | 46% | 60% | 72% | 7.5304 | Loss 5-10%
288 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN013 | TG-RJN013A-1 | DT-1 | SETHI PETROL PUMP:ID | 3 | 990 | 19500413 | 565 | 2019-06-30 01:30 | 222 | 919 | 179 | 740 | 164 | 683 | 214 | 718.5 |  |  |  | 0 | 57% | 44% | 48% | 56% | 2.7739 | Loss 0-5%
289 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN013 | TG-RJN013A-2 | DT-2 | SETHI PETROL PUMP:ID | 3 | 990 | 19504685 | 1161 | 2019-06-30 01:00 | 355 | 1483 | 309 | 1276 | 497 | 2094 | 736 | 454.5 | 202 | 43 | 19 | 264 | 117% | 81% | 82% | 107% | 2.7739 | Loss 0-5% | 931(32.5) | 1240(312.5) | 1357(484) | 1017(154) | 821(48.5)
290 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN013 | TG-RJN013A-3 | DT-3 | SETHI PETROL PUMP:ID | 3 | 630 | 19503046 | 171 | 2019-06-12 00:30 | 68 | 273 | 29 | 118 | 74 | 301 | 170 | 718.5 |  |  |  | 0 | 27% | 21% | 24% | 25% | 2.7739 | Loss 0-5%
291 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN019 | TG-RJN019A-1 | DT-1 | SRD BUILDING OFFICE:ID | 2 | 990 | 19503282 | 872 | 2019-06-29 23:30 | 310 | 1318 | 247 | 1046 | 314 | 1340 | 284 | 637 | 83 |  |  | 83 | 87% | 64% | 76% | 88% | 5.408 | Loss 5-10%
292 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN019 | TG-RJN019A-2 | DT-2 | SRD BUILDING OFFICE:ID | 2 | 990 | 19503296 | 266 | 2019-06-12 15:00 | 97 | 420 | 80 | 345 | 89 | 373 | 65 | 720 |  |  |  | 0 | 13% | 19% | 27% | 14% | 5.408 | Loss 5-10%
293 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN023 | TG-RJN023A-1 | DT-1 | NPL MULTI STORIES:ID | 1 | 630 | 19503308 | 508 | 2019-06-11 22:30 | 193 | 836 | 141 | 604 | 173 | 738 | 201 | 675 | 45 |  |  | 45 | 76% | 49% | 61% | 81% | 2.9781 | Loss 0-5% |  | 552(25.5) | 567(90)
294 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN081 | TG-RJN081A-1 | DT-1 | HANDIWALA ORN : K | 3 | 990 | 19503379 | 1021 | 2019-06-03 02:00 | 350 | 1459 | 355 | 1475 | 316 | 1322 | 147 | 600.5 | 106.5 | 8 | 1 | 115.5 | 103% | 70% | 78% | 95% | 7.5914 | Loss 5-10% |  | 1217(206) | 1092(241) | 957(100)
295 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN081 | TG-RJN081A-2 | DT-2 | HANDIWALA ORN : K | 3 | 630 | 19504310 | 595 | 2019-06-02 00:30 | 187 | 801 | 172 | 735 | 236 | 1022 | 260 | 531.5 | 186.5 | 1.5 |  | 188 | 94% | 67% | 90% | 90% | 7.5914 | Loss 5-10% |  |  | 501(30)
296 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN081 | TG-RJN081A-3 | DT-3 | HANDIWALA ORN : K | 3 | 630 | 19505206 | 736 | 2019-06-06 03:00 | 301 | 1363 | 106 | 431 | 329 | 1537 | 1030 | 578.5 | 126 | 14 | 0.5 | 140.5 | 117% | 70% | 74% | 96% | 7.5914 | Loss 5-10% |  |  | 577(43) | 563(77.5)
297 | 1141 | PNR | KIKARWALAN | PNR002 | TG-PNR002A-1 | DT-1 | SABZIWALA P.S RD. K. BAGH:PL | 3 | 990 | 19506085 | 664 | 2019-06-02 16:00 | 197 | 843 | 225 | 956 | 243 | 1049 | 179 | 719 |  |  |  | 0 | 58% | 52% | 67% | 56% | 8.953 | Loss 5-10% |  |  | 961(205.5) | 915(229) | 820(121.5) | 815(30)
298 | 1141 | PNR | KIKARWALAN | PNR002 | TG-PNR002A-2 | DT-2 | SABZIWALA P.S RD. K. BAGH:PL | 3 | 990 | 19506869 | 626 | 2019-06-28 15:30 | 168 | 699 | 224 | 948 | 233 | 983 | 269 | 719 |  |  |  | 0 | 57% | 36% | 63% | 50% | 8.953 | Loss 5-10%
299 | 1141 | PNR | KIKARWALAN | PNR002 | TG-PNR002A-3 | DT-3 | SABZIWALA P.S RD. K. BAGH:PL | 3 | 990 | 19505391 | 813 | 2019-06-02 16:00 | 265 | 1070 | 296 | 1205 | 252 | 1019 | 166 | 668.5 | 50.5 |  |  | 50.5 | 46% | 40% | 82% | 52% | 8.953 | Loss 5-10% |  |  | 1066(152) | 968(194.5) | 934(147.5) | 920(150)
300 | 1141 | PNR | KIKARWALAN | PNR003 | TG-PNR003A-1 | DT-1 | H.S. RD.P/M BAPA NGR:PL | 2 | 990 | 19506516 | 917 | 2019-06-30 | 280 | 1158 | 319 | 1317 | 318 | 1333 | 168 | 453.5 | 262 | 2.5 |  | 264.5 | 93% | 67% | 92% | 90% | 3.6771 | Loss 0-5% |  |  |  | 1019(268.5) | 957(207) | 816(43.5)
301 | 1141 | PNR | KIKARWALAN | PNR003 | TG-PNR003A-2 | DT-2 | H.S. RD.P/M BAPA NGR:PL | 2 | 990 | 19504414 | 1042 | 2019-06-30 | 329 | 1372 | 328 | 1367 | 385 | 1630 | 261 | 423.5 | 254 | 38.5 | 1.5 | 294 | 105% | 75% | 87% | 97% | 3.6771 | Loss 0-5% |  | 970(171) | 989(171.5) | 984(120) | 866(179.5) | 815(38.5)
302 | 1141 | PNR | KIKARWALAN | PNR005 | TG-PNR005A-1 | DT-1 | 17 B DEV NGR. K. BAGH:PL | 3 | 990 | 19504744 | 865 | 2019-06-29 23:00 | 266 | 1099 | 326 | 1347 | 273 | 1116 | 240 | 654 | 66 |  |  | 66 | 83% | 62% | 68% | 87% | 4.041 | Loss 0-5% |  | 806(37.5) | 885(89) | 862(84) | 774(33)
303 | 1141 | PNR | KIKARWALAN | PNR005 | TG-PNR005A-2 | DT-2 | 17 B DEV NGR. K. BAGH:PL | 3 | 990 | 19503772 | 588 | 2019-06-29 23:30 | 172 | 701 | 170 | 699 | 246 | 1002 | 302 | 720 |  |  |  | 0 | 57% | 47% | 56% | 59% | 4.041 | Loss 0-5%
304 | 1141 | PNR | KIKARWALAN | PNR005 | TG-PNR005A-3 | DT-3 | 17 B DEV NGR. K. BAGH:PL | 3 | 630 | 19505492 | 365 | 2019-06-29 23:30 | 120 | 504 | 130 | 554 | 115 | 486 | 61 | 720 |  |  |  | 0 | 57% | 39% | 49% | 58% | 4.041 | Loss 0-5%
305 | 1141 | PNR | KIKARWALAN | PNR006 | TG-PNR006A-1 | DT-1 | 11 B DEV NGR. A.S RD.:PL | 3 | 990 | 19503771 | 518 | 2019-06-30 00:30 | 118 | 481 | 196 | 807 | 204 | 833 | 340 | 720 |  |  |  | 0 | 52% | 36% | 46% | 49% | 10.9883 | Loss 10-20%
306 | 1141 | PNR | KIKARWALAN | PNR006 | TG-PNR006A-2 | DT-2 | 11 B DEV NGR. A.S RD.:PL | 3 | 990 | 19503773 | 885 | 2019-06-30 00:30 | 282 | 1143 | 343 | 1391 | 260 | 1041 | 312 | 627 | 93 |  |  | 93 | 89% | 55% | 60% | 81% | 10.9883 | Loss 10-20%
307 | 1141 | PNR | KIKARWALAN | PNR006 | TG-PNR006A-3 | DT-3 | 11 B DEV NGR. A.S RD.:PL | 3 | 630 | 19506069 | 318 | 2019-06-04 15:30 | 79 | 317 | 161 | 659 | 78 | 317 | 342 | 720 |  |  |  | 0 | 39% | 37% | 50% | 39% | 10.9883 | Loss 10-20%
308 | 1141 | PNR | KIKARWALAN | PNR007 | TG-PNR007A-1 | DT-1 | 13-B DEV NAGAR K. BAGH:PL | 1 | 990 | 19504424 | 807 | 2019-06-29 23:30 | 248 | 1083 | 322 | 1426 | 237 | 1036 | 369 | 673.5 | 45.5 |  |  | 45.5 | 81% | 63% | 64% | 82% | 5.7668 | Loss 5-10% |  |  | 847(42.5)
309 | 1141 | PNR | KIKARWALAN | PNR008 | TG-PNR008A-1 | DT-1 | 14-B MCD QTR. P.L. RD.:PL | 2 | 990 | 19505956 | 1112 | 2019-06-03 02:00 | 382 | 1645 | 343 | 1483 | 386 | 1670 | 176 | 493.5 | 187 | 21 | 15.5 | 223.5 | 112% | 77% | 102% | 106% | 6.7397 | Loss 5-10% |  | 1134(235.5) | 1234(465) | 1141(308.5) | 1082(233.5) | 846(34)
310 | 1141 | PNR | KIKARWALAN | PNR008 | TG-PNR008A-2 | DT-2 | 14-B MCD QTR. P.L. RD.:PL | 2 | 990 | 19505037 | 833 | 2019-06-12 | 263 | 1087 | 259 | 1069 | 310 | 1289 | 212 | 633.5 | 85 |  |  | 85 | 84% | 57% | 79% | 84% | 6.7397 | Loss 5-10% |  | 554(108.5) | 594(274.5) | 591(145) | 577(61.5)
311 | 1141 | PNR | KIKARWALAN | PNR010 | TG-PNR010A-1 | DT-1 | MILITARY ROAD (K):PL | 2 | 990 | 19504865 | 862 | 2019-06-01 21:30 | 250 | 981 | 311 | 1220 | 301 | 1186 | 224 | 617.5 | 102 |  |  | 102 | 84% | 58% | 64% | 87% | 11.2187 | Loss 10-20% |  | 881(46.5) | 948(132) | 928(97) | 876(41)
312 | 1141 | PNR | KIKARWALAN | PNR010 | TG-PNR010A-2 | DT-2 | MILITARY ROAD (K):PL | 2 | 990 | 19505039 | 876 | 2019-06-02 00:30 | 335 | 1372 | 289 | 1189 | 253 | 1034 | 293 | 663.5 | 56 |  |  | 56 | 89% | 57% | 64% | 86% | 11.2187 | Loss 10-20% |  |  | 837(64.5) | 819(42)
313 | 1141 | PNR | KIKARWALAN | PNR012 | TG-PNR012A-1 | DT-1 | TANK RD. KHATTA S/ST.:PL | 2 | 990 | 19500318 | 1201 | 2019-06-02 15:00 | 429 | 1867 | 441 | 1947 | 330 | 1440 | 472 | 509.5 | 101 | 39 | 66 | 206 | 42% | 35% | 121% | 42% | 2.9744 | Loss 0-5% | 841(111) | 1065(224.5) | 1108(133) |  |  | 918(170.5)
314 | 1141 | PNR | KIKARWALAN | PNR012 | TG-PNR012A-2 | DT-2 | TANK RD. KHATTA S/ST.:PL | 2 | 990 | 19505751 | 1035.481 | 2019-06-21 15:00 | 342.5325 | 1376.6829 | 334.1621 | 1356.1225 | 358.7864 | 1459.7867 | 95.0664 | 553.5 | 102 | 51.5 | 6.5 | 160 | 22% | 21% | 105% | 26% | 2.9744 | Loss 0-5% | [5 empty] | 911(150)
315 | 1141 | PNR | KIKARWALAN | PNR013 | TG-PNR013A-1 | DT-1 | TANK RD .BOOSTER PUMP:PL | 3 | 990 | 19500291 | 1016 | 2019-06-02 16:00 | 327 | 1353 | 341 | 1407 | 347 | 1426 | 65 | 456.5 | 200.5 | 59.5 | 2 | 262 | 65% | 61% | 103% | 77% | 4.9234 | Loss 0-5% | 995(246) | 1165(315.5) | 1190(312) | 1066(280.5) | 1002(154) | 1022(243)
316 | 1141 | PNR | KIKARWALAN | PNR013 | TG-PNR013A-2 | DT-2 | TANK RD .BOOSTER PUMP:PL | 3 | 990 | 19505172 | 948 | 2019-06-02 15:30 | 315 | 1381 | 280 | 1223 | 353 | 1562 | 294 | 546.5 | 168 | 4 |  | 172 | 45% | 44% | 96% | 50% | 4.9234 | Loss 0-5% | 787(55) | 1004(217) | 1013(241.5) | 996(224) | 974(196) | 862(142.5)
317 | 1141 | PNR | KIKARWALAN | PNR013 | TG-PNR013A-3 | DT-3 | TANK RD .BOOSTER PUMP:PL | 3 | 990 | 19505343 | 851 | 2019-06-12 16:00 | 278 | 1146 | 284 | 1174 | 289 | 1203 | 50 | 593 | 125.5 |  |  | 125.5 | 22% | 21% | 86% | 22% | 4.9234 | Loss 0-5% | 638(89) | 827(227) | 722(230) | 698(223) |  | 603(200.5)
318 | 1141 | PNR | KIKARWALAN | PNR015 | TG-PNR015A-1 | DT-1 | KRISHNA TIRATH DEV NAGAR | 2 | 990 | 19502800 | 990 | 2019-06-02 14:00 | 294 | 1243 | 338 | 1439 | 358 | 1521 | 247 | 522.5 | 125.5 | 70.5 |  | 196 | 17% | 15% | 100% | 22% | 3.8317 | Loss 0-5%
319 | 1141 | PNR | KIKARWALAN | PNR015 | TG-PNR015A-2 | DT-2 | KRISHNA TIRATH DEV NAGAR | 2 | 1600 | 19506094 | 1463.8372 | 2019-06-01 15:00 | 475.3528 | 2045.8479 | 504.0647 | 2166.8088 | 484.4198 | 2092.7971 | 105.6255 | 555.5 | 158.5 | 1.5 |  | 160 | 16% | 15% | 91% | 22% | 3.8317 | Loss 0-5% | 1372(238.5) | 1365(56.5) | 1297(118.5) |  | 992(155.5)
320 | 1141 | PNR | KIKARWALAN | PNR016 | TG-PNR016A-1 | DT-1 | REGER PURA ZONAL OFF INDOOR S/ST:ID | 2 | 630 | 19504459 | 548 | 2019-06-12 16:00 | 225 | 1021 | 143 | 651 | 179 | 799 | 323 | 561 | 158.5 |  |  | 158.5 | 83% | 63% | 87% | 82% | 12.3796 | Loss 10-20% |  |  | 641(112.5) | 699(269.5) | 620(219) | 545(83.5)
321 | 1141 | PNR | KIKARWALAN | PNR016 | TG-PNR016A-2 | DT-2 | REGER PURA ZONAL OFF INDOOR S/ST:ID | 2 | 990 | 19503212 | 875 | 2019-06-12 14:30 | 329 | 1491 | 264 | 1201 | 282 | 1286 | 258 | 609.5 | 110 |  |  | 110 | 77% | 53% | 88% | 77% | 12.3796 | Loss 10-20% |  | 992(184) | 1123(331.5) | 910(64)
322 | 1141 | PNR | KIKARWALAN | PNR125 | TG-PNR125A-1 | DT-1 | MILITARY ROAD S/ST. NO. 3:PM | 1 | 630 | 19506708 | 575 | 2019-06-02 01:30 | 194 | 805 | 204 | 844 | 177 | 730 | 100 | 392 | 326 | 2 |  | 328 | 91% | 84% | 89% | 87% | 12.3467 | Loss 10-20%
323 | 1141 | PNR | KIKARWALAN | PNR155 | TG-PNR155A-1 | DT-1 | VIJAY CHOWK | 1 | 990 | 19500300 | 931 | 2019-06-01 22:00 | 240 | 994 | 379 | 1600 | 313 | 1319 | 525 | 589.5 | 121 | 4 |  | 125 | 92% | 61% | 83% | 94% | 4.4812 | Loss 0-5% |  | 954(84.5) | 1024(237.5) | 975(167) | 996(87.5) | 824(32)
324 | 1141 | PNR | KIKARWALAN | PNR157 | TG-PNR157A-1 | DT-1 | 10-B, RAJENDRAPLACE | 1 | 990 | 19503741 | 791 | 2019-06-10 16:00 | 299 | 1298 | 246 | 1054 | 246 | 1059 | 241 | 205.5 | 27.5 |  |  | 27.5 | 49% | 51% | 80% | 50% | 5.2836 | Loss 5-10% |  |  | 845(111) | 801(43)
325 | 1141 | PNR | PATEL NAGAR | PNR018 | TG-PNR018A-1 | DT-1 | FARID PURI KIOSK:PL | 2 | 990 | 19501143 | 609 | 2019-06-08 06:30 | 189 | 760 | 198 | 801 | 223 | 907 | 132 | 720 |  |  |  | 0 | 56% | 62% | 51% | 55% | 3.51 | Loss 0-5%
326 | 1141 | PNR | PATEL NAGAR | PNR018 | TG-PNR018A-2 | DT-2 | FARID PURI KIOSK:PL | 2 | 990 | 19503573 | 875 | 2019-06-01 06:30 | 289 | 1189 | 261 | 1066 | 325 | 1344 | 241 | 667 | 53 |  |  | 53 | 84% | 88% | 75% | 85% | 3.51 | Loss 0-5% |  |  | 851(69.5) | 856(47)
327 | 1141 | PNR | PATEL NAGAR | PNR019 | TG-PNR019A-1 | DT-1 | FARID PURI NO.1 | 1 | 400 | 19506651 | 401 | 2019-06-29 17:30 | 133 | 559 | 138 | 575 | 130 | 544 | 27 | 646 | 54 | 17.5 | 0.5 | 72 | 99% | 95% | 100% | 97% | 13.9962 | Loss 10-20% |  | 357(41) | 378(57) | 378(50.5)
328 | 1141 | PNR | PATEL NAGAR | PNR020 | TG-PNR020A-1 | DT-1 | FARID PURI P/M NO. 2:PL | 1 | 990 | 19503407 | 1158 | 2019-06-02 05:30 | 376 | 1697 | 436 | 1997 | 346 | 1574 | 377 | 641.5 | 71.5 | 3 | 0.5 | 75 | 117% | 88% | 94% | 78% | 3.8215 | Loss 0-5% | 906(36) | 985(76) | 1056(211) | 1061(131) | 1071(103.5) | 982(32.5)
329 | 1141 | PNR | PATEL NAGAR | PNR021 | TG-PNR021A-1 | DT-1 | RAJASTHANI COLONY P/M-1:PM | 2 | 400 | 19502740 | 344 | 2019-06-04 05:30 | 146 | 603 | 80 | 324 | 117 | 481 | 242 | 707 | 13 |  |  | 13 | 86% | 84% | 76% | 74% | 5.9973 | Loss 5-10% | 424(42) | 470(149) | 503(442.5) | 500(293.5) |  | 463(70)
330 | 1141 | PNR | PATEL NAGAR | PNR021 | TG-PNR021A-2 | DT-2 | RAJASTHANI COLONY P/M-1:PM | 2 | 400 | 19506527 | 441 | 2019-06-13 05:30 | 144 | 590 | 132 | 544 | 165 | 690 | 129 | 630 | 51 | 17.5 | 21.5 | 90 | 110% | 108% | 109% | 86% | 5.9973 | Loss 5-10% |  |  |  | 498(218) |  | 495(66.5)
331 | 1141 | PNR | PATEL NAGAR | PNR028 | TG-PNR028A-1 | DT-1 | 12 BLOCK E.P. NAGAR P/M:PL | 2 | 990 | 19502604 | 538 | 2019-06-29 15:00 | 175 | 763 | 187 | 818 | 176 | 771 | 52 | 720 |  |  |  | 0 | 46% | 34% | 54% | 46% | 4.7962 | Loss 0-5%
332 | 1141 | PNR | PATEL NAGAR | PNR028 | TG-PNR028A-2 | DT-2 | 12 BLOCK E.P. NAGAR P/M:PL | 2 | 990 | 19505843 | 830 | 2019-06-04 15:00 | 259 | 1098 | 292 | 1242 | 279 | 1171 | 125 | 637.5 | 82.5 |  |  | 82.5 | 62% | 53% | 84% | 64% | 4.7962 | Loss 0-5% |  |  | 839(56.5) | 872(78)
333 | 1141 | PNR | PATEL NAGAR | PNR029 | TG-PNR029A-1 | DT-1 | 10 BLOCK E. P. NAGAR (K):PL | 3 | 990 | 19504670 | 638 | 2019-06-01 15:00 | 238 | 1040 | 190 | 832 | 210 | 919 | 181 | 720 |  |  |  | 0 | 54% | 41% | 64% | 57% | 4.3815 | Loss 0-5%
334 | 1141 | PNR | PATEL NAGAR | PNR029 | TG-PNR029A-2 | DT-2 | 10 BLOCK E. P. NAGAR (K):PL | 3 | 990 | 19506571 | 1030 | 2019-06-29 12:00 | 379 | 1751 | 243 | 1072 | 408 | 1837 | 726 | 565.5 | 148.5 | 5.5 | 0.5 | 154.5 | 60% | 48% | 104% | 66% | 4.3815 | Loss 0-5% | 1000(77.5) | 997(203) | 999(43.5)
335 | 1141 | PNR | PATEL NAGAR | PNR029 | TG-PNR029A-3 | DT-3 | 10 BLOCK E. P. NAGAR (K):PL | 3 | 630 | 19505103 | 380 | 2019-06-29 12:30 | 86 | 380 | 108 | 477 | 185 | 852 | 432 | 720 |  |  |  | 0 | 54% | 36% | 60% | 44% | 4.3815 | Loss 0-5% |  |  |  | 525(32.5)
336 | 1141 | PNR | PATEL NAGAR | PNR032 | TG-PNR032A-1 | DT-1 | 22 BLOCK W.P. NAGAR:PL | 2 | 990 | 19506441 | 864 | 2019-06-26 00:30 | 314 | 1301 | 275 | 1130 | 275 | 1132 | 170 | 626 | 94 |  |  | 94 | 87% | 69% | 71% | 86% | 5.4024 | Loss 5-10% |  |  | 1021(118) | 928(38.5)
337 | 1141 | PNR | PATEL NAGAR | PNR032 | TG-PNR032A-2 | DT-2 | 22 BLOCK W.P. NAGAR:PL | 2 | 990 | 19504944 | 845 | 2019-06-26 | 254 | 1095 | 274 | 1169 | 317 | 1367 | 244 | 656.5 | 63 |  |  | 63 | 85% | 62% | 62% | 82% | 5.4024 | Loss 5-10% |  | 877(43.5) | 873(97.5) | 888(24.5)
338 | 1141 | PNR | PATEL NAGAR | PNR043 | TG-PNR043A-1 | DT-1 | BALJIT NGR. BARAT GHAR:PL | 2 | 990 | 19505121 | 1120 | 2019-06-02 01:30 | 334 | 1414 | 442 | 1920 | 345 | 1480 | 476 | 434.5 | 188.5 | 64 | 33 | 285.5 | 113% | 74% | 89% | 103% | 8.2205 | Loss 5-10% |  | 1013(155.5) | 1171(309) | 1109(277) | 970(240) | 888(52.5)
339 | 1141 | PNR | PATEL NAGAR | PNR043 | TG-PNR043A-2 | DT-2 | BALJIT NGR. BARAT GHAR:PL | 2 | 990 | 19502619 | 869 | 2019-06-16 01:30 | 290 | 1199 | 336 | 1401 | 242 | 996 | 350 | 611 | 109 |  |  | 109 | 88% | 54% | 74% | 82% | 8.2205 | Loss 5-10% |  | 819(42) | 945(127) | 916(115.5) | 805(57)
340 | 1141 | PNR | PATEL NAGAR | PNR044 | TG-PNR044A-1 | DT-1 | BALJIT NAGAR AGGARWAL SWEET P/M:PM | 1 | 400 | 19506244 | 434 | 2019-06-10 02:00 | 134 | 612 | 129 | 588 | 172 | 792 | 193 | 539.5 | 157 | 18 | 5.5 | 180.5 | 109% | 82% | 72% | 98% | 3.4553 | Loss 0-5% |  | 340(51) | 363(148.5) | 354(99) | 331(93.5)
341 | 1141 | PNR | PATEL NAGAR | PNR047 | TG-PNR047A-1 | DT-1 | SHADI PUR DTC DEPOT:PL | 2 | 990 | 19502620 | 411 | 2019-06-01 03:00 | 182 | 713 | 116 | 453 | 113 | 445 | 265 | 720 |  |  |  | 0 | 41% | 30% | 36% | 39% | 3.4432 | Loss 0-5% |  | 916(51.5)
342 | 1141 | PNR | PATEL NAGAR | PNR047 | TG-PNR047A-2 | DT-2 | SHADI PUR DTC DEPOT:PL | 2 | 630 | 19506556 | 791 | 2019-06-02 23:30 | 242 | 960 | 213 | 845 | 336 | 1359 | 468 | 534.5 | 127 | 44 | 14.5 | 185.5 | 121% | 71% | 66% | 126% | 3.4432 | Loss 0-5%
343 | 1141 | PNR | PATEL NAGAR | PNR048 | TG-PNR048A-1 | DT-1 | BALJIT NAGAR SCHOOLWALA TR.1:PM | 2 | 990 | 19506083 | 1425 | 2019-06-05 06:00 | 555 | 2381 | 420 | 1791 | 450 | 1789 | 591 | 499 | 145 | 39.5 | 32.5 | 217 | 133% | 144% | 85% | 103% | 6.1794 | Loss 5-10% | 1048(30) | 1158(82) | 1292(172.5) | 1169(128.5) | 1145(119) | 1077(31)
344 | 1141 | PNR | PATEL NAGAR | PNR048 | TG-PNR048A-2 | DT-2 | BALJIT NAGAR SCHOOLWALA TR.1:PM | 2 | 990 | 19506082 | 1288 | 2019-06-02 01:00 | 464 | 2073 | 420 | 1848 | 405 | 1795 | 256 | 439.5 | 154.5 | 53 | 69 | 276.5 | 130% | 109% | 90% | 124% | 6.1794 | Loss 5-10% | 878(47) | 1165(207.5) | 1239(381.5) | 1124(321) | 1048(286.5) | 921(91)
345 | 1141 | PNR | PATEL NAGAR | PNR049 | TG-PNR049A-1 | DT-1 | BALJIT NAGAR JANTA PARK:PL | 2 | 990 | 19502781 | 1054 | 2019-06-30 05:00 | 354 | 1459 | 339 | 1396 | 361 | 1488 | 82 | 481 | 173 | 54.5 | 9.5 | 237 | 107% | 100% | 74% | 98% | 7.8778 | Loss 5-10% | 1363(56.5) | 1427(190) | 1284(199) | 1322(173.5) | 1248(133) | 1189(34.5)
346 | 1141 | PNR | PATEL NAGAR | PNR049 | TG-PNR049A-2 | DT-2 | BALJIT NAGAR JANTA PARK:PL | 2 | 990 | 19505937 | 1032 | 2019-06-18 01:00 | 309 | 1318 | 431 | 1885 | 293 | 1254 | 602 | 684 | 32.5 |  | 0.5 | 33 | 104% | 79% | 57% | 74% | 7.8778 | Loss 5-10% |  |  | 1149(52.5) | 795(29)
347 | 1141 | PNR | PATEL NAGAR | PNR050 | TG-PNR050A-1 | DT-1 | BALJIT NAGAR P/M J. WALAN CHOWK:PL | 2 | 990 | 19502614 | 1133 | 2019-06-05 05:00 | 374 | 1552 | 382 | 1587 | 378 | 1561 | 31 | 690.5 | 0.5 | 7 | 22 | 29.5 | 114% | 48% | 54% | 70% | 10.3622 | Loss 10-20% |  |  | 1090(24.5)
348 | 1141 | PNR | PATEL NAGAR | PNR050 | TG-PNR050A-2 | DT-2 | BALJIT NAGAR P/M J. WALAN CHOWK:PL | 2 | 630 | 19502588 | 485 | 2019-06-30 05:00 | 165 | 679 | 154 | 634 | 166 | 682 | 47 | 717 | 3 |  |  | 3 | 77% | 53% | 63% | 68% | 10.3622 | Loss 10-20%
349 | 1141 | PNR | PATEL NAGAR | PNR051 | TG-PNR051A-1 | DT-1 | DAV MULTAN:PL | 3 | 990 | 19502782 | 857 | 2019-06-03 17:00 | 274 | 1175 | 309 | 1323 | 274 | 1175 | 148 | 596.5 | 119.5 |  |  | 119.5 | 77% | 59% | 87% | 77% | 5.9523 | Loss 5-10% |  | 869(75) | 947(222.5) | 910(89)
350 | 1141 | PNR | PATEL NAGAR | PNR051 | TG-PNR051A-2 | DT-2 | DAV MULTAN:PL | 3 | 990 | 19502859 | 960 | 2019-06-01 12:00 | 310 | 1337 | 341 | 1480 | 308 | 1335 | 144 | 603 | 109 | 2.5 |  | 111.5 | 42% | 61% | 97% | 54% | 5.9523 | Loss 5-10% |  | 903(82) | 969(144.5) | 1048(165) | 797(60)
351 | 1141 | PNR | PATEL NAGAR | PNR051 | TG-PNR051A-3 | DT-3 | DAV MULTAN:PL | 3 | 630 | 19506440 | 620 | 2019-06-10 14:30 | 236 | 1020 | 207 | 891 | 177 | 766 | 220 | 473.5 | 228.5 | 18 |  | 246.5 | 87% | 59% | 98% | 88% | 5.9523 | Loss 5-10%
352 | 1141 | PNR | PATEL NAGAR | PNR052 | TG-PNR052A-1 | DT-1 | MUFFATLAL:PL | 1 | 990 | 19502785 | 819 | 2019-06-01 14:30 | 290 | 1311 | 278 | 1246 | 251 | 1121 | 167 | 647.5 | 72.5 |  |  | 72.5 | 77% | 55% | 83% | 74% | 3.5122 | Loss 0-5% |  | 803(46) | 861(169) | 806(78.5)
353 | 1141 | PNR | PATEL NAGAR | PNR054 | TG-PNR054A-1 | DT-1 | POLICE STN. W.P.NAGAR:PL | 2 | 990 | 19502603 | 1191 | 2019-06-02 01:00 | 373 | 1526 | 378 | 1548 | 440 | 1803 | 267 | 371.5 | 270.5 | 53 | 24 | 347.5 | 120% | 83% | 91% | 112% | 4.2127 | Loss 0-5% |  | 1168(344) | 1248(579) |  | 1018(353) | 908(95.5)
354 | 1141 | PNR | PATEL NAGAR | PNR054 | TG-PNR054A-2 | DT-2 | POLICE STN. W.P.NAGAR:PL | 2 | 630 | 19505460 | 580.9609 | 2019-06-28 01:00 | 160.4307 | 692.2873 | 249.576 | 1100.0839 | 170.9541 | 746.6551 | 383.5139 | 72 | 7 | 1 |  | 8 | 92% | 58% | 63% | 74% | 4.2127 | Loss 0-5%
355 | 1141 | PNR | PATEL NAGAR | PNR056 | TG-PNR056A-1 | DT-1 | F&G BLOCK W.P. NAGAR:PL | 2 | 990 | 19506652 | 948 | 2019-06-03 02:00 | 312 | 1311 | 305 | 1272 | 331 | 1403 | 117 | 546 | 159.5 | 14.5 |  | 174 | 96% | 74% | 82% | 95% | 10.2106 | Loss 10-20% |  | 922(60.5) | 966(168) | 901(86.5)
356 | 1141 | PNR | PATEL NAGAR | PNR056 | TG-PNR056A-2 | DT-2 | F&G BLOCK W.P. NAGAR:PL | 2 | 990 | 19500298 | 473 | 2019-06-30 01:30 | 153 | 653 | 124 | 523 | 196 | 837 | 273 | 720 |  |  |  | 0 | 48% | 32% | 36% | 45% | 10.2106 | Loss 10-20%
357 | 1141 | PNR | PATEL NAGAR | PNR057 | TG-PNR057A-1 | DT-1 | S- BLOCK W.P. NAGAR:PL | 3 | 990 | 19502608 | 614 | 2019-06-30 00:30 | 167 | 723 | 202 | 886 | 246 | 1074 | 305 | 719.5 |  |  |  | 0 | 62% | 40% | 47% | 60% | 10.55 | Loss 10-20%
358 | 1141 | PNR | PATEL NAGAR | PNR057 | TG-PNR057A-2 | DT-2 | S- BLOCK W.P. NAGAR:PL | 3 | 990 | 19506245 | 1019 | 2019-06-04 15:30 | 423 | 1853 | 375 | 1717 | 221 | 966 | 828 | 602 | 115 | 2 | 0.5 | 117.5 | 91% | 60% | 103% | 93% | 10.55 | Loss 10-20% |  |  | 846(79) | 853(41.5)
359 | 1141 | PNR | PATEL NAGAR | PNR057 | TG-PNR057A-3 | DT-3 | S- BLOCK W.P. NAGAR:PL | 3 | 630 | 19505748 | 512 | 2019-06-29 23:00 | 225 | 1041 | 148 | 673 | 139 | 629 | 391 | 679.5 | 40 |  |  | 40 | 80% | 68% | 70% | 81% | 10.55 | Loss 10-20% |  | 665(28.5) | 605(71) | 596(58) | 551(31.5)
360 | 1141 | PNR | PATEL NAGAR | PNR059 | TG-PNR059A-1 | DT-1 | BALJIT NGR. NO. 1 (DOGWALA):PL | 2 | 990 | 19506705 | 960 | 2019-06-28 23:00 | 283 | 1221 | 316 | 1372 | 360 | 1571 | 304 | 603 | 109.5 | 5 |  | 114.5 | 94% | 67% | 62% | 97% | 3.8632 | Loss 0-5% |  |  | 1086(59)
361 | 1141 | PNR | PATEL NAGAR | PNR059 | TG-PNR059A-2 | DT-2 | BALJIT NGR. NO. 1 (DOGWALA):PL | 2 | 630 | 19506478 | 724 | 2019-06-11 23:30 | 235 | 971 | 230 | 961 | 258 | 1081 | 115 | 606.5 | 90.5 | 17 | 3.5 | 111 | 114% | 62% | 64% | 115% | 3.8632 | Loss 0-5% |  |  | 715(98) | 582(80) | 586(62.5)
362 | 1141 | PNR | PATEL NAGAR | PNR062 | TG-PNR062A-1 | DT-1 | NALA (K) W.P. NAGAR:PL | 1 | 990 | 19502808 | 1113 | 2019-06-11 00:30 | 336 | 1451 | 413 | 1823 | 364 | 1576 | 328 | 448 | 160 | 75 | 34.5 | 269.5 | 112% | 98% | 80% | 112% | 4.3615 | Loss 0-5% |  | 918(85.5) | 1088(202.5) | 963(113) | 860(68)
363 | 1141 | PNR | PATEL NAGAR | PNR063 | TG-PNR063A-1 | DT-1 | Z-BLOCK, W.P. NAGAR:PL | 1 | 990 | 19502755 | 875 | 2019-06-30 20:00 | 314 | 1311 | 281 | 1171 | 280 | 1172 | 139 | 566 | 154 |  |  | 154 | 69% | 50% | 88% | 88% | 4.4057 | Loss 0-5% |  | 800(32.5) | 832(115) | 870(35)
364 | 1141 | PNR | PATEL NAGAR | PNR064 | TG-PNR064A-1 | DT-1 | D-BLOCK, W.P. NAGAR P/M:PM | 1 | 630 | 19500297 | 609 | 2019-06-02 03:00 | 198 | 838 | 193 | 810 | 218 | 923 | 102 | 580 | 133.5 | 6.5 |  | 140 | 97% | 76% | 71% | 90% | 8.1197 | Loss 5-10% |  | 580(54) | 599(156.5) | 577(80.5) | 517(44.5)
365 | 1141 | PNR | PATEL NAGAR | PNR066 | TG-PNR066A-1 | DT-1 | WEST PATEL NAGAR INDOOR:PL | 2 | 990 | 19502857 | 716 | 2019-06-12 | 210 | 892 | 262 | 1156 | 244 | 1080 | 235 | 719 | 1 |  |  | 1 | 72% | 55% | 52% | 70% | 5.7533 | Loss 5-10%
366 | 1141 | PNR | PATEL NAGAR | PNR066 | TG-PNR066A-2 | DT-2 | WEST PATEL NAGAR INDOOR:PL | 2 | 630 | 19501641 | 743 | 2019-06-12 00:30 | 243 | 1060 | 253 | 1135 | 247 | 1098 | 65 | 240 | 327.5 | 90.5 | 62 | 480 | 118% | 92% | 100% | 116% | 5.7533 | Loss 5-10% |  |  |  |  | 627(209.5) | 538(34)
367 | 1141 | PNR | PATEL NAGAR | PNR067 | TG-PNR067A-1 | DT-1 | 30 BLOCK WEST PATEL NAGAR:PL | 2 | 990 | 19504737 | 652 | 2019-06-11 23:30 | 214 | 914 | 182 | 807 | 256 | 1128 | 283 | 719 |  |  |  | 0 | 65% | 48% | 46% | 66% | 3.4221 | Loss 0-5%
368 | 1141 | PNR | PATEL NAGAR | PNR067 | TG-PNR067A-2 | DT-2 | 30 BLOCK WEST PATEL NAGAR:PL | 2 | 630 | 19504734 | 536 | 2019-06-02 23:30 | 205 | 899 | 160 | 704 | 171 | 753 | 176 | 656 | 63 |  |  | 63 | 83% | 56% | 56% | 85% | 3.4221 | Loss 0-5% |  | 522(26.5) | 677(76)
369 | 1141 | PNR | PATEL NAGAR | PNR094 | TG-PNR094A-1 | DT-1 | 29 BLOCK W.P. NAGAR:PL | 2 | 630 | 19503572 | 431 | 2019-06-27 23:30 | 126 | 554 | 131 | 575 | 174 | 769 | 204 | 719 |  |  |  | 0 | 67% | 44% | 52% | 68% | 3.51 | Loss 0-5%
370 | 1141 | PNR | PATEL NAGAR | PNR094 | TG-PNR094A-2 | DT-2 | 29 BLOCK W.P. NAGAR:PL | 2 | 990 | 19504444 | 949 | 2019-06-03 03:00 | 297 | 1243 | 299 | 1253 | 354 | 1492 | 244 | 615 | 99 | 3 |  | 102 | 96% | 70% | 61% | 87% | 3.51 | Loss 0-5% |  | 830(27.5) | 838(73) | 849(35)
371 | 1141 | PNR | PATEL NAGAR | PNR131 | TG-PNR131A-1 | DT-1 | HOLI CHOWK PATEL NAGAR | 1 | 990 | 19502792 | 819 | 2019-06-29 23:30 | 309 | 1331 | 306 | 1319 | 204 | 869 | 457 | 615.5 | 104.5 |  |  | 104.5 | 82% | 66% | 72% | 83% | 5.0059 | Loss 5-10% |  |  | 765(61) | 772(65.5) | 754(91.5)
372 | 1141 | PNR | PATEL NAGAR | PNR134 | TG-PNR134A-1 | DT-1 | NEPALI MANDIR BALJIT NAGAR | 1 | 630 | 19502798 | 494 | 2019-06-29 23:00 | 169 | 716 | 150 | 635 | 175 | 738 | 94 | 668.5 | 51.5 |  |  | 51.5 | 77% | 66% | 72% | 78% | 4.1143 | Loss 0-5% |  |  |  |  | 477(35.5)
373 | 1141 | PNR | PATEL NAGAR | PNR152 | TG-PNR152A-1 | DT-1 | 25 BLK WEST PATEL NAGAR | 2 | 990 | 19502853 | 1381 | 2019-06-11 00:30 | 416 | 1810 | 491 | 2170 | 474 | 2071 | 322 | 348 | 187 | 66 | 119 | 372 | 139% | 97% | 90% | 124% | 10.7339 | Loss 10-20% |  |  | 1271(245) | 1204(253) | 1036(132) | 890(42.5)
374 | 1141 | PNR | PATEL NAGAR | PNR152 | TG-PNR152A-2 | DT-2 | 25 BLK WEST PATEL NAGAR | 2 | 630 | 19505730 | 525 | 2019-06-11 00:30 | 168 | 738 | 176 | 765 | 182 | 793 | 48 | 692 | 27.5 |  |  | 27.5 | 83% | 66% | 64% | 76% | 10.7339 | Loss 10-20% |  |  | 658(37)
375 | 1141 | PNR | PATEL NAGAR | PNR153 | TG-PNR153A-1 | DT-1 | ROAD NO-20 BALJEET NAGAR | 2 | 990 | 19505847 | 1271 | 2019-06-13 05:30 | 401 | 1640 | 449 | 1856 | 421 | 1749 | 187 | 435 | 145.5 | 67.5 | 68 | 281 | 128% | 125% | 91% | 109% | 11.7715 | Loss 10-20% | 1105(32) | 1198(142.5) | 1391(273.5) | 1330(218) | 1239(210.5) | 1184(61.5)
376 | 1141 | PNR | PATEL NAGAR | PNR153 | TG-PNR153A-2 | DT-2 | ROAD NO-20 BALJEET NAGAR | 2 | 990 | 19502810 | 994 | 2019-06-14 06:00 | 342 | 1439 | 321 | 1346 | 330 | 1374 | 83 | 559.5 | 137 | 19.5 | 0.5 | 157 | 98% | 100% | 66% | 88% | 11.7715 | Loss 10-20% | 1210(27.5) | 1003(76.5) | 1141(158) | 985(52)
377 | 1141 | PNR | SARAI ROHILLA | PNR096 | TG-PNR096A-1 | DT-1 | DHAL WALA GALI NO-6 | 2 | 990 | 19505033 | 791 | 2019-06-20 16:00 | 253 | 1047 | 278 | 1151 | 261 | 1073 | 94 | 681 | 37 |  |  | 37 | 17% | 37% | 80% | 22% | 4.619 | Loss 0-5%
378 | 1141 | PNR | SARAI ROHILLA | PNR096 | TG-PNR096A-2 | DT-2 | DHAL WALA GALI NO-6 | 2 | 990 | 19502622 | 206 | 2019-06-30 16:30 | 64 | 253 | 76 | 304 | 66 | 265 | 46 | 719 |  |  |  | 0 | 4% | 7% | 21% | 6% | 4.619 | Loss 0-5%
379 | 1141 | PNR | SARAI ROHILLA | PNR099 | TG-PNR099A-1 | DT-1 | K. PAHAR G. NO. 8 S/ST-7:PL | 1 | 990 | 19502852 | 753 | 2019-06-09 11:00 | 251 | 1053 | 256 | 1071 | 246 | 1027 | 39 | 682 | 37 |  |  | 37 | 16% | 25% | 76% | 25% | 5.7727 | Loss 5-10% | 767(35) | 752(24) | 773(51.5) | 762(48) |  | 780(50.5)
380 | 1141 | PNR | SARAI ROHILLA | PNR100 | TG-PNR100A-1 | DT-1 | K. PAHR G. NO. 9:PL | 1 | 990 | 19506285 | 1015 | 2019-06-26 12:30 | 321 | 1389 | 334 | 1447 | 360 | 1550 | 142 | 501.5 | 204.5 | 10 | 0.5 | 215 | 29% | 33% | 102% | 38% | 6.6916 | Loss 5-10% | 800(79) | 980(73) | 814(71.5) | 850(125.5) | 838(107) | 841(105)
381 | 1141 | PNR | SARAI ROHILLA | PNR101 | TG-PNR101A-1 | DT-1 | S/STN NO.15 GALI NO.8 KALA PAHAR | 2 | 990 | 19506290 | 815 | 2019-06-29 12:30 | 265 | 1114 | 263 | 1112 | 287 | 1218 | 105 | 656.5 | 61 |  |  | 61 | 50% | 32% | 82% | 37% | 6.6799 | Loss 5-10% | 1057(191) | 1040(151.5) | 912(103) | 817(117) | 852(144.5) | 901(133)
382 | 1141 | PNR | SARAI ROHILLA | PNR101 | TG-PNR101A-2 | DT-2 | S/STN NO.15 GALI NO.8 KALA PAHAR | 2 | 990 | 19505749 | 990 | 2019-06-15 14:00 | 320 | 1398 | 327 | 1434 | 343 | 1501 | 90 | 477 | 202.5 | 38 | 0.5 | 241 | 24% | 39% | 100% | 39% | 6.6799 | Loss 5-10% | 1043(198.5) | 1157(211) | 1165(273.5) | 1169(272.5) | 1163(226) | 1204(283)
383 | 1141 | PNR | SARAI ROHILLA | PNR102 | TG-PNR102A-1 | DT-1 | NAGARWALA GHATTI RD.:PL | 1 | 990 | 19505845 | 1035 | 2019-06-30 17:00 | 359 | 1508 | 353 | 1471 | 323 | 1346 | 147 | 374 | 258.5 | 79 | 3.5 | 341 | 102% | 99% | 105% | 103% | 4.3062 | Loss 0-5% |  | 938(119) | 943(265.5) | 928(88) | 875(24)
384 | 1141 | PNR | SARAI ROHILLA | PNR104 | TG-PNR104A-1 | DT-1 | ZONAL OFF. K. PAHAR:PL | 2 | 990 | 19502593 | 534 | 2019-06-29 15:00 | 185 | 768 | 190 | 796 | 159 | 664 | 120 | 720 |  |  |  | 0 | 9% | 19% | 54% | 17% | 3.8856 | Loss 0-5%
385 | 1141 | PNR | SARAI ROHILLA | PNR104 | TG-PNR104A-2 | DT-2 | ZONAL OFF. K. PAHAR:PL | 2 | 990 | 19506080 | 836 | 2019-06-19 16:30 | 283 | 1165 | 291 | 1192 | 262 | 1073 | 108 | 581.5 | 138.5 |  |  | 138.5 | 26% | 36% | 84% | 29% | 3.8856 | Loss 0-5% | 829(84.5) | 897(113) | 829(115.5) |  | 925(166.5) | 889(62.5)
386 | 1141 | PNR | SARAI ROHILLA | PNR105 | TG-PNR105A-1 | DT-1 | POLICE POST K. PAHAR:PL | 1 | 990 | 19502802 | 783 | 2019-06-01 12:30 | 248 | 1071 | 261 | 1134 | 274 | 1180 | 95 | 644 | 76 |  |  | 76 | 26% | 30% | 79% | 34% | 8.0391 | Loss 5-10%
387 | 1141 | PNR | SARAI ROHILLA | PNR106 | TG-PNR106A-1 | DT-1 | TIN MKT. K. PAHAR:PL | 2 | 990 | 19505268 | 678 | 2019-06-27 16:30 | 226 | 935 | 234 | 971 | 218 | 904 | 58 | 720 |  |  |  | 0 | 18% | 25% | 68% | 34% | 3.9892 | Loss 0-5%
388 | 1141 | PNR | SARAI ROHILLA | PNR106 | TG-PNR106A-2 | DT-2 | TIN MKT. K. PAHAR:PL | 2 | 630 | 19505104 | 714 | 2019-06-01 16:30 | 242 | 1065 | 208 | 906 | 264 | 1176 | 235 | 438 | 170.5 | 68 | 43.5 | 282 | 63% | 65% | 113% | 76% | 3.9892 | Loss 0-5% | 1034(136.5) | 930(190.5) | 619(244.5) | 764(269) |  | 642(283)
389 | 1141 | PNR | SARAI ROHILLA | PNR107 | TG-PNR107A-1 | DT-1 | BANGALI DHABA K. PAHAR:PL | 1 | 990 | 19502628 | 905 | 2019-06-26 16:00 | 286 | 1139 | 302 | 1207 | 317 | 1266 | 110 | 555 | 164 | 1 |  | 165 | 19% | 31% | 91% | 29% | 5.1953 | Loss 5-10% | 831(43) |  |  |  | 890(77.5) | 939(193.5)
390 | 1141 | PNR | SARAI ROHILLA | PNR110 | TG-PNR110A-1 | DT-1 | G. NO. 11 BABU RAM K. PAHAR:PL | 1 | 990 | 19502737 | 820 | 2019-06-28 16:30 | 285 | 1168 | 246 | 1006 | 288 | 1183 | 170 | 609 | 111 |  |  | 111 | 21% | 33% | 83% | 28% | 7.8695 | Loss 5-10% |  |  | 757(31) | 796(34) | 837(74.5) | 825(97.5)
391 | 1141 | PNR | SARAI ROHILLA | PNR113 | TG-PNR113A-1 | DT-1 | SARAI ROHILLA:PL | 1 | 990 | 19503210 | 911 | 2019-06-30 03:00 | 321 | 1348 | 259 | 1080 | 331 | 1397 | 295 | 534.5 | 182 | 3 |  | 185 | 92% | 74% | 78% | 91% | 5.9779 | Loss 5-10% |  | 854(64) | 1027(187) | 883(106.5) | 776(41)
392 | 1141 | PNR | SARAI ROHILLA | PNR114 | TG-PNR114A-1 | DT-1 | KAMAL (K) K.PAHAR:PL | 1 | 630 | 19504060 | 590 | 2019-06-29 16:00 | 264 | 1146 | 156 | 669 | 171 | 730 | 450 | 620.5 | 95 | 4 |  | 99 | 76% | 53% | 94% | 79% | 3.9651 | Loss 0-5% |  |  | 551(40.5)
393 | 1141 | PNR | SARAI ROHILLA | PNR116 | TG-PNR116A-1 | DT-1 | GALI NO.1 NANAKWALA:PL | 2 | 630 | 19504411 | 357 | 2019-06-29 15:00 | 133 | 556 | 92 | 388 | 132 | 557 | 169 | 719.5 |  |  |  | 0 | 31% | 33% | 57% | 37% | 9.4164 | Loss 5-10%
394 | 1141 | PNR | SARAI ROHILLA | PNR116 | TG-PNR116A-2 | DT-2 | GALI NO.1 NANAKWALA:PL | 2 | 990 | 19506292 | 782 | 2019-06-30 11:00 | 266 | 1165 | 265 | 1162 | 250 | 1091 | 73 | 694 | 25.5 |  |  | 25.5 | 13% | 40% | 79% | 24% | 9.4164 | Loss 5-10% | 744(28) |  | 857(144.5) | 847(175) | 889(147) | 898(202.5)
395 | 1141 | PNR | SARAI ROHILLA | PNR120 | TG-PNR120A-1 | DT-1 | SOHAN SINGH K.PAHAR:PL | 3 | 630 | 19506568 | 599 | 2019-06-04 11:00 | 198 | 792 | 197 | 791 | 203 | 823 | 32 | 542.5 | 172 | 5.5 |  | 177.5 | 24% | 41% | 95% | 27% | 5.8034 | Loss 5-10% |  |  |  |  | 639(117.5) | 662(179)
396 | 1141 | PNR | SARAI ROHILLA | PNR120 | TG-PNR120A-2 | DT-2 | SOHAN SINGH K.PAHAR:PL | 3 | 630 | 19503506 | 354 | 2019-06-12 14:00 | 135 | 565 | 107 | 452 | 111 | 466 | 107 | 719.5 |  |  |  | 0 | 25% | 26% | 56% | 30% | 5.8034 | Loss 5-10%
397 | 1141 | PNR | SARAI ROHILLA | PNR120 | TG-PNR120A-3 | DT-3 | SOHAN SINGH K.PAHAR:PL | 3 | 630 | 19503574 | 569 | 2019-06-28 15:30 | 179 | 757 | 205 | 867 | 185 | 788 | 98 | 556.5 | 163 | 0.5 |  | 163.5 | 36% | 41% | 90% | 41% | 5.8034 | Loss 5-10% | 482(24.5) | 513(40.5) | 531(110.5) | 529(120.5) | 519(72) | 515(107)
398 | 1141 | PNR | SARAI ROHILLA | PNR121 | TG-PNR121A-1 | DT-1 | KHANNA S/STN, K.PAHAR:PL | 1 | 990 | 19503204 | 838 | 2019-06-29 16:00 | 299 | 1264 | 270 | 1145 | 269 | 1141 | 121 | 651 | 68.5 |  |  | 68.5 | 18% | 21% | 85% | 59% | 9.352 | Loss 5-10% | 789(88) | 825(87) | 817(119) | 844(151.5) | 848(100.5) | 837(163.5)
399 | 1141 | PNR | SARAI ROHILLA | PNR127 | TG-PNR127A-1 | DT-1 | MILITARY RD. P/M S/ST:PL | 2 | 990 | 19500313 | 637 | 2019-06-30 02:00 | 251 | 1036 | 175 | 720 | 211 | 863 | 274 | 719.5 |  |  |  | 0 | 64% | 48% | 48% | 58% | 3.7047 | Loss 0-5%
400 | 1141 | PNR | SARAI ROHILLA | PNR127 | TG-PNR127A-2 | DT-2 | MILITARY RD. P/M S/ST:PL | 2 | 990 | 19504393 | 998 | 2019-06-30 02:30 | 308 | 1213 | 280 | 1091 | 410 | 1620 | 480 | 626 | 86.5 | 4 | 0.5 | 91 | 101% | 75% | 72% | 93% | 3.7047 | Loss 0-5% |  |  | 851(33.5)
401 | 1141 | PNR | SARAI ROHILLA | PNR129 | TG-PNR129A-1 | DT-1 | GALI-4 POST OFFICE ANAND PARBAT | 1 | 990 | 19502933 | 793 | 2019-06-14 15:30 | 224 | 910 | 276 | 1123 | 293 | 1189 | 253 | 641.5 | 78.5 |  |  | 78.5 | 31% | 32% | 80% | 37% | 4.0156 | Loss 0-5% |  | 763(29) | 801(102) | 799(42.5) | 809(101) | 801(50)
402 | 1141 | PNR | SARAI ROHILLA | PNR130 | TG-PNR130A-1 | DT-1 | TAULUI WALA PATEL NAGAR | 1 | 990 | 19506739 | 865 | 2019-06-25 16:00 | 269 | 1091 | 289 | 1168 | 308 | 1257 | 144 | 550.5 | 169.5 |  |  | 169.5 | 38% | 42% | 87% | 45% | 4.7541 | Loss 0-5% |  |  |  |  | 863(91.5) | 806(77)
403 | 1141 | PNR | SARAI ROHILLA | PNR138 | TG-PNR138A-1 | DT-1 | RIWA GALI NO-4 | 1 | 990 | 19502594 | 806 | 2019-06-01 12:00 | 268 | 1111 | 270 | 1121 | 268 | 1107 | 12 | 647.5 | 72 |  |  | 72 | 18% | 23% | 81% | 43% | 8.3993 | Loss 5-10% | 798(49.5) | 804(50) | 831(127) | 909(185) | 942(118.5) | 957(181.5)
404 | 1141 | PNR | SARAI ROHILLA | PNR139 | TG-PNR139A-1 | DT-1 | POST OFFICE P/M GALI NO-2 | 1 | 400 | 19502809 | 335 | 2019-06-26 16:00 | 120 | 524 | 111 | 477 | 103 | 442 | 71 | 581.5 | 137 |  |  | 137 | 28% | 46% | 84% | 27% | 2.747 | Loss 0-5% | 310(26) | 327(59.5) | 454(117)
405 | 1141 | PNR | SARAI ROHILLA | PNR141 | TG-PNR141A-1 | DT-1 | TIKONA PARK GODODIA ROAD | 1 | 990 | 19502625 | 1113 | 2019-06-29 23:00 | 320 | 1362 | 439 | 1877 | 355 | 1510 | 459 | 322 | 280.5 | 73 | 42 | 395.5 | 110% | 79% | 95% | 112% | 3.884 | Loss 0-5% |  | 1030(207.5) | 1230(433) | 1116(349.5) | 976(174.5) | 799(40.5)
406 | 1141 | PNR | SARAI ROHILLA | PNR149 | TG-PNR149A-1 | DT-1 | HR. ROAD ANAND PARVAT | 2 | 630 | 19504684 | 651 | 2019-06-26 16:00 | 226 | 923 | 214 | 868 | 211 | 863 | 58 | 419 | 180 | 58 | 1.5 | 239.5 | 26% | 62% | 103% | 39% | 4.7164 | Loss 0-5% | 594(105.5) | 599(127.5) | 647(123.5) | 662(137) | 665(100.5) | 660(68)
407 | 1141 | PNR | SARAI ROHILLA | PNR149 | TG-PNR149A-2 | DT-2 | HR. ROAD ANAND PARVAT | 2 | 400 | 19505394 | 352 | 2019-06-22 16:00 | 121 | 502 | 105 | 435 | 126 | 525 | 82 | 612 | 106 |  |  | 106 | 68% | 54% | 88% | 65% | 4.7164 | Loss 0-5%
408 | 1141 | PNR | SARAI ROHILLA | PNR165 | TG-PNR165A-1 | DT-1 | Booster Pump Nai basti( Rajiv Vatika ) | 1 | 990 | 19504825 | 827 | 2019-06-11 23:30 | 278 | 1149 | 317 | 1298 | 232 | 951 | 302 | 616 | 104 |  |  | 104 | 82% | 65% | 70% | 84% | 7.861 | Loss 5-10% |  | 872(43) | 1078(164) | 886(79)
409 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI038 | TG-JHI038A-1 | DT-1 | D-BLK VIVEK VIHAR PLM:PL | 2 | 990 | 19501553 | 565 | 2019-06-11 23:30 | 232 | 1005 | 172 | 749 | 162 | 703 | 282 | 716.5 |  |  |  | 0 | 56% | 38% | 51% | 57% | 2.3245 | Loss 0-5%
410 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI038 | TG-JHI038A-2 | DT-2 | D-BLK VIVEK VIHAR PLM:PL | 2 | 630 | 19505944 | 546 | 2019-06-16 03:30 | 91 | 376 | 306 | 1357 | 150 | 601 | 890 | 680 | 38 |  |  | 38 | 87% | 51% | 62% | 78% | 2.3245 | Loss 0-5%
411 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI039 | TG-JHI039A-1 | DT-1 | PRATAP KHAND:ID | 3 | 630 | 19506635 | 374 | 2019-06-12 | 104 | 439 | 126 | 530 | 144 | 604 | 144 | 720 |  |  |  | 0 | 59% | 44% | 45% | 59% | 8.5496 | Loss 5-10%
412 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI039 | TG-JHI039A-2 | DT-2 | PRATAP KHAND:ID | 3 | 400 | 19505839 | 276 | 2019-06-16 03:30 | 73 | 290 | 154 | 673 | 50 | 208 | 430 | 720 |  |  |  | 0 | 69% | 41% | 44% | 59% | 8.5496 | Loss 5-10% |  | 375(92.5) | 373(50.5)
413 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI039 | TG-JHI039A-3 | DT-3 | PRATAP KHAND:ID | 3 | 630 | 19506493 | 496 | 2019-06-30 00:30 | 183 | 754 | 176 | 728 | 137 | 567 | 175 | 666.5 | 53.5 |  |  | 53.5 | 79% | 57% | 58% | 77% | 8.5496 | Loss 5-10%
414 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI061 | TG-JHI061A-1 | DT-1 | C-BLK VIVEK VIHAR(PARK WALA):PG | 2 | 990 | 19503696 | 502 | 2019-06-13 23:30 | 182 | 749 | 117 | 479 | 203 | 828 | 318 | 717.5 |  |  |  | 0 | 50% | 32% | 37% | 51% | 4.3282 | Loss 0-5%
415 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI061 | TG-JHI061A-2 | DT-2 | C-BLK VIVEK VIHAR(PARK WALA):PG | 2 | 630 | 19504197 | 572 | 2019-06-29 23:00 | 196 | 823 | 203 | 851 | 173 | 716 | 123 | 647 | 70 | 0.5 |  | 70.5 | 88% | 57% | 71% | 91% | 4.3282 | Loss 0-5% |  |  | 536(53.5)
416 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI062 | TG-JHI062A-1 | DT-1 | JANTA QTR. VIVEK VIHAR:PL | 2 | 630 | 19501614 | 584 | 2019-06-30 23:30 | 202 | 915 | 172 | 779 | 211 | 963 | 165 | 578 | 106 | 3 |  | 109 | 91% | 65% | 67% | 93% | 7.0972 | Loss 5-10% |  | 556(47.5) | 589(122) | 572(69.5)
417 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI062 | TG-JHI062A-2 | DT-2 | JANTA QTR. VIVEK VIHAR:PL | 2 | 630 | 19505586 | 312 | 2019-06-12 | 64 | 265 | 88 | 365 | 160 | 676 | 370 | 718 |  |  |  | 0 | 49% | 34% | 36% | 49% | 7.0972 | Loss 5-10%
418 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI063 | TG-JHI063A-1 | DT-1 | MAHILA COLLEGE VIVEK VIHAR:PL | 2 | 990 | 19503019 | 713 | 2019-06-03 03:30 | 230 | 949 | 234 | 975 | 249 | 1044 | 85 | 718.5 | 0.5 |  |  | 0.5 | 72% | 49% | 48% | 61% | 6.5748 | Loss 5-10%
419 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI063 | TG-JHI063A-2 | DT-2 | MAHILA COLLEGE VIVEK VIHAR:PL | 2 | 630 | 19505797 | 557 | 2019-06-30 23:30 | 169 | 717 | 158 | 676 | 230 | 989 | 294 | 623 | 95 |  |  | 95 | 87% | 57% | 63% | 88% | 6.5748 | Loss 5-10% |  | 506(27.5) | 697(106.5) | 550(50)
420 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI064 | TG-JHI064A-1 | DT-1 | SHIVA KHAND:PL | 2 | 630 | 19501632 | 545 | 2019-06-30 | 178 | 744 | 145 | 605 | 222 | 946 | 296 | 642 | 78 |  |  | 78 | 86% | 54% | 62% | 84% | 4.6933 | Loss 0-5% |  |  | 537(79) | 506(30)
421 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI064 | TG-JHI064A-2 | DT-2 | SHIVA KHAND:PL | 2 | 400 | 19501038 | 212 | 2019-06-11 | 76 | 338 | 76 | 338 | 60 | 265 | 73 | 720 |  |  |  | 0 | 53% | 32% | 41% | 51% | 4.6933 | Loss 0-5%
422 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI074 | TG-JHI074A-1 | DT-1 | C-BLK DSIDC JLM COLONY:ID | 2 | 400 | 19505838 | 402 | 2019-06-02 00:30 | 144 | 601 | 120 | 496 | 138 | 574 | 94 | 565.5 | 131.5 | 21.5 | 0.5 | 153.5 | 100% | 65% | 76% | 100% | 6.691 | Loss 5-10% |  | 331(24) | 359(119.5) | 366(75) | 339(60)
423 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI074 | TG-JHI074A-2 | DT-2 | C-BLK DSIDC JLM COLONY:ID | 2 | 400 | 19506228 | 191 | 2019-06-03 | 41 | 167 | 82 | 337 | 68 | 277 | 150 | 718.5 |  |  |  | 0 | 48% | 33% | 32% | 46% | 6.691 | Loss 5-10%
424 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI126 | TG-JHI126A-1 | DT-1 | A-BLK VIVEK VIHAR PH-2 | 2 | 990 | 19505009 | 811 | 2019-06-29 23:30 | 265 | 1115 | 279 | 1170 | 266 | 1130 | 49 | 685.5 | 34.5 |  |  | 34.5 | 77% | 51% | 70% | 82% | 4.7552 | Loss 0-5% |  |  | 804(45.5)
425 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI126 | TG-JHI126A-2 | DT-2 | A-BLK VIVEK VIHAR PH-2 | 2 | 400 | 19505428 | 298.0303 | 2019-06-13 23:00 | 115.7397 | 483.8618 | 105.5294 | 435.4781 | 76.7612 | 319.0406 | 146.739 | 707 | 12 |  |  | 12 | 73% | 51% | 55% | 75% | 4.7552 | Loss 0-5%
426 | 1210 | KKD | B-BLOCK VIVEK VIHAR | VNG002 | TG-VNG002A-1 | DT-1 | YOJNA VIHAR C-BLOCK:ID | 1 | 990 | 19504191 | 920 | 2019-06-11 23:00 | 287 | 1237 | 327 | 1408 | 305 | 1317 | 148 | 581 | 138 | 1 |  | 139 | 89% | 59% | 72% | 93% | 5.2078 | Loss 5-10% |  | 532(49.5) | 552(113.5) | 511(35.5)
427 | 1210 | KKD | B-BLOCK VIVEK VIHAR | VNG048 | TG-VNG048A-1 | DT-1 | SURAJ MAL VIHAR C-BLOCK:ID | 3 | 990 | 19502894 | 866 | 2019-06-03 02:00 | 314 | 1255 | 282 | 1126 | 270 | 1077 | 159 | 640 | 80 |  |  | 80 | 87% | 71% | 66% | 86% | 3.9787 | Loss 0-5% |  |  | 832(79.5)
428 | 1210 | KKD | B-BLOCK VIVEK VIHAR | VNG048 | TG-VNG048A-2 | DT-2 | SURAJ MAL VIHAR C-BLOCK:ID | 3 | 990 | 19502893 | 745 | 2019-06-13 22:00 | 270 | 1140 | 276 | 1176 | 199 | 844 | 316 | 704 | 16 |  |  | 16 | 75% | 51% | 60% | 75% | 3.9787 | Loss 0-5%
429 | 1210 | KKD | B-BLOCK VIVEK VIHAR | VNG048 | TG-VNG048A-3 | DT-3 | SURAJ MAL VIHAR C-BLOCK:ID | 3 | 630 | 19504546 | 510 | 2019-06-08 23:30 | 123 | 524 | 210 | 914 | 176 | 750 | 339 | 673.5 | 42 |  |  | 42 | 80% | 54% | 59% | 81% | 3.9787 | Loss 0-5% |  |  | 553(42)
430 | 1210 | KKD | B-BLOCK VIVEK VIHAR | VNG104 | TG-VNG104A-1 | DT-1 | YOJANA VIHAR B-BLOCK:ID | 2 | 990 | 19503000 | 385 | 2019-06-29 23:00 | 155 | 658 | 119 | 497 | 111 | 467 | 178 | 720 |  |  |  | 0 | 38% | 27% | 33% | 39% | 7.2788 | Loss 5-10%
431 | 1210 | KKD | B-BLOCK VIVEK VIHAR | VNG104 | TG-VNG104A-2 | DT-2 | YOJANA VIHAR B-BLOCK:ID | 2 | 400 | 19503016 | 348 | 2019-06-16 00:30 | 85 | 365 | 115 | 497 | 148 | 647 | 244 | 620 | 100 |  |  | 100 | 87% | 55% | 66% | 86% | 7.2788 | Loss 5-10% |  | 388(67.5) | 411(174.5) | 372(85.5)
432 | 1210 | KKD | B-BLOCK VIVEK VIHAR | VNG115 | TG-VNG115A-1 | DT-1 | SURAJ MAL VIHAR B-BLOCK:PG | 1 | 990 | 19501029 | 1038 | 2019-06-01 00:30 | 337 | 1442 | 366 | 1554 | 336 | 1435 | 115 | 531.5 | 145.5 | 40 | 2 | 187.5 | 105% | 68% | 77% | 101% | 6.2168 | Loss 5-10% |  | 823(45.5) | 910(119.5) | 903(70.5)
433 | 1210 | KKD | JWALA NAGAR | VNG007 | TG-VNG007A-1 | DT-1 | RAMA BLOCK(BABU RAM SCHOOL):K | 2 | 630 | 19501463 | 459 | 2019-06-11 23:00 | 189 | 799 | 140 | 584 | 129 | 541 | 239 | 714 | 6 |  |  | 6 | 70% | 52% | 58% | 73% | 7.9185 | Loss 5-10%
434 | 1210 | KKD | JWALA NAGAR | VNG007 | TG-VNG007A-2 | DT-2 | RAMA BLOCK(BABU RAM SCHOOL):K | 2 | 990 | 19503651 | 928 | 2019-06-12 | 353 | 1476 | 258 | 1072 | 317 | 1318 | 352 | 604.5 | 114 | 1.5 |  | 115.5 | 94% | 62% | 69% | 93% | 7.9185 | Loss 5-10% |  |  | 811(44)
435 | 1210 | KKD | JWALA NAGAR | VNG010 | TG-VNG010A-1 | DT-1 | ANAJ MANDI:K | 2 | 630 | 19504171 | 398 | 2019-06-12 13:30 | 116 | 487 | 146 | 623 | 136 | 571 | 119 | 720 |  |  |  | 0 | 60% | 44% | 63% | 59% | 6.5777 | Loss 5-10%
436 | 1210 | KKD | JWALA NAGAR | VNG010 | TG-VNG010A-2 | DT-2 | ANAJ MANDI:K | 2 | 990 | 19505882 | 954 | 2019-06-10 | 299 | 1242 | 365 | 1527 | 290 | 1205 | 305 | 620.5 | 96.5 | 3 |  | 99.5 | 96% | 59% | 86% | 92% | 6.5777 | Loss 5-10% |  | 847(31.5) | 914(105)
437 | 1210 | KKD | JWALA NAGAR | VNG011 | TG-VNG011A-1 | DT-1 | DELHI GATE:K | 2 | 990 | 19506806 | 792 | 2019-06-10 23:30 | 276 | 1180 | 291 | 1238 | 225 | 950 | 264 | 678 | 42 |  |  | 42 | 77% | 48% | 73% | 80% | 3.4264 | Loss 0-5% |  |  | 771(45.5)
438 | 1210 | KKD | JWALA NAGAR | VNG011 | TG-VNG011A-2 | DT-2 | DELHI GATE:K | 2 | 400 | 19504394 | 288 | 2019-06-11 23:30 | 104 | 435 | 104 | 434 | 80 | 334 | 101 | 717 | 2.5 |  |  | 2.5 | 72% | 55% | 52% | 72% | 3.4264 | Loss 0-5%
439 | 1210 | KKD | JWALA NAGAR | VNG013 | TG-VNG013A-1 | DT-1 | BIHARI COLONY:K | 3 | 990 | 19503502 | 981 | 2019-06-11 23:30 | 378 | 1583 | 248 | 1041 | 355 | 1509 | 509 | 563 | 142 | 15 |  | 157 | 94% | 60% | 75% | 99% | 7.415 | Loss 5-10% |  | 943(79) | 1030(199.5) | 995(122) | 837(78.5)
440 | 1210 | KKD | JWALA NAGAR | VNG013 | TG-VNG013A-2 | DT-2 | BIHARI COLONY:K | 3 | 990 | 19506743 | 855 | 2019-06-30 23:00 | 339 | 1410 | 278 | 1149 | 238 | 971 | 383 | 664 | 56 |  |  | 56 | 82% | 58% | 66% | 86% | 7.415 | Loss 5-10% |  | 849(41.5) | 959(126.5) | 885(66.5) | 771(27)
441 | 1210 | KKD | JWALA NAGAR | VNG013 | TG-VNG013A-3 | DT-3 | BIHARI COLONY:K | 3 | 990 | 19504190 | 1048 | 2019-06-11 00:30 | 354 | 1571 | 353 | 1587 | 341 | 1522 | 59 | 501 | 164.5 | 50 | 4.5 | 219 | 106% | 74% | 81% | 104% | 7.415 | Loss 5-10% |  | 886(55.5) | 954(145) | 910(82) | 783(37)
442 | 1210 | KKD | JWALA NAGAR | VNG017 | TG-VNG017A-1 | DT-1 | MUKESH NAGAR:PL | 2 | 990 | 19506922 | 978 | 2019-06-30 23:30 | 320 | 1371 | 361 | 1581 | 298 | 1289 | 261 | 323 | 84 | 10.5 |  | 94.5 | 97% | 75% | 73% | 99% | 9.4921 | Loss 5-10% |  | 845(58) | 923(180) | 900(121.5) | 835(70)
443 | 1210 | KKD | JWALA NAGAR | VNG017 | TG-VNG017A-2 | DT-2 | MUKESH NAGAR:PL | 2 | 990 | 19504777 | 683 | 2019-06-02 23:30 | 239 | 1014 | 180 | 766 | 265 | 1120 | 315 | 719 |  |  |  | 0 | 68% | 48% | 55% | 69% | 9.4921 | Loss 5-10%
444 | 1210 | KKD | JWALA NAGAR | VNG018 | TG-VNG018A-1 | DT-1 | TEL MILL:PL | 1 | 990 | 19505883 | 969 | 2019-06-09 | 443 | 1887 | 255 | 1072 | 271 | 1131 | 788 | 635 | 74.5 | 10.5 |  | 85 | 98% | 67% | 68% | 96% | 6.6391 | Loss 5-10% |  | 969(123) | 1053(235.5) | 999(176.5) | 991(126.5)
445 | 1210 | KKD | JWALA NAGAR | VNG022 | TG-VNG022A-1 | DT-1 | 4-POLE PANDAV ROAD:PL | 1 | 990 | 19505267 | 855 | 2019-06-10 23:30 | 232 | 1014 | 292 | 1283 | 331 | 1457 | 386 | 637.5 | 82.5 |  |  | 82.5 | 83% | 58% | 71% | 86% | 3.6933 | Loss 0-5%
446 | 1210 | KKD | JWALA NAGAR | VNG025 | TG-VNG025A-1 | DT-1 | MAHAVIR BLOCK:PL | 2 | 400 | 19505298 | 388 | 2019-06-02 23:30 | 109 | 437 | 172 | 698 | 107 | 428 | 265 | 618.5 | 95 | 6.5 |  | 101.5 | 95% | 62% | 67% | 97% | 4.7099 | Loss 0-5% |  | 318(26.5) | 348(104)
447 | 1210 | KKD | JWALA NAGAR | VNG025 | TG-VNG025A-2 | DT-2 | MAHAVIR BLOCK:PL | 2 | 400 | 19506616 | 307 | 2019-06-12 00:30 | 109 | 447 | 94 | 393 | 105 | 432 | 48 | 707 | 13 |  |  | 13 | 77% | 49% | 52% | 76% | 4.7099 | Loss 0-5% |  | 362(84)
448 | 1210 | KKD | JWALA NAGAR | VNG026 | TG-VNG026A-1 | DT-1 | DALAI MOHALLA:PL | 1 | 990 | 19504081 | 792 | 2019-06-12 14:30 | 224 | 936 | 268 | 1127 | 300 | 1248 | 272 | 565.5 | 36.5 |  |  | 36.5 | 67% | 58% | 80% | 70% | 3.0076 | Loss 0-5% |  | 817(64.5) | 843(99.5) | 824(38.5)
449 | 1210 | KKD | JWALA NAGAR | VNG027 | TG-VNG027A-1 | DT-1 | SHALIMAR PARK:K | 2 | 990 | 19505963 | 981 | 2019-06-10 23:30 | 390 | 1661 | 248 | 1051 | 343 | 1465 | 540 | 569 | 129.5 | 20 |  | 149.5 | 96% | 62% | 97% | 99% | 5.0551 | Loss 5-10% |  | 894(63.5) | 992(141) | 894(63)
450 | 1210 | KKD | JWALA NAGAR | VNG027 | TG-VNG027A-2 | DT-2 | SHALIMAR PARK:K | 2 | 630 | 19505354 | 374 | 2019-06-29 23:00 | 128 | 559 | 122 | 530 | 124 | 538 | 26 | 718.5 |  |  |  | 0 | 58% | 39% | 45% | 59% | 5.0551 | Loss 5-10%
451 | 1210 | KKD | JWALA NAGAR | VNG028 | TG-VNG028A-1 | DT-1 | MANI RAM MANDIR:PL | 3 | 990 | 19506740 | 1245 | 2019-06-27 03:00 | 368 | 1467 | 360 | 1413 | 517 | 2088 | 649 | 484 | 141 | 51 | 44 | 236 | 126% | 79% | 81% | 114% | 4.9515 | Loss 0-5% |  |  | 857(69)
452 | 1210 | KKD | JWALA NAGAR | VNG028 | TG-VNG028A-2 | DT-2 | MANI RAM MANDIR:PL | 3 | 990 | 19504924 | 800 | 2019-06-30 23:30 | 221 | 907 | 316 | 1311 | 264 | 1069 | 352 | 707.5 | 12.5 |  |  | 12.5 | 79% | 53% | 55% | 81% | 4.9515 | Loss 0-5% |  | 980(58) | 911(117.5) | 875(52)
453 | 1210 | KKD | JWALA NAGAR | VNG028 | TG-VNG028A-3 | DT-3 | MANI RAM MANDIR:PL | 3 | 630 | 19505681 | 648 | 2019-06-12 | 280 | 1180 | 220 | 896 | 148 | 607 | 496 | 656.5 | 59 | 4 | 0.5 | 63.5 | 103% | 57% | 64% | 94% | 4.9515 | Loss 0-5% |  |  | 595(83.5) | 559(39)
454 | 1210 | KKD | JWALA NAGAR | VNG029 | TG-VNG029A-1 | DT-1 | IDGAH BHOLA NATH NAGAR:PL | 1 | 990 | 19505511 | 1160.112 | 2019-06-10 23:30 | 457.9477 | 2048.7998 | 309.9058 | 1380.5495 | 392.2585 | 1779.5959 | 582.3518 | 440.5 | 211 | 52.5 | 14.5 | 278 | 109% | 78% | 89% | 117% | 7.3987 | Loss 5-10% |  | 1154(298.5) | 1229(240.5) |  | 924(38) | 821(46.5)
455 | 1210 | KKD | JWALA NAGAR | VNG030 | TG-VNG030A-1 | DT-1 | TELEWARA:PM | 1 | 400 | 19504455 | 347 | 2019-06-12 | 120 | 519 | 115 | 497 | 112 | 487 | 29 | 617.5 | 102 |  |  | 102 | 87% | 60% | 75% | 86% | 2.6793 | Loss 0-5% |  | 445(186.5) | 483(394.5) | 462(257.5) | 412(210.5) | 338(37)
456 | 1210 | KKD | JWALA NAGAR | VNG031 | TG-VNG031A-1 | DT-1 | TEJAB MILL:PL | 3 | 990 | 19503074 | 942 | 2019-06-11 00:30 | 291 | 1285 | 376 | 1667 | 275 | 1213 | 423 | 568 | 145 | 3 |  | 148 | 95% | 66% | 73% | 91% | 10.8309 | Loss 10-20% |  | 882(35) | 992(133) | 878(79) | 829(33.5)
457 | 1210 | KKD | JWALA NAGAR | VNG031 | TG-VNG031A-2 | DT-2 | TEJAB MILL:PL | 3 | 990 | 19504207 | 626 | 2019-06-30 23:30 | 228 | 1019 | 192 | 849 | 205 | 917 | 148 | 713.5 |  |  |  | 0 | 63% | 41% | 54% | 63% | 10.8309 | Loss 10-20%
458 | 1210 | KKD | JWALA NAGAR | VNG031 | TG-VNG031A-3 | DT-3 | TEJAB MILL:PL | 3 | 630 | 19506510 | 501 | 2019-06-30 | 184 | 742 | 136 | 546 | 181 | 724 | 188 | 700 | 15.5 |  |  | 15.5 | 79% | 54% | 67% | 77% | 10.8309 | Loss 10-20%
459 | 1210 | KKD | JWALA NAGAR | VNG032 | TG-VNG032A-1 | DT-1 | MAHA RAM MOHALLA:PL | 2 | 990 | 19506260 | 515 | 2019-06-26 | 259 | 1140 | 141 | 611 | 115 | 495 | 595 | 719 |  |  |  | 0 | 52% | 36% | 33% | 52% | 3.0255 | Loss 0-5% |  | 949(86) | 1049(201) | 978(143) | 879(93.5)
460 | 1210 | KKD | JWALA NAGAR | VNG032 | TG-VNG032A-2 | DT-2 | MAHA RAM MOHALLA:PL | 2 | 630 | 19506688 | 546 | 2019-06-30 00:30 | 204 | 830 | 159 | 645 | 183 | 747 | 161 | 622.5 | 96.5 |  |  | 96.5 | 87% | 61% | 64% | 84% | 3.0255 | Loss 0-5%
461 | 1210 | KKD | JWALA NAGAR | VNG036 | TG-VNG036A-1 | DT-1 | BHOLA NATH NAGAR:K | 3 | 990 | 19503515 | 809 | 2019-06-29 23:30 | 249 | 1051 | 261 | 1116 | 299 | 1249 | 175 | 666.5 | 53 |  |  | 53 | 81% | 55% | 64% | 82% | 9.4245 | Loss 5-10% |  |  | 755(26)
462 | 1210 | KKD | JWALA NAGAR | VNG036 | TG-VNG036A-2 | DT-2 | BHOLA NATH NAGAR:K | 3 | 990 | 19501600 | 805 | 2019-06-12 | 231 | 941 | 275 | 1142 | 300 | 1243 | 266 | 669 | 51 |  |  | 51 | 81% | 54% | 57% | 81% | 9.4245 | Loss 5-10% |  |  | 787(41)
463 | 1210 | KKD | JWALA NAGAR | VNG036 | TG-VNG036A-3 | DT-3 | BHOLA NATH NAGAR:K | 3 | 630 | 19506687 | 665 | 2019-06-10 01:30 | 210 | 887 | 169 | 710 | 285 | 1238 | 465 | 617 | 95.5 | 6.5 | 1 | 103 | 106% | 61% | 67% | 97% | 9.4245 | Loss 5-10%
464 | 1210 | KKD | JWALA NAGAR | VNG037 | TG-VNG037A-1 | DT-1 | PATHAN PURA:PL | 1 | 990 | 19505282 | 1165 | 2019-06-09 23:30 | 364 | 1656 | 500 | 2284 | 300 | 1321 | 847 | 590.5 | 126.5 | 2.5 | 0.5 | 129.5 | 91% | 65% | 72% | 118% | 5.2561 | Loss 5-10% |  | 934(87) | 1036(214.5) | 1285(148.5) | 895(89.5)
465 | 1210 | KKD | JWALA NAGAR | VNG038 | TG-VNG038A-1 | DT-1 | AGGARWAL BHAWAN:PM | 2 | 630 | 19501636 | 511 | 2019-06-11 23:30 | 179 | 744 | 176 | 732 | 156 | 656 | 83 | 688.5 | 31.5 |  |  | 31.5 | 77% | 54% | 61% | 81% | 7.2365 | Loss 5-10% |  |  | 514(45)
466 | 1210 | KKD | JWALA NAGAR | VNG038 | TG-VNG038A-2 | DT-2 | AGGARWAL BHAWAN:PM | 2 | 630 | 19506027 | 478 | 2019-06-09 23:00 | 156 | 688 | 126 | 555 | 196 | 888 | 291 | 719.5 | 0.5 |  |  | 0.5 | 55% | 38% | 46% | 76% | 7.2365 | Loss 5-10%
467 | 1210 | KKD | JWALA NAGAR | VNG064 | TG-VNG064A-1 | DT-1 | HALKANA KUNA NO-1:K | 4 | 630 | 19504605 | 540 | 2019-06-29 23:00 | 155 | 683 | 167 | 732 | 218 | 966 | 263 | 575.5 | 144 |  |  | 144 | 84% | 82% | 82% | 86% | 7.7783 | Loss 5-10% |  |  | 517(111.5) | 528(93) | 506(65.5)
468 | 1210 | KKD | JWALA NAGAR | VNG064 | TG-VNG064A-2 | DT-2 | HALKANA KUNA NO-1:K | 4 | 990 | 19504069 | 481 | 2019-06-30 | 167 | 672 | 152 | 614 | 162 | 651 | 51 | 720 |  |  |  | 0 | 49% | 40% | 43% | 48% | 7.7783 | Loss 5-10%
469 | 1210 | KKD | JWALA NAGAR | VNG064 | TG-VNG064A-3 | DT-3 | HALKANA KUNA NO-1:K | 4 | 990 | 19504070 | 679 | 2019-06-29 23:00 | 233 | 963 | 207 | 868 | 240 | 992 | 113 | 719.5 |  |  |  | 0 | 68% | 51% | 59% | 69% | 7.7783 | Loss 5-10%
470 | 1210 | KKD | JWALA NAGAR | VNG064 | TG-VNG064A-4 | DT-4 | HALKANA KUNA NO-1:K | 4 | 630 | 19506251 | 795 | 2019-06-29 15:00 | 54 | 221 | 335 | 1630 | 405 | 1773 | 1485 | 719 |  |  | 1 | 1 | 55% | 42% | 126% | 122% | 7.7783 | Loss 5-10%
471 | 1210 | KKD | JWALA NAGAR | VNG090 | TG-VNG090A-1 | DT-1 | GALI NO-10 VISHWAS NAGAR:PL | 2 | 990 | 19500425 | 268 | 2019-06-13 22:30 | 89 | 373 | 108 | 461 | 71 | 302 | 138 | 719.5 |  |  |  | 0 | 25% | 22% | 24% | 27% | 2.957 | Loss 0-5%
472 | 1210 | KKD | JWALA NAGAR | VNG090 | TG-VNG090A-2 | DT-2 | GALI NO-10 VISHWAS NAGAR:PL | 2 | 990 | 19505959 | 920 | 2019-06-30 23:30 | 233 | 1014 | 272 | 1197 | 415 | 1887 | 797 | 548 | 170 | 2 |  | 172 | 90% | 66% | 76% | 93% | 2.957 | Loss 0-5% |  | 866(40.5) | 923(152) | 901(84)
473 | 1210 | KKD | JWALA NAGAR | VNG111 | TG-VNG111A-1 | DT-1 | BIHARI COLONY EXT.;PL | 2 | 990 | 19506872 | 448 | 2019-06-30 23:00 | 102 | 419 | 221 | 927 | 125 | 512 | 468 | 720 |  |  |  | 0 | 44% | 37% | 43% | 45% | 6.9857 | Loss 5-10%
474 | 1210 | KKD | JWALA NAGAR | VNG111 | TG-VNG111A-2 | DT-2 | BIHARI COLONY EXT.;PL | 2 | 630 | 19505884 | 562 | 2019-06-03 | 142 | 576 | 200 | 827 | 220 | 910 | 302 | 628 | 92 |  |  | 92 | 89% | 64% | 72% | 84% | 6.9857 | Loss 5-10% |  |  | 847(87.5) | 561(36)
475 | 1210 | KKD | JWALA NAGAR | VNG158 | TG-VNG158A-1 | DT-1 | CIVIL HOSPITAL SHAHDARA S/STN | 1 | 990 | 19501461 | 911 | 2019-06-30 16:00 | 341 | 1492 | 295 | 1277 | 275 | 1188 | 270 | 596 | 121 | 3 |  | 124 | 56% | 41% | 92% | 58% | 6.7082 | Loss 5-10% |  |  | 827(126)
476 | 1210 | KKD | JWALA NAGAR | VNG177 | TG-VNG177A-1 | DT-1 | TELIWARA PARK NEAR GURUDWARA :OD | 1 | 630 | 19501469 | 509 | 2019-06-11 23:30 | 206 | 872 | 118 | 497 | 185 | 762 | 334 | 677.5 | 42.5 |  |  | 42.5 | 81% | 56% | 68% | 81% | 3.6358 | Loss 0-5%
477 | 1210 | KKD | SAINI ENCLAVE | VNG012 | TG-VNG012A-1 | DT-1 | LSC MKT A-BLK SURAJ MAL VIHAR:ID | 2 | 630 | 19501049 | 546 | 2019-06-29 16:30 | 163 | 697 | 214 | 932 | 169 | 726 | 223 | 631.5 | 88 |  |  | 88 | 72% | 51% | 87% | 75% | 6.7244 | Loss 5-10% |  |  | 527(92.5) | 519(27.5)
478 | 1210 | KKD | SAINI ENCLAVE | VNG012 | TG-VNG012A-2 | DT-2 | LSC MKT A-BLK SURAJ MAL VIHAR:ID | 2 | 630 | 19501050 | 198 | 2019-06-08 15:00 | 53 | 234 | 76 | 339 | 68 | 306 | 93 | 719.5 |  |  |  | 0 | 22% | 18% | 31% | 25% | 6.7244 | Loss 5-10%
479 | 1210 | KKD | SAINI ENCLAVE | VNG019 | TG-VNG019A-1 | DT-1 | ASHOKA NIKETAN:PG | 1 | 990 | 19504456 | 842 | 2019-06-11 23:30 | 330 | 1446 | 267 | 1169 | 246 | 1073 | 335 | 634.5 | 84 |  |  | 84 | 85% | 54% | 66% | 85% | 5.0128 | Loss 5-10% |  |  | 869(72.5) | 822(31)
480 | 1210 | KKD | SAINI ENCLAVE | VNG035 | TG-VNG035A-1 | DT-1 | KARKAR DOOMA VILLAGE:PM | 1 | 990 | 19506467 | 958 | 2019-06-29 23:30 | 349 | 1466 | 368 | 1551 | 241 | 1012 | 502 | 459.5 | 251 | 9.5 |  | 260.5 | 96% | 84% | 87% | 97% | 4.1713 | Loss 0-5% |  | 846(40) | 977(278.5) | 916(227) | 853(106.5)
481 | 1210 | KKD | SAINI ENCLAVE | VNG053 | TG-VNG053A-1 | DT-1 | ANAND VIHAR C-BLOCK:ID | 3 | 990 | 19502989 | 367 | 2019-06-11 23:30 | 143 | 626 | 124 | 544 | 100 | 435 | 166 | 718.5 |  |  |  | 0 | 36% | 25% | 31% | 37% | 4.0445 | Loss 0-5%
482 | 1210 | KKD | SAINI ENCLAVE | VNG053 | TG-VNG053A-2 | DT-2 | ANAND VIHAR C-BLOCK:ID | 3 | 990 | 19502988 | 956 | 2019-06-11 00:30 | 325 | 1395 | 346 | 1477 | 285 | 1212 | 235 | 563.5 | 147.5 | 7.5 |  | 155 | 97% | 67% | 75% | 94% | 4.0445 | Loss 0-5% |  | 793(26.5) | 812(72.5)
483 | 1210 | KKD | SAINI ENCLAVE | VNG053 | TG-VNG053A-3 | DT-3 | ANAND VIHAR C-BLOCK:ID | 3 | 990 | 19504618 | 745 | 2019-06-12 | 364 | 1549 | 190 | 804 | 191 | 804 | 745 | 705 | 14 |  |  | 14 | 75% | 48% | 54% | 75% | 4.0445 | Loss 0-5% |  |  | 778(46)
484 | 1210 | KKD | SAINI ENCLAVE | VNG070 | TG-VNG070A-1 | DT-1 | AGCR ENCLAVE:ID | 3 | 990 | 19502985 | 425 | 2019-06-11 23:00 | 128 | 510 | 166 | 661 | 131 | 526 | 144 | 720 |  |  |  | 0 | 43% | 30% | 34% | 43% | 6.8619 | Loss 5-10% |  |  | 916(38) | 813(29.5)
485 | 1210 | KKD | SAINI ENCLAVE | VNG070 | TG-VNG070A-2 | DT-2 | AGCR ENCLAVE:ID | 3 | 630 | 19502991 | 531 | 2019-06-30 01:00 | 214 | 861 | 140 | 563 | 177 | 713 | 258 | 661.5 | 34.5 |  |  | 34.5 | 84% | 55% | 61% | 79% | 6.8619 | Loss 5-10% |  | 522(24) | 549(45)
486 | 1210 | KKD | SAINI ENCLAVE | VNG070 | TG-VNG070A-3 | DT-3 | AGCR ENCLAVE:ID | 3 | 990 | 19504048 | 469 | 2019-06-30 20:00 | 171 | 686 | 137 | 549 | 160 | 638 | 120 | 720 |  |  |  | 0 | 38% | 25% | 47% | 41% | 6.8619 | Loss 5-10%
487 | 1210 | KKD | SAINI ENCLAVE | VNG071 | TG-VNG071A-1 | DT-1 | HARGOVIND ENCLAVE:ID | 3 | 990 | 19501110 | 830 | 2019-06-11 00:30 | 306 | 1354 | 283 | 1256 | 241 | 1063 | 257 | 664.5 | 55 |  |  | 55 | 84% | 61% | 80% | 79% | 3.9773 | Loss 0-5%
488 | 1210 | KKD | SAINI ENCLAVE | VNG071 | TG-VNG071A-2 | DT-2 | HARGOVIND ENCLAVE:ID | 3 | 990 | 19501074 | 771 | 2019-06-12 11:30 | 248 | 1047 | 257 | 1089 | 266 | 1121 | 64 | 712 | 5 |  |  | 5 | 65% | 61% | 78% | 67% | 3.9773 | Loss 0-5% |  | 860(47.5) | 922(149.5) | 840(91)
489 | 1210 | KKD | SAINI ENCLAVE | VNG071 | TG-VNG071A-3 | DT-3 | HARGOVIND ENCLAVE:ID | 3 | 630 | 19503063 | 720 | 2019-06-27 17:00 | 228 | 927 | 268 | 1107 | 224 | 919 | 184 | 475.5 | 207 | 21.5 | 13.5 | 242 | 79% | 82% | 114% | 101% | 3.9773 | Loss 0-5% |  | 581(183.5) | 613(316) | 610(260.5) | 552(215.5) | 478(24.5)
490 | 1210 | KKD | SAINI ENCLAVE | VNG073 | TG-VNG073A-1 | DT-1 | DELHI ADMN FLATS:ID | 2 | 630 | 19501084 | 568 | 2019-06-30 23:30 | 211 | 895 | 158 | 669 | 199 | 843 | 205 | 606.5 | 113 | 0.5 |  | 113.5 | 88% | 63% | 68% | 90% | 14.8145 | Loss 10-20%
491 | 1210 | KKD | SAINI ENCLAVE | VNG073 | TG-VNG073A-2 | DT-2 | DELHI ADMN FLATS:ID | 2 | 990 | 19501107 | 736 | 2019-06-17 07:00 | 221 | 888 | 270 | 1093 | 246 | 985 | 178 | 718.5 | 0.5 |  |  | 0.5 | 70% | 74% | 61% | 67% | 14.8145 | Loss 10-20% |  | 784(57.5) | 854(251.5) | 874(275) | 824(218) | 785(38)
492 | 1210 | KKD | SAINI ENCLAVE | VNG076 | TG-VNG076A-1 | DT-1 | SURYA NIKETAN:ID | 3 | 990 | 19501036 | 754 | 2019-06-11 23:30 | 221 | 927 | 300 | 1267 | 233 | 986 | 315 | 702 | 17 |  |  | 17 | 74% | 54% | 60% | 76% | 4.3465 | Loss 0-5% |  |  | 782(27)
493 | 1210 | KKD | SAINI ENCLAVE | VNG076 | TG-VNG076A-2 | DT-2 | SURYA NIKETAN:ID | 3 | 990 | 19501023 | 1047 | 2019-06-06 | 361 | 1552 | 323 | 1384 | 364 | 1550 | 167 | 495 | 184 | 37 | 4 | 225 | 106% | 75% | 91% | 105% | 4.3465 | Loss 0-5% |  |  | 1005(123) | 931(123) | 793(53.5)
494 | 1210 | KKD | SAINI ENCLAVE | VNG076 | TG-VNG076A-3 | DT-3 | SURYA NIKETAN:ID | 3 | 990 | 19502911 | 572 | 2019-06-11 23:30 | 195 | 812 | 156 | 654 | 221 | 920 | 232 | 720 |  |  |  | 0 | 56% | 35% | 41% | 58% | 4.3465 | Loss 0-5%
495 | 1210 | KKD | SAINI ENCLAVE | VNG078 | TG-VNG078A-1 | DT-1 | RAM VIHAR:ID | 3 | 990 | 19505058 | 455 | 2019-06-12 | 144 | 620 | 158 | 689 | 152 | 655 | 59 | 720 |  |  |  | 0 | 46% | 31% | 41% | 44% | 3.1225 | Loss 0-5%
496 | 1210 | KKD | SAINI ENCLAVE | VNG078 | TG-VNG078A-2 | DT-2 | RAM VIHAR:ID | 3 | 990 | 19502974 | 483 | 2019-06-12 01:00 | 167 | 678 | 172 | 696 | 144 | 582 | 106 | 720 |  |  |  | 0 | 49% | 37% | 38% | 47% | 3.1225 | Loss 0-5%
497 | 1210 | KKD | SAINI ENCLAVE | VNG078 | TG-VNG078A-3 | DT-3 | RAM VIHAR:ID | 3 | 630 | 19503470 | 492 | 2019-06-11 23:30 | 182 | 751 | 162 | 663 | 147 | 597 | 134 | 694 | 26 |  |  | 26 | 77% | 54% | 63% | 78% | 3.1225 | Loss 0-5%
498 | 1210 | KKD | SAINI ENCLAVE | VNG081 | TG-VNG081A-1 | DT-1 | ANAND VIHAR A-BLOCK:ID | 3 | 990 | 19501125 | 548 | 2019-06-11 23:00 | 164 | 682 | 174 | 733 | 210 | 877 | 175 | 720 |  |  |  | 0 | 52% | 42% | 55% | 55% | 5.373 | Loss 5-10%
499 | 1210 | KKD | SAINI ENCLAVE | VNG081 | TG-VNG081A-2 | DT-2 | ANAND VIHAR A-BLOCK:ID | 3 | 990 | 19501090 | 825 | 2019-06-11 | 270 | 1191 | 291 | 1277 | 264 | 1153 | 110 | 660 | 60 |  |  | 60 | 83% | 58% | 65% | 83% | 5.373 | Loss 5-10% |  |  | 756(28)
500 | 1210 | KKD | SAINI ENCLAVE | VNG081 | TG-VNG081A-3 | DT-3 | ANAND VIHAR A-BLOCK:ID | 3 | 630 | 19506753 | 356 | 2019-06-03 00:30 | 88 | 366 | 89 | 380 | 179 | 811 | 438 | 720 |  |  |  | 0 | 56% | 39% | 48% | 49% | 5.373 | Loss 5-10%
501 | 1210 | KKD | SAINI ENCLAVE | VNG099 | TG-VNG099A-1 | DT-1 | L.S.C SAINI ENCLAVE:ID | 2 | 630 | 19501087 | 176 | 2019-06-12 15:30 | 36 | 150 | 49 | 205 | 91 | 383 | 211 | 720 |  |  |  | 0 | 8% | 10% | 28% | 15% | 2.8496 | Loss 0-5%
502 | 1210 | KKD | SAINI ENCLAVE | VNG099 | TG-VNG099A-2 | DT-2 | L.S.C SAINI ENCLAVE:ID | 2 | 630 | 19501086 | 562 | 2019-06-10 16:00 | 215 | 925 | 169 | 707 | 179 | 753 | 199 | 567.5 | 152.5 |  |  | 152.5 | 81% | 57% | 89% | 81% | 2.8496 | Loss 0-5%
503 | 1210 | KKD | SAINI ENCLAVE | VNG103 | TG-VNG103A-1 | DT-1 | DAYANAND VIHAR 2:ID | 3 | 630 | 19501137 | 421 | 2019-06-29 23:00 | 139 | 592 | 119 | 504 | 164 | 706 | 175 | 718.5 |  |  |  | 0 | 65% | 41% | 48% | 67% | 3.6475 | Loss 0-5%
504 | 1210 | KKD | SAINI ENCLAVE | VNG103 | TG-VNG103A-2 | DT-2 | DAYANAND VIHAR 2:ID | 3 | 990 | 19501081 | 577 | 2019-06-29 13:30 | 171 | 718 | 222 | 934 | 184 | 769 | 195 | 719.5 |  |  |  | 0 | 46% | 39% | 58% | 46% | 3.6475 | Loss 0-5%
505 | 1210 | KKD | SAINI ENCLAVE | VNG103 | TG-VNG103A-3 | DT-3 | DAYANAND VIHAR 2:ID | 3 | 630 | 19505437 | 570 | 2019-06-29 16:00 | 186 | 788 | 193 | 816 | 191 | 805 | 25 | 625 | 94.5 | 0.5 |  | 95 | 55% | 55% | 90% | 72% | 3.6475 | Loss 0-5% |  | 590(81.5) | 630(210) | 557(118.5) | 526(69)
506 | 1210 | KKD | SAINI ENCLAVE | VNG109 | TG-VNG109A-1 | DT-1 | SURAJ MAL VIHAR A-BLOCK:ID | 2 | 990 | 19502994 | 358 | 2019-06-01 00:30 | 107 | 456 | 110 | 469 | 141 | 607 | 145 | 719.5 |  |  |  | 0 | 36% | 24% | 28% | 35% | 8.9516 | Loss 5-10%
507 | 1210 | KKD | SAINI ENCLAVE | VNG109 | TG-VNG109A-2 | DT-2 | SURAJ MAL VIHAR A-BLOCK:ID | 2 | 990 | 19504391 | 869 | 2019-06-01 01:00 | 347 | 1553 | 282 | 1251 | 240 | 1056 | 434 | 664 | 55.5 |  |  | 55.5 | 88% | 58% | 66% | 82% | 8.9516 | Loss 5-10% |  |  | 784(37)
508 | 1210 | KKD | SAINI ENCLAVE | VNG131 | TG-VNG131A-1 | DT-1 | MANAK VIHAR (VIGYAN LOK) | 2 | 630 | 19501109 | 532 | 2019-06-05 23:30 | 102 | 411 | 195 | 800 | 234 | 964 | 492 | 657 | 63 |  |  | 63 | 82% | 52% | 67% | 84% | 8.6591 | Loss 5-10%
509 | 1210 | KKD | SAINI ENCLAVE | VNG131 | TG-VNG131A-2 | DT-2 | MANAK VIHAR (VIGYAN LOK) | 2 | 990 | 19501108 | 221 | 2019-06-01 23:30 | 59 | 242 | 100 | 413 | 62 | 254 | 165 | 720 |  |  |  | 0 | 22% | 16% | 18% | 22% | 8.6591 | Loss 5-10%
510 | 1210 | KKD | SAINI ENCLAVE | VNG133 | TG-VNG133A-1 | DT-1 | D BLOCK ANAND VIHAR | 1 | 990 | 19501012 | 1199 | 2019-06-11 23:30 | 468 | 2030 | 353 | 1517 | 378 | 1626 | 469 | 462 | 168.5 | 58.5 | 29.5 | 256.5 | 120% | 76% | 90% | 121% | 4.6595 | Loss 0-5% |  | 946(98) | 1024(194.5) | 1034(115) | 801(34.5)
511 | 1210 | KKD | SAINI ENCLAVE | VNG147 | TG-VNG147A-1 | DT-1 | AGCR ENCLAVE:PKG STN | 1 | 990 | 19501011 | 871 | 2019-06-11 23:00 | 266 | 1103 | 344 | 1438 | 261 | 1085 | 345 | 601 | 119 |  |  | 119 | 87% | 62% | 71% | 88% | 4.9881 | Loss 0-5%
512 | 1211 | GTR | E&F DILSHAD GARDEN | DGN069 | TG-DGN069A-1 | DT-1 | A-BLOCK JHILMIL INDILSHAD AREA:ID | 4 | 990 | 19505452 | 753 | 2019-06-22 14:30 | 248 | 1042 | 253 | 1070 | 251 | 1060 | 25 | 715.5 | 4.5 |  |  | 4.5 | 37% | 43% | 76% | 39% | 5.5581 | Loss 5-10% | 926(135) | 1448(255) | 1437(269.5) | 1047(236) | 1155(216.5)
513 | 1211 | GTR | E&F DILSHAD GARDEN | DGN069 | TG-DGN069A-2 | DT-2 | A-BLOCK JHILMIL INDILSHAD AREA:ID | 4 | 990 | 19501371 | 856 | 2019-06-01 13:00 | 298 | 1273 | 278 | 1194 | 280 | 1194 | 79 | 640 | 80 |  |  | 80 | 43% | 43% | 86% | 62% | 5.5581 | Loss 5-10% |  |  | 967(63) | 971(79) | 1314(122) | 1431(233.5)
514 | 1211 | GTR | E&F DILSHAD GARDEN | DGN069 | TG-DGN069A-3 | DT-3 | A-BLOCK JHILMIL INDILSHAD AREA:ID | 4 | 990 | 19506328 | 1088 | 2019-06-01 11:30 | 367 | 1571 | 361 | 1542 | 360 | 1532 | 35 | 384 | 200.5 | 116 | 14.5 | 331 | 81% | 79% | 110% | 78% | 5.5581 | Loss 5-10% | 1119(160.5) | 1151(204) |  |  |  | 857(165.5)
515 | 1211 | GTR | E&F DILSHAD GARDEN | DGN069 | TG-DGN069A-4 | DT-4 | A-BLOCK JHILMIL INDILSHAD AREA:ID | 4 | 990 | 19506858 | 893 | 2019-06-28 14:30 | 309 | 1323 | 302 | 1296 | 282 | 1201 | 111 | 656.5 | 60.5 | 0.5 |  | 61 | 42% | 47% | 90% | 42% | 5.5581 | Loss 5-10%
516 | 1211 | GTR | E&F DILSHAD GARDEN | DGN071 | TG-DGN071A-1 | DT-1 | B-BLK COMPLAINT CENTER JLM IND AREA:ID | 3 | 990 | 19506356 | 953 | 2019-06-29 15:00 | 313 | 1265 | 317 | 1274 | 324 | 1315 | 46 | 554 | 156 | 10 |  | 166 | 57% | 76% | 96% | 68% | 3.5863 | Loss 0-5% | 1124(230) |  | 1280(237) | 1230(207.5) | 1179(223.5) | 1144(224.5)
517 | 1211 | GTR | E&F DILSHAD GARDEN | DGN071 | TG-DGN071A-2 | DT-2 | B-BLK COMPLAINT CENTER JLM IND AREA:ID | 3 | 990 | 19501446 | 775 | 2019-06-13 13:00 | 246 | 1007 | 250 | 1022 | 280 | 1154 | 139 | 697 | 23 |  |  | 23 | 47% | 38% | 78% | 47% | 3.5863 | Loss 0-5% | 1022(196) | 1019(224.5) | 1055(214) | 987(132) | 1138(245) | 1160(253)
518 | 1211 | GTR | E&F DILSHAD GARDEN | DGN071 | TG-DGN071A-3 | DT-3 | B-BLK COMPLAINT CENTER JLM IND AREA:ID | 3 | 990 | 19506610 | 1127 | 2019-06-22 12:30 | 380 | 1631 | 378 | 1608 | 369 | 1575 | 48 | 437.5 | 103.5 | 125.5 | 53.5 | 282.5 | 52% | 60% | 114% | 55% | 3.5863 | Loss 0-5%
519 | 1211 | GTR | E&F DILSHAD GARDEN | DGN072 | TG-DGN072A-1 | DT-1 | PREM ICE FACTORY:ID | 1 | 990 | 19506735 | 1024 | 2019-06-29 15:30 | 343 | 1409 | 339 | 1397 | 342 | 1412 | 13 | 615 | 75.5 | 26 | 2.5 | 104 | 42% | 43% | 103% | 52% | 3.8128 | Loss 0-5% | 910(123.5) | 986(170.5) | 1027(195.5) | 987(182) | 952(158.5) | 939(144.5)
520 | 1211 | GTR | E&F DILSHAD GARDEN | DGN073 | TG-DGN073A-1 | DT-1 | SARDAR ALUMINIUM:ID | 1 | 990 | 19501448 | 911 | 2019-06-22 15:00 | 312 | 1298 | 308 | 1286 | 291 | 1215 | 78 | 524.5 | 192.5 | 1.5 |  | 194 | 45% | 47% | 92% | 64% | 4.1295 | Loss 0-5% |  |  |  |  | 887(66) | 866(53.5)
521 | 1211 | GTR | E&F DILSHAD GARDEN | DGN077 | TG-DGN077A-1 | DT-1 | SANSAR:K | 3 | 990 | 19500679 | 803 | 2019-06-28 11:00 | 269 | 1113 | 273 | 1126 | 262 | 1081 | 40 | 698 | 22 |  |  | 22 | 25% | 42% | 81% | 28% | 2.7204 | Loss 0-5% | 1061(198.5) | 1006(162.5) | 1044(79.5) | 1048(156) | 1120(150) | 1425(139)
522 | 1211 | GTR | E&F DILSHAD GARDEN | DGN077 | TG-DGN077A-2 | DT-2 | SANSAR:K | 3 | 990 | 19505904 | 867 | 2019-06-21 15:30 | 290 | 1200 | 297 | 1232 | 279 | 1157 | 65 | 635.5 | 84.5 |  |  | 84.5 | 41% | 53% | 88% | 45% | 2.7204 | Loss 0-5% | 978(123) | 1000(146.5) | 1030(175.5) | 1053(203) | 1106(215.5) | 1082(62.5)
523 | 1211 | GTR | E&F DILSHAD GARDEN | DGN077 | TG-DGN077A-3 | DT-3 | SANSAR:K | 3 | 990 | 19506621 | 1125 | 2019-06-26 12:00 | 383 | 1551 | 367 | 1477 | 375 | 1513 | 64 | 456.5 | 199 | 57.5 | 6.5 | 263 | 68% | 78% | 114% | 80% | 2.7204 | Loss 0-5%
524 | 1211 | GTR | E&F DILSHAD GARDEN | DGN080 | TG-DGN080A-1 | DT-1 | SITA FLATS,DILSHAD GARDEN:ID | 3 | 630 | 19503174 | 456 | 2019-06-08 14:30 | 148 | 661 | 167 | 752 | 141 | 631 | 108 | 719.5 | 0.5 |  |  | 0.5 | 51% | 45% | 72% | 54% | 3.2709 | Loss 0-5% |  |  | 519(32.5)
525 | 1211 | GTR | E&F DILSHAD GARDEN | DGN080 | TG-DGN080A-2 | DT-2 | SITA FLATS,DILSHAD GARDEN:ID | 3 | 630 | 19504241 | 549 | 2019-06-22 18:30 | 178 | 766 | 187 | 805 | 185 | 797 | 35 | 663 | 57 |  |  | 57 | 52% | 43% | 87% | 58% | 3.2709 | Loss 0-5% | 537(43.5) | 540(37.5) |  | 579(28) | 526(34) | 564(34)
526 | 1211 | GTR | E&F DILSHAD GARDEN | DGN080 | TG-DGN080A-3 | DT-3 | SITA FLATS,DILSHAD GARDEN:ID | 3 | 630 | 19503631 | 367 | 2019-06-12 | 146 | 591 | 100 | 402 | 121 | 485 | 164 | 719.5 |  |  |  | 0 | 58% | 36% | 41% | 58% | 3.2709 | Loss 0-5%
527 | 1211 | GTR | E&F DILSHAD GARDEN | DGN081 | TG-DGN081A-1 | DT-1 | DILSHAD GDN S/STN-4:ID | 4 | 990 | 19505788 | 703 | 2019-06-20 15:30 | 220 | 917 | 235 | 982 | 248 | 1038 | 105 | 719.5 | 0.5 |  |  | 0.5 | 64% | 46% | 71% | 43% | 5.3544 | Loss 5-10% |  |  | 775(26.5)
528 | 1211 | GTR | E&F DILSHAD GARDEN | DGN081 | TG-DGN081A-2 | DT-2 | DILSHAD GDN S/STN-4:ID | 4 | 990 | 19505787 | 753 | 2019-06-02 03:30 | 164 | 700 | 384 | 1708 | 205 | 880 | 931 | 707.5 | 12.5 |  |  | 12.5 | 76% | 44% | 53% | 76% | 5.3544 | Loss 5-10% |  |  | 899(47) | 888(86) | 887(107.5) | 1158(51.5)
529 | 1211 | GTR | E&F DILSHAD GARDEN | DGN081 | TG-DGN081A-3 | DT-3 | DILSHAD GDN S/STN-4:ID | 4 | 630 | 19504435 | 623 | 2019-06-13 11:30 | 221 | 903 | 209 | 847 | 193 | 783 | 103 | 489 | 217 | 14 |  | 231 | 81% | 78% | 99% | 80% | 5.3544 | Loss 5-10% | 558(71.5) | 642(114.5) | 653(151.5) | 640(156) | 576(46.5) | 658(188.5)
530 | 1211 | GTR | E&F DILSHAD GARDEN | DGN081 | TG-DGN081A-4 | DT-4 | DILSHAD GDN S/STN-4:ID | 4 | 990 | 19504966 | 881 | 2019-06-27 11:00 | 270 | 1114 | 326 | 1346 | 285 | 1177 | 208 | 655.5 | 64 |  |  | 64 | 44% | 53% | 89% | 48% | 5.3544 | Loss 5-10%
531 | 1211 | GTR | E&F DILSHAD GARDEN | DGN083 | TG-DGN083A-1 | DT-1 | R.BLK DILSHAD GARDEN S/S NO-1:ID | 2 | 990 | 19505369 | 459 | 2019-06-15 16:30 | 136 | 584 | 161 | 691 | 162 | 705 | 115 | 720 |  |  |  | 0 | 40% | 24% | 46% | 41% | 5.1265 | Loss 5-10%
532 | 1211 | GTR | E&F DILSHAD GARDEN | DGN083 | TG-DGN083A-2 | DT-2 | R.BLK DILSHAD GARDEN S/S NO-1:ID | 2 | 630 | 19503033 | 552 | 2019-06-29 16:00 | 212 | 877 | 180 | 741 | 160 | 659 | 191 | 614.5 | 105.5 |  |  | 105.5 | 67% | 56% | 88% | 66% | 5.1265 | Loss 5-10% |  | 524(40) | 548(124.5) | 515(42.5)
533 | 1211 | GTR | E&F DILSHAD GARDEN | DGN085 | TG-DGN085A-1 | DT-1 | A-PKT,DILSHAD GDN:ID | 3 | 630 | 19501381 | 558 | 2019-06-11 01:30 | 193 | 850 | 216 | 954 | 149 | 647 | 271 | 667 | 52.5 |  |  | 52.5 | 89% | 50% | 56% | 87% | 3.2962 | Loss 0-5% |  | 577(63) | 768(162) | 653(96.5) | 497(29)
534 | 1211 | GTR | E&F DILSHAD GARDEN | DGN085 | TG-DGN085A-2 | DT-2 | A-PKT,DILSHAD GDN:ID | 3 | 630 | 19501390 | 507 | 2019-06-11 01:30 | 187 | 825 | 185 | 817 | 134 | 588 | 233 | 705 | 14.5 |  |  | 14.5 | 80% | 42% | 55% | 77% | 3.2962 | Loss 0-5% |  |  | 637(50.5)
535 | 1211 | GTR | E&F DILSHAD GARDEN | DGN085 | TG-DGN085A-3 | DT-3 | A-PKT,DILSHAD GDN:ID | 3 | 630 | 19506709 | 198 | 2019-06-12 | 66 | 262 | 35 | 138 | 97 | 391 | 219 | 719.5 |  |  |  | 0 | 31% | 26% | 26% | 30% | 3.2962 | Loss 0-5%
536 | 1211 | GTR | E&F DILSHAD GARDEN | DGN091 | TG-DGN091A-1 | DT-1 | O&P PKT DILSHAD GARDEN:ID | 2 | 630 | 19506580 | 647 | 2019-06-03 06:00 | 221 | 911 | 245 | 999 | 181 | 738 | 230 | 640 | 78.5 | 1 | 0.5 | 80 | 96% | 103% | 70% | 93% | 5.5108 | Loss 5-10% |  | 1059(24) | 515(27)
537 | 1211 | GTR | E&F DILSHAD GARDEN | DGN091 | TG-DGN091A-2 | DT-2 | O&P PKT DILSHAD GARDEN:ID | 2 | 630 | 19506560 | 585 | 2019-06-02 01:00 | 244 | 1009 | 159 | 647 | 181 | 741 | 325 | 612 | 106.5 | 1.5 |  | 108 | 93% | 61% | 83% | 91% | 5.5108 | Loss 5-10% |  |  | 565(82)
538 | 1211 | GTR | E&F DILSHAD GARDEN | DGN092 | TG-DGN092A-1 | DT-1 | Q-POCKET DILSHAD GARDEN:ID | 2 | 630 | 19505790 | 291 | 2019-06-30 00:30 | 145 | 594 | 65 | 266 | 81 | 329 | 302 | 648 |  |  |  | 0 | 46% | 29% | 32% | 46% | 3.9793 | Loss 0-5%
539 | 1211 | GTR | E&F DILSHAD GARDEN | DGN092 | TG-DGN092A-2 | DT-2 | Q-POCKET DILSHAD GARDEN:ID | 2 | 400 | 19505791 | 371 | 2019-06-02 | 164 | 697 | 96 | 399 | 110 | 456 | 274 | 666 | 53.5 | 0.5 |  | 54 | 93% | 51% | 61% | 82% | 3.9793 | Loss 0-5%
540 | 1211 | GTR | E&F DILSHAD GARDEN | DGN098 | TG-DGN098A-1 | DT-1 | OLD SEEMAPURI (BUS STOP):ID | 3 | 990 | 19504962 | 912 | 2019-06-11 23:30 | 391 | 1606 | 259 | 1058 | 262 | 1064 | 545 | 421 | 246.5 | 3.5 |  | 250 | 91% | 82% | 83% | 92% | 9.7418 | Loss 5-10% |  | 882(105.5) | 947(267.5)
541 | 1211 | GTR | E&F DILSHAD GARDEN | DGN098 | TG-DGN098A-2 | DT-2 | OLD SEEMAPURI (BUS STOP):ID | 3 | 990 | 19503080 | 548 | 2019-06-30 20:00 | 164 | 685 | 152 | 641 | 231 | 979 | 318 | 671 |  |  |  | 0 | 54% | 47% | 55% | 55% | 9.7418 | Loss 5-10%
542 | 1211 | GTR | E&F DILSHAD GARDEN | DGN098 | TG-DGN098A-3 | DT-3 | OLD SEEMAPURI (BUS STOP):ID | 3 | 400 | 19504148 | 261 | 2019-06-27 17:30 | 79 | 321 | 95 | 391 | 87 | 353 | 60 | 670.5 |  |  |  | 0 | 41% | 44% | 65% | 48% | 9.7418 | Loss 5-10%
543 | 1211 | GTR | E&F DILSHAD GARDEN | DGN099 | TG-DGN099A-1 | DT-1 | POLICE STATION OLD SEEMAPURI:ID | 1 | 990 | 19505491 | 761 | 2019-06-11 23:30 | 278 | 1144 | 249 | 1015 | 234 | 958 | 165 | 680.5 | 39 |  |  | 39 | 76% | 62% | 76% | 77% | 6.0772 | Loss 5-10%
544 | 1211 | GTR | E&F DILSHAD GARDEN | DGN101 | TG-DGN101A-1 | DT-1 | B-BLK DSIDC SHED JLM IA NO-3:ID | 2 | 630 | 19501370 | 396 | 2019-06-06 11:30 | 131 | 535 | 144 | 589 | 122 | 496 | 81 | 720 |  |  |  | 0 | 9% | 27% | 63% | 18% | 3.5132 | Loss 0-5%
545 | 1211 | GTR | E&F DILSHAD GARDEN | DGN101 | TG-DGN101A-2 | DT-2 | B-BLK DSIDC SHED JLM IA NO-3:ID | 2 | 630 | 19501353 | 758 | 2019-06-29 11:00 | 247 | 1057 | 260 | 1106 | 251 | 1076 | 42 | 500.5 | 122.5 | 64.5 | 29 | 216 | 57% | 59% | 120% | 57% | 3.5132 | Loss 0-5% | 721(153.5) | 624(113.5) | 713(162.5) | 831(185.5) | 811(139) | 801(190)
546 | 1211 | GTR | E&F DILSHAD GARDEN | DGN103 | TG-DGN103A-1 | DT-1 | A BLK TAHIRPUR(JLM IND AREA) S/STN-1:ID | 3 | 630 | 19501361 | 567 | 2019-06-27 14:30 | 185 | 697 | 187 | 701 | 195 | 739 | 41 | 697 | 23 |  |  | 23 | 40% | 50% | 90% | 42% | 4.9492 | Loss 0-5%
547 | 1211 | GTR | E&F DILSHAD GARDEN | DGN103 | TG-DGN103A-2 | DT-2 | A BLK TAHIRPUR(JLM IND AREA) S/STN-1:ID | 3 | 630 | 19501356 | 672 | 2019-06-21 13:00 | 230 | 986 | 221 | 953 | 221 | 945 | 38 | 529 | 168.5 | 19 | 3.5 | 191 | 54% | 59% | 107% | 64% | 4.9492 | Loss 0-5% | 902(213) | 918(149.5) | 614(127.5) | 633(110) | 615(83) | 645(100)
548 | 1211 | GTR | E&F DILSHAD GARDEN | DGN103 | TG-DGN103A-3 | DT-3 | A BLK TAHIRPUR(JLM IND AREA) S/STN-1:ID | 3 | 630 | 19504773 | 474 | 2019-06-06 10:00 | 156 | 676 | 168 | 723 | 151 | 658 | 58 | 716 | 4 |  |  | 4 | 39% | 45% | 75% | 40% | 4.9492 | Loss 0-5%
549 | 1211 | GTR | E&F DILSHAD GARDEN | DGN104 | TG-DGN104A-1 | DT-1 | A BLK TAHIRPUR(JLM IND AREA) S/STN-3:ID | 4 | 630 | 19505489 | 637 | 2019-06-09 16:30 | 209 | 893 | 216 | 929 | 212 | 909 | 31 | 568.5 | 145.5 | 5.5 | 0.5 | 151.5 | 61% | 62% | 101% | 64% | 3.5456 | Loss 0-5% | 1019(163) | 696(129) | 595(113) | 661(100) | 687(114) | 690(215)
550 | 1211 | GTR | E&F DILSHAD GARDEN | DGN104 | TG-DGN104A-2 | DT-2 | A BLK TAHIRPUR(JLM IND AREA) S/STN-3:ID | 4 | 630 | 19501369 | 577 | 2019-06-29 16:00 | 195 | 723 | 199 | 741 | 184 | 683 | 51 | 609.5 | 109.5 | 1 |  | 110.5 | 29% | 49% | 92% | 44% | 3.5456 | Loss 0-5% | 622(107.5) | 653(128) | 663(160) | 592(100.5) | 657(96.5) | 668(131.5)
551 | 1211 | GTR | E&F DILSHAD GARDEN | DGN104 | TG-DGN104A-3 | DT-3 | A BLK TAHIRPUR(JLM IND AREA) S/STN-3:ID | 4 | 630 | 19501368 | 424 | 2019-06-27 12:00 | 143 | 599 | 148 | 627 | 133 | 561 | 58 | 489.5 |  |  |  | 0 | 31% | 29% | 67% | 28% | 3.5456 | Loss 0-5% | 791(184.5) | 774(209.5) | 746(131.5) |  | 791(195) | 830(225)
552 | 1211 | GTR | E&F DILSHAD GARDEN | DGN104 | TG-DGN104A-4 | DT-4 | A BLK TAHIRPUR(JLM IND AREA) S/STN-3:ID | 4 | 630 | 19506355 | 520 | 2019-06-24 16:30 | 180 | 740 | 171 | 699 | 169 | 688 | 47 | 699.5 | 20.5 |  |  | 20.5 | 23% | 34% | 82% | 22% | 3.5456 | Loss 0-5%
553 | 1211 | GTR | E&F DILSHAD GARDEN | DGN107 | TG-DGN107A-1 | DT-1 | B BLK OPP SWAHNEY IND.:PL | 3 | 990 | 19505328 | 876 | 2019-06-13 17:00 | 292 | 1266 | 268 | 1161 | 316 | 1366 | 178 | 424.5 | 62.5 |  |  | 62.5 | 39% | 47% | 89% | 36% | 3.5087 | Loss 0-5% |  | 779(31)
554 | 1211 | GTR | E&F DILSHAD GARDEN | DGN107 | TG-DGN107A-2 | DT-2 | B BLK OPP SWAHNEY IND.:PL | 3 | 630 | 19505690 | 449 | 2019-06-30 15:00 | 206 | 860 | 127 | 522 | 117 | 479 | 361 | 716.5 | 2 |  |  | 2 | 67% | 64% | 71% | 68% | 3.5087 | Loss 0-5% |  | 691(288.5) | 657(481) | 768(553.5) | 669(531.5) | 649(451)
555 | 1211 | GTR | E&F DILSHAD GARDEN | DGN107 | TG-DGN107A-3 | DT-3 | B BLK OPP SWAHNEY IND.:PL | 3 | 630 | 19506841 | 316 | 2019-06-27 12:30 | 107 | 444 | 102 | 422 | 108 | 447 | 24 | 718.5 |  |  |  | 0 | 28% | 39% | 50% | 36% | 3.5087 | Loss 0-5%
556 | 1211 | GTR | E&F DILSHAD GARDEN | DGN109 | TG-DGN109A-1 | DT-1 | B-34 JLM INDUSTRIAL AREA | 1 | 990 | 19501836 | 1088 | 2019-06-24 11:30 | 355 | 1525 | 367 | 1581 | 366 | 1568 | 51 | 481 | 162 | 64.5 | 12.5 | 239 | 35% | 44% | 110% | 38% | 4.5922 | Loss 0-5% | 1018(132.5) | 1016(120) | 1106(154.5) | 1122(196.5) | 1219(164) | 1166(209)
557 | 1211 | GTR | E&F DILSHAD GARDEN | DGN112 | TG-DGN112A-1 | DT-1 | DAMODAR PARK,DILSHAD GARDEN:PL | 4 | 990 | 19506505 | 1313 | 2019-06-21 16:00 | 440 | 1846 | 430 | 1805 | 443 | 1861 | 51 | 436 | 63 | 84 | 137 | 284 | 72% | 72% | 133% | 72% | 4.3892 | Loss 0-5% | 1302(267) |  | 1324(96) | 1466(279.5)
558 | 1211 | GTR | E&F DILSHAD GARDEN | DGN112 | TG-DGN112A-2 | DT-2 | DAMODAR PARK,DILSHAD GARDEN:PL | 4 | 990 | 19502279 | 1045 | 2019-06-08 11:00 | 348 | 1518 | 348 | 1523 | 349 | 1521 | 4 | 482 | 193 | 41 | 3.5 | 237.5 | 61% | 65% | 106% | 61% | 4.3892 | Loss 0-5% | 1052(203) | 1141(193) | 1214(165.5) | 1283(287.5) | 1298(285) | 1216(357.5)
559 | 1211 | GTR | E&F DILSHAD GARDEN | DGN112 | TG-DGN112A-3 | DT-3 | DAMODAR PARK,DILSHAD GARDEN:PL | 4 | 990 | 19505439 | 1327 | 2019-06-23 11:30 | 480 | 1954 | 431 | 1738 | 416 | 1696 | 240 | 383.5 | 76 | 73 | 187.5 | 336.5 | 85% | 88% | 134% | 81% | 4.3892 | Loss 0-5% | 1084(153) | 1193(188.5) | 1117(225.5) | 1213(234.5) | 1268(229) | 1374(269.5)
560 | 1211 | GTR | E&F DILSHAD GARDEN | DGN112 | TG-DGN112A-4 | DT-4 | DAMODAR PARK,DILSHAD GARDEN:PL | 4 | 990 | 19502634 | 852 | 2019-06-22 11:30 | 283 | 1186 | 284 | 1187 | 284 | 1191 | 5 | 695 | 25 |  |  | 25 | 52% | 51% | 86% | 49% | 4.3892 | Loss 0-5% | 940(49) |  | 1033(93.5) | 1162(202) | 1184(167) | 1275(170)
561 | 1211 | GTR | E&F DILSHAD GARDEN | DGN114 | TG-DGN114A-1 | DT-1 | JHULFE BENGAL S/S NO. 2:PL | 3 | 630 | 19506419 | 789 | 2019-06-28 15:30 | 250 | 1037 | 279 | 1166 | 261 | 1092 | 112 | 326.5 | 226.5 | 89.5 | 68.5 | 384.5 | 88% | 93% | 125% | 89% | 4.4184 | Loss 0-5% |  | 782(269) | 1030(339) | 832(352)
562 | 1211 | GTR | E&F DILSHAD GARDEN | DGN114 | TG-DGN114A-2 | DT-2 | JHULFE BENGAL S/S NO. 2:PL | 3 | 630 | 19506330 | 512 | 2019-06-21 12:00 | 179 | 780 | 189 | 839 | 145 | 635 | 181 | 706 | 14 |  |  | 14 | 30% | 61% | 81% | 33% | 4.4184 | Loss 0-5% | [5 empty] | 563(34.5)
563 | 1211 | GTR | E&F DILSHAD GARDEN | DGN114 | TG-DGN114A-3 | DT-3 | JHULFE BENGAL S/S NO. 2:PL | 3 | 990 | 19500063 | 1146 | 2019-06-22 15:30 | 386 | 1651 | 384 | 1635 | 376 | 1594 | 52 | 446.5 | 160 | 84.5 | 26.5 | 271 | 77% | 78% | 116% | 75% | 4.4184 | Loss 0-5% | 955(109) | 880(74.5) | 840(86) | 939(101) | 875(41.5)
564 | 1211 | GTR | E&F DILSHAD GARDEN | DGN116 | TG-DGN116A-1 | DT-1 | E-BLK NEW SEEMA PURI:PL | 2 | 630 | 19506588 | 645 | 2019-06-25 23:00 | 230 | 1003 | 219 | 949 | 196 | 849 | 135 | 607.5 | 108.5 | 0.5 | 0.5 | 109.5 | 81% | 76% | 91% | 102% | 4.3756 | Loss 0-5% |  | 561(41.5) | 582(115.5)
565 | 1211 | GTR | E&F DILSHAD GARDEN | DGN116 | TG-DGN116A-2 | DT-2 | E-BLK NEW SEEMA PURI:PL | 2 | 990 | 19505340 | 780 | 2019-06-08 03:00 | 189 | 782 | 366 | 1548 | 225 | 935 | 702 | 713.5 | 3.5 |  |  | 3.5 | 79% | 71% | 75% | 68% | 4.3756 | Loss 0-5%
566 | 1211 | GTR | E&F DILSHAD GARDEN | DGN124 | TG-DGN124A-1 | DT-1 | G.T ROAD SEEMA PURI BORDER:PM | 1 | 630 | 19506420 | 637 | 2019-06-15 15:30 | 228 | 953 | 205 | 848 | 203 | 844 | 108 | 589 | 122 | 5.5 | 0.5 | 128 | 60% | 64% | 101% | 52% | 2.7242 | Loss 0-5%
567 | 1211 | GTR | E&F DILSHAD GARDEN | DGN125 | TG-DGN125A-1 | DT-1 | NEW SEEMAPURI DDA FLAT:ID | 2 | 990 | 19504891 | 779 | 2019-06-30 | 240 | 1016 | 313 | 1326 | 226 | 945 | 351 | 465.5 | 26 |  |  | 26 | 79% | 54% | 56% | 78% | 7.9928 | Loss 5-10%
568 | 1211 | GTR | E&F DILSHAD GARDEN | DGN125 | TG-DGN125A-2 | DT-2 | NEW SEEMAPURI DDA FLAT:ID | 2 | 630 | 19506317 | 627 | 2019-06-25 21:30 | 212 | 924 | 195 | 842 | 220 | 951 | 98 | 717 | 0.5 | 0.5 |  | 1 | 70% | 53% | 59% | 99% | 7.9928 | Loss 5-10%
569 | 1211 | GTR | E&F DILSHAD GARDEN | DGN128 | TG-DGN128A-1 | DT-1 | JULFE BENGAL S/S NO.I | 3 | 990 | 19505545 | 847 | 2019-06-28 15:00 | 274 | 1156 | 293 | 1232 | 280 | 1175 | 69 | 650.5 | 58 |  |  | 58 | 65% | 68% | 86% | 70% | 3.8325 | Loss 0-5% | 1043(150) | 1135(220) | 1127(215.5) | 1121(217) | 1111(246.5)
570 | 1211 | GTR | E&F DILSHAD GARDEN | DGN128 | TG-DGN128A-2 | DT-2 | JULFE BENGAL S/S NO.I | 3 | 990 | 19505758 | 1181 | 2019-06-07 12:30 | 395 | 1698 | 400 | 1708 | 386 | 1661 | 43 | 479 | 122.5 | 82.5 | 24 | 229 | 43% | 53% | 119% | 44% | 3.8325 | Loss 0-5% |  | 819(53.5) | 840(40) | 925(123) |  | 938(118.5)
571 | 1211 | GTR | E&F DILSHAD GARDEN | DGN128 | TG-DGN128A-3 | DT-3 | JULFE BENGAL S/S NO.I | 3 | 630 | 19506329 | 906 | 2019-06-07 17:00 | 313 | 1340 | 295 | 1255 | 298 | 1291 | 73 | 454.5 | 159 | 49 | 45 | 253 | 111% | 109% | 144% | 95% | 3.8325 | Loss 0-5% | 562(61) | 623(105.5) | 610(130) | 786(152.5) | 696(168.5) | 787(187)
572 | 1211 | GTR | E&F DILSHAD GARDEN | DGN130 | TG-DGN130A-1 | DT-1 | LOCAL SHOPPING CENTER DILSHAD GARDEN:ID | 2 | 990 | 19504967 | 857 | 2019-06-03 13:30 | 278 | 1194 | 280 | 1190 | 299 | 1278 | 86 | 610 | 107.5 |  |  | 107.5 | 36% | 51% | 87% | 40% | 3.9027 | Loss 0-5% |  | 868(48) | 926(62.5) | 890(90) | 893(75) | 803(34.5)
573 | 1211 | GTR | E&F DILSHAD GARDEN | DGN130 | TG-DGN130A-2 | DT-2 | LOCAL SHOPPING CENTER DILSHAD GARDEN:ID | 2 | 630 | 19504294 | 493 | 2019-06-28 16:30 | 159 | 686 | 169 | 732 | 164 | 708 | 40 | 709.5 | 8 |  |  | 8 | 13% | 20% | 78% | 23% | 3.9027 | Loss 0-5% | 530(60.5) | 583(79.5) | 616(69) | 627(145.5) | 635(168) | 643(174)
574 | 1211 | GTR | E&F DILSHAD GARDEN | DGN132 | TG-DGN132A-1 | DT-1 | E&F PKT. DILSHAD GARDEN:ID | 2 | 990 | 19501450 | 860 | 2019-06-10 22:30 | 338 | 1486 | 288 | 1276 | 233 | 1024 | 401 | 618 | 77.5 |  |  | 77.5 | 84% | 45% | 70% | 87% | 3.8043 | Loss 0-5%
575 | 1211 | GTR | E&F DILSHAD GARDEN | DGN132 | TG-DGN132A-2 | DT-2 | E&F PKT. DILSHAD GARDEN:ID | 2 | 990 | 19504483 | 426 | 2019-06-30 | 112 | 452 | 209 | 855 | 105 | 426 | 417 | 380.5 |  |  |  | 0 | 43% | 24% | 30% | 42% | 3.8043 | Loss 0-5%
576 | 1211 | GTR | E&F DILSHAD GARDEN | DGN133 | TG-DGN133A-1 | DT-1 | B-BLOCK OLD SEEMAPURI :PL | 4 | 990 | 19504194 | 333 | 2019-06-29 19:30 | 109 | 438 | 121 | 483 | 103 | 410 | 64 | 672 |  |  |  | 0 | 32% | 25% | 34% | 33% | 11.9552 | Loss 10-20%
577 | 1211 | GTR | E&F DILSHAD GARDEN | DGN133 | TG-DGN133A-2 | DT-2 | B-BLOCK OLD SEEMAPURI :PL | 4 | 990 | 19501372 | 524 | 2019-06-29 23:30 | 188 | 804 | 123 | 520 | 213 | 915 | 353 | 671.5 |  |  |  | 0 | 52% | 45% | 48% | 53% | 11.9552 | Loss 10-20%
578 | 1211 | GTR | E&F DILSHAD GARDEN | DGN133 | TG-DGN133A-3 | DT-3 | B-BLOCK OLD SEEMAPURI :PL | 4 | 630 | 19503779 | 386 | 2019-06-30 00:30 | 212 | 903 | 119 | 503 | 54 | 226 | 590 | 671.5 |  |  |  | 0 | 61% | 50% | 54% | 61% | 11.9552 | Loss 10-20%
579 | 1211 | GTR | E&F DILSHAD GARDEN | DGN133 | TG-DGN133A-4 | DT-4 | B-BLOCK OLD SEEMAPURI :PL | 4 | 630 | 19504208 | 656 | 2019-06-29 22:30 | 240 | 1039 | 172 | 733 | 245 | 1053 | 313 | 324 | 289.5 | 54 | 4.5 | 348 | 102% | 84% | 89% | 104% | 11.9552 | Loss 10-20% | 487(30) | 614(292) | 665(444) | 662(407.5) | 648(392) | 606(236.5)
580 | 1211 | GTR | E&F DILSHAD GARDEN | DGN134 | TG-DGN134A-1 | DT-1 | TAHIRPUR SARAI:PM | 1 | 400 | 19504602 | 445 | 2019-06-14 02:00 | 193 | 794 | 122 | 494 | 131 | 532 | 283 | 430.5 | 163 | 95 | 25 | 283 | 111% | 77% | 81% | 109% | 9.8294 | Loss 5-10% |  | 371(152.5) | 405(261) | 422(218.5) | 380(209) | 329(59)
581 | 1211 | GTR | E&F DILSHAD GARDEN | DGN135 | TG-DGN135A-1 | DT-1 | KHERA VILLAGE:PM | 1 | 630 | 19506547 | 585 | 2019-06-10 21:30 | 224 | 935 | 164 | 687 | 197 | 841 | 217 | 498 | 220 | 2 |  | 222 | 92% | 92% | 84% | 93% | 5.6496 | Loss 5-10% |  | 534(65.5) |  |  | 582(177.5) | 489(42.5)
582 | 1211 | GTR | E&F DILSHAD GARDEN | DGN141 | TG-DGN141A-1 | DT-1 | B-BLK DILSHAD CLY:PM | 3 | 990 | 19506373 | 610 | 2019-06-29 23:30 | 182 | 783 | 252 | 1091 | 176 | 755 | 323 | 719.5 |  |  |  | 0 | 62% | 37% | 41% | 62% | 5.3249 | Loss 5-10%
583 | 1211 | GTR | E&F DILSHAD GARDEN | DGN141 | TG-DGN141A-2 | DT-2 | B-BLK DILSHAD CLY:PM | 3 | 990 | 19505287 | 1031 | 2019-06-30 00:30 | 321 | 1342 | 352 | 1477 | 359 | 1500 | 148 | 573 | 108 | 34 | 3.5 | 145.5 | 104% | 61% | 69% | 103% | 5.3249 | Loss 5-10% |  | 911(40.5) | 1114(138) |  | 831(51.5)
584 | 1211 | GTR | E&F DILSHAD GARDEN | DGN141 | TG-DGN141A-3 | DT-3 | B-BLK DILSHAD CLY:PM | 3 | 630 | 19505585 | 146 | 2019-06-10 06:00 | 51 | 199 | 53 | 208 | 42 | 163 | 41 | 720 |  |  |  | 0 | 16% | 23% | 21% | 18% | 5.3249 | Loss 5-10%
585 | 1211 | GTR | E&F DILSHAD GARDEN | DGN147 | TG-DGN147A-1 | DT-1 | SATISH STEEL ROLLING MILL:ID | 2 | 630 | 19506363 | 510 | 2019-06-13 15:30 | 172 | 718 | 171 | 708 | 167 | 696 | 19 | 643.5 | 73.5 |  |  | 73.5 | 64% | 62% | 81% | 63% | 7.0939 | Loss 5-10% |  |  |  |  | 584(48) | 575(130.5)
586 | 1211 | GTR | E&F DILSHAD GARDEN | DGN147 | TG-DGN147A-2 | DT-2 | SATISH STEEL ROLLING MILL:ID | 2 | 630 | 19504244 | 445 | 2019-06-08 16:30 | 149 | 652 | 148 | 647 | 148 | 645 | 6 | 719.5 | 0.5 |  |  | 0.5 | 21% | 31% | 71% | 23% | 7.0939 | Loss 5-10%
587 | 1211 | GTR | E&F DILSHAD GARDEN | DGN162 | TG-DGN162A-1 | DT-1 | F-BLOCK DILSHAD COLONY:ID | 4 | 990 | 19504839 | 908 | 2019-06-29 23:30 | 364 | 1510 | 299 | 1236 | 245 | 1006 | 437 | 591 | 77 | 1.5 |  | 78.5 | 89% | 53% | 72% | 92% | 6.1394 | Loss 5-10% |  |  | 861(61) | 880(40.5)
588 | 1211 | GTR | E&F DILSHAD GARDEN | DGN162 | TG-DGN162A-2 | DT-2 | F-BLOCK DILSHAD COLONY:ID | 4 | 990 | 19505806 | 799 | 2019-06-30 | 287 | 1170 | 232 | 947 | 279 | 1145 | 212 | 685.5 | 30.5 |  |  | 30.5 | 81% | 46% | 56% | 80% | 6.1394 | Loss 5-10% |  |  | 818(24.5)
589 | 1211 | GTR | E&F DILSHAD GARDEN | DGN162 | TG-DGN162A-3 | DT-3 | F-BLOCK DILSHAD COLONY:ID | 4 | 990 | 19501791 | 1139 | 2019-06-30 01:30 | 340 | 1363 | 432 | 1756 | 367 | 1467 | 353 | 543 | 105 | 17.5 | 3 | 125.5 | 115% | 67% | 73% | 101% | 6.1394 | Loss 5-10% |  | 901(56.5) | 971(120.5) | 978(85.5) | 782(30)
590 | 1211 | GTR | E&F DILSHAD GARDEN | DGN162 | TG-DGN162A-4 | DT-4 | F-BLOCK DILSHAD COLONY:ID | 4 | 630 | 19504902 | 442 | 2019-06-30 | 175 | 696 | 131 | 519 | 136 | 540 | 167 | 666.5 | 0.5 |  |  | 0.5 | 70% | 40% | 68% | 69% | 6.1394 | Loss 5-10%
591 | 1211 | GTR | E&F DILSHAD GARDEN | DGN190 | TG-DGN190A-1 | DT-1 | NEW POLICE BOTH DILSHAD CLY | 1 | 990 | 19506003 | 996 | 2019-06-30 23:30 | 340 | 1464 | 325 | 1408 | 331 | 1436 | 49 | 565 | 136 | 18.5 | 0.5 | 155 | 94% | 61% | 74% | 101% | 7.985 | Loss 5-10% |  | 909(64.5) | 1101(183) | 1015(116.5) | 834(56)
592 | 1211 | GTR | E&F DILSHAD GARDEN | DGN197 | TG-DGN197A-1 | DT-1 | C- BLK DILSHAD COLONY SSTN NO.-2:PL | 2 | 630 | 19506596 | 582 | 2019-06-29 23:30 | 192 | 768 | 185 | 740 | 205 | 816 | 66 | 626 | 83 | 1.5 |  | 84.5 | 91% | 57% | 77% | 92% | 6.5746 | Loss 5-10% |  | 546(27) | 561(81.5) | 582(50)
593 | 1211 | GTR | E&F DILSHAD GARDEN | DGN197 | TG-DGN197A-2 | DT-2 | C- BLK DILSHAD COLONY SSTN NO.-2:PL | 2 | 630 | 19505164 | 310 | 2019-06-14 08:00 | 104 | 430 | 119 | 496 | 87 | 362 | 116 | 716.5 |  |  |  | 0 | 46% | 49% | 46% | 45% | 6.5746 | Loss 5-10%
594 | 1211 | GTR | E&F DILSHAD GARDEN | DGN207 | TG-DGN207A-1 | DT-1 | SHANKAR KE DP,A-BLK.JLM IA. | 1 | 990 | 19506501 | 960 | 2019-06-29 11:00 | 303 | 1322 | 325 | 1422 | 332 | 1449 | 116 | 664.5 | 54.5 | 1 |  | 55.5 | 16% | 39% | 97% | 21% | 5.468 | Loss 5-10%
595 | 1211 | GTR | E&F DILSHAD GARDEN | DGN225 | TG-DGN225A-1 | DT-1 | Oberai compound | 2 | 990 | 19504360 | 1039 | 2019-06-01 11:30 | 352 | 1478 | 352 | 1490 | 335 | 1416 | 70 | 639.5 | 66 | 11.5 | 0.5 | 78 | 33% | 39% | 105% | 45% | 5.6285 | Loss 5-10% | 922(97) | 966(125.5) | 1023(164.5) | 1013(161.5) | 1112(168) | 1247(251)
596 | 1211 | GTR | E&F DILSHAD GARDEN | DGN225 | TG-DGN225A-2 | DT-2 | Oberai compound | 2 | 990 | 19506760 | 1093 | 2019-06-20 11:00 | 367 | 1614 | 365 | 1611 | 361 | 1595 | 17 | 491.5 | 117 | 23.5 | 1.5 | 142 | 43% | 43% | 110% | 45% | 5.6285 | Loss 5-10% | 637(157) | 733(226) | 784(242.5) | 840(283.5) | 750(213) | 831(249)
597 | 1211 | GTR | E&F DILSHAD GARDEN | DGN228 | TG-DGN228A-1 | DT-1 | A-BLK DILSHAD COLONY | 1 | 990 | 19504330 | 1053 | 2019-06-30 00:30 | 292 | 1155 | 342 | 1369 | 420 | 1692 | 469 | 556 | 115.5 | 42.5 | 6 | 164 | 106% | 71% | 72% | 104% | 6.9048 | Loss 5-10% | 626(36.5) | 855(245.5) | 1057(424.5) | 997(360) |  | 715(106.5)
598 | 1211 | GTR | E&F DILSHAD GARDEN | DGN232 | TG-DGN232A-1 | DT-1 | DSIDC SUBSTATION NO-2 | 4 | 630 | 19506918 | 700 | 2019-06-07 16:30 | 230 | 1029 | 234 | 1040 | 235 | 1049 | 17 | 601 | 24.5 | 5.5 | 4 | 34 | 59% | 58% | 111% | 57% | 4.0223 | Loss 0-5% | 535(40) | 543(52) | 566(85.5) | 559(77) | 603(104.5)
599 | 1211 | GTR | E&F DILSHAD GARDEN | DGN232 | TG-DGN232A-2 | DT-2 | DSIDC SUBSTATION NO-2 | 4 | 990 | 19501354 | 978 | 2019-06-24 12:00 | 331 | 1468 | 317 | 1408 | 330 | 1474 | 63 | 551.5 | 152 | 15 |  | 167 | 22% | 30% | 99% | 33% | 4.0223 | Loss 0-5%
600 | 1211 | GTR | E&F DILSHAD GARDEN | DGN232 | TG-DGN232A-3 | DT-3 | DSIDC SUBSTATION NO-2 | 4 | 990 | 19505129 | 1313 | 2019-06-22 18:00 | 436 | 1823 | 435 | 1808 | 442 | 1838 | 26 | 344.5 | 166.5 | 77.5 | 129.5 | 373.5 | 89% | 92% | 133% | 88% | 4.0223 | Loss 0-5% | 1055(103.5) |  | 919(55.5) | 1144(236) | 1311(410.5) | 1402(353.5)
601 | 1211 | GTR | E&F DILSHAD GARDEN | DGN232 | TG-DGN232A-4 | DT-4 | DSIDC SUBSTATION NO-2 | 4 | 990 | 19504958 | 958 | 2019-06-15 10:30 | 318 | 1292 | 331 | 1345 | 310 | 1257 | 77 | 592 | 121 | 5 |  | 126 | 42% | 49% | 97% | 43% | 4.0223 | Loss 0-5% | 1281(190.5) | 1189(180.5) | 1188(153) | 1165(161) | 1377(128.5) | 1399(188)
602 | 1211 | GTR | E&F DILSHAD GARDEN | DGN233 | TG-DGN233A-1 | DT-1 | G Block Dilshad Colony ( Park Wala) | 1 | 990 | 19505277 | 1188.5711 | 2019-06-11 23:30 | 425.769 | 1889.0323 | 391.2125 | 1735.6368 | 371.5896 | 1640.4997 | 217.1977 | 499 | 143 | 47.5 | 29 | 219.5 | 114% | 81% | 86% | 120% | 4.4493 | Loss 0-5% |  |  | 1216(190) | 1136(158.5) | 911(98.5)
603 | 1211 | GTR | E&F DILSHAD GARDEN | DGN237 | TG-DGN237A-1 | DT-1 | B-42 JHILMIL IND AREA NEARRAILWAY LINE | 2 | 630 | 19505962 | 577 | 2019-06-21 10:30 | 188 | 811 | 190 | 823 | 200 | 868 | 52 | 687 | 32.5 | 0.5 |  | 33 | 34% | 36% | 92% | 39% | 3.0408 | Loss 0-5% | 698(41.5) | 768(243) | 766(103.5) | 625(87.5) | 587(90.5) | 604(113.5)
604 | 1211 | GTR | E&F DILSHAD GARDEN | DGN237 | TG-DGN237A-2 | DT-2 | B-42 JHILMIL IND AREA NEARRAILWAY LINE | 2 | 990 | 19505961 | 895 | 2019-06-19 11:00 | 298 | 1200 | 297 | 1199 | 300 | 1207 | 8 | 650 | 69.5 | 0.5 |  | 70 | 31% | 42% | 90% | 37% | 3.0408 | Loss 0-5% |  |  |  | 842(60) | 979(120.5) | 1062(213.5)
605 | 1211 | GTR | E&F DILSHAD GARDEN | DGN249 | TG-DGN249A-1 | DT-1 | Police Booth A BLK JLM IA | 1 | 990 | 19506423 | 956 | 2019-06-17 14:00 | 310 | 1320 | 328 | 1393 | 318 | 1354 | 63 | 558.5 | 157.5 | 2.5 |  | 160 | 52% | 58% | 97% | 50% | 2.329 | Loss 0-5%
606 | 1211 | GTR | E&F DILSHAD GARDEN | DGN252 | TG-DGN252A-1 | DT-1 | RAILWAY LINE IN FRONT OF B-43 JHILMIL | 1 | 990 | 19506619 | 1135 | 2019-06-08 18:00 | 375 | 1531 | 371 | 1519 | 390 | 1604 | 79 | 467 | 205.5 | 43.5 | 4 | 253 | 66% | 86% | 115% | 67% | 9.2448 | Loss 5-10%
607 | 1211 | GTR | E&F DILSHAD GARDEN | DGN254 | TG-DGN254A-1 | DT-1 | DAMODAR PARK S/S NO. 2 | 2 | 630 | 19506877 | 492 | 2019-06-01 14:00 | 170 | 730 | 155 | 664 | 167 | 713 | 59 | 713 | 7 |  |  | 7 | 47% | 49% | 78% | 48% | 4.2761 | Loss 0-5%
608 | 1211 | GTR | E&F DILSHAD GARDEN | DGN254 | TG-DGN254A-2 | DT-2 | DAMODAR PARK S/S NO. 2 | 2 | 630 | 19506876 | 837 | 2019-06-10 12:30 | 279 | 1159 | 283 | 1173 | 275 | 1140 | 29 | 422 | 74.5 | 57 | 166.5 | 298 | 83% | 90% | 133% | 82% | 4.2761 | Loss 0-5%
609 | 1211 | GTR | GT ROAD SHAHDRA | DGN032 | TG-DGN032A-1 | DT-1 | J-Block MS Park Package Near Dispensary | 1 | 990 | 19501019 | 989 | 2019-06-11 | 349 | 1520 | 316 | 1375 | 324 | 1393 | 136 | 548 | 141 | 29.5 |  | 170.5 | 100% | 76% | 74% | 99% | 5.4789 | Loss 5-10% |  | 963(46.5) | 897(120.5) | 897(56)
610 | 1211 | GTR | GT ROAD SHAHDRA | DGN038 | TG-DGN038A-1 | DT-1 | MOTI RAM ROAD G.T.ROAD FLYOVER S/STN | 2 | 990 | 19501709 | 314 | 2019-06-10 15:30 | 106 | 420 | 116 | 478 | 93 | 384 | 82 | 695 |  |  |  | 0 | 21% | 16% | 32% | 22% | 6.0809 | Loss 5-10%
611 | 1211 | GTR | GT ROAD SHAHDRA | DGN038 | TG-DGN038A-2 | DT-2 | MOTI RAM ROAD G.T.ROAD FLYOVER S/STN | 2 | 990 | 19501708 | 844 | 2019-06-29 23:30 | 250 | 1067 | 340 | 1478 | 254 | 1092 | 399 | 580 | 113 |  |  | 113 | 85% | 69% | 74% | 85% | 6.0809 | Loss 5-10% |  |  | 878(121.5) | 835(71.5)
612 | 1211 | GTR | GT ROAD SHAHDRA | DGN039 | TG-DGN039A-1 | DT-1 | MANSAROVER PARK MOTHER DAIRY | 3 | 990 | 19506343 | 907 | 2019-06-10 23:00 | 343 | 1513 | 315 | 1383 | 250 | 1089 | 376 | 593.5 | 122.5 | 2.5 |  | 125 | 91% | 71% | 69% | 92% | 4.0829 | Loss 0-5% |  | 955(107) | 930(83)
613 | 1211 | GTR | GT ROAD SHAHDRA | DGN039 | TG-DGN039A-2 | DT-2 | MANSAROVER PARK MOTHER DAIRY | 3 | 990 | 19506342 | 865.8276 | 2019-06-29 23:30 | 299.3608 | 1261.5289 | 319.1749 | 1346.3888 | 247.2919 | 1036.7329 | 277.1473 | 618 | 100 |  |  | 100 | 87% | 62% | 74% | 87% | 4.0829 | Loss 0-5% |  |  | 900(68.5)
614 | 1211 | GTR | GT ROAD SHAHDRA | DGN039 | TG-DGN039A-3 | DT-3 | MANSAROVER PARK MOTHER DAIRY | 3 | 630 | 19505670 | 467 | 2019-06-12 01:00 | 69 | 296 | 150 | 659 | 249 | 1106 | 702 | 715 | 3 |  |  | 3 | 74% | 42% | 47% | 71% | 4.0829 | Loss 0-5% |  | 556(37.5) | 590(108) | 563(40)
615 | 1211 | GTR | GT ROAD SHAHDRA | DGN042 | TG-DGN042A-1 | DT-1 | MOTI RAM PEER WALA S/STN | 2 | 630 | 19506929 | 183 | 2019-06-26 14:30 | 44 | 186 | 63 | 268 | 76 | 325 | 121 | 228.5 |  |  |  | 0 | 25% | 18% | 29% | 26% | 5.0023 | Loss 5-10%
616 | 1211 | GTR | GT ROAD SHAHDRA | DGN042 | TG-DGN042A-2 | DT-2 | MOTI RAM PEER WALA S/STN | 2 | 630 | 19505471 | 592 | 2019-06-11 | 93 | 411 | 286 | 1312 | 212 | 956 | 786 | 602.5 | 112.5 | 2 |  | 114.5 | 94% | 58% | 81% | 91% | 5.0023 | Loss 5-10%
617 | 1211 | GTR | GT ROAD SHAHDRA | DGN044 | TG-DGN044A-1 | DT-1 | JAISWAL MARG:PM | 2 | 990 | 19501798 | 866 | 2019-06-03 01:00 | 290 | 1185 | 278 | 1156 | 298 | 1232 | 67 | 650.5 | 68 |  |  | 68 | 87% | 52% | 58% | 86% | 5.8442 | Loss 5-10%
618 | 1211 | GTR | GT ROAD SHAHDRA | DGN044 | TG-DGN044A-2 | DT-2 | JAISWAL MARG:PM | 2 | 630 | 19506422 | 504 | 2019-06-03 00:30 | 189 | 784 | 176 | 730 | 139 | 567 | 196 | 672 | 46 |  |  | 46 | 80% | 54% | 75% | 78% | 5.8442 | Loss 5-10%
619 | 1211 | GTR | GT ROAD SHAHDRA | DGN045 | TG-DGN045A-1 | DT-1 | MANDOLI ROAD:PL | 2 | 990 | 19501758 | 921 | 2019-06-30 23:30 | 346 | 1489 | 257 | 1094 | 319 | 1349 | 347 | 212.5 | 38.5 | 2 |  | 40.5 | 90% | 59% | 75% | 93% | 7.5003 | Loss 5-10% |  | 865(36.5) | 998(102.5) | 838(28.5)
620 | 1211 | GTR | GT ROAD SHAHDRA | DGN045 | TG-DGN045A-2 | DT-2 | MANDOLI ROAD:PL | 2 | 990 | 19501756 | 656 | 2019-06-10 | 143 | 561 | 220 | 872 | 293 | 1179 | 535 | 694.5 |  |  |  | 0 | 66% | 45% | 57% | 66% | 7.5003 | Loss 5-10%
621 | 1211 | GTR | GT ROAD SHAHDRA | DGN046 | TG-DGN046A-1 | DT-1 | RAM NAGAR SCHOOL:PL | 2 | 990 | 19501705 | 1481 | 2019-06-11 23:30 | 549 | 2221 | 434 | 1779 | 498 | 2044 | 385 | 224.5 | 246.5 | 61.5 | 186.5 | 494.5 | 148% | 93% | 105% | 150% | 8.7649 | Loss 5-10% |  | 1005(79.5) | 1206(166) | 997(89.5) | 921(74.5)
622 | 1211 | GTR | GT ROAD SHAHDRA | DGN046 | TG-DGN046A-2 | DT-2 | RAM NAGAR SCHOOL:PL | 2 | 630 | 19504949 | 377 | 2019-06-11 23:30 | 116 | 471 | 110 | 438 | 151 | 612 | 160 | 719 |  |  |  | 0 | 57% | 40% | 42% | 60% | 8.7649 | Loss 5-10% |  |  | 647(41) | 676(146) | 691(166.5) | 552(30.5)
623 | 1211 | GTR | GT ROAD SHAHDRA | DGN047 | TG-DGN047A-1 | DT-1 | BHAGWANPUR KHERA NO-1:PL | 1 | 990 | 19500681 | 1004 | 2019-06-09 23:30 | 318 | 1357 | 322 | 1393 | 364 | 1564 | 191 | 547 | 152.5 | 19.5 | 0.5 | 172.5 | 95% | 68% | 75% | 101% | 7.8723 | Loss 5-10% |  | 799(34) | 941(137) | 926(84) | 817(42)
624 | 1211 | GTR | GT ROAD SHAHDRA | DGN049 | TG-DGN049A-1 | DT-1 | BHAGWANPUR KHERA NO-3:PL | 1 | 990 | 19506736 | 1058 | 2019-06-29 23:30 | 342 | 1487 | 388 | 1694 | 328 | 1426 | 243 | 178 | 58 | 14 | 3 | 75 | 104% | 66% | 93% | 107% | 6.1923 | Loss 5-10% |  | 912(75) |  |  | 858(70)
625 | 1211 | GTR | GT ROAD SHAHDRA | DGN050 | TG-DGN050A-1 | DT-1 | NEW MODERN SHAHDRA NO I GALI NO 13:PL | 2 | 990 | 19505901 | 966 | 2019-06-08 01:30 | 307 | 1384 | 299 | 1345 | 360 | 1626 | 263 | 626 | 89 | 4.5 |  | 93.5 | 98% | 63% | 67% | 94% | 5.4409 | Loss 5-10% |  | 845(33.5) | 1025(111) | 849(57.5) | 807(29.5)
626 | 1211 | GTR | GT ROAD SHAHDRA | DGN050 | TG-DGN050A-2 | DT-2 | NEW MODERN SHAHDRA NO I GALI NO 13:PL | 2 | 630 | 19506893 | 354 | 2019-06-30 23:00 | 87 | 378 | 98 | 427 | 169 | 748 | 348 | 719.5 |  |  |  | 0 | 55% | 44% | 42% | 56% | 5.4409 | Loss 5-10%
627 | 1211 | GTR | GT ROAD SHAHDRA | DGN051 | TG-DGN051A-1 | DT-1 | NEW MODERN SHAHDARA NO 2 GALI NO7,8 | 2 | 990 | 19505900 | 947.9923 | 2019-06-08 00:30 | 179.0657 | 780.1066 | 238.6608 | 1018.786 | 530.2659 | 2188.8297 | 1305.8466 | 649.5 | 60.5 | 4 |  | 64.5 | 96% | 55% | 68% | 93% | 4.8269 | Loss 0-5% |  | 814(31) | 997(87) | 883(43)
628 | 1211 | GTR | GT ROAD SHAHDRA | DGN051 | TG-DGN051A-2 | DT-2 | NEW MODERN SHAHDARA NO 2 GALI NO7,8 | 2 | 630 | 19505357 | 709 | 2019-06-09 23:30 | 261 | 1085 | 171 | 697 | 277 | 1141 | 419 | 693.5 | 19.5 | 2 | 2 | 23.5 | 109% | 65% | 81% | 113% | 4.8269 | Loss 0-5%
629 | 1211 | GTR | GT ROAD SHAHDRA | DGN052 | TG-DGN052A-1 | DT-1 | SUBHASH MARG NEW MODERN SHAHDARA:PL | 2 | 990 | 19501759 | 716 | 2019-06-15 01:00 | 262 | 1140 | 191 | 811 | 263 | 1135 | 326 | 719.5 | 0.5 |  |  | 0.5 | 72% | 49% | 47% | 68% | 4.1816 | Loss 0-5%
630 | 1211 | GTR | GT ROAD SHAHDRA | DGN052 | TG-DGN052A-2 | DT-2 | SUBHASH MARG NEW MODERN SHAHDARA:PL | 2 | 990 | 19505898 | 949 | 2019-06-11 23:30 | 266 | 1103 | 328 | 1395 | 355 | 1536 | 382 | 607.5 | 107.5 | 5 |  | 112.5 | 95% | 60% | 76% | 96% | 4.1816 | Loss 0-5% |  | 885(28.5) | 957(66) | 883(35.5)
631 | 1211 | GTR | GT ROAD SHAHDRA | DGN074 | TG-DGN074A-1 | DT-1 | RAJ ENGG.COMPOUND | 2 | 990 | 19501787 | 1072 | 2019-06-23 11:00 | 355 | 1456 | 361 | 1490 | 355 | 1455 | 34 | 500 | 194.5 | 23.5 | 1.5 | 219.5 | 68% | 64% | 108% | 69% | 4.7376 | Loss 0-5% |  |  |  |  | 858(53) | 993(154)
632 | 1211 | GTR | GT ROAD SHAHDRA | DGN074 | TG-DGN074A-2 | DT-2 | RAJ ENGG.COMPOUND | 2 | 990 | 19504955 | 733 | 2019-06-10 12:00 | 253 | 1112 | 242 | 1064 | 238 | 1043 | 61 | 716.5 | 3.5 |  |  | 3.5 | 26% | 42% | 74% | 20% | 4.7376 | Loss 0-5% | 825(36.5)
633 | 1211 | GTR | GT ROAD SHAHDRA | DGN075 | TG-DGN075A-1 | DT-1 | PAPER PRODUCT | 2 | 990 | 19505761 | 1026 | 2019-06-23 11:00 | 350 | 1525 | 342 | 1487 | 334 | 1446 | 69 | 566.5 | 138 | 11.5 | 0.5 | 150 | 45% | 61% | 104% | 51% | 3.2598 | Loss 0-5% |  | 923(84.5) | 951(124) | 987(80.5) | 906(98.5) | 1010(169.5)
634 | 1211 | GTR | GT ROAD SHAHDRA | DGN075 | TG-DGN075A-2 | DT-2 | PAPER PRODUCT | 2 | 630 | 19505760 | 493 | 2019-06-21 15:30 | 166 | 711 | 171 | 736 | 156 | 674 | 54 | 697 | 21.5 |  |  | 21.5 | 30% | 36% | 78% | 37% | 3.2598 | Loss 0-5% | 514(36) |  | 543(87) | 520(46) | 596(112) | 606(192)
635 | 1211 | GTR | GT ROAD SHAHDRA | DGN105 | TG-DGN105A-1 | DT-1 | SHAMBU NATH COMP.(F.COL):ID | 5 | 990 | 19505392 | 1187 | 2019-06-02 14:00 | 391 | 1784 | 392 | 1792 | 404 | 1842 | 54 | 425 | 191 | 67 | 36 | 294 | 81% | 82% | 120% | 82% | 4.2685 | Loss 0-5% |  |  |  | 1133(56.5) | 1322(248)
636 | 1211 | GTR | GT ROAD SHAHDRA | DGN105 | TG-DGN105A-2 | DT-2 | SHAMBU NATH COMP.(F.COL):ID | 5 | 990 | 19505488 | 914 | 2019-06-09 16:00 | 299 | 1346 | 304 | 1362 | 311 | 1404 | 52 | 660 | 59.5 | 0.5 |  | 60 | 58% | 64% | 92% | 59% | 4.2685 | Loss 0-5% | 975(161.5) | 1040(198) | 1029(232.5) | 1018(214.5) | 1073(220)
637 | 1211 | GTR | GT ROAD SHAHDRA | DGN105 | TG-DGN105A-3 | DT-3 | SHAMBU NATH COMP.(F.COL):ID | 5 | 990 | 19505434 | 1021 | 2019-06-26 11:00 | 332 | 1421 | 336 | 1422 | 354 | 1509 | 87 | 645 | 65.5 | 4.5 | 2 | 72 | 54% | 65% | 103% | 56% | 4.2685 | Loss 0-5% | 1141(229) | 1027(170) | 1123(230) | 1108(233.5) | 1117(240.5) | 1259(357.5)
638 | 1211 | GTR | GT ROAD SHAHDRA | DGN105 | TG-DGN105A-4 | DT-4 | SHAMBU NATH COMP.(F.COL):ID | 5 | 990 | 19505076 | 856 | 2019-06-24 15:00 | 279 | 1139 | 292 | 1193 | 285 | 1158 | 48 | 600 | 120 |  |  | 120 | 39% | 43% | 86% | 42% | 4.2685 | Loss 0-5% | 845(34.5) | 807(38) | 815(32.5) | 939(121.5) | 915(136.5) | 987(165)
639 | 1211 | GTR | GT ROAD SHAHDRA | DGN105 | TG-DGN105A-5 | DT-5 | SHAMBU NATH COMP.(F.COL):ID | 5 | 1600 | 19506742 | 1203 | 2019-06-22 11:30 | 392 | 1651 | 409 | 1726 | 402 | 1704 | 67 | 706 | 4 |  |  | 4 | 30% | 36% | 75% | 27% | 4.2685 | Loss 0-5%
640 | 1211 | GTR | GT ROAD SHAHDRA | DGN110 | TG-DGN110A-1 | DT-1 | VERMA CASTLE:PL | 6 | 990 | 19503035 | 1150 | 2019-06-01 12:00 | 370 | 1470 | 374 | 1500 | 406 | 1636 | 153 | 581 | 76.5 | 19 | 10 | 105.5 | 44% | 73% | 116% | 41% | 3.7951 | Loss 0-5% | 1022(172.5) | 1129(224) | 1229(245) | 1240(166.5) | 1231(140.5) | 1336(204)
641 | 1211 | GTR | GT ROAD SHAHDRA | DGN110 | TG-DGN110A-2 | DT-2 | VERMA CASTLE:PL | 6 | 990 | 19506744 | 974.8176 | 2019-06-02 11:00 | 328.8769 | 1448.0951 | 333.0491 | 1462.6022 | 312.8916 | 1359.3345 | 96.8326 | 593 | 109.5 | 3.5 |  | 113 | 59% | 58% | 98% | 42% | 3.7951 | Loss 0-5% | 900(37) | 988(105.5) | 1004(97.5) | 1007(104) | 1166(128.5) | 1151(110)
642 | 1211 | GTR | GT ROAD SHAHDRA | DGN110 | TG-DGN110A-3 | DT-3 | VERMA CASTLE:PL | 6 | 630 | 19505004 | 552 | 2019-06-26 16:00 | 185 | 766 | 179 | 741 | 188 | 781 | 35 | 645.5 | 63.5 |  |  | 63.5 | 32% | 42% | 88% | 33% | 3.7951 | Loss 0-5% | 579(79) | 596(82) | 648(155) | 600(136) | 631(149.5) | 653(182.5)
643 | 1211 | GTR | GT ROAD SHAHDRA | DGN110 | TG-DGN110A-4 | DT-4 | VERMA CASTLE:PL | 6 | 630 | 19506339 | 700.3905 | 2019-06-03 10:30 | 232.099 | 966.9584 | 243.274 | 1008.6405 | 225.0174 | 926.6077 | 71.0456 | 690 | 16 | 1.5 | 1 | 18.5 | 54% | 63% | 111% | 42% | 3.7951 | Loss 0-5% |  |  |  |  | 623(28) | 680(160)
644 | 1211 | GTR | GT ROAD SHAHDRA | DGN110 | TG-DGN110A-5 | DT-5 | VERMA CASTLE:PL | 6 | 990 | 19506053 | 1118 | 2019-06-23 12:30 | 376 | 1606 | 369 | 1588 | 373 | 1608 | 19 | 502.5 | 145.5 | 52 | 17 | 214.5 | 57% | 52% | 113% | 57% | 3.7951 | Loss 0-5% | 1010(145.5) | 945(86) | 907(108.5) | 1167(185) | 1211(166)
645 | 1211 | GTR | GT ROAD SHAHDRA | DGN110 | TG-DGN110A-6 | DT-6 | VERMA CASTLE:PL | 6 | 990 | 19501793 | 991 | 2019-06-17 11:30 | 329 | 1310 | 327 | 1305 | 335 | 1335 | 27 | 561 | 128.5 | 26 | 0.5 | 155 | 48% | 84% | 100% | 48% | 3.7951 | Loss 0-5%
646 | 1211 | GTR | GT ROAD SHAHDRA | DGN111 | TG-DGN111A-1 | DT-1 | FRIENDS COLONY GALI NO.1 | 3 | 990 | 19500654 | 883 | 2019-06-23 12:00 | 295 | 1206 | 299 | 1220 | 290 | 1179 | 37 | 576.5 | 142 |  |  | 142 | 40% | 49% | 89% | 58% | 5.5303 | Loss 5-10% | 828(41.5) |  | 879(30.5) | 836(26.5) | 968(107.5) | 996(126)
647 | 1211 | GTR | GT ROAD SHAHDRA | DGN111 | TG-DGN111A-2 | DT-2 | FRIENDS COLONY GALI NO.1 | 3 | 990 | 19504999 | 666 | 2019-06-22 15:30 | 228 | 914 | 225 | 903 | 213 | 856 | 53 | 718 |  |  |  | 0 | 48% | 45% | 67% | 49% | 5.5303 | Loss 5-10%
648 | 1211 | GTR | GT ROAD SHAHDRA | DGN111 | TG-DGN111A-3 | DT-3 | FRIENDS COLONY GALI NO.1 | 3 | 990 | 19505689 | 867 | 2019-06-28 11:30 | 284 | 1152 | 287 | 1164 | 295 | 1206 | 50 | 688 | 30.5 |  |  | 30.5 | 62% | 61% | 88% | 64% | 5.5303 | Loss 5-10%
649 | 1211 | GTR | GT ROAD SHAHDRA | DGN120 | TG-DGN120A-1 | DT-1 | GALI NO.3 FRIENDS COLONY:PL | 2 | 990 | 19503629 | 1010 | 2019-06-24 11:30 | 339 | 1398 | 341 | 1410 | 330 | 1355 | 50 | 482 | 201.5 | 34.5 | 2 | 238 | 52% | 55% | 102% | 57% | 6.5453 | Loss 5-10% | [5 empty] | 949(156)
650 | 1211 | GTR | GT ROAD SHAHDRA | DGN120 | TG-DGN120A-2 | DT-2 | GALI NO.3 FRIENDS COLONY:PL | 2 | 630 | 19505759 | 272 | 2019-06-22 12:30 | 91 | 378 | 86 | 357 | 94 | 390 | 29 | 720 |  |  |  | 0 | 29% | 30% | 43% | 32% | 6.5453 | Loss 5-10% |  |  |  | 922(84) | 913(71.5) | 883(39)
651 | 1211 | GTR | GT ROAD SHAHDRA | DGN127 | TG-DGN127A-1 | DT-1 | GALI NO.1B FRIENDS COLONY:PL | 4 | 990 | 19500650 | 833 | 2019-06-01 11:30 | 271 | 1150 | 268 | 1129 | 294 | 1234 | 96 | 696.5 | 22.5 |  |  | 22.5 | 38% | 55% | 84% | 49% | 2.8373 | Loss 0-5% | 1004(94) | 1013(87) | 908(124.5) | 930(158) | 910(133.5) | 996(172.5)
652 | 1211 | GTR | GT ROAD SHAHDRA | DGN127 | TG-DGN127A-2 | DT-2 | GALI NO.1B FRIENDS COLONY:PL | 4 | 990 | 19504119 | 889 | 2019-06-27 16:30 | 283 | 1211 | 317 | 1351 | 290 | 1240 | 128 | 622 | 98 |  |  | 98 | 35% | 43% | 90% | 38% | 2.8373 | Loss 0-5% | 904(28.5) | 893(48.5) | 831(33) | 899(55) | 975(121.5) | 976(179)
653 | 1211 | GTR | GT ROAD SHAHDRA | DGN127 | TG-DGN127A-3 | DT-3 | GALI NO.1B FRIENDS COLONY:PL | 4 | 990 | 19505853 | 939 | 2019-06-27 15:30 | 319 | 1375 | 317 | 1364 | 303 | 1313 | 57 | 612.5 | 105 | 2.5 |  | 107.5 | 61% | 48% | 95% | 57% | 2.8373 | Loss 0-5% | 926(69.5) | 918(78) | 947(105.5) |  | 1003(109.5) | 1010(127.5)
654 | 1211 | GTR | GT ROAD SHAHDRA | DGN127 | TG-DGN127A-4 | DT-4 | GALI NO.1B FRIENDS COLONY:PL | 4 | 630 | 19506340 | 448 | 2019-06-21 15:00 | 149 | 632 | 144 | 607 | 154 | 646 | 35 | 718.5 | 0.5 |  |  | 0.5 | 48% | 46% | 71% | 47% | 2.8373 | Loss 0-5% | 592(59.5) | 580(68.5) | 591(129.5) | 685(123) | 750(187.5) | 730(238)
655 | 1211 | GTR | GT ROAD SHAHDRA | DGN129 | TG-DGN129A-1 | DT-1 | FRIENDS COLONY GALI NO-5-6 NEAR RLY.LINE:PM | 6 | 990 | 19504943 | 708 | 2019-06-13 11:00 | 234 | 981 | 240 | 1006 | 233 | 980 | 26 | 719.5 | 0.5 |  |  | 0.5 | 19% | 39% | 71% | 19% | 4.5058 | Loss 0-5% | 839(42) | 807(32.5) | 882(55) | 853(62.5) | 957(146)
656 | 1211 | GTR | GT ROAD SHAHDRA | DGN129 | TG-DGN129A-2 | DT-2 | FRIENDS COLONY GALI NO-5-6 NEAR RLY.LINE:PM | 6 | 990 | 19506017 | 1201 | 2019-06-21 12:00 | 412 | 1798 | 399 | 1728 | 390 | 1703 | 86 | 480 | 108 | 63 | 66 | 237 | 45% | 64% | 121% | 44% | 4.5058 | Loss 0-5% | 1126(178.5) |  | 1149(214) | 1209(239.5) | 1193(66.5) | 1345(44.5)
657 | 1211 | GTR | GT ROAD SHAHDRA | DGN129 | TG-DGN129A-3 | DT-3 | FRIENDS COLONY GALI NO-5-6 NEAR RLY.LINE:PM | 6 | 990 | 19503739 | 767 | 2019-06-22 12:30 | 253 | 1104 | 252 | 1101 | 262 | 1142 | 40 | 702.5 | 17.5 |  |  | 17.5 | 24% | 42% | 77% | 31% | 4.5058 | Loss 0-5% | 920(36.5) |  | 898(84.5) | 913(108) | 936(88) | 1055(103)
658 | 1211 | GTR | GT ROAD SHAHDRA | DGN129 | TG-DGN129A-4 | DT-4 | FRIENDS COLONY GALI NO-5-6 NEAR RLY.LINE:PM | 6 | 990 | 19505079 | 1131 | 2019-06-27 15:00 | 377 | 1525 | 375 | 1505 | 379 | 1526 | 20 | 471.5 | 130.5 | 82 | 36 | 248.5 | 53% | 60% | 114% | 58% | 4.5058 | Loss 0-5% | 841(29) | 894(68.5) | 876(45) | 1070(69) | 979(87) | 984(137)
659 | 1211 | GTR | GT ROAD SHAHDRA | DGN129 | TG-DGN129A-5 | DT-5 | FRIENDS COLONY GALI NO-5-6 NEAR RLY.LINE:PM | 6 | 990 | 19505896 | 578 | 2019-06-19 10:30 | 198 | 815 | 187 | 767 | 193 | 795 | 41 | 717 |  |  |  | 0 | 26% | 28% | 58% | 26% | 4.5058 | Loss 0-5% | [5 empty] | 831(50)
660 | 1211 | GTR | GT ROAD SHAHDRA | DGN129 | TG-DGN129A-6 | DT-6 | FRIENDS COLONY GALI NO-5-6 NEAR RLY.LINE:PM | 6 | 990 | 19506813 | 1099 | 2019-06-22 11:30 | 360 | 1558 | 380 | 1644 | 359 | 1560 | 85 | 505.5 | 162.5 | 42 | 10 | 214.5 | 53% | 65% | 111% | 54% | 4.5058 | Loss 0-5%
661 | 1211 | GTR | GT ROAD SHAHDRA | DGN131 | TG-DGN131A-1 | DT-1 | GALI NO.1A FRIENDS COLONY UNDER FLYOVER: PL | 2 | 990 | 19504318 | 1141 | 2019-06-19 15:00 | 384 | 1607 | 370 | 1545 | 387 | 1621 | 70 | 600 | 113 | 3 | 4 | 120 | 46% | 61% | 115% | 49% | 5.5513 | Loss 5-10% |  |  | 1142(43.5) | 1180(134.5) | 1272(111) | 1256(182.5)
662 | 1211 | GTR | GT ROAD SHAHDRA | DGN131 | TG-DGN131A-2 | DT-2 | GALI NO.1A FRIENDS COLONY UNDER FLYOVER: PL | 2 | 630 | 19504366 | 554 | 2019-06-12 12:00 | 174 | 729 | 187 | 788 | 193 | 816 | 76 | 628 | 92 |  |  | 92 | 45% | 54% | 88% | 47% | 5.5513 | Loss 5-10%
663 | 1211 | GTR | GT ROAD SHAHDRA | DGN178 | TG-DGN178A-1 | DT-1 | HANSRAJ COMPOUND S/STN | 4 | 990 | 19505895 | 980 | 2019-06-01 15:00 | 344 | 1472 | 325 | 1392 | 311 | 1341 | 115 | 569 | 149.5 | 1 |  | 150.5 | 47% | 50% | 99% | 49% | 4.4256 | Loss 0-5% | 927(92.5) | 931(75.5) | 1033(201.5) | 1045(200) | 1084(149)
664 | 1211 | GTR | GT ROAD SHAHDRA | DGN178 | TG-DGN178A-2 | DT-2 | HANSRAJ COMPOUND S/STN | 4 | 990 | 19504236 | 715 | 2019-06-03 15:00 | 238 | 998 | 227 | 955 | 250 | 1046 | 79 | 713 | 3 |  |  | 3 | 27% | 31% | 72% | 30% | 4.4256 | Loss 0-5% |  |  |  |  | 816(34) | 1002(94.5)
665 | 1211 | GTR | GT ROAD SHAHDRA | DGN178 | TG-DGN178A-3 | DT-3 | HANSRAJ COMPOUND S/STN | 4 | 630 | 19503413 | 701 | 2019-06-29 12:00 | 247 | 982 | 239 | 945 | 215 | 852 | 116 | 486.5 | 142.5 | 72 | 17 | 231.5 | 41% | 51% | 111% | 58% | 4.4256 | Loss 0-5%
666 | 1211 | GTR | GT ROAD SHAHDRA | DGN178 | TG-DGN178A-4 | DT-4 | HANSRAJ COMPOUND S/STN | 4 | 990 | 19505688 | 915 | 2019-06-07 16:00 | 294 | 1259 | 316 | 1359 | 304 | 1298 | 87 | 620.5 | 98 | 1 |  | 99 | 34% | 38% | 92% | 35% | 4.4256 | Loss 0-5%
667 | 1211 | GTR | GT ROAD SHAHDRA | DGN198 | TG-DGN198A-1 | DT-1 | GALI NO-1 METRO PARKING SS-2 | 3 | 990 | 19506421 | 1183 | 2019-06-28 14:30 | 393 | 1723 | 392 | 1717 | 397 | 1737 | 18 | 442.5 | 120.5 | 81 | 69.5 | 271 | 81% | 94% | 119% | 84% | 5.8289 | Loss 5-10%
668 | 1211 | GTR | GT ROAD SHAHDRA | DGN198 | TG-DGN198A-2 | DT-2 | GALI NO-1 METRO PARKING SS-2 | 3 | 990 | 19506921 | 1082 | 2019-06-20 16:00 | 351 | 1527 | 372 | 1631 | 359 | 1567 | 91 | 184.5 | 66.5 | 20.5 | 4 | 91 | 38% | 57% | 109% | 42% | 5.8289 | Loss 5-10% | 897(26.5) | 934(69) |  | 875(83.5) | 886(59) | 1036(125.5)
669 | 1211 | GTR | GT ROAD SHAHDRA | DGN198 | TG-DGN198A-3 | DT-3 | GALI NO-1 METRO PARKING SS-2 | 3 | 990 | 19504954 | 994 | 2019-06-27 12:30 | 334 | 1384 | 327 | 1343 | 333 | 1382 | 40 | 489 | 191.5 | 37 | 0.5 | 229 | 67% | 63% | 100% | 66% | 5.8289 | Loss 5-10%
670 | 1211 | GTR | GT ROAD SHAHDRA | DGN231 | TG-DGN231A-1 | DT-1 | GALI NO-1 RAILWAY LINE FRIENDS COLONY | 2 | 990 | 19504996 | 916 | 2019-06-20 16:00 | 294 | 1256 | 306 | 1305 | 316 | 1349 | 80 | 522 | 186.5 | 6.5 |  | 193 | 44% | 48% | 93% | 43% | 6.6913 | Loss 5-10% | [5 empty] | 1029(114)
671 | 1211 | GTR | GT ROAD SHAHDRA | DGN231 | TG-DGN231A-2 | DT-2 | GALI NO-1 RAILWAY LINE FRIENDS COLONY | 2 | 630 | 19506054 | 696 | 2019-06-07 11:30 | 231 | 989 | 235 | 1006 | 230 | 979 | 23 | 487 | 169.5 | 50 | 8 | 227.5 | 78% | 80% | 110% | 76% | 6.6913 | Loss 5-10% | 567(66) | 745(104.5) | 678(164) | 671(154.5) | 655(217) | 725(256)
672 | 1211 | GTR | GT ROAD SHAHDRA | DGN236 | TG-DGN236A-1 | DT-1 | 1B Friends colony near railway line. | 1 | 990 | 19505054 | 893 | 2019-06-24 14:30 | 307 | 1246 | 301 | 1221 | 285 | 1156 | 81 | 602.5 | 117 | 0.5 |  | 117.5 | 46% | 55% | 90% | 48% | 6.8449 | Loss 5-10% | 709(127.5) | 752(190) | 760(191.5) | 728(183) | 716(131) | 776(220.5)
673 | 1211 | GTR | GT ROAD SHAHDRA | DGN255 | TG-DGN255A-1 | DT-1 | GALI NO. 00 FRIENDS COLONY(THAKUR WALA) | 1 | 990 | 19506892 | 967 | 2019-06-24 17:00 | 329 | 1379 | 317 | 1331 | 321 | 1337 | 46 | 603.5 | 112 | 2 |  | 114 | 47% | 57% | 98% | 48% | 5.1 | Loss 5-10%
674 | 1211 | GTR | ZAFFRABAD | DGN001 | TG-DGN001A-1 | DT-1 | ZAFRABAD AE OFFICE | 1 | 990 | 19501728 | 925 | 2019-06-30 01:30 | 349 | 1428 | 339 | 1403 | 237 | 969 | 447 | 587.5 | 128.5 | 4 |  | 132.5 | 93% | 74% | 67% | 88% | 5.3432 | Loss 5-10% |  | 789(41) | 862(134) | 876(76)
675 | 1211 | GTR | ZAFFRABAD | DGN002 | TG-DGN002A-1 | DT-1 | ZAFRABAD CONSTRUCTION OFFICE:ID | 3 | 990 | 19505244 | 533 | 2019-06-21 14:00 | 183 | 765 | 183 | 756 | 167 | 692 | 70 | 720 |  |  |  | 0 | 49% | 46% | 54% | 51% | 8.0384 | Loss 5-10%
676 | 1211 | GTR | ZAFFRABAD | DGN002 | TG-DGN002A-2 | DT-2 | ZAFRABAD CONSTRUCTION OFFICE:ID | 3 | 990 | 19505261 | 1011 | 2019-06-03 00:30 | 311 | 1351 | 291 | 1255 | 410 | 1762 | 467 | 686 | 22.5 | 8 | 1.5 | 32 | 102% | 74% | 75% | 96% | 8.0384 | Loss 5-10% |  | 1017(120) | 1095(219) | 875(77) | 875(109)
677 | 1211 | GTR | ZAFFRABAD | DGN002 | TG-DGN002A-3 | DT-3 | ZAFRABAD CONSTRUCTION OFFICE:ID | 3 | 630 | 19506878 | 304 | 2019-06-06 01:00 | 84 | 345 | 110 | 459 | 110 | 461 | 115 | 718 |  |  |  | 0 | 48% | 36% | 36% | 45% | 8.0384 | Loss 5-10%
678 | 1211 | GTR | ZAFFRABAD | DGN003 | TG-DGN003A-1 | DT-1 | NAV DURGA MANDIR | 3 | 990 | 19501845 | 819 | 2019-06-11 23:30 | 318 | 1296 | 213 | 868 | 289 | 1181 | 383 | 681.5 | 38 |  |  | 38 | 82% | 49% | 53% | 83% | 6.7313 | Loss 5-10% |  | 1150(134.5) | 1297(273.5)
679 | 1211 | GTR | ZAFFRABAD | DGN003 | TG-DGN003A-2 | DT-2 | NAV DURGA MANDIR | 3 | 990 | 19506346 | 1091 | 2019-06-11 | 352 | 1486 | 417 | 1785 | 322 | 1353 | 383 | 493.5 | 136.5 | 62.5 | 27.5 | 226.5 | 110% | 73% | 76% | 110% | 6.7313 | Loss 5-10% | 1099(69)
680 | 1211 | GTR | ZAFFRABAD | DGN003 | TG-DGN003A-3 | DT-3 | NAV DURGA MANDIR | 3 | 630 | 19506487 | 511 | 2019-06-30 23:30 | 203 | 870 | 138 | 584 | 170 | 721 | 248 | 674.5 | 45.5 |  |  | 45.5 | 79% | 54% | 56% | 81% | 6.7313 | Loss 5-10% |  |  | 574(34.5)
681 | 1211 | GTR | ZAFFRABAD | DGN004 | TG-DGN004A-1 | DT-1 | GORAKH PARK NALA (ASHOK WALA) | 1 | 630 | 19504422 | 550 | 2019-06-10 23:30 | 235 | 1064 | 158 | 703 | 157 | 708 | 359 | 667 | 53 |  |  | 53 | 87% | 57% | 66% | 87% | 3.3467 | Loss 0-5% |  |  | 552(68)
682 | 1211 | GTR | ZAFFRABAD | DGN008 | TG-DGN008A-1 | DT-1 | SUBHASH PARK CHAND RAM | 1 | 990 | 19506345 | 1071 | 2019-06-30 23:30 | 349 | 1446 | 349 | 1455 | 373 | 1556 | 106 | 311 | 298 | 82.5 | 28.5 | 409 | 107% | 85% | 96% | 108% | 4.0856 | Loss 0-5% | 851(42) | 1047(264.5) | 1112(458.5) | 1013(229.5) | 1012(347.5) | 890(105.5)
683 | 1211 | GTR | ZAFFRABAD | DGN009 | TG-DGN009A-1 | DT-1 | SUBHASH PARK ICE FACTORY | 2 | 990 | 19501797 | 961 | 2019-06-12 01:30 | 319 | 1305 | 247 | 997 | 395 | 1630 | 548 | 577 | 133 | 10 |  | 143 | 97% | 61% | 74% | 95% | 4.3033 | Loss 0-5% |  | 798(24) | 937(86)
684 | 1211 | GTR | ZAFFRABAD | DGN009 | TG-DGN009A-2 | DT-2 | SUBHASH PARK ICE FACTORY | 2 | 990 | 19506593 | 816 | 2019-06-08 02:30 | 200 | 795 | 448 | 1901 | 167 | 682 | 1166 | 671.5 | 48.5 |  |  | 48.5 | 82% | 52% | 61% | 82% | 4.3033 | Loss 0-5% |  | 820(27) | 889(60)
685 | 1211 | GTR | ZAFFRABAD | DGN010 | TG-DGN010A-1 | DT-1 | PANCH SHEEL PARK (JHULE WALA):K | 3 | 990 | 19501710 | 1071 | 2019-06-12 | 408 | 1650 | 398 | 1585 | 266 | 1060 | 560 | 519.5 | 119 | 52 | 29 | 200 | 108% | 70% | 75% | 108% | 3.9722 | Loss 0-5% |  | 1027(106) | 1163(207) | 936(34) | 889(72.5)
686 | 1211 | GTR | ZAFFRABAD | DGN010 | TG-DGN010A-2 | DT-2 | PANCH SHEEL PARK (JHULE WALA):K | 3 | 990 | 19505472 | 1195 | 2019-06-11 01:00 | 321 | 1387 | 498 | 2201 | 376 | 1611 | 728 | 504 | 121 | 52 | 42.5 | 215.5 | 121% | 69% | 84% | 117% | 3.9722 | Loss 0-5% |  | 1032(90) | 1076(185) | 974(59) | 915(102.5)
687 | 1211 | GTR | ZAFFRABAD | DGN010 | TG-DGN010A-3 | DT-3 | PANCH SHEEL PARK (JHULE WALA):K | 3 | 630 | 19506058 | 469 | 2019-06-30 23:30 | 166 | 761 | 166 | 758 | 136 | 618 | 142 | 717 | 3 |  |  | 3 | 71% | 48% | 59% | 74% | 3.9722 | Loss 0-5%
688 | 1211 | GTR | ZAFFRABAD | DGN011 | TG-DGN011A-1 | DT-1 | H-BLOCK NAVEEN SHAHDARA:PL | 4 | 990 | 19501828 | 811 | 2019-06-03 | 267 | 1154 | 242 | 1054 | 302 | 1323 | 236 | 564.5 | 25 |  |  | 25 | 82% | 55% | 63% | 82% | 2.9524 | Loss 0-5%
689 | 1211 | GTR | ZAFFRABAD | DGN011 | TG-DGN011A-2 | DT-2 | H-BLOCK NAVEEN SHAHDARA:PL | 4 | 990 | 19506935 | 623 | 2019-06-29 23:30 | 177 | 745 | 273 | 1171 | 173 | 723 | 438 | 227 |  |  |  | 0 | 58% | 34% | 46% | 63% | 2.9524 | Loss 0-5% |  |  | 914(49.5)
690 | 1211 | GTR | ZAFFRABAD | DGN011 | TG-DGN011A-3 | DT-3 | H-BLOCK NAVEEN SHAHDARA:PL | 4 | 990 | 19505334 | 866 | 2019-06-01 01:00 | 285 | 1139 | 258 | 1035 | 323 | 1285 | 218 | 650.5 | 66.5 |  |  | 66.5 | 87% | 51% | 61% | 84% | 2.9524 | Loss 0-5% |  |  | 860(55)
691 | 1211 | GTR | ZAFFRABAD | DGN011 | TG-DGN011A-4 | DT-4 | H-BLOCK NAVEEN SHAHDARA:PL | 4 | 630 | 19506255 | 666 | 2019-06-12 | 286 | 1238 | 219 | 929 | 161 | 682 | 483 | 614 | 95 | 7 | 1 | 103 | 106% | 65% | 78% | 93% | 2.9524 | Loss 0-5%
692 | 1211 | GTR | ZAFFRABAD | DGN012 | TG-DGN012A-1 | DT-1 | MOHAN PARK | 2 | 990 | 19505755 | 1057 | 2019-06-09 | 294 | 1252 | 387 | 1682 | 377 | 1645 | 412 | 529.5 | 137 | 45.5 | 6.5 | 189 | 107% | 69% | 87% | 106% | 4.9652 | Loss 0-5% | 1062(66) | 1362(301.5) | 1420(462) | 1333(327) | 1095(44)
693 | 1211 | GTR | ZAFFRABAD | DGN012 | TG-DGN012A-2 | DT-2 | MOHAN PARK | 2 | 400 | 19506546 | 449 | 2019-06-11 23:30 | 149 | 623 | 112 | 459 | 189 | 801 | 296 | 519.5 | 135.5 | 52.5 | 11.5 | 199.5 | 107% | 66% | 88% | 112% | 4.9652 | Loss 0-5%
694 | 1211 | GTR | ZAFFRABAD | DGN013 | TG-DGN013A-1 | DT-1 | K-BLOCK NAVEEN SHAHDARA:PL | 2 | 990 | 19506344 | 633 | 2019-06-15 01:00 | 201 | 856 | 314 | 1413 | 117 | 504 | 794 | 720 |  |  |  | 0 | 64% | 41% | 51% | 63% | 5.5503 | Loss 5-10%
695 | 1211 | GTR | ZAFFRABAD | DGN013 | TG-DGN013A-2 | DT-2 | K-BLOCK NAVEEN SHAHDARA:PL | 2 | 630 | 19506402 | 495 | 2019-06-13 22:30 | 123 | 530 | 220 | 958 | 151 | 657 | 381 | 694 | 26 |  |  | 26 | 78% | 46% | 56% | 79% | 5.5503 | Loss 5-10%
696 | 1211 | GTR | ZAFFRABAD | DGN014 | TG-DGN014A-1 | DT-1 | LONI ROAD KHATTEWALA:PL | 2 | 990 | 19506738 | 651 | 2019-06-30 23:30 | 326 | 1431 | 123 | 525 | 202 | 872 | 792 | 720 |  |  |  | 0 | 63% | 43% | 45% | 66% | 5.2176 | Loss 5-10%
697 | 1211 | GTR | ZAFFRABAD | DGN014 | TG-DGN014A-2 | DT-2 | LONI ROAD KHATTEWALA:PL | 2 | 630 | 19505770 | 622 | 2019-06-04 23:30 | 199 | 832 | 133 | 542 | 289 | 1213 | 582 | 513 | 176 | 31 |  | 207 | 96% | 64% | 75% | 99% | 5.2176 | Loss 5-10% |  | 602(87.5) | 733(219) | 836(147.5) | 621(93)
698 | 1211 | GTR | ZAFFRABAD | DGN018 | TG-DGN018A-1 | DT-1 | R. BLOCK NAVEEN SHAHDARA:PL | 2 | 990 | 19501725 | 681 | 2019-06-11 23:30 | 250 | 1072 | 252 | 1071 | 179 | 762 | 309 | 719 |  |  |  | 0 | 68% | 47% | 53% | 69% | 7.0892 | Loss 5-10%
699 | 1211 | GTR | ZAFFRABAD | DGN018 | TG-DGN018A-2 | DT-2 | R. BLOCK NAVEEN SHAHDARA:PL | 2 | 630 | 19505754 | 481 | 2019-06-12 | 118 | 487 | 248 | 1048 | 114 | 475 | 568 | 690.5 | 27.5 |  |  | 27.5 | 76% | 45% | 60% | 74% | 7.0892 | Loss 5-10% |  | 625(88) | 709(182.5) | 654(46)
700 | 1211 | GTR | ZAFFRABAD | DGN019 | TG-DGN019A-1 | DT-1 | KABOOL NAGAR KIOSK | 2 | 990 | 19506055 | 949 | 2019-06-02 23:30 | 268 | 1125 | 256 | 1090 | 425 | 1843 | 736 | 591 | 126.5 | 2 |  | 128.5 | 93% | 71% | 81% | 96% | 7.7523 | Loss 5-10% |  |  | 930(90.5)
701 | 1211 | GTR | ZAFFRABAD | DGN019 | TG-DGN019A-2 | DT-2 | KABOOL NAGAR KIOSK | 2 | 630 | 19501829 | 389 | 2019-06-12 | 127 | 521 | 147 | 605 | 114 | 474 | 114 | 720 |  |  |  | 0 | 62% | 39% | 58% | 61% | 7.7523 | Loss 5-10%
702 | 1211 | GTR | ZAFFRABAD | DGN020 | TG-DGN020A-1 | DT-1 | KABOOL NAGAR MOTHER DAIRY:PL | 2 | 630 | 19505195 | 330 | 2019-06-15 01:30 | 155 | 678 | 79 | 328 | 96 | 403 | 319 | 720 |  |  |  | 0 | 52% | 38% | 41% | 45% | 3.1479 | Loss 0-5%
703 | 1211 | GTR | ZAFFRABAD | DGN020 | TG-DGN020A-2 | DT-2 | KABOOL NAGAR MOTHER DAIRY:PL | 2 | 990 | 19506492 | 967 | 2019-06-12 | 359 | 1507 | 296 | 1234 | 311 | 1289 | 250 | 567.5 | 132 | 20.5 |  | 152.5 | 98% | 63% | 73% | 97% | 3.1479 | Loss 0-5% |  |  | 933(80.5)
704 | 1211 | GTR | ZAFFRABAD | DGN021 | TG-DGN021A-1 | DT-1 | KABOOL NAGAR RAIN BASERA:PM | 2 | 630 | 19506755 | 629 | 2019-06-27 01:00 | 102 | 407 | 324 | 1341 | 203 | 833 | 810 | 543.5 | 167.5 | 3 |  | 170.5 | 100% | 61% | 88% | 95% | 7.9972 | Loss 5-10%
705 | 1211 | GTR | ZAFFRABAD | DGN021 | TG-DGN021A-2 | DT-2 | KABOOL NAGAR RAIN BASERA:PM | 2 | 990 | 19506357 | 580 | 2019-06-11 22:00 | 136 | 575 | 315 | 1328 | 130 | 541 | 771 | 713.5 |  |  |  | 0 | 56% | 41% | 59% | 59% | 7.9972 | Loss 5-10%
706 | 1211 | GTR | ZAFFRABAD | DGN022 | TG-DGN022A-1 | DT-1 | SHAHI MOHALLA:K | 4 | 990 | 19504163 | 875 | 2019-06-01 23:30 | 321 | 1342 | 343 | 1422 | 212 | 871 | 515 | 600 | 116 |  |  | 116 | 88% | 53% | 81% | 88% | 5.0084 | Loss 5-10%
707 | 1211 | GTR | ZAFFRABAD | DGN022 | TG-DGN022A-2 | DT-2 | SHAHI MOHALLA:K | 4 | 990 | 19501765 | 973 | 2019-06-30 | 367 | 1597 | 307 | 1324 | 299 | 1294 | 289 | 585 | 118.5 | 14 |  | 132.5 | 98% | 67% | 72% | 97% | 5.0084 | Loss 5-10% |  |  | 867(73)
708 | 1211 | GTR | ZAFFRABAD | DGN022 | TG-DGN022A-3 | DT-3 | SHAHI MOHALLA:K | 4 | 990 | 19501749 | 634 | 2019-06-03 | 230 | 989 | 182 | 779 | 223 | 971 | 201 | 716.5 |  |  |  | 0 | 64% | 42% | 51% | 64% | 5.0084 | Loss 5-10%
709 | 1211 | GTR | ZAFFRABAD | DGN022 | TG-DGN022A-4 | DT-4 | SHAHI MOHALLA:K | 4 | 630 | 19503146 | 548 | 2019-06-02 22:00 | 208 | 915 | 179 | 786 | 161 | 705 | 183 | 684.5 | 32.5 |  |  | 32.5 | 79% | 51% | 84% | 87% | 5.0084 | Loss 5-10%
710 | 1211 | GTR | ZAFFRABAD | DGN023 | TG-DGN023A-1 | DT-1 | SHIVAJI PARK ARYA SAMAJ MANDIR | 1 | 1600 | 19501792 | 1612 | 2019-06-11 00:30 | 534 | 2155 | 471 | 1903 | 606 | 2441 | 466 | 607 | 106.5 | 2.5 | 0.5 | 109.5 | 101% | 63% | 64% | 88% | 4.6009 | Loss 0-5% | 902(25.5) | 1241(228) | 1325(237) |  |  | 911(34.5)
711 | 1211 | GTR | ZAFFRABAD | DGN024 | TG-DGN024A-1 | DT-1 | GORAKH PARK HANUMAN MANDIR PM | 1 | 400 | 19502520 | 363 | 2019-06-02 21:00 | 114 | 472 | 122 | 509 | 127 | 531 | 52 | 512.5 | 206.5 | 1 |  | 207.5 | 81% | 51% | 90% | 91% | 2.7036 | Loss 0-5% |  |  |  |  | 373(113.5)
712 | 1211 | GTR | ZAFFRABAD | DGN025 | TG-DGN025A-1 | DT-1 | GORAKH PARK KISOK:K | 4 | 990 | 19505226 | 730 | 2019-06-11 22:30 | 219 | 933 | 252 | 1063 | 259 | 1117 | 164 | 717.5 | 2 |  |  | 2 | 70% | 49% | 50% | 74% | 5.6429 | Loss 5-10% |  | 1212(70)
713 | 1211 | GTR | ZAFFRABAD | DGN025 | TG-DGN025A-2 | DT-2 | GORAKH PARK KISOK:K | 4 | 990 | 19505562 | 969 | 2019-06-12 | 358 | 1441 | 325 | 1314 | 285 | 1152 | 251 | 570 | 129 | 20.5 |  | 149.5 | 98% | 67% | 67% | 98% | 5.6429 | Loss 5-10% |  | 1036(36.5) | 946(122.5) | 810(28.5) | 761(26.5)
714 | 1211 | GTR | ZAFFRABAD | DGN025 | TG-DGN025A-3 | DT-3 | GORAKH PARK KISOK:K | 4 | 990 | 19501702 | 682 | 2019-06-29 23:30 | 268 | 1097 | 225 | 921 | 190 | 779 | 275 | 719.5 |  |  |  | 0 | 69% | 43% | 47% | 69% | 5.6429 | Loss 5-10%
715 | 1211 | GTR | ZAFFRABAD | DGN025 | TG-DGN025A-4 | DT-4 | GORAKH PARK KISOK:K | 4 | 630 | 19504758 | 683 | 2019-06-11 23:30 | 257 | 1080 | 212 | 884 | 213 | 881 | 198 | 538 | 127.5 | 42 | 12.5 | 182 | 105% | 66% | 71% | 108% | 5.6429 | Loss 5-10% |  |  | 763(144) | 569(27) | 550(69.5)
716 | 1211 | GTR | ZAFFRABAD | DGN026 | TG-DGN026A-1 | DT-1 | BALBIR NAGA NALA GALI NO.14:PL | 2 | 990 | 19505547 | 1089 | 2019-06-12 | 339 | 1353 | 355 | 1411 | 394 | 1589 | 214 | 501.5 | 134 | 53 | 31.5 | 218.5 | 110% | 68% | 92% | 110% | 4.5736 | Loss 0-5% |  |  | 1168(131) | 1087(152) | 989(112)
717 | 1211 | GTR | ZAFFRABAD | DGN026 | TG-DGN026A-2 | DT-2 | BALBIR NAGA NALA GALI NO.14:PL | 2 | 990 | 19505928 | 764 | 2019-06-12 | 248 | 1058 | 161 | 679 | 356 | 1532 | 740 | 703 | 16 |  |  | 16 | 77% | 43% | 54% | 75% | 4.5736 | Loss 0-5% | 665(37) | 982(355.5) | 1004(222.5)
718 | 1211 | GTR | ZAFFRABAD | DGN027 | TG-DGN027A-1 | DT-1 | BALBIR NAGAR NALA GALI NO. 16:PL | 1 | 990 | 19505217 | 1179 | 2019-06-06 22:30 | 352 | 1509 | 387 | 1639 | 439 | 1929 | 372 | 498.5 | 123.5 | 59.5 | 38.5 | 221.5 | 117% | 75% | 85% | 119% | 7.4796 | Loss 5-10% |  | 886(28.5) | 1139(161) | 967(94.5) | 833(46.5)
719 | 1211 | GTR | ZAFFRABAD | DGN028 | TG-DGN028A-1 | DT-1 | BALBIR NAGAR NALA GALI.4 GORAKH PUR:PL | 2 | 990 | 19506685 | 951 | 2019-06-29 23:30 | 247 | 1058 | 356 | 1553 | 349 | 1520 | 480 | 615 | 99.5 | 5 |  | 104.5 | 94% | 58% | 60% | 96% | 6.7345 | Loss 5-10% |  | 866(44.5) | 1055(118)
720 | 1211 | GTR | ZAFFRABAD | DGN028 | TG-DGN028A-2 | DT-2 | BALBIR NAGAR NALA GALI.4 GORAKH PUR:PL | 2 | 630 | 19505945 | 605 | 2019-06-11 00:30 | 209 | 857 | 160 | 652 | 236 | 968 | 278 | 648 | 70.5 | 1 |  | 71.5 | 96% | 54% | 60% | 90% | 6.7345 | Loss 5-10%
721 | 1211 | GTR | ZAFFRABAD | DGN029 | TG-DGN029A-1 | DT-1 | BEHAL GALI | 1 | 990 | 19506361 | 1221 | 2019-06-06 22:00 | 332 | 1467 | 501 | 2295 | 387 | 1711 | 736 | 439 | 154 | 60.5 | 66.5 | 281 | 117% | 76% | 80% | 123% | 4.7932 | Loss 0-5% |  | 986(81.5) | 1072(193.5) | 875(57) | 871(95.5)
722 | 1211 | GTR | ZAFFRABAD | DGN030 | TG-DGN030A-1 | DT-1 | BALBIR NAGAR EXTN. 60 F ROAD:PM:PL | 2 | 990 | 19505863 | 1159.4614 | 2019-06-11 23:00 | 355.9034 | 1529.1233 | 403.4672 | 1734.4477 | 400.0907 | 1734.7732 | 205.4873 | 459 | 144 | 58.5 | 54 | 256.5 | 114% | 75% | 99% | 117% | 4.0457 | Loss 0-5% |  |  |  | 1162(132) | 995(118)
723 | 1211 | GTR | ZAFFRABAD | DGN030 | TG-DGN030A-2 | DT-2 | BALBIR NAGAR EXTN. 60 F ROAD:PM:PL | 2 | 630 | 19505007 | 840 | 2019-06-29 04:30 | 234 | 998 | 302 | 1315 | 304 | 1314 | 316 | 547.5 | 124 | 37.5 | 7 | 168.5 | 133% | 115% | 80% | 103% | 4.0457 | Loss 0-5% | 621(41) | 786(201) | 918(145.5) | 566(44.5) | 509(26)
724 | 1211 | GTR | ZAFFRABAD | DGN031 | TG-DGN031A-1 | DT-1 | BALBIR NAGAR SCHOOL:K | 3 | 990 | 19506056 | 1328 | 2019-06-30 | 497 | 2051 | 421 | 1750 | 410 | 1696 | 331 | 420.5 | 148 | 47.5 | 103.5 | 299 | 134% | 75% | 95% | 133% | 5.4471 | Loss 5-10% |  | 1270(149.5) | 1121(178) | 928(52) | 940(115) | 928(35)
725 | 1211 | GTR | ZAFFRABAD | DGN031 | TG-DGN031A-2 | DT-2 | BALBIR NAGAR SCHOOL:K | 3 | 990 | 19504165 | 985 | 2019-06-03 | 319 | 1278 | 316 | 1249 | 350 | 1397 | 135 | 573 | 122.5 | 24.5 |  | 147 | 100% | 59% | 64% | 98% | 5.4471 | Loss 5-10% |  | 970(37.5) | 979(100)
726 | 1211 | GTR | ZAFFRABAD | DGN031 | TG-DGN031A-3 | DT-3 | BALBIR NAGAR SCHOOL:K | 3 | 630 | 19506057 | 672 | 2019-06-11 22:00 | 199 | 822 | 224 | 943 | 249 | 1064 | 210 | 575 | 121.5 | 21 | 2.5 | 145 | 101% | 60% | 71% | 107% | 5.4471 | Loss 5-10% |  | 652(104.5) | 949(239.5) | 590(69.5) | 593(111)
727 | 1211 | GTR | ZAFFRABAD | DGN034 | TG-DGN034A-1 | DT-1 | LONI ROAD TIKONA PARK:PL | 2 | 630 | 19506828 | 573 | 2019-06-03 02:00 | 236 | 988 | 192 | 785 | 145 | 601 | 336 | 682.5 | 31 | 1.5 |  | 32.5 | 91% | 62% | 63% | 86% | 4.3398 | Loss 0-5% |  |  | 540(63)
728 | 1211 | GTR | ZAFFRABAD | DGN034 | TG-DGN034A-2 | DT-2 | LONI ROAD TIKONA PARK:PL | 2 | 630 | 19505075 | 508 | 2019-06-11 22:30 | 181 | 786 | 128 | 549 | 199 | 849 | 274 | 516.5 | 10 |  |  | 10 | 72% | 48% | 57% | 81% | 4.3398 | Loss 0-5%
729 | 1211 | GTR | ZAFFRABAD | DGN053 | TG-DGN053A-1 | DT-1 | EAST ROHTAS NAGAR:PL | 2 | 990 | 19501729 | 1084 | 2019-06-15 | 383 | 1567 | 372 | 1535 | 330 | 1350 | 202 | 561.5 | 126 | 28.5 | 3 | 157.5 | 109% | 69% | 65% | 98% | 4.3141 | Loss 0-5% |  | 925(54) | 1020(127) | 924(64.5)
730 | 1211 | GTR | ZAFFRABAD | DGN053 | TG-DGN053A-2 | DT-2 | EAST ROHTAS NAGAR:PL | 2 | 630 | 19505470 | 309 | 2019-06-11 23:00 | 50 | 204 | 119 | 487 | 140 | 567 | 330 | 720 |  |  |  | 0 | 49% | 31% | 40% | 49% | 4.3141 | Loss 0-5%
731 | 1220 | KNR | GAGAN VIHAR | JAG001 | TG-JAG001A-1 | DT-1 | ARAM PARK:PL | 1 | 990 | 19500853 | 1406 | 2019-06-11 23:00 | 463 | 1979 | 504 | 2156 | 439 | 1857 | 260 | 296.5 | 212 | 50 | 158.5 | 420.5 | 142% | 99% | 95% | 142% | 8.8418 | Loss 5-10% |  |  |  |  | 1083(178) | 948(72)
732 | 1220 | KNR | GAGAN VIHAR | JAG002 | TG-JAG002A-1 | DT-1 | BEDI MKT:ID | 3 | 990 | 19506105 | 1022 | 2019-06-03 02:00 | 303 | 1265 | 415 | 1772 | 304 | 1279 | 501 | 566 | 129.5 | 16 | 1.5 | 147 | 103% | 86% | 76% | 95% | 5.5705 | Loss 5-10% |  | 881(54) | 901(92) | 875(48.5)
733 | 1220 | KNR | GAGAN VIHAR | JAG002 | TG-JAG002A-2 | DT-2 | BEDI MKT:ID | 3 | 1600 | 19506104 | 2307 | 2019-06-08 23:00 | 457 | 1978 | 874 | 4198 | 976 | 4330 | 2289 | 554.5 | 123.5 | 31 | 5.5 | 160 | 107% | 80% | 74% | 144% | 5.5705 | Loss 5-10% |  | 1075(167) | 1167(278.5) | 1196(154) | 934(137.5)
734 | 1220 | KNR | GAGAN VIHAR | JAG002 | TG-JAG002A-3 | DT-3 | BEDI MKT:ID | 3 | 990 | 19506656 | 1057 | 2019-06-11 00:30 | 398 | 1668 | 337 | 1408 | 321 | 1339 | 300 | 549 | 129.5 | 31.5 | 4.5 | 165.5 | 107% | 84% | 72% | 104% | 5.5705 | Loss 5-10% |  |  | 948(120) | 928(39.5)
735 | 1220 | KNR | GAGAN VIHAR | JAG003 | TG-JAG003A-1 | DT-1 | BALDEV PARK:K | 2 | 990 | 19505023 | 664 | 2019-06-30 | 192 | 763 | 233 | 926 | 239 | 951 | 177 | 719 |  |  |  | 0 | 67% | 43% | 48% | 66% | 6.6039 | Loss 5-10%
736 | 1220 | KNR | GAGAN VIHAR | JAG003 | TG-JAG003A-2 | DT-2 | BALDEV PARK:K | 2 | 990 | 19500831 | 907.8625 | 2019-06-12 | 287.0211 | 1240.4751 | 313.2638 | 1351.2067 | 307.5776 | 1322.7436 | 99.5986 | 596.5 | 121 | 1.5 |  | 122.5 | 92% | 59% | 68% | 91% | 6.6039 | Loss 5-10% |  | 807(33.5) | 834(85)
737 | 1220 | KNR | GAGAN VIHAR | JAG004 | TG-JAG004A-1 | DT-1 | BALDEV PARK(PARK WALA):PL | 2 | 990 | 19504993 | 760 | 2019-06-30 23:30 | 182 | 801 | 239 | 1078 | 340 | 1537 | 643 | 693.5 | 26 |  |  | 26 | 75% | 49% | 51% | 77% | 6.7151 | Loss 5-10% |  |  | 782(34)
738 | 1220 | KNR | GAGAN VIHAR | JAG004 | TG-JAG004A-2 | DT-2 | BALDEV PARK(PARK WALA):PL | 2 | 630 | 19505834 | 640 | 2019-06-11 01:00 | 241 | 1080 | 288 | 1404 | 111 | 502 | 792 | 714 | 5 |  | 0.5 | 5.5 | 102% | 52% | 52% | 70% | 6.7151 | Loss 5-10%
739 | 1220 | KNR | GAGAN VIHAR | JAG005 | TG-JAG005A-1 | DT-1 | BRIJPURI:PL | 1 | 990 | 19500854 | 1081.0185 | 2019-06-30 02:00 | 413.5829 | 1807.2226 | 350.7725 | 1525.098 | 316.6631 | 1378.1742 | 377.6661 | 420.5 | 233 | 53 | 12.5 | 298.5 | 109% | 87% | 82% | 104% | 3.827 | Loss 0-5% |  | 949(195.5) | 1030(363.5) | 1006(278.5) | 889(177)
740 | 1220 | KNR | GAGAN VIHAR | JAG006 | TG-JAG006A-1 | DT-1 | CHANDER NAGAR:ID | 2 | 1600 | 19500790 | 895 | 2019-06-01 00:30 | 265 | 1112 | 350 | 1488 | 280 | 1199 | 341 | 720 |  |  |  | 0 | 56% | 40% | 43% | 55% | 15.4489 | Loss 10-20% |  |  | 902(54.5) | 874(73.5)
741 | 1220 | KNR | GAGAN VIHAR | JAG006 | TG-JAG006A-2 | DT-2 | CHANDER NAGAR:ID | 2 | 990 | 19500787 | 983 | 2019-06-11 18:30 | 296 | 1284 | 362 | 1590 | 325 | 1416 | 266 | 554 | 130 | 35.5 |  | 165.5 | 76% | 60% | 99% | 94% | 15.4489 | Loss 10-20% | 1464(403.5) |  |  |  | 1332(480.5) | 1134(212)
742 | 1220 | KNR | GAGAN VIHAR | JAG008 | TG-JAG008A-1 | DT-1 | GAGAN VIHAR:ID | 3 | 990 | 19506658 | 699 | 2019-06-03 13:00 | 225 | 962 | 234 | 1000 | 240 | 1024 | 55 | 719.5 | 0.5 |  |  | 0.5 | 66% | 49% | 71% | 66% | 5.504 | Loss 5-10%
743 | 1220 | KNR | GAGAN VIHAR | JAG008 | TG-JAG008A-2 | DT-2 | GAGAN VIHAR:ID | 3 | 990 | 19506108 | 889 | 2019-06-12 00:30 | 237 | 985 | 391 | 1659 | 262 | 1099 | 624 | 630.5 | 89.5 |  |  | 89.5 | 90% | 56% | 60% | 89% | 5.504 | Loss 5-10% |  |  | 981(91.5) | 832(31.5)
744 | 1220 | KNR | GAGAN VIHAR | JAG008 | TG-JAG008A-3 | DT-3 | GAGAN VIHAR:ID | 3 | 630 | 19505113 | 511 | 2019-06-03 | 156 | 672 | 125 | 531 | 230 | 1001 | 417 | 693 | 27 |  |  | 27 | 81% | 55% | 55% | 80% | 5.504 | Loss 5-10% |  |  | 566(57)
745 | 1220 | KNR | GAGAN VIHAR | JAG009 | TG-JAG009A-1 | DT-1 | GAGAN VIHAR EXT:ID | 2 | 990 | 19506647 | 706 | 2019-06-26 23:00 | 232 | 1009 | 216 | 931 | 258 | 1112 | 158 | 718 | 1.5 |  |  | 1.5 | 68% | 45% | 51% | 71% | 5.363 | Loss 5-10%
746 | 1220 | KNR | GAGAN VIHAR | JAG009 | TG-JAG009A-2 | DT-2 | GAGAN VIHAR EXT:ID | 2 | 990 | 19506155 | 1397 | 2019-06-11 01:30 | 464 | 1946 | 416 | 1740 | 517 | 2199 | 398 | 495.5 | 104 | 29 | 91 | 224 | 141% | 84% | 85% | 134% | 5.363 | Loss 5-10% |  | 972(102.5) | 1086(201.5) | 1008(113) | 911(51) | 857(42)
747 | 1220 | KNR | GAGAN VIHAR | JAG010 | TG-JAG010A-1 | DT-1 | GANDHI PARK:PL | 2 | 990 | 19500851 | 845 | 2019-06-11 00:30 | 222 | 966 | 227 | 963 | 395 | 1694 | 729 | 637.5 | 82 |  |  | 82 | 85% | 62% | 62% | 84% | 18.5044 | Loss 10-20% |  | 864(32.5) | 865(101.5) | 848(54)
748 | 1220 | KNR | GAGAN VIHAR | JAG010 | TG-JAG010A-2 | DT-2 | GANDHI PARK:PL | 2 | 990 | 19500750 | 869 | 2019-06-11 | 269 | 1143 | 278 | 1190 | 322 | 1366 | 203 | 640.5 | 78.5 |  |  | 78.5 | 88% | 66% | 63% | 84% | 18.5044 | Loss 10-20% |  |  | 813(43.5)
749 | 1220 | KNR | GAGAN VIHAR | JAG011 | TG-JAG011A-1 | DT-1 | GANESH PARK:PL | 2 | 990 | 19500776 | 1006.82 | 2019-06-30 | 267.321 | 1068.2586 | 338.3303 | 1370.924 | 401.1686 | 1630.1041 | 487.058 | 503 | 161.5 | 28.5 | 2 | 192 | 102% | 73% | 69% | 101% | 4.8945 | Loss 0-5% |  | 915(57.5) | 976(194.5) | 959(150.5)
750 | 1220 | KNR | GAGAN VIHAR | JAG011 | TG-JAG011A-2 | DT-2 | GANESH PARK:PL | 2 | 990 | 19505000 | 926 | 2019-06-30 | 303 | 1251 | 343 | 1409 | 280 | 1142 | 232 | 579 | 134.5 | 5.5 |  | 140 | 94% | 68% | 71% | 92% | 4.8945 | Loss 0-5% |  | 1003(86.5) | 1002(179.5) | 881(79) | 774(30)
751 | 1220 | KNR | GAGAN VIHAR | JAG012 | TG-JAG012A-1 | DT-1 | GOLDEN PARK:ID | 2 | 990 | 19502152 | 564 | 2019-06-03 | 201 | 882 | 174 | 763 | 189 | 825 | 103 | 720 |  |  |  | 0 | 57% | 45% | 53% | 57% | 21.1299 | Loss 20-30%
752 | 1220 | KNR | GAGAN VIHAR | JAG012 | TG-JAG012A-2 | DT-2 | GOLDEN PARK:ID | 2 | 990 | 19500817 | 827 | 2019-06-03 | 260 | 1135 | 262 | 1134 | 305 | 1312 | 178 | 647.5 | 72.5 |  |  | 72.5 | 84% | 56% | 67% | 83% | 21.1299 | Loss 20-30%
753 | 1220 | KNR | GAGAN VIHAR | JAG013 | TG-JAG013A-1 | DT-1 | GOPAL PARK:PL | 2 | 990 | 19506543 | 1408.0413 | 2019-06-02 02:00 | 492.6622 | 2114.4301 | 459.5723 | 1942.9766 | 455.8068 | 1954.7424 | 165.8838 | 468.5 | 111 | 53.5 | 83.5 | 248 | 142% | 92% | 88% | 129% | 5.9213 | Loss 5-10% |  |  |  |  | 982(103.5) | 820(28)
754 | 1220 | KNR | GAGAN VIHAR | JAG013 | TG-JAG013A-2 | DT-2 | GOPAL PARK:PL | 2 | 990 | 19506648 | 998.2955 | 2019-06-02 23:30 | 271.1006 | 1164.972 | 466.6589 | 2100.553 | 260.536 | 1140.8504 | 947.8721 | 589.5 | 118 | 10 | 0.5 | 128.5 | 99% | 62% | 66% | 101% | 5.9213 | Loss 5-10%
755 | 1220 | KNR | GAGAN VIHAR | JAG016 | TG-JAG016A-1 | DT-1 | GOVIND PURA(OLD):ID | 2 | 990 | 19503083 | 758 | 2019-06-03 00:30 | 209 | 928 | 190 | 840 | 359 | 1594 | 714 | 713.5 | 6.5 |  |  | 6.5 | 77% | 54% | 56% | 72% | 6.7925 | Loss 5-10%
756 | 1220 | KNR | GAGAN VIHAR | JAG016 | TG-JAG016A-2 | DT-2 | GOVIND PURA(OLD):ID | 2 | 990 | 19505580 | 884 | 2019-06-10 03:00 | 320 | 1330 | 313 | 1296 | 251 | 1025 | 290 | 632.5 | 87.5 |  |  | 87.5 | 89% | 64% | 61% | 83% | 6.7925 | Loss 5-10% |  |  | 920(63.5)
757 | 1220 | KNR | GAGAN VIHAR | JAG018 | TG-JAG018A-1 | DT-1 | JAGAT PURI A BLK:PL | 3 | 990 | 19504763 | 870 | 2019-06-30 01:00 | 258 | 1051 | 280 | 1130 | 331 | 1344 | 262 | 646 | 74 |  |  | 74 | 88% | 69% | 71% | 81% | 4.2076 | Loss 0-5% |  | 960(127.5) | 1128(315) | 938(79.5) | 927(158.5) | 774(30)
758 | 1220 | KNR | GAGAN VIHAR | JAG018 | TG-JAG018A-2 | DT-2 | JAGAT PURI A BLK:PL | 3 | 630 | 19506823 | 464 | 2019-06-30 01:00 | 221 | 896 | 123 | 498 | 120 | 481 | 406 | 717 | 3 |  |  | 3 | 74% | 60% | 61% | 72% | 4.2076 | Loss 0-5%
759 | 1220 | KNR | GAGAN VIHAR | JAG018 | TG-JAG018A-3 | DT-3 | JAGAT PURI A BLK:PL | 3 | 630 | 19505712 | 824 | 2019-06-30 06:00 | 307 | 1262 | 283 | 1142 | 234 | 944 | 278 | 481.5 | 153.5 | 48 | 36.5 | 238 | 125% | 131% | 81% | 117% | 4.2076 | Loss 0-5%
760 | 1220 | KNR | GAGAN VIHAR | JAG020 | TG-JAG020A-1 | DT-1 | JAGAT PURI F BLK:PL | 2 | 990 | 19506790 | 930 | 2019-06-30 14:00 | 351 | 1433 | 290 | 1175 | 289 | 1182 | 254 | 451.5 | 267.5 | 1 |  | 268.5 | 87% | 66% | 94% | 87% | 7.4305 | Loss 5-10% |  | 962(171.5) | 942(124) | 789(24) | 782(27)
761 | 1220 | KNR | GAGAN VIHAR | JAG020 | TG-JAG020A-2 | DT-2 | JAGAT PURI F BLK:PL | 2 | 990 | 19506785 | 430 | 2019-06-15 15:30 | 151 | 633 | 132 | 548 | 146 | 608 | 75 | 720 |  |  |  | 0 | 24% | 19% | 43% | 25% | 7.4305 | Loss 5-10%
762 | 1220 | KNR | GAGAN VIHAR | JAG022 | TG-JAG022A-1 | DT-1 | JITAR NAGAR:K | 2 | 990 | 19506657 | 693 | 2019-06-30 | 226 | 905 | 171 | 692 | 296 | 1193 | 436 | 719 | 0.5 |  |  | 0.5 | 70% | 50% | 52% | 69% | 5.1934 | Loss 5-10%
763 | 1220 | KNR | GAGAN VIHAR | JAG022 | TG-JAG022A-2 | DT-2 | JITAR NAGAR:K | 2 | 990 | 19506650 | 1053 | 2019-06-18 17:00 | 477 | 2083 | 394 | 1927 | 183 | 793 | 1219 | 531.5 | 146.5 | 39.5 | 2 | 188 | 101% | 66% | 106% | 101% | 5.1934 | Loss 5-10% |  | 883(61) | 938(126.5) | 899(70.5)
764 | 1220 | KNR | GAGAN VIHAR | JAG023 | TG-JAG023A-1 | DT-1 | KHUREJI:ID | 2 | 630 | 19506153 | 544 | 2019-06-12 | 193 | 801 | 179 | 741 | 171 | 712 | 79 | 567 | 152 |  |  | 152 | 86% | 73% | 78% | 84% | 8.8305 | Loss 5-10% |  |  |  | 529(83)
765 | 1220 | KNR | GAGAN VIHAR | JAG023 | TG-JAG023A-2 | DT-2 | KHUREJI:ID | 2 | 990 | 19503528 | 1014 | 2019-06-30 | 298 | 1265 | 361 | 1555 | 355 | 1528 | 278 | 302 | 356.5 | 56.5 | 3.5 | 416.5 | 102% | 89% | 90% | 100% | 8.8305 | Loss 5-10% |  | 934(233) | 991(485) | 989(397.5) | 942(253.5) | 788(34)
766 | 1220 | KNR | GAGAN VIHAR | JAG024 | TG-JAG024A-1 | DT-1 | MAUSAM VIHAR:ID | 2 | 990 | 19505935 | 540 | 2019-06-12 00:30 | 181 | 754 | 174 | 728 | 184 | 767 | 34 | 720 |  |  |  | 0 | 55% | 36% | 40% | 53% | 4.3993 | Loss 0-5%
767 | 1220 | KNR | GAGAN VIHAR | JAG024 | TG-JAG024A-2 | DT-2 | MAUSAM VIHAR:ID | 2 | 630 | 19505721 | 533 | 2019-06-11 00:30 | 202 | 861 | 149 | 633 | 183 | 785 | 202 | 683.5 | 36 |  |  | 36 | 85% | 50% | 57% | 81% | 4.3993 | Loss 0-5% |  |  | 522(40)
768 | 1220 | KNR | GAGAN VIHAR | JAG025 | TG-JAG025A-1 | DT-1 | NEW LAYALPUR:K | 3 | 990 | 19506786 | 931 | 2019-06-01 00:30 | 271 | 1160 | 293 | 1262 | 367 | 1594 | 394 | 609 | 103.5 | 7.5 |  | 111 | 94% | 60% | 93% | 94% | 7.2161 | Loss 5-10%
769 | 1220 | KNR | GAGAN VIHAR | JAG025 | TG-JAG025A-2 | DT-2 | NEW LAYALPUR:K | 3 | 990 | 19506781 | 904 | 2019-06-30 | 275 | 1151 | 247 | 1038 | 382 | 1639 | 553 | 610 | 107 | 1 |  | 108 | 91% | 61% | 65% | 91% | 7.2161 | Loss 5-10% |  | 891(24.5) | 1130(210.5) | 1153(111)
770 | 1220 | KNR | GAGAN VIHAR | JAG025 | TG-JAG025A-3 | DT-3 | NEW LAYALPUR:K | 3 | 630 | 19506855 | 492 | 2019-06-10 23:00 | 127 | 578 | 168 | 767 | 197 | 904 | 283 | 711 | 9 |  |  | 9 | 75% | 52% | 48% | 78% | 7.2161 | Loss 5-10%
771 | 1220 | KNR | GAGAN VIHAR | JAG027 | TG-JAG027A-1 | DT-1 | RADHEY SHAYAM PARK:PL | 1 | 990 | 19506867 | 1075 | 2019-06-11 00:30 | 329 | 1400 | 515 | 2252 | 231 | 986 | 1118 | 556 | 130.5 | 28.5 | 4 | 163 | 109% | 63% | 63% | 105% | 4.6912 | Loss 0-5% | 860(40.5) | 1148(194) | 1219(296.5) |  | 1028(199.5) | 931(48)
772 | 1220 | KNR | GAGAN VIHAR | JAG028 | TG-JAG028A-1 | DT-1 | RAM NAGAR EXT:K | 2 | 990 | 19505825 | 883 | 2019-06-12 02:00 | 269 | 1076 | 379 | 1529 | 235 | 941 | 533 | 668 | 51.5 |  |  | 51.5 | 89% | 55% | 56% | 81% | 13.9584 | Loss 10-20% |  | 878(53.5) | 1231(226.5) | 1122(164.5) | 1047(102.5)
773 | 1220 | KNR | GAGAN VIHAR | JAG028 | TG-JAG028A-2 | DT-2 | RAM NAGAR EXT:K | 2 | 1600 | 19506788 | 882 | 2019-06-12 00:30 | 257 | 1075 | 244 | 1025 | 381 | 1619 | 571 | 720 |  |  |  | 0 | 55% | 34% | 46% | 54% | 13.9584 | Loss 10-20% | [5 empty] | 586(32)
774 | 1220 | KNR | GAGAN VIHAR | JAG029 | TG-JAG029A-1 | DT-1 | SHIV PURI:PM | 1 | 990 | 19506151 | 976 | 2019-06-29 23:00 | 320 | 1424 | 407 | 1856 | 249 | 1106 | 652 | 587.5 | 127 | 3.5 |  | 130.5 | 93% | 62% | 88% | 99% | 7.0254 | Loss 5-10%
775 | 1220 | KNR | GAGAN VIHAR | JAG030 | TG-JAG030A-1 | DT-1 | SILVER PARK:ID | 1 | 990 | 19506008 | 944 | 2019-06-02 15:30 | 202 | 907 | 373 | 1742 | 369 | 1702 | 815 | 627 | 88 | 2 |  | 90 | 95% | 65% | 95% | 88% | 14.4604 | Loss 10-20% |  | 804(38.5) | 920(204) | 971(49)
776 | 1220 | KNR | GAGAN VIHAR | JAG031 | TG-JAG031A-1 | DT-1 | SOUTH ANARKALI:PL | 3 | 990 | 19506660 | 1035 | 2019-06-05 02:30 | 346 | 1464 | 378 | 1597 | 311 | 1301 | 256 | 545.5 | 133 | 35.5 | 2 | 170.5 | 105% | 70% | 71% | 98% | 5.5306 | Loss 5-10%
777 | 1220 | KNR | GAGAN VIHAR | JAG031 | TG-JAG031A-2 | DT-2 | SOUTH ANARKALI:PL | 3 | 990 | 19506868 | 1166 | 2019-06-10 00:30 | 395 | 1779 | 355 | 1587 | 416 | 1875 | 254 | 497.5 | 131 | 55.5 | 32.5 | 219 | 118% | 89% | 74% | 112% | 5.5306 | Loss 5-10% | 882(35) | 1165(162.5) | 1042(183) | 1066(151) | 943(107.5)
778 | 1220 | KNR | GAGAN VIHAR | JAG031 | TG-JAG031A-3 | DT-3 | SOUTH ANARKALI:PL | 3 | 630 | 19506472 | 712 | 2019-06-10 00:30 | 266 | 1192 | 226 | 1001 | 220 | 981 | 202 | 497.5 | 136 | 61 | 22 | 219 | 113% | 86% | 76% | 112% | 5.5306 | Loss 5-10% |  |  | 524(40)
779 | 1220 | KNR | GAGAN VIHAR | JAG032 | TG-JAG032A-1 | DT-1 | SOUTH ANARKALI (NALAH):PL | 1 | 990 | 19506107 | 778 | 2019-06-11 00:30 | 254 | 1111 | 231 | 999 | 293 | 1276 | 242 | 690.5 | 29.5 |  |  | 29.5 | 79% | 54% | 54% | 77% | 6.2049 | Loss 5-10% |  | 872(52) | 935(102.5) | 961(68.5)
780 | 1220 | KNR | GAGAN VIHAR | JAG034 | TG-JAG034A-1 | DT-1 | JAGAT PURI G BLK:PL | 2 | 990 | 19505835 | 971 | 2019-06-30 | 299 | 1282 | 331 | 1432 | 342 | 1483 | 180 | 588.5 | 124 | 7.5 |  | 131.5 | 98% | 64% | 62% | 96% | 5.5243 | Loss 5-10% |  | 912(72) | 1049(170) | 1018(111.5) | 854(67)
781 | 1220 | KNR | GAGAN VIHAR | JAG034 | TG-JAG034A-2 | DT-2 | JAGAT PURI G BLK:PL | 2 | 990 | 19505711 | 818 | 2019-06-11 23:30 | 237 | 995 | 351 | 1474 | 230 | 958 | 499 | 650.5 | 69.5 |  |  | 69.5 | 82% | 58% | 56% | 83% | 5.5243 | Loss 5-10%
782 | 1220 | KNR | GAGAN VIHAR | JAG039 | TG-JAG039A-1 | DT-1 | R.S. PARK (PARKWALA) | 2 | 990 | 19505833 | 1009.759 | 2019-06-11 00:30 | 329.1388 | 1437.35 | 360.5541 | 1575.0223 | 320.0661 | 1411.6618 | 152.1515 | 538 | 143 | 30.5 | 4 | 177.5 | 102% | 72% | 71% | 99% | 9.419 | Loss 5-10% |  | 1063(85.5) | 983(167.5) |  | 813(54)
783 | 1220 | KNR | GAGAN VIHAR | JAG039 | TG-JAG039A-2 | DT-2 | R.S. PARK (PARKWALA) | 2 | 630 | 19506106 | 584 | 2019-06-11 23:30 | 141 | 577 | 177 | 728 | 266 | 1120 | 486 | 627.5 | 87.5 | 3 |  | 90.5 | 92% | 72% | 59% | 93% | 9.419 | Loss 5-10%
784 | 1220 | KNR | GANDHI NAGAR | GAN001 | TG-GAN001A-1 | DT-1 | AHATA KARAM CHAND:PL | 1 | 990 | 19505208 | 759 | 2019-06-30 16:00 | 247 | 1054 | 284 | 1207 | 228 | 948 | 225 | 680 | 40 |  |  | 40 | 48% | 60% | 77% | 66% | 15.4387 | Loss 10-20% | 776(106) | 1226(184.5) | 1220(145) | 816(150.5) | 785(98) | 825(102.5)
785 | 1220 | KNR | GANDHI NAGAR | GAN002 | TG-GAN002A-1 | DT-1 | AJIT NAGAR GALI NO 8:PL | 1 | 990 | 19506803 | 924 | 2019-06-02 12:30 | 311 | 1362 | 285 | 1232 | 328 | 1428 | 172 | 439 | 275 | 5.5 |  | 280.5 | 76% | 72% | 93% | 83% | 14.8639 | Loss 10-20%
786 | 1220 | KNR | GANDHI NAGAR | GAN003 | TG-GAN003A-1 | DT-1 | AMAR MOHALLA:PL | 2 | 990 | 19506101 | 1237 | 2019-06-30 17:30 | 457 | 2015 | 378 | 1640 | 402 | 1740 | 336 | 443.5 | 218.5 | 53.5 | 3 | 275 | 70% | 66% | 125% | 84% | 15.1922 | Loss 10-20% | 765(85) | 927(224.5) | 1021(277.5) | 980(268) | 968(170.5) | 844(50.5)
787 | 1220 | KNR | GANDHI NAGAR | GAN003 | TG-GAN003A-2 | DT-2 | AMAR MOHALLA:PL | 2 | 630 | 19506348 | 532 | 2019-06-02 16:00 | 156 | 664 | 160 | 671 | 217 | 939 | 272 | 682 | 36.5 |  |  | 36.5 | 58% | 60% | 84% | 71% | 15.1922 | Loss 10-20% | 555(237) | 879(348.5) | 676(378) | 952(359.5) |  | 611(316.5)
788 | 1220 | KNR | GANDHI NAGAR | GAN005 | TG-GAN005A-1 | DT-1 | CHEMALI DEVI (INSIDE):PL | 1 | 990 | 19500172 | 947 | 2019-06-30 16:00 | 313 | 1345 | 320 | 1369 | 314 | 1350 | 21 | 482.5 | 223 | 14.5 |  | 237.5 | 73% | 57% | 96% | 75% | 11.8238 | Loss 10-20% | 790(62) | 997(203.5) | 1036(292.5) | 1027(267) | 955(189) | 779(39)
789 | 1220 | KNR | GANDHI NAGAR | GAN007 | TG-GAN007A-1 | DT-1 | DUDLELA CHOWK:PL | 2 | 990 | 19506102 | 796 | 2019-06-02 14:30 | 227 | 994 | 271 | 1198 | 298 | 1315 | 282 | 678.5 | 41.5 |  |  | 41.5 | 62% | 60% | 80% | 67% | 9.0319 | Loss 5-10%
790 | 1220 | KNR | GANDHI NAGAR | GAN007 | TG-GAN007A-2 | DT-2 | DUDLELA CHOWK:PL | 2 | 990 | 19506103 | 733 | 2019-06-28 09:00 | 217 | 931 | 264 | 1130 | 252 | 1074 | 178 | 714.5 | 5.5 |  |  | 5.5 | 69% | 60% | 74% | 71% | 9.0319 | Loss 5-10% |  |  | 766(42.5)
791 | 1220 | KNR | GANDHI NAGAR | GAN008 | TG-GAN008A-1 | DT-1 | GALI GURDWARA NO. 2:ID | 4 | 990 | 19506797 | 725 | 2019-06-30 15:00 | 267 | 1131 | 242 | 1026 | 216 | 902 | 199 | 717.5 | 2.5 |  |  | 2.5 | 47% | 40% | 73% | 49% | 4.6064 | Loss 0-5% |  | 930(67.5) | 996(217.5) | 965(219.5) | 916(183) | 826(146.5)
792 | 1220 | KNR | GANDHI NAGAR | GAN008 | TG-GAN008A-2 | DT-2 | GALI GURDWARA NO. 2:ID | 4 | 1600 | 19506796 | 1217 | 2019-06-02 16:00 | 406 | 1692 | 388 | 1619 | 423 | 1753 | 116 | 689.5 | 30.5 |  |  | 30.5 | 60% | 50% | 76% | 63% | 4.6064 | Loss 0-5% | 863(152.5) | 1030(372.5) | 1092(474) | 1025(422) | 1015(334) | 881(219.5)
793 | 1220 | KNR | GANDHI NAGAR | GAN008 | TG-GAN008A-3 | DT-3 | GALI GURDWARA NO. 2:ID | 4 | 400 | 19505541 | 393 | 2019-06-30 15:00 | 142 | 599 | 101 | 427 | 149 | 640 | 196 | 537.5 | 163.5 | 15.5 |  | 179 | 27% | 34% | 98% | 38% | 4.6064 | Loss 0-5% | 413(249) | 532(286) | 548(261) | 405(232) | 407(212.5) | 384(215)
794 | 1220 | KNR | GANDHI NAGAR | GAN008 | TG-GAN008A-4 | DT-4 | GALI GURDWARA NO. 2:ID | 4 | 400 | 19504381 | 322 | 2019-06-02 16:30 | 67 | 277 | 152 | 652 | 104 | 440 | 326 | 632 | 84.5 |  |  | 84.5 | 16% | 21% | 81% | 27% | 4.6064 | Loss 0-5% |  |  |  | 322(87) | 327(104.5) | 304(26.5)
795 | 1220 | KNR | GANDHI NAGAR | GAN010 | TG-GAN010A-1 | DT-1 | GANDHI NAGAR POLICE ST.:PL | 2 | 990 | 19506799 | 786 | 2019-06-02 15:00 | 230 | 1024 | 324 | 1440 | 233 | 1025 | 416 | 658 | 61 |  |  | 61 | 18% | 21% | 79% | 25% | 5.0528 | Loss 5-10% |  |  | 865(172) | 830(46)
796 | 1220 | KNR | GANDHI NAGAR | GAN010 | TG-GAN010A-2 | DT-2 | GANDHI NAGAR POLICE ST.:PL | 2 | 990 | 19506802 | 832 | 2019-06-29 15:00 | 282 | 1229 | 204 | 884 | 346 | 1524 | 555 | 608.5 | 110.5 |  |  | 110.5 | 16% | 24% | 84% | 25% | 5.0528 | Loss 5-10% |  |  |  | 796(57) | 802(95.5) | 771(52)
797 | 1220 | KNR | GANDHI NAGAR | GAN012 | TG-GAN012A-1 | DT-1 | JANTA PARK NO. 1:PL | 3 | 990 | 19505864 | 1057 | 2019-06-30 11:30 | 314 | 1369 | 360 | 1571 | 383 | 1683 | 275 | 585.5 | 131.5 |  | 0.5 | 132 | 11% | 19% | 107% | 19% | 6.8672 | Loss 5-10% |  | 1032(103.5) | 1091(181) | 890(137.5) | 862(148.5) | 786(53)
798 | 1220 | KNR | GANDHI NAGAR | GAN012 | TG-GAN012A-2 | DT-2 | JANTA PARK NO. 1:PL | 3 | 990 | 19506604 | 810 | 2019-06-28 17:00 | 259 | 1116 | 298 | 1279 | 253 | 1087 | 180 | 618 | 99.5 |  |  | 99.5 | 9% | 14% | 82% | 15% | 6.8672 | Loss 5-10% | 925(114.5) | 1096(215.5) | 1120(220.5) |  | 1074(36) | 1080(240)
799 | 1220 | KNR | GANDHI NAGAR | GAN012 | TG-GAN012A-3 | DT-3 | JANTA PARK NO. 1:PL | 3 | 990 | 19505184 | 805 | 2019-06-30 14:30 | 362 | 1744 | 219 | 993 | 224 | 971 | 763 | 657 | 60.5 |  |  | 60.5 | 4% | 5% | 81% | 11% | 6.8672 | Loss 5-10% |  | 807(41.5)
800 | 1220 | KNR | GANDHI NAGAR | GAN014 | TG-GAN014A-1 | DT-1 | KAILASH NAGAR NO. 1:PL | 3 | 990 | 19505517 | 811 | 2019-06-26 14:30 | 262 | 1117 | 266 | 1136 | 283 | 1200 | 76 | 675 | 45 |  |  | 45 | 76% | 49% | 82% | 76% | 5.0521 | Loss 5-10%
801 | 1220 | KNR | GANDHI NAGAR | GAN014 | TG-GAN014A-2 | DT-2 | KAILASH NAGAR NO. 1:PL | 3 | 990 | 19505862 | 675 | 2019-06-29 23:00 | 243 | 1021 | 208 | 878 | 224 | 943 | 124 | 373 |  |  |  | 0 | 65% | 43% | 65% | 68% | 5.0521 | Loss 5-10% |  |  |  | 1003(65)
802 | 1220 | KNR | GANDHI NAGAR | GAN014 | TG-GAN014A-3 | DT-3 | KAILASH NAGAR NO. 1:PL | 3 | 990 | 19506861 | 598 | 2019-06-01 15:30 | 175 | 745 | 221 | 945 | 203 | 867 | 175 | 720 |  |  |  | 0 | 46% | 42% | 60% | 48% | 5.0521 | Loss 5-10% |  |  | 812(51)
803 | 1220 | KNR | GANDHI NAGAR | GAN015 | TG-GAN015A-1 | DT-1 | KAILASH NAGAR NO. 15:PL | 3 | 990 | 19505931 | 846 | 2019-06-03 01:00 | 208 | 857 | 285 | 1184 | 354 | 1467 | 529 | 639 | 81 |  |  | 81 | 85% | 57% | 76% | 85% | 3.9055 | Loss 0-5% |  |  | 843(130)
804 | 1220 | KNR | GANDHI NAGAR | GAN015 | TG-GAN015A-2 | DT-2 | KAILASH NAGAR NO. 15:PL | 3 | 990 | 19505011 | 746 | 2019-06-30 15:00 | 242 | 1020 | 237 | 1040 | 267 | 1152 | 123 | 698.5 | 21 |  |  | 21 | 63% | 56% | 75% | 65% | 3.9055 | Loss 0-5% |  | 807(55.5) | 855(160) | 874(136) | 786(101)
805 | 1220 | KNR | GANDHI NAGAR | GAN015 | TG-GAN015A-3 | DT-3 | KAILASH NAGAR NO. 15:PL | 3 | 990 | 19506875 | 795 | 2019-06-30 14:00 | 369 | 1672 | 208 | 860 | 218 | 929 | 779 | 693.5 | 26 |  |  | 26 | 73% | 53% | 80% | 75% | 3.9055 | Loss 0-5% | 781(87) | 1021(356)
806 | 1220 | KNR | GANDHI NAGAR | GAN016 | TG-GAN016A-1 | DT-1 | KAILASH NAGAR SCHOOL:PL | 2 | 990 | 19506801 | 953 | 2019-06-30 14:00 | 276 | 1178 | 328 | 1446 | 350 | 1601 | 370 | 506 | 191.5 | 22.5 |  | 214 | 42% | 43% | 96% | 52% | 5.437 | Loss 5-10% |  |  | 782(44.5) | 744(35.5)
807 | 1220 | KNR | GANDHI NAGAR | GAN016 | TG-GAN016A-2 | DT-2 | KAILASH NAGAR SCHOOL:PL | 2 | 630 | 19506645 | 297 | 2019-06-01 16:30 | 85 | 353 | 87 | 373 | 126 | 533 | 171 | 720 |  |  |  | 0 | 22% | 22% | 47% | 26% | 5.437 | Loss 5-10%
808 | 1220 | KNR | GANDHI NAGAR | GAN023 | TG-GAN023A-1 | DT-1 | PEEPAL WALA SCHOOL:PL | 2 | 990 | 19506794 | 811 | 2019-06-02 12:00 | 275 | 1127 | 259 | 1061 | 276 | 1132 | 68 | 638.5 | 81.5 |  |  | 81.5 | 29% | 31% | 82% | 40% | 3.806 | Loss 0-5% |  | 901(58.5) | 858(143.5) | 808(78.5) | 878(146.5) | 851(162.5)
809 | 1220 | KNR | GANDHI NAGAR | GAN023 | TG-GAN023A-2 | DT-2 | PEEPAL WALA SCHOOL:PL | 2 | 630 | 19506795 | 575 | 2019-06-02 17:30 | 302 | 1283 | 127 | 525 | 146 | 597 | 725 | 666 | 53.5 | 0.5 |  | 54 | 15% | 33% | 91% | 32% | 3.806 | Loss 0-5% |  |  | 527(55.5) | 507(57) | 542(127.5) | 522(143)
810 | 1220 | KNR | GANDHI NAGAR | GAN024 | TG-GAN024A-1 | DT-1 | R. PURA GALI NO. 8:PL | 1 | 990 | 19506002 | 920 | 2019-06-02 15:30 | 300 | 1229 | 311 | 1286 | 309 | 1279 | 54 | 542.5 | 174 | 3.5 |  | 177.5 | 48% | 43% | 93% | 66% | 10.9652 | Loss 10-20% | 790(55) | 950(176.5) | 969(487) |  | 937(231) | 913(186)
811 | 1220 | KNR | GANDHI NAGAR | GAN025 | TG-GAN025A-1 | DT-1 | R.PURA GALI NO 6 (IN SIDE):PL | 1 | 990 | 19506600 | 1025 | 2019-06-01 12:30 | 333 | 1403 | 335 | 1423 | 356 | 1516 | 105 | 468 | 178 | 72.5 | 1.5 | 252 | 30% | 47% | 103% | 64% | 6.8535 | Loss 5-10% | 973(263) | 1151(291.5) | 1278(275.5) |  | 1044(43) | 1149(287)
812 | 1220 | KNR | GANDHI NAGAR | GAN028 | TG-GAN028A-1 | DT-1 | SEELAMPUR OLD PR. SCHOOL NO. 1:K | 4 | 990 | 19505116 | 907 | 2019-06-02 16:30 | 310 | 1292 | 305 | 1288 | 292 | 1244 | 46 | 642.5 | 74.5 | 3 |  | 77.5 | 81% | 78% | 92% | 82% | 18.9796 | Loss 10-20% |  | 913(257.5) | 954(444) | 932(473.5) |  | 829(244)
813 | 1220 | KNR | GANDHI NAGAR | GAN028 | TG-GAN028A-2 | DT-2 | SEELAMPUR OLD PR. SCHOOL NO. 1:K | 4 | 990 | 19505099 | 823 | 2019-06-01 16:30 | 321 | 1413 | 252 | 1112 | 250 | 1105 | 304 | 640.5 | 79.5 |  |  | 79.5 | 62% | 68% | 83% | 74% | 18.9796 | Loss 10-20% |  | 773(33) | 774(39.5)
814 | 1220 | KNR | GANDHI NAGAR | GAN028 | TG-GAN028A-3 | DT-3 | SEELAMPUR OLD PR. SCHOOL NO. 1:K | 4 | 630 | 19505100 | 492 | 2019-06-18 01:30 | 245 | 1028 | 97 | 396 | 149 | 611 | 556 | 706.5 | 11 |  |  | 11 | 78% | 76% | 78% | 68% | 18.9796 | Loss 10-20% | 583(45) | 593(186) | 662(190) | 605(198) | 565(149.5) | 610(108.5)
815 | 1220 | KNR | GANDHI NAGAR | GAN028 | TG-GAN028A-4 | DT-4 | SEELAMPUR OLD PR. SCHOOL NO. 1:K | 4 | 990 | 19505119 | 683 | 2019-06-26 11:30 | 230 | 965 | 230 | 957 | 222 | 934 | 28 | 720 |  |  |  | 0 | 37% | 45% | 69% | 58% | 18.9796 | Loss 10-20%
816 | 1220 | KNR | GANDHI NAGAR | GAN029 | TG-GAN029A-1 | DT-1 | SEELAMPUR PHATAK:PL | 2 | 990 | 19506480 | 965 | 2019-06-29 15:00 | 292 | 1292 | 360 | 1583 | 313 | 1399 | 255 | 402 | 148 | 3 |  | 151 | 59% | 77% | 97% | 68% | 65.3141 | Loss >30% | 1063(422.5) |  | 1265(247) |  | 1364(597) | 1251(527)
817 | 1220 | KNR | GANDHI NAGAR | GAN029 | TG-GAN029A-2 | DT-2 | SEELAMPUR PHATAK:PL | 2 | 630 | 19505653 | 384.1368 | 2019-06-28 18:00 | 85.2976 | 347.3878 | 165.7628 | 681.9271 | 133.0764 | 542.3719 | 291.0421 | 130 |  |  |  | 0 | 41% | 52% | 61% | 49% | 65.3141 | Loss >30% |  |  | 815(59)
818 | 1220 | KNR | GANDHI NAGAR | GAN032 | TG-GAN032A-1 | DT-1 | SHIV KUTI R.L.G. NO. 1:ID | 7 | 990 | 19502033 | 658 | 2019-06-01 12:30 | 227 | 989 | 197 | 850 | 235 | 1020 | 156 | 720 |  |  |  | 0 | 16% | 17% | 67% | 41% | 10.0398 | Loss 10-20% |  | 810(39) | 803(46.5) | 815(148) | 851(152) | 817(144.5)
819 | 1220 | KNR | GANDHI NAGAR | GAN032 | TG-GAN032A-2 | DT-2 | SHIV KUTI R.L.G. NO. 1:ID | 7 | 990 | 19506574 | 863 | 2019-06-30 16:00 | 262 | 1107 | 311 | 1312 | 289 | 1215 | 178 | 565.5 | 154.5 |  |  | 154.5 | 29% | 16% | 87% | 18% | 10.0398 | Loss 10-20% |  | 940(172.5) | 910(25) |  |  | 939(205.5)
820 | 1220 | KNR | GANDHI NAGAR | GAN032 | TG-GAN032A-3 | DT-3 | SHIV KUTI R.L.G. NO. 1:ID | 7 | 990 | 19505443 | 692 | 2019-06-02 16:00 | 270 | 1133 | 214 | 898 | 208 | 865 | 253 | 720 |  |  |  | 0 | 13% | 21% | 70% | 24% | 10.0398 | Loss 10-20%
821 | 1220 | KNR | GANDHI NAGAR | GAN032 | TG-GAN032A-4 | DT-4 | SHIV KUTI R.L.G. NO. 1:ID | 7 | 990 | 19505384 | 1009 | 2019-06-02 12:00 | 329 | 1389 | 375 | 1585 | 305 | 1291 | 259 | 470 | 173 | 76.5 | 0.5 | 250 | 36% | 52% | 102% | 59% | 10.0398 | Loss 10-20% |  | 863(106.5) | 901(189) | 866(208) | 881(195) | 879(206)
822 | 1220 | KNR | GANDHI NAGAR | GAN032 | TG-GAN032A-5 | DT-5 | SHIV KUTI R.L.G. NO. 1:ID | 7 | 990 | 19505393 | 666 | 2019-06-02 12:00 | 192 | 822 | 271 | 1156 | 203 | 870 | 313 | 720 |  |  |  | 0 | 17% | 31% | 67% | 34% | 10.0398 | Loss 10-20% | 736(28.5) | 834(87.5)
823 | 1220 | KNR | GANDHI NAGAR | GAN032 | TG-GAN032A-6 | DT-6 | SHIV KUTI R.L.G. NO. 1:ID | 7 | 990 | 19505140 | 795 | 2019-06-26 16:00 | 276 | 1160 | 215 | 902 | 304 | 1281 | 335 | 601.5 | 118.5 |  |  | 118.5 | 13% | 13% | 80% | 40% | 10.0398 | Loss 10-20% |  | 979(152.5) | 1088(233.5) | 977(241) | 1084(239) | 1007(238.5)
824 | 1220 | KNR | GANDHI NAGAR | GAN032 | TG-GAN032A-7 | DT-7 | SHIV KUTI R.L.G. NO. 1:ID | 7 | 630 | 19505967 | 284 | 2019-06-02 12:00 | 64 | 274 | 104 | 442 | 116 | 492 | 198 | 720 |  |  |  | 0 | 15% | 19% | 45% | 27% | 10.0398 | Loss 10-20%
825 | 1220 | KNR | GANDHI NAGAR | GAN033 | TG-GAN033A-1 | DT-1 | SUBHASH MOHALLA NO.1:PM | 4 | 990 | 19505968 | 707 | 2019-06-30 16:30 | 230 | 994 | 232 | 999 | 245 | 1047 | 51 | 712.5 | 7 |  |  | 7 | 26% | 30% | 71% | 45% | 7.4512 | Loss 5-10% | 926(230) | 1095(267.5) | 1133(246) | 991(249.5) | 1017(222.5) | 928(221.5)
826 | 1220 | KNR | GANDHI NAGAR | GAN033 | TG-GAN033A-2 | DT-2 | SUBHASH MOHALLA NO.1:PM | 4 | 990 | 19505124 | 855 | 2019-06-01 18:00 | 301 | 1242 | 294 | 1208 | 260 | 1056 | 172 | 570 | 147.5 |  |  | 147.5 | 42% | 41% | 86% | 59% | 7.4512 | Loss 5-10% |  | 863(153.5) | 1002(204) | 859(223.5) | 870(183) | 824(147.5)
827 | 1220 | KNR | GANDHI NAGAR | GAN033 | TG-GAN033A-3 | DT-3 | SUBHASH MOHALLA NO.1:PM | 4 | 990 | 19506659 | 863 | 2019-06-01 12:00 | 268 | 1125 | 294 | 1245 | 300 | 1269 | 133 | 555 | 164.5 |  |  | 164.5 | 30% | 41% | 87% | 50% | 7.4512 | Loss 5-10% | 1153(279) | 1166(219.5) | 920(164) | 942(239) | 948(205)
828 | 1220 | KNR | GANDHI NAGAR | GAN033 | TG-GAN033A-4 | DT-4 | SUBHASH MOHALLA NO.1:PM | 4 | 990 | 19505135 | 926 | 2019-06-23 15:30 | 298 | 1237 | 323 | 1337 | 305 | 1271 | 89 | 659 | 60.5 | 0.5 |  | 61 | 59% | 47% | 94% | 73% | 7.4512 | Loss 5-10% |  |  | 530(96.5) | 526(130) | 507(78) | 468(34.5)
829 | 1220 | KNR | GANDHI NAGAR | GAN034 | TG-GAN034A-1 | DT-1 | AJIT NAGAR GALI NO 10:PL | 2 | 990 | 19506811 | 757 | 2019-06-29 22:00 | 273 | 1137 | 270 | 1127 | 214 | 894 | 239 | 691 | 27.5 |  |  | 27.5 | 71% | 64% | 75% | 76% | 12.4562 | Loss 10-20% |  | 761(24) | 752(58) | 761(29.5)
830 | 1220 | KNR | GANDHI NAGAR | GAN034 | TG-GAN034A-2 | DT-2 | AJIT NAGAR GALI NO 10:PL | 2 | 990 | 19505987 | 826 | 2019-06-08 03:30 | 327 | 1403 | 366 | 1518 | 132 | 539 | 926 | 718.5 | 0.5 |  |  | 0.5 | 83% | 51% | 57% | 58% | 12.4562 | Loss 10-20%
831 | 1220 | KNR | GANDHI NAGAR | GAN036 | TG-GAN036A-1 | DT-1 | KOTHI BHAGWAN DAS OUTSIDE:PL | 1 | 990 | 19506539 | 1099 | 2019-06-02 16:00 | 397 | 1665 | 353 | 1501 | 349 | 1470 | 182 | 506 | 94.5 | 76 | 41 | 211.5 | 11% | 19% | 111% | 38% | 9.7321 | Loss 5-10%
832 | 1220 | KNR | GANDHI NAGAR | GAN040 | TG-GAN040A-1 | DT-1 | GYAN MOHLLA | 1 | 990 | 19502011 | 924 | 2019-06-01 16:30 | 327 | 1448 | 313 | 1373 | 284 | 1256 | 168 | 539 | 178.5 | 2.5 |  | 181 | 34% | 39% | 93% | 55% | 4.1193 | Loss 0-5% | 885(218.5) | 1007(256) | 1093(210.5) |  | 967(107.5) | 931(219)
833 | 1220 | KNR | GANDHI NAGAR | GAN045 | TG-GAN045A-1 | DT-1 | SJ/STN RATTEY WALA SUBHASH MOHALLA | 1 | 990 | 19506863 | 840 | 2019-06-02 16:30 | 253 | 1056 | 297 | 1258 | 289 | 1225 | 187 | 593.5 | 126.5 |  |  | 126.5 | 13% | 31% | 85% | 31% | 9.7229 | Loss 5-10% |  | 866(124.5) | 870(158.5) | 827(152.5) | 869(175.5) | 974(203)
834 | 1220 | KNR | GEETA COLONY | GCL002 | TG-GCL002A-1 | DT-1 | ALOK BHARTI | 1 | 990 | 19503703 | 941 | 2019-06-30 | 376 | 1596 | 307 | 1293 | 259 | 1081 | 448 | 549.5 | 167 | 3.5 |  | 170.5 | 95% | 75% | 77% | 95% | 5.9868 | Loss 5-10% |  | 835(95.5) | 908(235.5) | 895(158) | 832(84)
835 | 1220 | KNR | GEETA COLONY | GCL004 | TG-GCL004A-1 | DT-1 | B.T.S MULTANI MOHOLLA:PL | 2 | 990 | 19505189 | 639 | 2019-06-30 16:30 | 226 | 945 | 268 | 1115 | 146 | 611 | 445 | 720 |  |  |  | 0 | 64% | 42% | 65% | 61% | 8.7685 | Loss 5-10%
836 | 1220 | KNR | GEETA COLONY | GCL004 | TG-GCL004A-2 | DT-2 | B.T.S MULTANI MOHOLLA:PL | 2 | 400 | 19506538 | 324 | 2019-06-05 | 163 | 736 | 74 | 317 | 88 | 382 | 391 | 686 | 34 |  |  | 34 | 81% | 56% | 80% | 77% | 8.7685 | Loss 5-10%
837 | 1220 | KNR | GEETA COLONY | GCL005 | TG-GCL005A-1 | DT-1 | JHEEL (BHOOSA MANDI):PL | 2 | 990 | 19506909 | 880 | 2019-06-27 | 251 | 1048 | 348 | 1451 | 281 | 1183 | 355 | 693 | 27 |  |  | 27 | 89% | 55% | 69% | 88% | 6.0827 | Loss 5-10% |  |  | 863(77) | 847(41)
838 | 1220 | KNR | GEETA COLONY | GCL005 | TG-GCL005A-2 | DT-2 | JHEEL (BHOOSA MANDI):PL | 2 | 400 | 19505932 | 443 | 2019-06-12 00:30 | 165 | 695 | 85 | 359 | 193 | 826 | 418 | 553 | 105 | 41 | 21 | 167 | 111% | 71% | 88% | 108% | 6.0827 | Loss 5-10%
839 | 1220 | KNR | GEETA COLONY | GCL011 | TG-GCL011A-1 | DT-1 | GEETA COLONY, 14 BLK:ID | 1 | 990 | 19505719 | 955 | 2019-06-11 01:00 | 290 | 1294 | 224 | 1043 | 440 | 2230 | 1084 | 605 | 113.5 | 0.5 |  | 114 | 96% | 65% | 74% | 85% | 9.7752 | Loss 5-10% |  | 829(54.5) | 901(141.5) | 864(79) | 751(25.5)
840 | 1220 | KNR | GEETA COLONY | GCL014 | TG-GCL014A-1 | DT-1 | GEETA COLONY,11, BLK:PL | 1 | 990 | 19502875 | 996 | 2019-06-11 01:00 | 332 | 1381 | 293 | 1249 | 371 | 1587 | 296 | 593 | 121.5 | 3.5 | 1 | 126 | 101% | 81% | 62% | 97% | 4.896 | Loss 0-5% |  | 886(63) | 909(132) | 886(68.5)
841 | 1220 | KNR | GEETA COLONY | GCL015 | TG-GCL015A-1 | DT-1 | GEETA COLONY,12, BLK:K | 2 | 990 | 19503665 | 754 | 2019-06-30 | 267 | 1145 | 220 | 941 | 266 | 1131 | 197 | 701 | 19 |  |  | 19 | 76% | 59% | 62% | 75% | 5.5539 | Loss 5-10%
842 | 1220 | KNR | GEETA COLONY | GCL015 | TG-GCL015A-2 | DT-2 | GEETA COLONY,12, BLK:K | 2 | 630 | 19506809 | 556 | 2019-06-29 23:30 | 102 | 433 | 168 | 726 | 286 | 1238 | 705 | 615.5 | 104.5 |  |  | 104.5 | 87% | 57% | 73% | 88% | 5.5539 | Loss 5-10%
843 | 1220 | KNR | GEETA COLONY | GCL016 | TG-GCL016A-1 | DT-1 | GEETA COLONY,13, BLK:ID | 4 | 990 | 19506146 | 815 | 2019-06-11 01:30 | 265 | 1147 | 280 | 1220 | 270 | 1166 | 65 | 681 | 39 |  |  | 39 | 82% | 50% | 60% | 77% | 4.4645 | Loss 0-5%
844 | 1220 | KNR | GEETA COLONY | GCL016 | TG-GCL016A-2 | DT-2 | GEETA COLONY,13, BLK:ID | 4 | 990 | 19506110 | 1134.3448 | 2019-06-12 00:30 | 322.5094 | 1425.3297 | 523.7515 | 2336.8203 | 288.0839 | 1253.5743 | 1008.399 | 579.5 | 82.5 | 38 | 16.5 | 137 | 115% | 76% | 67% | 112% | 4.4645 | Loss 0-5% |  |  | 1097(201) |  | 887(101.5)
845 | 1220 | KNR | GEETA COLONY | GCL016 | TG-GCL016A-3 | DT-3 | GEETA COLONY,13, BLK:ID | 4 | 990 | 19501569 | 793 | 2019-06-11 01:30 | 289 | 1282 | 218 | 973 | 286 | 1289 | 312 | 695.5 | 24 |  |  | 24 | 80% | 49% | 52% | 74% | 4.4645 | Loss 0-5% |  | 974(117) | 1083(200) | 1170(145.5) | 863(92)
846 | 1220 | KNR | GEETA COLONY | GCL016 | TG-GCL016A-4 | DT-4 | GEETA COLONY,13, BLK:ID | 4 | 630 | 19505933 | 497 | 2019-06-30 03:30 | 205 | 890 | 140 | 596 | 152 | 648 | 271 | 716.5 | 2 |  |  | 2 | 79% | 54% | 55% | 71% | 4.4645 | Loss 0-5% |  |  | 651(48.5)
847 | 1220 | KNR | GEETA COLONY | GCL017 | TG-GCL017A-1 | DT-1 | GEETA COLONY,15, BLK:PL | 2 | 990 | 19501030 | 521 | 2019-06-30 | 197 | 850 | 129 | 547 | 195 | 833 | 295 | 720 |  |  |  | 0 | 53% | 34% | 39% | 52% | 6.7417 | Loss 5-10% |  | 842(28.5)
848 | 1220 | KNR | GEETA COLONY | GCL017 | TG-GCL017A-2 | DT-2 | GEETA COLONY,15, BLK:PL | 2 | 630 | 19506379 | 666 | 2019-06-11 01:00 | 200 | 902 | 292 | 1384 | 174 | 750 | 574 | 621 | 98.5 |  | 0.5 | 99 | 106% | 55% | 64% | 90% | 6.7417 | Loss 5-10%
849 | 1220 | KNR | GEETA COLONY | GCL018 | TG-GCL018A-1 | DT-1 | GEETA COLONY,17, BLK COM CENTRE:PL | 2 | 630 | 19505190 | 590 | 2019-06-30 00:30 | 194 | 856 | 197 | 870 | 198 | 871 | 14 | 662 | 50 | 3 |  | 53 | 94% | 66% | 66% | 90% | 6.3725 | Loss 5-10% |  | 668(101) | 694(187) | 616(109) | 520(52.5)
850 | 1220 | KNR | GEETA COLONY | GCL018 | TG-GCL018A-2 | DT-2 | GEETA COLONY,17, BLK COM CENTRE:PL | 2 | 630 | 19506741 | 627 | 2019-06-15 00:30 | 207 | 928 | 231 | 1037 | 188 | 843 | 168 | 706.5 | 6.5 | 3 |  | 9.5 | 99% | 63% | 56% | 93% | 6.3725 | Loss 5-10%
851 | 1220 | KNR | GEETA COLONY | GCL019 | TG-GCL019A-1 | DT-1 | GEETA COLONY,17,BLK:PL | 2 | 990 | 19506130 | 1196 | 2019-06-30 02:00 | 393 | 1666 | 439 | 1973 | 364 | 1635 | 323 | 393 | 205 | 78.5 | 42.5 | 326 | 121% | 87% | 82% | 115% | 7.6169 | Loss 5-10% |  |  | 1062(305) |  | 956(190.5) | 854(35.5)
852 | 1220 | KNR | GEETA COLONY | GCL019 | TG-GCL019A-2 | DT-2 | GEETA COLONY,17,BLK:PL | 2 | 630 | 19504388 | 621 | 2019-06-12 | 209 | 882 | 237 | 1007 | 175 | 735 | 235 | 644.5 | 64 | 10.5 |  | 74.5 | 99% | 63% | 63% | 91% | 7.6169 | Loss 5-10% |  | 634(74.5) | 659(161) | 646(96) | 564(78)
853 | 1220 | KNR | GEETA COLONY | GCL022 | TG-GCL022A-1 | DT-1 | GEETA COLONY,3, BLK:K | 2 | 990 | 19505141 | 794 | 2019-06-12 01:00 | 295 | 1235 | 262 | 1154 | 236 | 988 | 218 | 685 | 34.5 |  |  | 34.5 | 80% | 53% | 55% | 73% | 4.4618 | Loss 0-5%
854 | 1220 | KNR | GEETA COLONY | GCL022 | TG-GCL022A-2 | DT-2 | GEETA COLONY,3, BLK:K | 2 | 630 | 19505718 | 473 | 2019-06-12 01:00 | 134 | 573 | 147 | 634 | 191 | 818 | 221 | 706 | 14 |  |  | 14 | 75% | 48% | 45% | 72% | 4.4618 | Loss 0-5%
855 | 1220 | KNR | GEETA COLONY | GCL024 | TG-GCL024A-1 | DT-1 | GEETA COLONY,6, BLK:PL | 2 | 990 | 19506114 | 801 | 2019-06-11 23:30 | 287 | 1252 | 246 | 1074 | 268 | 1158 | 154 | 655 | 65 |  |  | 65 | 80% | 56% | 70% | 81% | 4.7657 | Loss 0-5%
856 | 1220 | KNR | GEETA COLONY | GCL024 | TG-GCL024A-2 | DT-2 | GEETA COLONY,6, BLK:PL | 2 | 630 | 19505716 | 586.4537 | 2019-06-12 | 184.7647 | 786.3332 | 184.0559 | 779.6995 | 217.6331 | 919.2527 | 136.3575 | 606 | 110.5 | 2.5 |  | 113 | 93% | 71% | 63% | 92% | 4.7657 | Loss 0-5% | 733(78) | 817(159.5) | 672(199.5) | 632(123.5) | 550(80.5)
857 | 1220 | KNR | GEETA COLONY | GCL025 | TG-GCL025A-1 | DT-1 | GEETA COLONY,7, BLK:PL | 1 | 990 | 19506865 | 1022 | 2019-06-11 01:00 | 230 | 1032 | 383 | 1880 | 409 | 1978 | 901 | 645 | 74.5 |  | 0.5 | 75 | 103% | 52% | 58% | 84% | 5.6796 | Loss 5-10% |  | 946(94) | 962(174.5) | 950(110.5) | 805(51)
858 | 1220 | KNR | GEETA COLONY | GCL026 | TG-GCL026A-1 | DT-1 | GEETA COLONY,8,BLK;PL | 2 | 990 | 19506452 | 1008 | 2019-06-02 23:30 | 136 | 607 | 434 | 2107 | 437 | 2009 | 1453 | 719.5 |  |  | 0.5 | 0.5 | 61% | 48% | 42% | 102% | 7.0832 | Loss 5-10% |  | 780(24) | 844(80) | 783(26.5)
859 | 1220 | KNR | GEETA COLONY | GCL026 | TG-GCL026A-2 | DT-2 | GEETA COLONY,8,BLK;PL | 2 | 400 | 19506115 | 357 | 2019-06-16 01:00 | 108 | 444 | 142 | 591 | 107 | 447 | 146 | 550 | 170 |  |  | 170 | 89% | 78% | 80% | 87% | 7.0832 | Loss 5-10%
860 | 1220 | KNR | GEETA COLONY | GCL027 | TG-GCL027A-1 | DT-1 | GEETA COLONY,8-A,BLK:ID | 2 | 990 | 19506019 | 919 | 2019-06-11 23:30 | 363 | 1555 | 243 | 1029 | 313 | 1336 | 458 | 598.5 | 120 | 1.5 |  | 121.5 | 92% | 87% | 67% | 93% | 8.665 | Loss 5-10% |  |  | 963(106.5) | 830(52)
861 | 1220 | KNR | GEETA COLONY | GCL027 | TG-GCL027A-2 | DT-2 | GEETA COLONY,8-A,BLK:ID | 2 | 630 | 19505112 | 259 | 2019-06-11 01:00 | 97 | 398 | 95 | 391 | 68 | 280 | 115 | 720 |  |  |  | 0 | 41% | 30% | 35% | 38% | 8.665 | Loss 5-10%
862 | 1220 | KNR | GEETA COLONY | GCL028 | TG-GCL028A-1 | DT-1 | GEETA COLONY,POL.STATION | 2 | 630 | 19505717 | 550 | 2019-06-04 01:30 | 129 | 537 | 250 | 1065 | 171 | 715 | 465 | 671.5 | 48.5 |  |  | 48.5 | 87% | 56% | 76% | 83% | 9.3711 | Loss 5-10% |  |  | 536(57.5)
863 | 1220 | KNR | GEETA COLONY | GCL028 | TG-GCL028A-2 | DT-2 | GEETA COLONY,POL.STATION | 2 | 630 | 19504342 | 671.9452 | 2019-06-03 | 130.8245 | 572.2357 | 196.0723 | 848.2469 | 345.0484 | 1492.7469 | 818.2003 | 438.5 | 32.5 |  |  | 32.5 | 78% | 54% | 72% | 79% | 9.3711 | Loss 5-10%
864 | 1220 | KNR | GEETA COLONY | GCL030 | TG-GCL030A-1 | DT-1 | NEW LAHORE (MUNSHI COLONY):PL | 1 | 990 | 19506789 | 1099 | 2019-06-10 02:00 | 383 | 1722 | 351 | 1549 | 365 | 1643 | 149 | 476.5 | 166 | 64.5 | 11.5 | 242 | 111% | 86% | 83% | 108% | 5.3845 | Loss 5-10% |  | 963(153.5) | 1070(235.5) |  | 891(143)
865 | 1220 | KNR | GEETA COLONY | GCL031 | TG-GCL031A-1 | DT-1 | NEW LAHORE EXTENSION:PL | 2 | 630 | 19506882 | 692 | 2019-06-29 | 237 | 1024 | 206 | 885 | 249 | 1074 | 170 | 698.5 | 10.5 | 6.5 | 1.5 | 18.5 | 110% | 73% | 93% | 107% | 4.9099 | Loss 0-5%
866 | 1220 | KNR | GEETA COLONY | GCL031 | TG-GCL031A-2 | DT-2 | NEW LAHORE EXTENSION:PL | 2 | 990 | 19506866 | 1078 | 2019-06-28 | 389 | 1625 | 375 | 1546 | 314 | 1303 | 291 | 572 | 134 | 5.5 | 4 | 143.5 | 109% | 84% | 69% | 107% | 4.9099 | Loss 0-5% |  |  | 825(49) | 844(75)
867 | 1220 | KNR | GEETA COLONY | GCL032 | TG-GCL032A-1 | DT-1 | RANI GARDEN NO.2,PARK WALA:PL | 2 | 990 | 19506148 | 838 | 2019-06-30 01:30 | 267 | 1111 | 250 | 1043 | 321 | 1329 | 259 | 612.5 | 106.5 |  |  | 106.5 | 85% | 76% | 75% | 84% | 5.0761 | Loss 5-10% |  | 903(161) | 920(151) | 822(78)
868 | 1220 | KNR | GEETA COLONY | GCL032 | TG-GCL032A-2 | DT-2 | RANI GARDEN NO.2,PARK WALA:PL | 2 | 630 | 19505143 | 668 | 2019-06-06 10:00 | 264 | 1175 | 152 | 646 | 252 | 1085 | 490 | 716 | 3.5 |  | 0.5 | 4 | 80% | 67% | 106% | 57% | 5.0761 | Loss 5-10% |  |  | 491(28.5)
869 | 1220 | KNR | GEETA COLONY | GCL034 | TG-GCL034A-1 | DT-1 | RANI GARDEN SWITCHING S/STN:PL | 1 | 630 | 19506864 | 598 | 2019-06-30 | 183 | 788 | 215 | 930 | 200 | 862 | 123 | 586 | 125.5 | 7.5 |  | 133 | 95% | 63% | 77% | 94% | 4.7581 | Loss 0-5% |  | 526(45.5) | 572(115.5) | 532(51.5)
870 | 1220 | KNR | GEETA COLONY | GCL035 | TG-GCL035A-1 | DT-1 | SARASWATI BHANDAR:PL | 1 | 630 | 19505989 | 580 | 2019-06-02 14:30 | 179 | 751 | 196 | 820 | 205 | 862 | 97 | 521 | 198 | 1 |  | 199 | 15% | 34% | 92% | 19% | 6.5743 | Loss 5-10% |  |  |  |  | 540(82.5)
871 | 1220 | KNR | GEETA COLONY | GCL036 | TG-GCL036A-1 | DT-1 | SAROJINI PARK:PKG | 1 | 990 | 19506408 | 820 | 2019-06-11 23:30 | 256 | 1069 | 270 | 1161 | 294 | 1241 | 149 | 654 | 66 |  |  | 66 | 82% | 54% | 61% | 83% | 6.2642 | Loss 5-10% |  |  | 858(73) | 859(44.5)
872 | 1220 | KNR | GEETA COLONY | GCL038 | TG-GCL038A-1 | DT-1 | SHASTRI PARK NAGAR, NO-2:K | 1 | 990 | 19506782 | 914 | 2019-06-09 00:30 | 319 | 1395 | 319 | 1379 | 276 | 1192 | 196 | 646 | 73.5 | 0.5 |  | 74 | 92% | 64% | 63% | 88% | 6.1171 | Loss 5-10% |  | 829(43.5) | 811(41)
873 | 1220 | KNR | GEETA COLONY | GCL041 | TG-GCL041A-1 | DT-1 | SUBASH ROAD, TIKONA PARK:K | 4 | 990 | 19505574 | 936 | 2019-06-29 16:00 | 322 | 1353 | 313 | 1328 | 301 | 1264 | 79 | 510 | 188.5 | 18.5 |  | 207 | 20% | 22% | 95% | 27% | 5.2095 | Loss 5-10% |  | 768(35) | 936(153.5) | 786(78) | 825(47.5)
874 | 1220 | KNR | GEETA COLONY | GCL041 | TG-GCL041A-2 | DT-2 | SUBASH ROAD, TIKONA PARK:K | 4 | 990 | 19501917 | 944 | 2019-06-02 15:00 | 288 | 1256 | 307 | 1333 | 349 | 1510 | 226 | 557.5 | 125.5 | 33.5 |  | 159 | 19% | 39% | 95% | 20% | 5.2095 | Loss 5-10% |  |  | 891(33) |  | 961(113.5) | 817(69)
875 | 1220 | KNR | GEETA COLONY | GCL041 | TG-GCL041A-3 | DT-3 | SUBASH ROAD, TIKONA PARK:K | 4 | 990 | 19506377 | 714 | 2019-06-13 12:00 | 204 | 840 | 281 | 1170 | 229 | 957 | 290 | 629.5 | 0.5 |  |  | 0.5 | 7% | 27% | 72% | 8% | 5.2095 | Loss 5-10% | 978(171) | 996(225.5) | 1069(217) | 950(214.5) | 958(212) | 860(196.5)
876 | 1220 | KNR | GEETA COLONY | GCL041 | TG-GCL041A-4 | DT-4 | SUBASH ROAD, TIKONA PARK:K | 4 | 990 | 19506152 | 778 | 2019-06-30 14:00 | 272 | 1198 | 178 | 747 | 328 | 1498 | 655 | 696 | 18.5 |  |  | 18.5 | 6% | 16% | 79% | 8% | 5.2095 | Loss 5-10% |  | 783(34) | 962(125.5) | 748(25.5) | 882(41.5)
877 | 1220 | KNR | KANTI NAGAR | GAN017 | TG-GAN017A-1 | DT-1 | KAUSHIK PURI KIOSK:K | 1 | 990 | 19502029 | 813 | 2019-06-01 19:30 | 350 | 1476 | 232 | 979 | 231 | 938 | 519 | 687 | 33 |  |  | 33 | 74% | 69% | 82% | 79% | 5.5284 | Loss 5-10% |  | 839(82) | 778(45.5)
878 | 1220 | KNR | KANTI NAGAR | GAN018 | TG-GAN018A-1 | DT-1 | KAUSHIK PURI PARK:PL | 2 | 990 | 19506930 | 534 | 2019-06-30 14:00 | 168 | 723 | 156 | 675 | 210 | 917 | 222 | 249.5 |  |  |  | 0 | 48% | 48% | 54% | 53% | 20.6085 | Loss 20-30%
879 | 1220 | KNR | KANTI NAGAR | GAN018 | TG-GAN018A-2 | DT-2 | KAUSHIK PURI PARK:PL | 2 | 630 | 19504747 | 491 | 2019-06-01 19:30 | 151 | 610 | 140 | 564 | 201 | 807 | 224 | 692 | 28 |  |  | 28 | 73% | 67% | 78% | 77% | 20.6085 | Loss 20-30% |  | 478(29.5) |  | 467(24.5)
880 | 1220 | KNR | KANTI NAGAR | GAN026 | TG-GAN026A-1 | DT-1 | SATSANG MARG:PL | 2 | 990 | 19500930 | 850 | 2019-06-30 00:30 | 329 | 1437 | 260 | 1120 | 261 | 1133 | 311 | 685.5 | 34 |  |  | 34 | 86% | 59% | 78% | 84% | 4.3717 | Loss 0-5%
881 | 1220 | KNR | KANTI NAGAR | GAN026 | TG-GAN026A-2 | DT-2 | SATSANG MARG:PL | 2 | 630 | 19500966 | 669 | 2019-06-01 23:30 | 231 | 1023 | 206 | 905 | 233 | 1026 | 120 | 571.5 | 96 | 37.5 | 14 | 147.5 | 106% | 68% | 74% | 106% | 4.3717 | Loss 0-5% |  |  |  | 646(94) | 554(95)
882 | 1220 | KNR | KANTI NAGAR | GAN027 | TG-GAN027A-1 | DT-1 | SEELAMPUR DOUBLE STORY:ID | 2 | 990 | 19505501 | 1179 | 2019-06-30 15:30 | 384 | 1728 | 428 | 1927 | 367 | 1627 | 264 | 416.5 | 117.5 | 80 | 17.5 | 215 | 55% | 48% | 119% | 74% | 10.3226 | Loss 10-20% | 986(234.5) | 1074(269) | 902(118) | 838(82.5)
883 | 1220 | KNR | KANTI NAGAR | GAN027 | TG-GAN027A-2 | DT-2 | SEELAMPUR DOUBLE STORY:ID | 2 | 990 | 19505502 | 541 | 2019-06-04 15:00 | 174 | 754 | 213 | 925 | 154 | 662 | 232 | 708.5 |  |  |  | 0 | 25% | 22% | 55% | 27% | 10.3226 | Loss 10-20%
884 | 1220 | KNR | KANTI NAGAR | GAN035 | TG-GAN035A-1 | DT-1 | CHAMELI DEVI OUTSIDE:PL | 1 | 990 | 19506068 | 809 | 2019-06-30 15:30 | 274 | 1174 | 219 | 941 | 316 | 1371 | 373 | 669 | 49 |  |  | 49 | 51% | 45% | 82% | 54% | 6.9158 | Loss 5-10% |  |  |  |  | 853(104.5) | 794(82.5)
885 | 1220 | KNR | KANTI NAGAR | KRI002 | TG-KRI002A-1 | DT-1 | AZAD NAGAR WATER TANK:PL | 1 | 990 | 19503599 | 895 | 2019-06-29 23:30 | 311 | 1257 | 275 | 1108 | 309 | 1237 | 140 | 597.5 | 121.5 | 1 |  | 122.5 | 89% | 59% | 67% | 90% | 4.773 | Loss 0-5% |  | 854(51) | 886(115.5) | 891(69.5)
886 | 1220 | KNR | KANTI NAGAR | KRI006 | TG-KRI006A-1 | DT-1 | BHAGAT SINGH PARK NO 1:PL | 2 | 990 | 19501914 | 1127 | 2019-06-14 | 383 | 1618 | 366 | 1532 | 378 | 1601 | 79 | 530.5 | 126 | 50 | 11 | 187 | 114% | 75% | 79% | 110% | 4.4852 | Loss 0-5% |  | 934(66.5) | 1067(190) | 897(31.5) | 876(89)
887 | 1220 | KNR | KANTI NAGAR | KRI006 | TG-KRI006A-2 | DT-2 | BHAGAT SINGH PARK NO 1:PL | 2 | 630 | 19505735 | 727 | 2019-06-02 23:30 | 263 | 1107 | 224 | 929 | 240 | 1010 | 154 | 705.5 | 8 | 2.5 | 2 | 12.5 | 111% | 60% | 79% | 115% | 4.4852 | Loss 0-5%
888 | 1220 | KNR | KANTI NAGAR | KRI023 | TG-KRI023A-1 | DT-1 | JHEEL NO. 4 NO 1:ID | 2 | 630 | 19505187 | 143 | 2019-06-05 04:30 | 11 | 45 | 12 | 50 | 119 | 497 | 450 | 719 |  |  |  | 0 | 23% | 9% | 21% | 16% | 8.2995 | Loss 5-10%
889 | 1220 | KNR | KANTI NAGAR | KRI023 | TG-KRI023A-2 | DT-2 | JHEEL NO. 4 NO 1:ID | 2 | 990 | 19501978 | 781 | 2019-06-29 16:30 | 246 | 1103 | 258 | 1164 | 278 | 1238 | 117 | 687 | 32.5 |  |  | 32.5 | 63% | 42% | 79% | 64% | 8.2995 | Loss 5-10% |  |  | 796(42)
890 | 1220 | KNR | KANTI NAGAR | KRI026 | TG-KRI026A-1 | DT-1 | KANTI NAGAR EXT. GALI NO. 5:PL | 1 | 990 | 19504956 | 925 | 2019-06-02 00:30 | 303 | 1242 | 296 | 1215 | 326 | 1329 | 104 | 422 | 285.5 | 11 |  | 296.5 | 93% | 70% | 92% | 93% | 7.3476 | Loss 5-10% |  | 892(186.5) | 959(304.5) | 916(221.5) | 826(149.5)
891 | 1220 | KNR | KANTI NAGAR | KRI027 | TG-KRI027A-1 | DT-1 | KANTI NAGAR EXT. GALI NO. 9:PL | 2 | 990 | 19505349 | 520 | 2019-06-28 21:30 | 155 | 622 | 198 | 798 | 167 | 666 | 158 | 720 |  |  |  | 0 | 51% | 41% | 49% | 52% | 5.327 | Loss 5-10%
892 | 1220 | KNR | KANTI NAGAR | KRI027 | TG-KRI027A-2 | DT-2 | KANTI NAGAR EXT. GALI NO. 9:PL | 2 | 990 | 19505347 | 892 | 2019-06-30 23:30 | 274 | 1114 | 243 | 975 | 374 | 1532 | 503 | 665.5 | 54 | 0.5 |  | 54.5 | 90% | 65% | 73% | 90% | 5.327 | Loss 5-10% |  | 790(32) | 861(64.5) | 807(29.5)
893 | 1220 | KNR | KANTI NAGAR | KRI039 | TG-KRI039A-1 | DT-1 | RAJGARH EXTN.(MINI STADIUM):ID | 2 | 990 | 19506625 | 793 | 2019-06-11 01:00 | 236 | 1099 | 207 | 914 | 350 | 1707 | 719 | 714 | 4.5 |  |  | 4.5 | 80% | 49% | 53% | 73% | 5.2021 | Loss 5-10%
894 | 1220 | KNR | KANTI NAGAR | KRI039 | TG-KRI039A-2 | DT-2 | RAJGARH EXTN.(MINI STADIUM):ID | 2 | 990 | 19505976 | 1007 | 2019-06-29 23:00 | 441 | 2016 | 259 | 1145 | 307 | 1347 | 789 | 339.5 | 47.5 | 3.5 | 1 | 52 | 95% | 58% | 66% | 102% | 5.2021 | Loss 5-10% |  |  | 1204(216.5) | 1033(82) | 974(131.5)
895 | 1220 | KNR | KANTI NAGAR | KRI040 | TG-KRI040A-1 | DT-1 | RAJGARH MOTHER DAIRY GALI NO 6:PL | 2 | 990 | 19500881 | 963 | 2019-06-11 | 334 | 1476 | 337 | 1503 | 292 | 1297 | 194 | 582.5 | 125.5 | 10.5 |  | 136 | 97% | 74% | 69% | 94% | 6.7233 | Loss 5-10% |  | 1047(69) | 1050(149.5) | 905(70.5) | 787(26.5)
896 | 1220 | KNR | KANTI NAGAR | KRI040 | TG-KRI040A-2 | DT-2 | RAJGARH MOTHER DAIRY GALI NO 6:PL | 2 | 990 | 19504387 | 836 | 2019-06-12 02:30 | 334 | 1416 | 246 | 1031 | 257 | 1087 | 360 | 665.5 | 53.5 |  |  | 53.5 | 84% | 60% | 57% | 79% | 6.7233 | Loss 5-10%
897 | 1220 | KNR | KANTI NAGAR | KRI045 | TG-KRI045A-1 | DT-1 | SHANKAR NAGAR MAIN ROAD SCHOOL NO 1:PL | 2 | 990 | 19501909 | 740 | 2019-06-29 23:30 | 285 | 1233 | 225 | 959 | 230 | 988 | 261 | 713.5 | 5.5 |  |  | 5.5 | 75% | 51% | 62% | 75% | 8.1425 | Loss 5-10%
898 | 1220 | KNR | KANTI NAGAR | KRI045 | TG-KRI045A-2 | DT-2 | SHANKAR NAGAR MAIN ROAD SCHOOL NO 1:PL | 2 | 990 | 19506354 | 1018 | 2019-06-01 01:00 | 335 | 1366 | 432 | 1765 | 251 | 1018 | 647 | 578 | 138.5 | 1.5 | 1 | 141 | 103% | 66% | 82% | 91% | 8.1425 | Loss 5-10% |  |  |  |  | 902(127)
899 | 1220 | KNR | KANTI NAGAR | KRI052 | TG-KRI052A-1 | DT-1 | WEST AZAD NAGAR (RASGULLA):PL | 1 | 990 | 19506565 | 882 | 2019-06-11 23:30 | 252 | 1015 | 318 | 1268 | 312 | 1256 | 247 | 620.5 | 96.5 |  |  | 96.5 | 87% | 68% | 60% | 89% | 3.9573 | Loss 0-5%
900 | 1220 | KNR | KANTI NAGAR | KRI053 | TG-KRI053A-1 | DT-1 | WEST AZAD NAGAR SHD ROAD B&D BL NO. 1:ID | 3 | 990 | 19506717 | 832 | 2019-06-10 23:00 | 251 | 1021 | 371 | 1994 | 210 | 915 | 1031 | 694 | 24 |  |  | 24 | 77% | 65% | 72% | 84% | 5.0986 | Loss 5-10%
901 | 1220 | KNR | KANTI NAGAR | KRI053 | TG-KRI053A-2 | DT-2 | WEST AZAD NAGAR SHD ROAD B&D BL NO. 1:ID | 3 | 990 | 19501884 | 954 | 2019-06-10 03:00 | 322 | 1346 | 281 | 1151 | 351 | 1463 | 273 | 603 | 109.5 | 5 |  | 114.5 | 96% | 62% | 69% | 95% | 5.0986 | Loss 5-10% |  | 1045(119) | 939(66) | 866(53.5)
902 | 1220 | KNR | KANTI NAGAR | KRI053 | TG-KRI053A-3 | DT-3 | WEST AZAD NAGAR SHD ROAD B&D BL NO. 1:ID | 3 | 630 | 19505228 | 768 | 2019-06-11 01:00 | 253 | 1090 | 258 | 1129 | 257 | 1123 | 36 | 406.5 | 191.5 | 66 | 53 | 310.5 | 122% | 86% | 86% | 112% | 5.0986 | Loss 5-10% | 732(93) | 976(628) | 1013(579.5) | 701(284) | 691(222.5) | 545(50)
903 | 1220 | KNR | KANTI NAGAR | KRI055 | TG-KRI055A-1 | DT-1 | WEST AZAD NAGAR(KEHAR SINGH)RLG NO 1:ID | 2 | 990 | 19501973 | 888 | 2019-06-30 23:30 | 290 | 1237 | 300 | 1302 | 298 | 1286 | 59 | 657 | 62.5 |  |  | 62.5 | 90% | 57% | 59% | 90% | 6.0902 | Loss 5-10%
904 | 1220 | KNR | KANTI NAGAR | KRI055 | TG-KRI055A-2 | DT-2 | WEST AZAD NAGAR(KEHAR SINGH)RLG NO 1:ID | 2 | 990 | 19501602 | 785 | 2019-06-11 23:30 | 296 | 1262 | 210 | 882 | 279 | 1194 | 351 | 688.5 | 31 |  |  | 31 | 78% | 53% | 60% | 79% | 6.0902 | Loss 5-10% |  |  | 799(44.5)
905 | 1220 | KNR | KANTI NAGAR | KRI057 | TG-KRI057A-1 | DT-1 | WEST KANTI NAGAR:ID | 1 | 990 | 19504088 | 866 | 2019-06-29 22:30 | 244 | 990 | 280 | 1140 | 342 | 1390 | 350 | 614 | 106 |  |  | 106 | 82% | 73% | 79% | 87% | 8.4094 | Loss 5-10% | 858(106) | 1084(521) | 987(529.5) | 992(523) | 939(445.5) | 858(130.5)
906 | 1220 | KNR | KANTI NAGAR | KRI066 | TG-KRI066A-1 | DT-1 | East Azad Nagar Primary School | 1 | 990 | 19506021 | 874 | 2019-06-02 23:00 | 268 | 1102 | 283 | 1170 | 323 | 1324 | 197 | 614 | 105 |  |  | 105 | 88% | 77% | 71% | 88% | 7.0287 | Loss 5-10% |  |  | 1101(40) | 818(32)
907 | 1220 | KNR | KRISHNA NAGAR | KRI001 | TG-KRI001A-1 | DT-1 | A-BLOCK KRN:PL | 2 | 990 | 19505570 | 896 | 2019-06-11 01:00 | 249 | 1104 | 372 | 1718 | 275 | 1254 | 555 | 589.5 | 129.5 | 0.5 |  | 130 | 91% | 74% | 76% | 88% | 4.7581 | Loss 0-5%
908 | 1220 | KNR | KRISHNA NAGAR | KRI001 | TG-KRI001A-2 | DT-2 | A-BLOCK KRN:PL | 2 | 630 | 19505929 | 275 | 2019-06-11 17:00 | 66 | 270 | 103 | 429 | 106 | 443 | 166 | 719 |  |  |  | 0 | 15% | 13% | 44% | 26% | 4.7581 | Loss 0-5%
909 | 1220 | KNR | KRISHNA NAGAR | KRI003 | TG-KRI003A-1 | DT-1 | B-BLOCK KRISHNA NAGAR 8/24:PM | 1 | 630 | 19505516 | 587 | 2019-06-12 00:30 | 205 | 877 | 201 | 866 | 180 | 769 | 103 | 583.5 | 133.5 | 3 |  | 136.5 | 93% | 62% | 67% | 87% | 4.7734 | Loss 0-5% |  | 507(39) | 591(110.5) | 539(56.5)
910 | 1220 | KNR | KRISHNA NAGAR | KRI004 | TG-KRI004A-1 | DT-1 | K-BLK KRN GHONOLI CHOWK:PL | 2 | 990 | 19500863 | 953 | 2019-06-12 | 300 | 1254 | 351 | 1475 | 302 | 1265 | 216 | 407.5 | 298.5 | 14 |  | 312.5 | 96% | 72% | 84% | 95% | 18.6935 | Loss 10-20% |  | 859(78.5) | 899(267.5) | 905(168) | 817(85.5)
911 | 1220 | KNR | KRISHNA NAGAR | KRI004 | TG-KRI004A-2 | DT-2 | K-BLK KRN GHONOLI CHOWK:PL | 2 | 990 | 19504624 | 756 | 2019-06-27 00:30 | 290 | 1198 | 271 | 1122 | 195 | 796 | 370 | 704 | 16 |  |  | 16 | 76% | 56% | 64% | 74% | 18.6935 | Loss 10-20%
912 | 1220 | KNR | KRISHNA NAGAR | KRI008 | TG-KRI008A-1 | DT-1 | C-BLOCK KRISHNA NAGAR NO 1:ID | 2 | 990 | 19505740 | 876 | 2019-06-01 20:30 | 303 | 1253 | 285 | 1171 | 288 | 1194 | 74 | 608 | 112 |  |  | 112 | 84% | 53% | 89% | 87% | 7.0106 | Loss 5-10% |  | 768(26.5) | 849(44)
913 | 1220 | KNR | KRISHNA NAGAR | KRI008 | TG-KRI008A-2 | DT-2 | C-BLOCK KRISHNA NAGAR NO 1:ID | 2 | 990 | 19506020 | 1185 | 2019-06-01 19:30 | 220 | 927 | 438 | 2069 | 527 | 2370 | 1319 | 480 | 204 | 34.5 | 1.5 | 240 | 78% | 52% | 120% | 96% | 7.0106 | Loss 5-10% |  | 872(99.5) | 932(165.5) | 1023(123.5)
914 | 1220 | KNR | KRISHNA NAGAR | KRI011 | TG-KRI011A-1 | DT-1 | D-BLOCK KRISHNA NAGAR:PL | 1 | 990 | 19506772 | 1201 | 2019-06-01 19:00 | 449 | 1967 | 309 | 1313 | 444 | 2053 | 701 | 579.5 | 138 | 0.5 | 0.5 | 139 | 86% | 50% | 121% | 82% | 19.0766 | Loss 10-20%
915 | 1220 | KNR | KRISHNA NAGAR | KRI013 | TG-KRI013A-1 | DT-1 | F-BLOCK KRISHNA NAGAR:K | 2 | 990 | 19506776 | 1058.1356 | 2019-06-01 19:00 | 364.2844 | 1638.8537 | 424.5189 | 1845.574 | 269.3322 | 1131.6956 | 636.2252 | 389 | 262.5 | 54.5 | 8 | 325 | 104% | 66% | 107% | 105% | 14.4912 | Loss 10-20% |  | 1008(144) | 1133(312) | 1044(193.5) | 885(117)
916 | 1220 | KNR | KRISHNA NAGAR | KRI013 | TG-KRI013A-2 | DT-2 | F-BLOCK KRISHNA NAGAR:K | 2 | 630 | 19505739 | 404 | 2019-06-30 23:30 | 129 | 550 | 129 | 561 | 146 | 617 | 62 | 716 |  |  |  | 0 | 62% | 43% | 51% | 64% | 14.4912 | Loss 10-20%
917 | 1220 | KNR | KRISHNA NAGAR | KRI014 | TG-KRI014A-1 | DT-1 | E-BLOCK KRN (PARK) E 15,16:PL | 1 | 990 | 19506370 | 899 | 2019-06-11 23:00 | 210 | 886 | 265 | 1145 | 423 | 1807 | 823 | 675.5 | 44 | 0.5 |  | 44.5 | 79% | 46% | 55% | 91% | 4.7829 | Loss 0-5% |  |  | 804(42.5)
918 | 1220 | KNR | KRISHNA NAGAR | KRI015 | TG-KRI015A-1 | DT-1 | E-BLOCK KRN LAJ PAT RAI CHOWK:PL | 2 | 990 | 19505576 | 760 | 2019-06-11 01:00 | 170 | 778 | 410 | 2012 | 180 | 800 | 1223 | 662 | 0.5 |  |  | 0.5 | 77% | 36% | 69% | 55% | 9.579 | Loss 5-10%
919 | 1220 | KNR | KRISHNA NAGAR | KRI015 | TG-KRI015A-2 | DT-2 | E-BLOCK KRN LAJ PAT RAI CHOWK:PL | 2 | 630 | 19505772 | 537 | 2019-06-11 01:00 | 228 | 1103 | 172 | 794 | 136 | 607 | 433 | 673 | 45.5 |  |  | 45.5 | 85% | 62% | 84% | 78% | 9.579 | Loss 5-10%
920 | 1220 | KNR | KRISHNA NAGAR | KRI017 | TG-KRI017A-1 | DT-1 | F-BLOCK KRN PLM:PL | 2 | 990 | 19506778 | 986 | 2019-06-11 03:30 | 427 | 2101 | 297 | 1384 | 262 | 1224 | 809 | 686.5 | 27.5 | 0.5 |  | 28 | 100% | 52% | 67% | 86% | 15.218 | Loss 10-20% |  | 932(40.5)
921 | 1220 | KNR | KRISHNA NAGAR | KRI017 | TG-KRI017A-2 | DT-2 | F-BLOCK KRN PLM:PL | 2 | 630 | 19506503 | 556 | 2019-06-11 01:00 | 147 | 652 | 228 | 1011 | 181 | 799 | 312 | 673.5 | 41 |  |  | 41 | 88% | 52% | 69% | 86% | 15.218 | Loss 10-20%
922 | 1220 | KNR | KRISHNA NAGAR | KRI018 | TG-KRI018A-1 | DT-1 | H-BLOCK KRISHNA NAGAR (MOTHER DAIRY):K | 2 | 990 | 19506775 | 735.1891 | 2019-06-03 12:00 | 209.8819 | 924.7938 | 254.4 | 1130.6667 | 270.9072 | 1220.2476 | 262.3941 | 716.5 |  |  |  | 0 | 58% | 41% | 63% | 56% | 6.6704 | Loss 5-10%
923 | 1220 | KNR | KRISHNA NAGAR | KRI018 | TG-KRI018A-2 | DT-2 | H-BLOCK KRISHNA NAGAR (MOTHER DAIRY):K | 2 | 630 | 19506531 | 629 | 2019-06-11 00:30 | 167 | 751 | 222 | 995 | 240 | 1074 | 291 | 633 | 80.5 | 4 |  | 84.5 | 100% | 64% | 73% | 93% | 6.6704 | Loss 5-10% |  | 481(25)
924 | 1220 | KNR | KRISHNA NAGAR | KRI019 | TG-KRI019A-1 | DT-1 | J-BLOCK KRN:PL | 2 | 1600 | 19506883 | 1299 | 2019-06-03 | 382 | 1663 | 360 | 1564 | 556 | 2455 | 846 | 689.5 | 29.5 |  |  | 29.5 | 81% | 49% | 54% | 78% | 4.7205 | Loss 0-5% |  | 1180(176) | 1230(285) | 1139(91)
925 | 1220 | KNR | KRISHNA NAGAR | KRI019 | TG-KRI019A-2 | DT-2 | J-BLOCK KRN:PL | 2 | 990 | 19505280 | 1013 | 2019-06-11 03:30 | 335 | 1417 | 334 | 1419 | 343 | 1445 | 27 | 507 | 189.5 | 20.5 | 1 | 211 | 102% | 75% | 86% | 94% | 4.7205 | Loss 0-5% |  | 870(43.5) | 980(142.5) | 866(76.5)
926 | 1220 | KNR | KRISHNA NAGAR | KRI020 | TG-KRI020A-1 | DT-1 | JHEEL NO. 1:PL | 1 | 630 | 19503581 | 528 | 2019-06-02 16:00 | 172 | 729 | 183 | 775 | 173 | 723 | 49 | 594 | 126 |  |  | 126 | 65% | 44% | 84% | 74% | 10.0607 | Loss 10-20% |  | 489(31.5) | 539(122.5) | 530(71) | 493(47.5)
927 | 1220 | KNR | KRISHNA NAGAR | KRI021 | TG-KRI021A-1 | DT-1 | JHEEL NO. 2:PL | 2 | 990 | 19506780 | 885 | 2019-06-30 16:00 | 298 | 1255 | 279 | 1176 | 307 | 1303 | 110 | 510.5 | 208 |  |  | 208 | 89% | 67% | 89% | 84% | 15.2796 | Loss 10-20% |  | 814(36.5) | 904(147) | 847(99.5)
928 | 1220 | KNR | KRISHNA NAGAR | KRI021 | TG-KRI021A-2 | DT-2 | JHEEL NO. 2:PL | 2 | 630 | 19506368 | 240 | 2019-06-12 17:30 | 85 | 350 | 79 | 324 | 76 | 310 | 36 | 718.5 |  |  |  | 0 | 14% | 22% | 38% | 29% | 15.2796 | Loss 10-20%
929 | 1220 | KNR | KRISHNA NAGAR | KRI034 | TG-KRI034A-1 | DT-1 | OLD ANARKALI:ID | 3 | 990 | 19505248 | 711 | 2019-06-30 01:00 | 241 | 976 | 225 | 906 | 245 | 995 | 81 | 717.5 | 1 |  |  | 1 | 72% | 50% | 47% | 69% | 5.2244 | Loss 5-10% |  | 1053(139.5) | 1104(257.5) | 1106(182) | 909(122) | 831(27)
930 | 1220 | KNR | KRISHNA NAGAR | KRI034 | TG-KRI034A-2 | DT-2 | OLD ANARKALI:ID | 3 | 990 | 19506681 | 1155.2748 | 2019-06-11 23:30 | 434.2842 | 1825.3371 | 333.0169 | 1392.2691 | 387.9737 | 1609.5823 | 375.0487 | 499.5 | 116 | 53 | 49.5 | 218.5 | 116% | 71% | 78% | 117% | 5.2244 | Loss 5-10% |  | 1076(71.5) | 1119(216) | 1089(152.5) | 943(114)
931 | 1220 | KNR | KRISHNA NAGAR | KRI034 | TG-KRI034A-3 | DT-3 | OLD ANARKALI:ID | 3 | 630 | 19506766 | 538 | 2019-06-30 23:30 | 214 | 918 | 170 | 721 | 153 | 649 | 241 | 635.5 | 84.5 |  |  | 84.5 | 85% | 61% | 66% | 85% | 5.2244 | Loss 5-10%
932 | 1220 | KNR | KRISHNA NAGAR | KRI035 | TG-KRI035A-1 | DT-1 | PANDIT PARK:PM | 1 | 990 | 19500865 | 1067.1793 | 2019-06-01 16:00 | 324.445 | 1399.4348 | 368.913 | 1605.5751 | 373.8213 | 1604.4523 | 205.5812 | 423.5 | 259.5 | 33.5 | 3 | 296 | 78% | 63% | 108% | 77% | 36.8993 | Loss >30% | 848(119) | 990(192) | 1138(298) | 1052(286) | 998(281)
933 | 1220 | KNR | KRISHNA NAGAR | KRI036 | TG-KRI036A-1 | DT-1 | RADHA PURI EXTN.(NALAH) NO. 1:PL | 2 | 990 | 19506680 | 915 | 2019-06-30 23:00 | 224 | 969 | 361 | 1583 | 329 | 1449 | 559 | 581 | 132.5 | 6 |  | 138.5 | 92% | 62% | 63% | 92% | 4.2564 | Loss 0-5% |  | 819(43) | 920(134) | 899(74) | 783(28.5)
934 | 1220 | KNR | KRISHNA NAGAR | KRI036 | TG-KRI036A-2 | DT-2 | RADHA PURI EXTN.(NALAH) NO. 1:PL | 2 | 630 | 19505285 | 376 | 2019-06-12 | 176 | 739 | 125 | 521 | 75 | 310 | 371 | 719.5 |  |  |  | 0 | 60% | 39% | 38% | 58% | 4.2564 | Loss 0-5%
935 | 1220 | KNR | KRISHNA NAGAR | KRI038 | TG-KRI038A-1 | DT-1 | RADHA PURI NEW KRISHNA NAGAR:PL | 1 | 990 | 19506679 | 849 | 2019-06-30 23:30 | 164 | 705 | 285 | 1228 | 399 | 1723 | 882 | 650.5 | 69.5 |  |  | 69.5 | 84% | 52% | 58% | 86% | 3.4673 | Loss 0-5%
936 | 1220 | KNR | KRISHNA NAGAR | KRI041 | TG-KRI041A-1 | DT-1 | RAM NAGAR L.N.MANDIR:PL | 1 | 1600 | 19506779 | 1465 | 2019-06-11 01:00 | 776 | 3572 | 313 | 1264 | 375 | 1596 | 2161 | 665 | 54.5 | 0.5 |  | 55 | 92% | 53% | 58% | 82% | 19.8907 | Loss 10-20% |  | 964(101.5) | 1176(198) | 1052(134.5) | 868(87.5)
937 | 1220 | KNR | KRISHNA NAGAR | KRI042 | TG-KRI042A-1 | DT-1 | RAM NAGAR PARK(PLM) | 2 | 990 | 19506848 | 552 | 2019-06-11 01:00 | 147 | 604 | 287 | 1334 | 119 | 516 | 777 | 719 |  |  |  | 0 | 56% | 31% | 33% | 49% | 20.721 | Loss 20-30%
938 | 1220 | KNR | KRISHNA NAGAR | KRI042 | TG-KRI042A-2 | DT-2 | RAM NAGAR PARK(PLM) | 2 | 990 | 19505114 | 826.7989 | 2019-06-11 19:30 | 208.5421 | 891.8152 | 297.6415 | 1280.1783 | 320.6154 | 1381.308 | 447.5804 | 683.5 | 36 |  |  | 36 | 71% | 47% | 84% | 75% | 20.721 | Loss 20-30% |  |  | 821(29)
939 | 1220 | KNR | KRISHNA NAGAR | KRI047 | TG-KRI047A-1 | DT-1 | SHASTRI PARK:PL | 1 | 990 | 19502447 | 989 | 2019-06-11 23:30 | 315 | 1363 | 336 | 1466 | 338 | 1472 | 106 | 405.5 | 282.5 | 30 |  | 312.5 | 99% | 73% | 93% | 100% | 36.7223 | Loss >30% |  | 966(192.5) | 976(447) | 1014(336) | 893(275.5) | 810(69.5)
940 | 1220 | KNR | KRISHNA NAGAR | KRI048 | TG-KRI048A-1 | DT-1 | ST.LIGHT OPP SWARN CINEMA ROAD NO 57:PM | 1 | 630 | 19505726 | 569 | 2019-06-26 23:30 | 150 | 649 | 129 | 557 | 289 | 1288 | 690 | 640.5 | 79 | 0.5 |  | 79.5 | 90% | 55% | 60% | 90% | 2.465 | Loss 0-5%
941 | 1220 | KNR | KRISHNA NAGAR | KRI051 | TG-KRI051A-1 | DT-1 | WEST ARJUN NAGAR:ID | 2 | 990 | 19506783 | 704 | 2019-06-12 | 232 | 962 | 246 | 1022 | 226 | 936 | 76 | 718 | 0.5 |  |  | 0.5 | 71% | 47% | 54% | 70% | 7.9875 | Loss 5-10%
942 | 1220 | KNR | KRISHNA NAGAR | KRI051 | TG-KRI051A-2 | DT-2 | WEST ARJUN NAGAR:ID | 2 | 630 | 19506784 | 621 | 2019-06-09 23:30 | 198 | 813 | 193 | 794 | 230 | 952 | 149 | 459.5 | 236.5 | 23 |  | 259.5 | 96% | 64% | 95% | 99% | 7.9875 | Loss 5-10% |  | 644(129) |  |  | 544(112.5)
943 | 1230 | LNR | ANAND VIHAR ISBT | MAN022 | TG-MAN022A-1 | DT-1 | JOSHI COLONY:ID | 2 | 630 | 19501921 | 306 | 2019-06-11 23:30 | 145 | 623 | 82 | 353 | 80 | 340 | 277 | 719.5 |  |  |  | 0 | 47% | 42% | 42% | 49% | 4.1643 | Loss 0-5%
944 | 1230 | LNR | ANAND VIHAR ISBT | MAN022 | TG-MAN022A-2 | DT-2 | JOSHI COLONY:ID | 2 | 990 | 19505405 | 900 | 2019-06-29 23:00 | 316 | 1382 | 300 | 1324 | 285 | 1248 | 116 | 595.5 | 123 | 1 |  | 124 | 90% | 71% | 76% | 91% | 4.1643 | Loss 0-5%
945 | 1230 | LNR | ANAND VIHAR ISBT | MAN049 | TG-MAN049A-1 | DT-1 | MADHU VIHAR S/STN-1:ID | 2 | 990 | 19506121 | 801 | 2019-06-29 16:00 | 248 | 1042 | 267 | 1120 | 286 | 1209 | 145 | 600 | 118.5 |  |  | 118.5 | 51% | 39% | 81% | 70% | 3.836 | Loss 0-5% |  |  |  |  | 853(57)
946 | 1230 | LNR | ANAND VIHAR ISBT | MAN049 | TG-MAN049A-2 | DT-2 | MADHU VIHAR S/STN-1:ID | 2 | 990 | 19501135 | 917 | 2019-06-12 17:00 | 324 | 1306 | 299 | 1205 | 294 | 1185 | 113 | 511.5 | 205.5 | 2 |  | 207.5 | 70% | 64% | 93% | 80% | 3.836 | Loss 0-5% |  | 1004(82.5) | 997(183.5) | 985(199.5) | 781(54.5)
947 | 1230 | LNR | ANAND VIHAR ISBT | MAN052 | TG-MAN052A-1 | DT-1 | HASANPUR VILLAGE:PL | 1 | 990 | 19504543 | 847 | 2019-06-11 15:00 | 280 | 1155 | 266 | 1089 | 300 | 1234 | 126 | 615.5 | 104.5 |  |  | 104.5 | 48% | 40% | 86% | 50% | 4.2201 | Loss 0-5% |  |  | 853(66)
948 | 1230 | LNR | ANAND VIHAR ISBT | MAN053 | TG-MAN053A-1 | DT-1 | GAZIPUR VILLAGE NEAR TEMPEL:PL | 1 | 990 | 19506444 | 876 | 2019-06-27 22:30 | 295 | 1224 | 298 | 1230 | 282 | 1168 | 59 | 548.5 | 170.5 |  |  | 170.5 | 88% | 72% | 85% | 88% | 16.9067 | Loss 10-20% |  | 805(28.5) | 872(402) | 939(225) | 844(62.5)
949 | 1230 | LNR | ANAND VIHAR ISBT | MAN054 | TG-MAN054A-1 | DT-1 | GAZIPUR VILLAGE NEAR SCHOOL:PL | 2 | 990 | 19502869 | 991 | 2019-06-13 15:00 | 371 | 1488 | 285 | 1232 | 336 | 1415 | 228 | 143 | 532.5 | 42 | 0.5 | 575 | 87% | 79% | 100% | 91% | 36.1615 | Loss >30% | 752(29.5) | 904(318) | 911(522) | 937(544) | 969(482.5) | 849(237)
950 | 1230 | LNR | ANAND VIHAR ISBT | MAN054 | TG-MAN054A-2 | DT-2 | GAZIPUR VILLAGE NEAR SCHOOL:PL | 2 | 630 | 19505949 | 427 | 2019-06-29 20:30 | 150 | 614 | 154 | 636 | 122 | 502 | 125 | 719 |  |  |  | 0 | 57% | 57% | 68% | 62% | 36.1615 | Loss >30% |  |  |  | 485(26)
951 | 1230 | LNR | ANAND VIHAR ISBT | MAN066 | TG-MAN066A-1 | DT-1 | S/STN.NO-9, PPG CGHS:ID | 2 | 990 | 19500433 | 441 | 2019-06-30 23:00 | 171 | 710 | 132 | 558 | 139 | 579 | 143 | 719.5 |  |  |  | 0 | 41% | 29% | 35% | 45% | 13.1165 | Loss 10-20% |  | 1101(116.5) | 1166(320.5) | 1169(270)
952 | 1230 | LNR | ANAND VIHAR ISBT | MAN066 | TG-MAN066A-2 | DT-2 | S/STN.NO-9, PPG CGHS:ID | 2 | 630 | 19506561 | 791 | 2019-06-30 23:30 | 245 | 1039 | 259 | 1103 | 288 | 1219 | 158 | 384.5 | 207.5 | 71 | 57 | 335.5 | 116% | 91% | 96% | 126% | 13.1165 | Loss 10-20% |  |  |  |  | 679(132.5) | 537(40)
953 | 1230 | LNR | ANAND VIHAR ISBT | MAN068 | TG-MAN068A-1 | DT-1 | S/STN.NO-13, PPG CGHS:ID | 1 | 400 | 19502466 | 312 | 2019-06-30 23:00 | 92 | 408 | 128 | 568 | 91 | 403 | 162 | 679.5 | 40.5 |  |  | 40.5 | 73% | 64% | 69% | 78% | 4.8531 | Loss 0-5% |  |  |  | 313(64.5) | 294(40.5)
954 | 1230 | LNR | ANAND VIHAR ISBT | MAN252 | TG-MAN252A-1 | DT-1 | S/STN NO-10, CGHS, PPG | 2 | 630 | 19504304 | 113 | 2019-06-10 14:30 | 45 | 191 | 39 | 167 | 29 | 120 | 62 | 720 |  |  |  | 0 | 9% | 7% | 18% | 16% | 4.0334 | Loss 0-5%
955 | 1230 | LNR | ANAND VIHAR ISBT | MAN252 | TG-MAN252A-2 | DT-2 | S/STN NO-10, CGHS, PPG | 2 | 630 | 19504305 | 714 | 2019-06-30 23:30 | 210 | 953 | 276 | 1274 | 227 | 1037 | 289 | 206.5 | 401.5 | 90 | 22 | 513.5 | 108% | 82% | 98% | 113% | 4.0334 | Loss 0-5%
956 | 1230 | LNR | ANAND VIHAR ISBT | MAN292 | TG-MAN292A-1 | DT-1 | GAZIPUR PARK NEAR ASHOK DAIRY STN:OD | 1 | 990 | 19506443 | 868 | 2019-06-29 16:00 | 265 | 1058 | 276 | 1113 | 328 | 1327 | 247 | 404 | 314 |  |  | 314 | 78% | 69% | 88% | 87% | 37.9141 | Loss >30% |  | 832(139.5) | 822(595) | 1040(283) | 840(272) | 767(91.5)
957 | 1230 | LNR | ANAND VIHAR ISBT | PVR032 | TG-PVR032A-1 | DT-1 | S/STN. NO.7 F.I.E., PPG:ID | 2 | 990 | 19505236 | 841 | 2019-06-20 14:30 | 220 | 923 | 306 | 1300 | 316 | 1328 | 392 | 656 | 57.5 |  |  | 57.5 | 26% | 27% | 85% | 26% | 5.6528 | Loss 5-10%
958 | 1230 | LNR | ANAND VIHAR ISBT | PVR032 | TG-PVR032A-2 | DT-2 | S/STN. NO.7 F.I.E., PPG:ID | 2 | 630 | 19506697 | 426 | 2019-06-29 12:00 | 150 | 621 | 142 | 593 | 134 | 554 | 58 | 719.5 |  |  |  | 0 | 15% | 23% | 68% | 16% | 5.6528 | Loss 5-10% | 555(52.5) | 551(86) | 529(45.5) | 519(31)
959 | 1230 | LNR | ANAND VIHAR ISBT | PVR034 | TG-PVR034A-1 | DT-1 | S/STN. NO.8 F.I.E., PPG:ID | 3 | 630 | 19505921 | 577 | 2019-06-12 15:00 | 191 | 806 | 190 | 798 | 195 | 820 | 19 | 596 | 121 | 3 |  | 124 | 42% | 50% | 92% | 44% | 8.0328 | Loss 5-10% | 556(53) | 599(102.5) | 590(45.5) | 654(27) | 702(111) | 705(158)
960 | 1230 | LNR | ANAND VIHAR ISBT | PVR034 | TG-PVR034A-2 | DT-2 | S/STN. NO.8 F.I.E., PPG:ID | 3 | 630 | 19500757 | 468 | 2019-06-24 15:30 | 145 | 577 | 167 | 667 | 155 | 620 | 78 | 711.5 | 8.5 |  |  | 8.5 | 23% | 34% | 74% | 26% | 8.0328 | Loss 5-10% | 613(160.5) | 561(43.5) | 532(70.5) | 524(52.5) | 531(65.5) | 555(97)
961 | 1230 | LNR | ANAND VIHAR ISBT | PVR034 | TG-PVR034A-3 | DT-3 | S/STN. NO.8 F.I.E., PPG:ID | 3 | 990 | 19505812 | 860 | 2019-06-03 18:00 | 278 | 1148 | 290 | 1200 | 292 | 1211 | 59 | 698 | 22 |  |  | 22 | 56% | 60% | 87% | 61% | 8.0328 | Loss 5-10%
962 | 1230 | LNR | ANAND VIHAR ISBT | PVR035 | TG-PVR035A-1 | DT-1 | S/STN. NO.9 F.I.E., PPG:ID | 1 | 990 | 19504874 | 799 | 2019-06-27 12:30 | 250 | 1006 | 280 | 1129 | 268 | 1078 | 107 | 678 | 36.5 |  |  | 36.5 | 17% | 31% | 81% | 19% | 2.9671 | Loss 0-5% |  |  | 875(104) | 832(56) | 851(70.5) | 814(26)
963 | 1230 | LNR | ANAND VIHAR ISBT | PVR039 | TG-PVR039A-1 | DT-1 | S/STN. NO.14 F.I.E., PPG:ID | 2 | 630 | 19505920 | 539 | 2019-06-28 17:00 | 183 | 757 | 170 | 698 | 186 | 767 | 65 | 686.5 | 33.5 |  |  | 33.5 | 46% | 44% | 85% | 43% | 4.5327 | Loss 0-5% | 562(156.5) | 639(191) | 654(226.5) | 661(221) | 630(211) | 654(186)
964 | 1230 | LNR | ANAND VIHAR ISBT | PVR039 | TG-PVR039A-2 | DT-2 | S/STN. NO.14 F.I.E., PPG:ID | 2 | 630 | 19506770 | 311 | 2019-06-26 11:00 | 100 | 411 | 100 | 409 | 111 | 456 | 46 | 720 |  |  |  | 0 | 22% | 26% | 49% | 25% | 4.5327 | Loss 0-5%
965 | 1230 | LNR | ANAND VIHAR ISBT | PVR040 | TG-PVR040A-1 | DT-1 | S/STN. NO.15 F.I.E., PPG:ID | 2 | 990 | 19504935 | 616 | 2019-06-12 15:00 | 216 | 890 | 205 | 848 | 195 | 809 | 70 | 719.5 |  |  |  | 0 | 15% | 26% | 62% | 15% | 3.361 | Loss 0-5% |  |  |  | 821(30.5)
966 | 1230 | LNR | ANAND VIHAR ISBT | PVR040 | TG-PVR040A-2 | DT-2 | S/STN. NO.15 F.I.E., PPG:ID | 2 | 400 | 19504783 | 384 | 2019-06-06 11:30 | 121 | 520 | 149 | 640 | 114 | 491 | 137 | 598 | 118 | 4 |  | 122 | 32% | 35% | 96% | 35% | 3.361 | Loss 0-5% | 388(118.5) | 440(123) | 445(187.5) | 460(220) |  | 475(198.5)
967 | 1230 | LNR | ANAND VIHAR ISBT | PVR041 | TG-PVR041A-1 | DT-1 | S/STN. NO.16 F.I.E., PPG:ID | 2 | 630 | 19502418 | 288 | 2019-06-29 10:30 | 100 | 417 | 95 | 398 | 93 | 388 | 25 | 720 |  |  |  | 0 | 14% | 16% | 46% | 15% | 3.4315 | Loss 0-5%
968 | 1230 | LNR | ANAND VIHAR ISBT | PVR041 | TG-PVR041A-2 | DT-2 | S/STN. NO.16 F.I.E., PPG:ID | 2 | 630 | 19502874 | 573 | 2019-06-29 13:00 | 195 | 801 | 180 | 738 | 198 | 818 | 74 | 611.5 | 108 | 0.5 |  | 108.5 | 34% | 30% | 91% | 35% | 3.4315 | Loss 0-5% | 525(47) | 543(56) | 581(110) | 534(92.5) | 538(72.5) | 512(41)
969 | 1230 | LNR | ANAND VIHAR ISBT | PVR045 | TG-PVR045A-1 | DT-1 | S/STN. NO.20 F.I.E., PPG:ID | 3 | 400 | 19505036 | 351 | 2019-06-13 12:30 | 121 | 516 | 117 | 503 | 113 | 488 | 24 | 627.5 | 92.5 |  |  | 92.5 | 36% | 43% | 88% | 42% | 3.8502 | Loss 0-5%
970 | 1230 | LNR | ANAND VIHAR ISBT | PVR045 | TG-PVR045A-2 | DT-2 | S/STN. NO.20 F.I.E., PPG:ID | 3 | 630 | 19505034 | 330 | 2019-06-13 11:00 | 105 | 448 | 111 | 473 | 114 | 481 | 30 | 720 |  |  |  | 0 | 20% | 25% | 52% | 22% | 3.8502 | Loss 0-5%
971 | 1230 | LNR | ANAND VIHAR ISBT | PVR045 | TG-PVR045A-3 | DT-3 | S/STN. NO.20 F.I.E., PPG:ID | 3 | 630 | 19505035 | 589 | 2019-06-03 15:30 | 199 | 827 | 216 | 903 | 174 | 724 | 156 | 580 | 136.5 | 3.5 |  | 140 | 43% | 43% | 94% | 43% | 3.8502 | Loss 0-5% |  | 544(54.5) | 576(125) | 527(98.5) | 548(114) | 554(87)
972 | 1230 | LNR | ANAND VIHAR ISBT | PVR046 | TG-PVR046A-1 | DT-1 | S/STN. NO.21 F.I.E., PPG:ID | 2 | 630 | 19506665 | 485 | 2019-06-07 16:00 | 164 | 716 | 164 | 723 | 157 | 689 | 32 | 693.5 | 26.5 |  |  | 26.5 | 14% | 31% | 77% | 15% | 3.0005 | Loss 0-5% |  | 533(52) | 501(70) | 522(83)
973 | 1230 | LNR | ANAND VIHAR ISBT | PVR046 | TG-PVR046A-2 | DT-2 | S/STN. NO.21 F.I.E., PPG:ID | 2 | 630 | 19504984 | 458 | 2019-06-26 14:30 | 150 | 653 | 159 | 697 | 148 | 640 | 52 | 715 | 2.5 |  |  | 2.5 | 29% | 25% | 73% | 34% | 3.0005 | Loss 0-5% | 475(27) | 507(71.5) | 512(99) | 508(82.5) | 515(26.5) | 516(55)
974 | 1230 | LNR | ANAND VIHAR ISBT | PVR047 | TG-PVR047A-1 | DT-1 | S/STN. NO.22 F.I.E., PPG:ID | 2 | 630 | 19506769 | 782 | 2019-06-06 17:00 | 271 | 1097 | 257 | 1032 | 254 | 1028 | 67 | 469.5 | 69.5 | 67.5 | 113.5 | 250.5 | 30% | 51% | 124% | 38% | 5.8263 | Loss 5-10% |  | 567(45) | 748(228.5) | 730(229.5) | 712(222.5) | 714(194)
975 | 1230 | LNR | ANAND VIHAR ISBT | PVR047 | TG-PVR047A-2 | DT-2 | S/STN. NO.22 F.I.E., PPG:ID | 2 | 630 | 19504981 | 643 | 2019-06-08 14:00 | 193 | 799 | 228 | 956 | 222 | 925 | 144 | 521 | 135.5 | 59.5 | 1.5 | 196.5 | 25% | 36% | 102% | 25% | 5.8263 | Loss 5-10% | 653(183) | 741(240.5) | 563(62.5)
976 | 1230 | LNR | ANAND VIHAR ISBT | PVR049 | TG-PVR049A-1 | DT-1 | S/STN. NO.24 F.I.E., PPG:ID | 2 | 400 | 19505052 | 217 | 2019-06-28 10:30 | 77 | 309 | 72 | 285 | 68 | 270 | 33 | 720 |  |  |  | 0 | 18% | 34% | 54% | 18% | 4.0718 | Loss 0-5%
977 | 1230 | LNR | ANAND VIHAR ISBT | PVR049 | TG-PVR049A-2 | DT-2 | S/STN. NO.24 F.I.E., PPG:ID | 2 | 630 | 19506489 | 576 | 2019-06-14 14:30 | 190 | 808 | 174 | 745 | 212 | 911 | 145 | 591 | 127.5 | 1.5 |  | 129 | 18% | 35% | 91% | 22% | 4.0718 | Loss 0-5% |  |  | 745(197) | 747(241.5) | 725(253.5)
978 | 1230 | LNR | LAXMI NAGAR | LGR001 | TG-LGR001A-1 | DT-1 | PRIYADARSHINI VIHAR:ID | 2 | 990 | 19505699 | 961.7521 | 2019-06-27 | 302.3323 | 1368.8865 | 327.9906 | 1485.734 | 331.4292 | 1493.1933 | 120.7501 | 672.5 | 42.5 | 3 |  | 45.5 | 97% | 61% | 70% | 90% | 3.5476 | Loss 0-5% |  |  | 844(35.5)
979 | 1230 | LNR | LAXMI NAGAR | LGR001 | TG-LGR001A-2 | DT-2 | PRIYADARSHINI VIHAR:ID | 2 | 990 | 19506908 | 896 | 2019-06-10 11:30 | 277 | 1161 | 292 | 1213 | 328 | 1381 | 200 | 717.5 |  | 0.5 |  | 0.5 | 58% | 37% | 91% | 58% | 3.5476 | Loss 0-5%
980 | 1230 | LNR | LAXMI NAGAR | LGR002 | TG-LGR002A-1 | DT-1 | PNB BANK ENCLAVE:ID | 3 | 990 | 19505159 | 619.2019 | 2019-06-29 23:30 | 219.9527 | 913.1594 | 212.9155 | 887.0369 | 186.3337 | 764.4774 | 137.4946 | 129 |  |  |  | 0 | 62% | 39% | 55% | 63% | 4.3519 | Loss 0-5%
981 | 1230 | LNR | LAXMI NAGAR | LGR002 | TG-LGR002A-2 | DT-2 | PNB BANK ENCLAVE:ID | 3 | 990 | 19502526 | 650 | 2019-06-30 | 164 | 678 | 272 | 1172 | 215 | 911 | 428 | 671 |  |  |  | 0 | 66% | 41% | 50% | 65% | 4.3519 | Loss 0-5%
982 | 1230 | LNR | LAXMI NAGAR | LGR002 | TG-LGR002A-3 | DT-3 | PNB BANK ENCLAVE:ID | 3 | 990 | 19504436 | 1045 | 2019-06-12 00:30 | 391 | 1644 | 320 | 1326 | 334 | 1396 | 289 | 491.5 | 143 | 45 | 12 | 200 | 106% | 86% | 80% | 105% | 4.3519 | Loss 0-5% |  | 1050(111) | 1044(211.5) | 1058(136.5) | 879(66.5)
983 | 1230 | LNR | LAXMI NAGAR | LGR003 | TG-LGR003A-1 | DT-1 | LNR COMPLAINT CENTER:ID | 3 | 630 | 19502778 | 523 | 2019-06-30 20:00 | 239 | 988 | 145 | 586 | 139 | 569 | 410 | 613.5 | 106.5 |  |  | 106.5 | 76% | 52% | 83% | 83% | 3.5995 | Loss 0-5% |  |  | 527(62.5)
984 | 1230 | LNR | LAXMI NAGAR | LGR003 | TG-LGR003A-2 | DT-2 | LNR COMPLAINT CENTER:ID | 3 | 990 | 19505889 | 766 | 2019-06-02 21:00 | 368 | 1603 | 260 | 1110 | 138 | 592 | 876 | 703 | 17 |  |  | 17 | 64% | 45% | 76% | 77% | 3.5995 | Loss 0-5%
985 | 1230 | LNR | LAXMI NAGAR | LGR003 | TG-LGR003A-3 | DT-3 | LNR COMPLAINT CENTER:ID | 3 | 990 | 19505700 | 462 | 2019-06-10 15:30 | 131 | 540 | 96 | 388 | 235 | 989 | 541 | 720 |  |  |  | 0 | 38% | 28% | 47% | 43% | 3.5995 | Loss 0-5%
986 | 1230 | LNR | LAXMI NAGAR | LGR004 | TG-LGR004A-1 | DT-1 | KISHAN KUNJ:K | 3 | 990 | 19505542 | 1036 | 2019-06-30 00:30 | 355 | 1502 | 336 | 1409 | 345 | 1445 | 82 | 580.5 | 129.5 | 5.5 | 2 | 137 | 105% | 72% | 65% | 93% | 8.7407 | Loss 5-10% |  | 1051(107.5) | 939(135.5) | 889(78)
987 | 1230 | LNR | LAXMI NAGAR | LGR004 | TG-LGR004A-2 | DT-2 | KISHAN KUNJ:K | 3 | 990 | 19505955 | 1288 | 2019-06-30 00:30 | 470 | 2013 | 417 | 1756 | 401 | 1689 | 296 | 490.5 | 132.5 | 62 | 33 | 227.5 | 130% | 82% | 77% | 111% | 8.7407 | Loss 5-10% |  | 934(27) | 1190(192) | 1066(173.5) | 914(121)
988 | 1230 | LNR | LAXMI NAGAR | LGR004 | TG-LGR004A-3 | DT-3 | KISHAN KUNJ:K | 3 | 990 | 19506173 | 1313 | 2019-06-30 00:30 | 476 | 2043 | 448 | 1904 | 389 | 1642 | 353 | 394.5 | 177 | 67 | 80 | 324 | 133% | 89% | 91% | 126% | 8.7407 | Loss 5-10% |  | 1109(126.5) | 1146(282.5) | 1128(220.5) | 978(168) | 828(28)
989 | 1230 | LNR | LAXMI NAGAR | LGR007 | TG-LGR007A-1 | DT-1 | WALIA NURSHING HOME:PL | 2 | 990 | 19505671 | 658 | 2019-06-08 16:00 | 180 | 777 | 231 | 992 | 247 | 1072 | 264 | 719.5 |  |  |  | 0 | 30% | 22% | 66% | 57% | 4.4856 | Loss 0-5% |  |  | 877(94)
990 | 1230 | LNR | LAXMI NAGAR | LGR007 | TG-LGR007A-2 | DT-2 | WALIA NURSHING HOME:PL | 2 | 630 | 19505459 | 631 | 2019-06-08 15:00 | 208 | 906 | 207 | 912 | 215 | 940 | 32 | 543 | 168.5 | 7 | 0.5 | 176 | 73% | 54% | 100% | 73% | 4.4856 | Loss 0-5% |  |  | 521(62.5) | 590(114) | 617(116.5) | 518(39.5)
991 | 1230 | LNR | LAXMI NAGAR | LGR008 | TG-LGR008A-1 | DT-1 | LALITA PARK:K | 3 | 990 | 19506683 | 825 | 2019-06-28 23:30 | 272 | 1230 | 232 | 1033 | 320 | 1432 | 346 | 665 | 54.5 |  |  | 54.5 | 79% | 55% | 57% | 83% | 5.1258 | Loss 5-10% |  |  | 789(57)
992 | 1230 | LNR | LAXMI NAGAR | LGR008 | TG-LGR008A-2 | DT-2 | LALITA PARK:K | 3 | 990 | 19505453 | 531 | 2019-06-30 23:00 | 190 | 793 | 160 | 666 | 181 | 755 | 113 | 720 |  |  |  | 0 | 53% | 37% | 43% | 54% | 5.1258 | Loss 5-10%
993 | 1230 | LNR | LAXMI NAGAR | LGR008 | TG-LGR008A-3 | DT-3 | LALITA PARK:K | 3 | 990 | 19506761 | 785 | 2019-06-28 23:30 | 308 | 1371 | 191 | 842 | 286 | 1287 | 493 | 682.5 | 37 |  |  | 37 | 77% | 51% | 59% | 79% | 5.1258 | Loss 5-10%
994 | 1230 | LNR | LAXMI NAGAR | LGR009 | TG-LGR009A-1 | DT-1 | RAMESH PARK AKHARA:PL | 2 | 990 | 19503006 | 855 | 2019-06-01 04:30 | 273 | 1139 | 251 | 1040 | 332 | 1403 | 324 | 680 | 39.5 |  |  | 39.5 | 86% | 76% | 73% | 73% | 5.077 | Loss 5-10% |  | 929(187.5) | 1023(390.5) | 989(232) | 843(132.5)
995 | 1230 | LNR | LAXMI NAGAR | LGR009 | TG-LGR009A-2 | DT-2 | RAMESH PARK AKHARA:PL | 2 | 990 | 19506036 | 917 | 2019-06-01 19:00 | 363 | 1740 | 396 | 1763 | 158 | 673 | 1078 | 661.5 | 56 | 0.5 |  | 56.5 | 49% | 38% | 93% | 51% | 5.077 | Loss 5-10%
996 | 1230 | LNR | LAXMI NAGAR | LGR011 | TG-LGR011A-1 | DT-1 | JAGAT RAM PARK:K | 5 | 990 | 19502822 | 934 | 2019-06-30 00:30 | 359 | 1503 | 283 | 1197 | 292 | 1219 | 296 | 584.5 | 128.5 | 7 |  | 135.5 | 94% | 67% | 64% | 92% | 8.6892 | Loss 5-10% | 931(27) | 1098(197.5) | 1130(219) | 912(104) | 803(51.5)
997 | 1230 | LNR | LAXMI NAGAR | LGR011 | TG-LGR011A-2 | DT-2 | JAGAT RAM PARK:K | 5 | 990 | 19502825 | 906 | 2019-06-06 03:30 | 312 | 1349 | 302 | 1296 | 292 | 1269 | 70 | 606.5 | 112 | 0.5 |  | 112.5 | 91% | 63% | 65% | 89% | 8.6892 | Loss 5-10% |  |  | 870(78) | 870(70)
998 | 1230 | LNR | LAXMI NAGAR | LGR011 | TG-LGR011A-3 | DT-3 | JAGAT RAM PARK:K | 5 | 990 | 19506037 | 928 | 2019-06-03 23:00 | 365 | 1607 | 355 | 1510 | 207 | 885 | 679 | 620.5 | 99 | 0.5 |  | 99.5 | 85% | 60% | 66% | 94% | 8.6892 | Loss 5-10% |  | 1034(30) | 1005(96.5) | 844(48.5)
999 | 1230 | LNR | LAXMI NAGAR | LGR011 | TG-LGR011A-4 | DT-4 | JAGAT RAM PARK:K | 5 | 630 | 19504472 | 480 | 2019-06-02 23:30 | 163 | 731 | 180 | 810 | 137 | 611 | 174 | 712.5 | 7.5 |  |  | 7.5 | 74% | 47% | 50% | 76% | 8.6892 | Loss 5-10% |  | 659(150.5) | 676(246) | 666(177) | 594(143.5)
1000 | 1230 | LNR | LAXMI NAGAR | LGR011 | TG-LGR011A-5 | DT-5 | JAGAT RAM PARK:K | 5 | 630 | 19506715 | 441 | 2019-06-18 01:30 | 93 | 384 | 204 | 854 | 144 | 598 | 407 | 719.5 | 0.5 |  |  | 0.5 | 70% | 36% | 48% | 55% | 8.6892 | Loss 5-10%
1001 | 1230 | LNR | LAXMI NAGAR | LGR012 | TG-LGR012A-1 | DT-1 | GURU RAM DASS NAGAR:PL | 3 | 990 | 19502826 | 891 | 2019-06-30 23:30 | 298 | 1285 | 318 | 1368 | 276 | 1181 | 162 | 615.5 | 104.5 |  |  | 104.5 | 90% | 60% | 66% | 90% | 5.962 | Loss 5-10% |  | 1158(174.5) | 1085(216) | 1148(156) | 884(113)
1002 | 1230 | LNR | LAXMI NAGAR | LGR012 | TG-LGR012A-2 | DT-2 | GURU RAM DASS NAGAR:PL | 3 | 990 | 19502829 | 1153.7459 | 2019-06-12 | 364.1066 | 1501.9659 | 377.1575 | 1548.4561 | 412.4819 | 1714.531 | 193.5538 | 296.5 | 101.5 | 43.5 | 48.5 | 193.5 | 117% | 78% | 84% | 116% | 5.962 | Loss 5-10% | 843(49) | 1058(104.5) | 1125(276.5) | 1075(205) | 974(181) | 840(35)
1003 | 1230 | LNR | LAXMI NAGAR | LGR012 | TG-LGR012A-3 | DT-3 | GURU RAM DASS NAGAR:PL | 3 | 990 | 19505569 | 1059 | 2019-06-30 01:30 | 395 | 1655 | 367 | 1557 | 297 | 1238 | 378 | 555.5 | 141 | 18.5 | 3 | 162.5 | 107% | 72% | 69% | 96% | 5.962 | Loss 5-10% |  | 1014(190) | 775(345) | 808(271)
1004 | 1230 | LNR | LAXMI NAGAR | LGR014 | TG-LGR014A-1 | DT-1 | TIKONA PARK:ID | 4 | 990 | 19502942 | 1007 | 2019-06-11 23:30 | 257 | 1050 | 366 | 1516 | 384 | 1597 | 511 | 504 | 192 | 21 | 0.5 | 213.5 | 100% | 70% | 86% | 102% | 8.6616 | Loss 5-10% |  | 1032(141.5) | 1130(358) | 1116(194) | 794(41)
1005 | 1230 | LNR | LAXMI NAGAR | LGR014 | TG-LGR014A-2 | DT-2 | TIKONA PARK:ID | 4 | 990 | 19505669 | 865 | 2019-06-30 23:30 | 241 | 1049 | 362 | 1591 | 262 | 1145 | 501 | 685.5 | 34.5 |  |  | 34.5 | 84% | 59% | 81% | 87% | 8.6616 | Loss 5-10% |  | 1167(197) | 1244(305.5)
1006 | 1230 | LNR | LAXMI NAGAR | LGR014 | TG-LGR014A-3 | DT-3 | TIKONA PARK:ID | 4 | 630 | 19505467 | 727 | 2019-06-11 23:30 | 295 | 1191 | 198 | 794 | 234 | 935 | 349 | 468.5 | 161.5 | 53 | 37 | 251.5 | 115% | 75% | 81% | 115% | 8.6616 | Loss 5-10% |  |  | 669(120.5) | 750(310.5) | 658(237) | 567(47.5)
1007 | 1230 | LNR | LAXMI NAGAR | LGR014 | TG-LGR014A-4 | DT-4 | TIKONA PARK:ID | 4 | 630 | 19505750 | 505 | 2019-06-11 23:30 | 232 | 949 | 134 | 545 | 139 | 561 | 396 | 701 | 19 |  |  | 19 | 79% | 50% | 57% | 80% | 8.6616 | Loss 5-10%
1008 | 1230 | LNR | LAXMI NAGAR | LGR016 | TG-LGR016A-1 | DT-1 | WEST GURU ANGAD NAGAR, SCHOOL WALA | 1 | 990 | 19502944 | 755 | 2019-06-10 00:30 | 224 | 938 | 265 | 1126 | 265 | 1117 | 184 | 693 | 27 |  |  | 27 | 76% | 56% | 69% | 76% | 3.1758 | Loss 0-5% |  |  | 788(39.5)
1009 | 1230 | LNR | LAXMI NAGAR | LGR017 | TG-LGR017A-1 | DT-1 | POLICE QTR SHAKARPUR:ID | 2 | 990 | 19505830 | 224 | 2019-06-30 | 90 | 381 | 75 | 315 | 60 | 256 | 108 | 720 |  |  |  | 0 | 23% | 16% | 21% | 22% | 9.1818 | Loss 5-10%
1010 | 1230 | LNR | LAXMI NAGAR | LGR017 | TG-LGR017A-2 | DT-2 | POLICE QTR SHAKARPUR:ID | 2 | 990 | 19503391 | 784 | 2019-06-30 00:30 | 283 | 1252 | 237 | 1049 | 264 | 1170 | 177 | 664.5 | 31.5 |  |  | 31.5 | 79% | 64% | 60% | 76% | 9.1818 | Loss 5-10% |  |  | 804(100.5) | 840(57.5)
1011 | 1230 | LNR | LAXMI NAGAR | LGR018 | TG-LGR018A-1 | DT-1 | D BLOCK KHATTA VIKAS MARG:PL | 3 | 990 | 19506589 | 719 | 2019-06-10 23:00 | 268 | 1224 | 225 | 1011 | 226 | 1012 | 212 | 714 | 5.5 |  |  | 5.5 | 71% | 50% | 62% | 73% | 9.5255 | Loss 5-10%
1012 | 1230 | LNR | LAXMI NAGAR | LGR018 | TG-LGR018A-2 | DT-2 | D BLOCK KHATTA VIKAS MARG:PL | 3 | 990 | 19504830 | 830 | 2019-06-11 22:30 | 312 | 1363 | 283 | 1239 | 235 | 1038 | 284 | 545.5 | 174.5 |  |  | 174.5 | 82% | 64% | 79% | 84% | 9.5255 | Loss 5-10% |  | 871(173.5) | 987(469.5) | 1121(385) | 989(346) | 766(71.5)
1013 | 1230 | LNR | LAXMI NAGAR | LGR018 | TG-LGR018A-3 | DT-3 | D BLOCK KHATTA VIKAS MARG:PL | 3 | 630 | 19506175 | 384 | 2019-06-25 16:00 | 141 | 586 | 124 | 515 | 119 | 488 | 87 | 720 |  |  |  | 0 | 34% | 25% | 61% | 33% | 9.5255 | Loss 5-10%
1014 | 1230 | LNR | LAXMI NAGAR | LGR019 | TG-LGR019A-1 | DT-1 | RAMESH PARK J & K BLOCK:PL | 1 | 1600 | 19502336 | 1286 | 2019-06-01 | 421 | 1847 | 471 | 2103 | 393 | 1728 | 332 | 672 | 48 |  |  | 48 | 80% | 53% | 58% | 79% | 8.5694 | Loss 5-10% |  | 1183(199.5)
1015 | 1230 | LNR | LAXMI NAGAR | LGR020 | TG-LGR020A-1 | DT-1 | MASTER BLOCK SHAKARPUR:PL | 2 | 990 | 19502830 | 593 | 2019-06-11 01:30 | 282 | 1243 | 169 | 768 | 142 | 650 | 544 | 696 |  |  |  | 0 | 60% | 41% | 49% | 58% | 3.0777 | Loss 0-5%
1016 | 1230 | LNR | LAXMI NAGAR | LGR020 | TG-LGR020A-2 | DT-2 | MASTER BLOCK SHAKARPUR:PL | 2 | 630 | 19505481 | 546 | 2019-06-28 23:00 | 158 | 698 | 154 | 673 | 234 | 1044 | 359 | 650 | 70 |  |  | 70 | 86% | 57% | 62% | 87% | 3.0777 | Loss 0-5%
1017 | 1230 | LNR | LAXMI NAGAR | LGR021 | TG-LGR021A-1 | DT-1 | G-BLOCK SHAKARPUR:K | 2 | 990 | 19504461 | 1055 | 2019-06-12 | 367 | 1564 | 359 | 1533 | 330 | 1417 | 134 | 493 | 131.5 | 56 | 14.5 | 202 | 107% | 83% | 76% | 105% | 9.4444 | Loss 5-10%
1018 | 1230 | LNR | LAXMI NAGAR | LGR021 | TG-LGR021A-2 | DT-2 | G-BLOCK SHAKARPUR:K | 2 | 990 | 19502945 | 1186 | 2019-06-30 01:00 | 406 | 1720 | 384 | 1638 | 396 | 1690 | 72 | 512.5 | 130.5 | 57.5 | 16.5 | 204.5 | 120% | 77% | 77% | 108% | 9.4444 | Loss 5-10% |  | 975(98.5) | 1121(203.5) | 1090(141) | 1038(93)
1019 | 1230 | LNR | LAXMI NAGAR | LGR022 | TG-LGR022A-1 | DT-1 | WB BLOCK SHAKARPUR:K | 4 | 990 | 19506691 | 1031 | 2019-06-30 23:00 | 336 | 1432 | 331 | 1384 | 363 | 1540 | 139 | 543.5 | 137 | 35.5 | 4 | 176.5 | 101% | 66% | 74% | 104% | 4.679 | Loss 0-5% |  |  | 846(64.5) | 866(51.5) | 855(30)
1020 | 1230 | LNR | LAXMI NAGAR | LGR022 | TG-LGR022A-2 | DT-2 | WB BLOCK SHAKARPUR:K | 4 | 990 | 19502950 | 984 | 2019-06-30 23:30 | 348 | 1486 | 361 | 1563 | 274 | 1157 | 373 | 546 | 149.5 | 23.5 |  | 173 | 98% | 65% | 72% | 99% | 4.679 | Loss 0-5% |  | 871(55) | 1089(196) | 1096(182.5) | 956(68)
1021 | 1230 | LNR | LAXMI NAGAR | LGR022 | TG-LGR022A-3 | DT-3 | WB BLOCK SHAKARPUR:K | 4 | 990 | 19504770 | 870 | 2019-06-29 23:30 | 258 | 1073 | 315 | 1320 | 298 | 1258 | 223 | 632.5 | 62.5 |  |  | 62.5 | 87% | 57% | 64% | 88% | 4.679 | Loss 0-5% |  | 886(70) | 1009(96.5)
1022 | 1230 | LNR | LAXMI NAGAR | LGR022 | TG-LGR022A-4 | DT-4 | WB BLOCK SHAKARPUR:K | 4 | 630 | 19506276 | 639 | 2019-06-03 00:30 | 187 | 800 | 213 | 908 | 240 | 1040 | 209 | 589.5 | 124.5 | 3.5 | 0.5 | 128.5 | 101% | 65% | 67% | 93% | 4.679 | Loss 0-5% |  | 541(39) | 548(103) | 530(45)
1023 | 1230 | LNR | LAXMI NAGAR | LGR024 | TG-LGR024A-1 | DT-1 | SHAKARPUR SANJAY PARK | 2 | 990 | 19505154 | 1211 | 2019-06-02 00:30 | 417 | 1835 | 489 | 2257 | 305 | 1329 | 804 | 438 | 174 | 69 | 37 | 280 | 122% | 81% | 87% | 110% | 12.3224 | Loss 10-20% | 958(55.5) |  | 1086(271.5) | 1066(202.5) | 965(171)
1024 | 1230 | LNR | LAXMI NAGAR | LGR024 | TG-LGR024A-2 | DT-2 | SHAKARPUR SANJAY PARK | 2 | 990 | 19502827 | 1061 | 2019-06-11 23:30 | 345 | 1568 | 374 | 1705 | 342 | 1563 | 139 | 511.5 | 152.5 | 41 | 14 | 207.5 | 107% | 86% | 79% | 107% | 12.3224 | Loss 10-20% |  | 967(66.5) | 1141(229) | 1089(184.5) | 908(130)
1025 | 1230 | LNR | LAXMI NAGAR | LGR025 | TG-LGR025A-1 | DT-1 | DALL MILL SHAKARPUR:PM | 1 | 990 | 19502941 | 892 | 2019-06-29 23:30 | 316 | 1331 | 264 | 1098 | 313 | 1310 | 223 | 581 | 138.5 | 0.5 |  | 139 | 90% | 68% | 69% | 90% | 13.3322 | Loss 10-20% |  | 773(29) | 836(122.5) | 852(88.5) | 791(36.5)
1026 | 1230 | LNR | LAXMI NAGAR | LGR026 | TG-LGR026A-1 | DT-1 | POLICE BOOTH S. PUR, V. MARG:PL | 1 | 990 | 19506000 | 843 | 2019-06-10 23:30 | 263 | 1204 | 209 | 939 | 371 | 1723 | 691 | 590.5 | 128 |  |  | 128 | 84% | 70% | 82% | 85% | 8.6678 | Loss 5-10% |  |  | 907(123) | 1226(32)
1027 | 1230 | LNR | LAXMI NAGAR | LGR027 | TG-LGR027A-1 | DT-1 | U BLOCK SHAKARPUR, V. MARG:PL | 2 | 990 | 19506384 | 864 | 2019-06-15 23:30 | 333 | 1516 | 236 | 1065 | 296 | 1350 | 395 | 717 | 2.5 |  |  | 2.5 | 69% | 49% | 65% | 87% | 4.8678 | Loss 0-5%
1028 | 1230 | LNR | LAXMI NAGAR | LGR027 | TG-LGR027A-2 | DT-2 | U BLOCK SHAKARPUR, V. MARG:PL | 2 | 990 | 19504762 | 840 | 2019-06-29 16:00 | 310 | 1318 | 257 | 1111 | 273 | 1159 | 187 | 605.5 | 114 |  |  | 114 | 53% | 43% | 85% | 53% | 4.8678 | Loss 0-5%
1029 | 1230 | LNR | LAXMI NAGAR | LGR030 | TG-LGR030A-1 | DT-1 | BODH VIHAR LAXMI NAGAR:K | 2 | 990 | 19503402 | 815 | 2019-06-01 | 229 | 1030 | 308 | 1413 | 278 | 1260 | 333 | 647.5 | 72 |  |  | 72 | 82% | 58% | 59% | 82% | 6.2016 | Loss 5-10% |  | 960(45.5) | 909(134.5) | 1063(81.5) | 818(29.5)
1030 | 1230 | LNR | LAXMI NAGAR | LGR030 | TG-LGR030A-2 | DT-2 | BODH VIHAR LAXMI NAGAR:K | 2 | 630 | 19504644 | 580 | 2019-06-05 03:30 | 189 | 766 | 215 | 884 | 175 | 719 | 148 | 589 | 129.5 | 1 |  | 130.5 | 92% | 62% | 66% | 91% | 6.2016 | Loss 5-10% |  |  |  |  | 545(29.5)
1031 | 1230 | LNR | LAXMI NAGAR | LGR031 | TG-LGR031A-1 | DT-1 | MANGAL BAZAR LAXMI NAGAR:PL | 3 | 990 | 19504511 | 1213 | 2019-06-12 00:30 | 387 | 1620 | 461 | 1944 | 364 | 1536 | 373 | 389 | 239.5 | 64 | 26 | 329.5 | 122% | 77% | 94% | 108% | 7.6228 | Loss 5-10% |  | 1261(224) | 1290(322.5) |  |  | 783(26.5)
1032 | 1230 | LNR | LAXMI NAGAR | LGR031 | TG-LGR031A-2 | DT-2 | MANGAL BAZAR LAXMI NAGAR:PL | 3 | 990 | 19502775 | 691 | 2019-06-11 23:30 | 258 | 1082 | 192 | 800 | 240 | 1011 | 254 | 719.5 |  |  |  | 0 | 69% | 45% | 57% | 70% | 7.6228 | Loss 5-10%
1033 | 1230 | LNR | LAXMI NAGAR | LGR031 | TG-LGR031A-3 | DT-3 | MANGAL BAZAR LAXMI NAGAR:PL | 3 | 990 | 19506025 | 830 | 2019-06-10 23:30 | 319 | 1367 | 256 | 1094 | 255 | 1098 | 271 | 658 | 61.5 |  |  | 61.5 | 84% | 54% | 64% | 84% | 7.6228 | Loss 5-10% |  |  | 906(33)
1034 | 1230 | LNR | LAXMI NAGAR | LGR032 | TG-LGR032A-1 | DT-1 | KULDEEP NURSING HOME LNG:K | 3 | 990 | 19502461 | 902 | 2019-06-11 21:30 | 287 | 1171 | 298 | 1227 | 318 | 1304 | 116 | 588 | 127.5 | 1 |  | 128.5 | 85% | 59% | 85% | 91% | 5.4971 | Loss 5-10% |  | 846(72) | 897(153) | 881(76) | 782(28.5)
1035 | 1230 | LNR | LAXMI NAGAR | LGR032 | TG-LGR032A-2 | DT-2 | KULDEEP NURSING HOME LNG:K | 3 | 990 | 19502463 | 917 | 2019-06-12 00:30 | 310 | 1253 | 284 | 1148 | 323 | 1315 | 146 | 600 | 118.5 | 1.5 |  | 120 | 93% | 60% | 62% | 91% | 5.4971 | Loss 5-10% |  | 1126(160.5) | 1153(208.5) | 862(47)
1036 | 1230 | LNR | LAXMI NAGAR | LGR032 | TG-LGR032A-3 | DT-3 | KULDEEP NURSING HOME LNG:K | 3 | 990 | 19505951 | 727 | 2019-06-28 23:00 | 264 | 1149 | 225 | 985 | 238 | 1041 | 145 | 716.5 | 3 |  |  | 3 | 72% | 48% | 50% | 73% | 5.4971 | Loss 5-10%
1037 | 1230 | LNR | LAXMI NAGAR | LGR034 | TG-LGR034A-1 | DT-1 | MOHAN PARK LAXMI NAGAR:K | 1 | 990 | 19502470 | 910 | 2019-06-11 19:30 | 305 | 1298 | 293 | 1254 | 312 | 1330 | 66 | 532.5 | 186.5 | 0.5 |  | 187 | 72% | 80% | 92% | 85% | 6.3201 | Loss 5-10% |  | 822(55.5) | 896(130) | 854(47.5)
1038 | 1230 | LNR | LAXMI NAGAR | LGR035 | TG-LGR035A-1 | DT-1 | N.GANESH NAGAR SHAKARPUR:PL | 1 | 630 | 19502820 | 563 | 2019-06-30 | 151 | 668 | 205 | 922 | 208 | 917 | 251 | 601.5 | 118.5 |  |  | 118.5 | 89% | 59% | 66% | 88% | 3.915 | Loss 0-5% |  | 650(127.5) | 771(93.5) | 716(202.5) | 749(157.5)
1039 | 1230 | LNR | LAXMI NAGAR | LGR036 | TG-LGR036A-1 | DT-1 | SHIROMANI SCHOOL, SHAKARPUR:PL | 2 | 990 | 19506252 | 1033 | 2019-06-30 23:30 | 357 | 1551 | 242 | 1048 | 433 | 1908 | 748 | 569 | 132.5 | 18 | 0.5 | 151 | 99% | 64% | 71% | 104% | 5.0908 | Loss 5-10%
1040 | 1230 | LNR | LAXMI NAGAR | LGR036 | TG-LGR036A-2 | DT-2 | SHIROMANI SCHOOL, SHAKARPUR:PL | 2 | 990 | 19504467 | 597 | 2019-06-30 | 145 | 602 | 242 | 998 | 211 | 874 | 351 | 480.5 |  |  |  | 0 | 60% | 43% | 46% | 60% | 5.0908 | Loss 5-10%
1041 | 1230 | LNR | LAXMI NAGAR | LGR040 | TG-LGR040A-1 | DT-1 | J EXTN. LAXMI NAGAR:PM | 1 | 990 | 19503409 | 1156 | 2019-06-30 01:30 | 351 | 1489 | 365 | 1626 | 440 | 1926 | 387 | 468 | 186.5 | 54 | 6.5 | 247 | 117% | 87% | 77% | 97% | 3.6605 | Loss 0-5% |  | 884(119.5) | 999(251) | 996(188.5) | 1106(157) | 929(77.5)
1042 | 1230 | LNR | LAXMI NAGAR | LGR041 | TG-LGR041A-1 | DT-1 | KUNDAN NAGAR, LAXMI NAGAR:K | 1 | 990 | 19505457 | 1052 | 2019-06-11 01:00 | 348 | 1512 | 313 | 1354 | 391 | 1710 | 308 | 506.5 | 126 | 11.5 | 0.5 | 138 | 106% | 62% | 75% | 99% | 3.336 | Loss 0-5% |  | 920(74) | 928(59.5)
1043 | 1230 | LNR | LAXMI NAGAR | LGR042 | TG-LGR042A-1 | DT-1 | V. SAVARKAR BLOCK, SHAKARPUR:PL | 1 | 990 | 19506382 | 975 | 2019-06-10 15:00 | 304 | 1266 | 339 | 1415 | 332 | 1401 | 143 | 586.5 | 132 | 0.5 |  | 132.5 | 15% | 15% | 98% | 23% | 3.9973 | Loss 0-5% |  | 970(80) | 938(139) |  | 766(36.5)
1044 | 1230 | LNR | LAXMI NAGAR | LGR043 | TG-LGR043A-1 | DT-1 | SUNDER BLOCK, SHAKARPUR:PL | 1 | 1600 | 19502815 | 1768.3862 | 2019-06-30 01:30 | 380.2798 | 1630.5626 | 397.481 | 1707.686 | 990.6254 | 4230.9105 | 2562.6567 | 483.5 | 137 | 30 | 16.5 | 183.5 | 111% | 96% | 98% | 110% | 4.4588 | Loss 0-5% |  | 992(116) | 1203(217.5)
1045 | 1230 | LNR | LAXMI NAGAR | LGR049 | TG-LGR049A-1 | DT-1 | R BLOCK SHAKARPUR:PL | 2 | 990 | 19504568 | 441 | 2019-06-01 15:00 | 134 | 593 | 119 | 516 | 188 | 814 | 268 | 720 |  |  |  | 0 | 34% | 26% | 45% | 37% | 9.7215 | Loss 5-10%
1046 | 1230 | LNR | LAXMI NAGAR | LGR049 | TG-LGR049A-2 | DT-2 | R BLOCK SHAKARPUR:PL | 2 | 630 | 19504448 | 544 | 2019-06-29 23:30 | 205 | 896 | 205 | 891 | 134 | 578 | 315 | 593.5 | 126.5 |  |  | 126.5 | 84% | 57% | 82% | 86% | 9.7215 | Loss 5-10% |  | 508(31.5) | 546(94)
1047 | 1230 | LNR | LAXMI NAGAR | LGR051 | TG-LGR051A-1 | DT-1 | H BLOCK LAXMI NAGAR:PL | 2 | 990 | 19502010 | 552 | 2019-06-08 15:30 | 225 | 1025 | 202 | 916 | 125 | 562 | 419 | 719 |  |  |  | 0 | 50% | 33% | 56% | 50% | 5.4756 | Loss 5-10%
1048 | 1230 | LNR | LAXMI NAGAR | LGR051 | TG-LGR051A-2 | DT-2 | H BLOCK LAXMI NAGAR:PL | 2 | 630 | 19504765 | 696 | 2019-06-26 14:30 | 206 | 893 | 280 | 1226 | 210 | 904 | 327 | 417.5 | 190.5 | 76.5 | 34.5 | 301.5 | 63% | 51% | 110% | 78% | 5.4756 | Loss 5-10% |  | 500(35.5) | 551(80) | 529(56.5) | 522(34.5)
1049 | 1230 | LNR | LAXMI NAGAR | LGR052 | TG-LGR052A-1 | DT-1 | RAMESH PARK, G NO.12, LN:PL | 2 | 990 | 19504589 | 903 | 2019-06-30 00:30 | 283 | 1203 | 368 | 1576 | 253 | 1085 | 444 | 559 | 158 | 3 |  | 161 | 91% | 72% | 70% | 90% | 3.6871 | Loss 0-5% |  | 844(100.5) | 923(211) | 927(121.5) | 785(50.5)
1050 | 1230 | LNR | LAXMI NAGAR | LGR052 | TG-LGR052A-2 | DT-2 | RAMESH PARK, G NO.12, LN:PL | 2 | 990 | 19506150 | 799 | 2019-06-03 01:00 | 270 | 1183 | 262 | 1134 | 267 | 1165 | 43 | 674.5 | 45.5 |  |  | 45.5 | 81% | 62% | 61% | 77% | 3.6871 | Loss 0-5% |  |  | 820(39.5) | 880(35)
1051 | 1230 | LNR | LAXMI NAGAR | LGR054 | TG-LGR054A-1 | DT-1 | KISHAN KUNJ ENTN.:PL | 2 | 990 | 19503404 | 793 | 2019-06-02 23:30 | 251 | 1013 | 238 | 969 | 304 | 1237 | 249 | 652.5 | 67.5 |  |  | 67.5 | 79% | 62% | 64% | 80% | 3.9884 | Loss 0-5%
1052 | 1230 | LNR | LAXMI NAGAR | LGR054 | TG-LGR054A-2 | DT-2 | KISHAN KUNJ ENTN.:PL | 2 | 630 | 19506147 | 579 | 2019-06-11 01:00 | 164 | 710 | 208 | 987 | 208 | 949 | 260 | 606 | 113.5 | 0.5 |  | 114 | 92% | 60% | 67% | 87% | 3.9884 | Loss 0-5% | 639(37) | 727(227.5) | 747(275.5) | 523(25.5)
1053 | 1230 | LNR | LAXMI NAGAR | LGR080 | TG-LGR080A-1 | DT-1 | GALI MASJID ANAR WALI | 1 | 990 | 19506548 | 1118 | 2019-06-30 01:00 | 370 | 1595 | 396 | 1704 | 352 | 1499 | 178 | 347 | 221.5 | 89.5 | 59.5 | 370.5 | 113% | 91% | 88% | 111% | 7.2213 | Loss 5-10% | 917(41.5) |  |  |  | 1225(76.5)
1054 | 1230 | LNR | LAXMI NAGAR | LGR082 | TG-LGR082A-1 | DT-1 | E BLOCK ,VIKAS MARG | 3 | 990 | 19506667 | 1152 | 2019-06-08 16:00 | 389 | 1684 | 407 | 1762 | 356 | 1539 | 196 | 419.5 | 146.5 | 75 | 78 | 299.5 | 67% | 53% | 116% | 78% | 5.5722 | Loss 5-10% |  | 1031(193) | 1178(261) | 1107(261) | 1083(173.5)
1055 | 1230 | LNR | LAXMI NAGAR | LGR082 | TG-LGR082A-2 | DT-2 | E BLOCK ,VIKAS MARG | 3 | 990 | 19502776 | 685 | 2019-06-08 15:30 | 178 | 753 | 223 | 946 | 284 | 1206 | 393 | 719.5 |  |  |  | 0 | 36% | 30% | 69% | 42% | 5.5722 | Loss 5-10% | 843(61) | 1026(202.5) | 1225(258.5) | 996(63)
1056 | 1230 | LNR | LAXMI NAGAR | LGR082 | TG-LGR082A-3 | DT-3 | E BLOCK ,VIKAS MARG | 3 | 990 | 19506528 | 719 | 2019-06-06 14:30 | 236 | 990 | 293 | 1252 | 190 | 800 | 393 | 717 | 0.5 |  |  | 0.5 | 54% | 39% | 73% | 52% | 5.5722 | Loss 5-10%
1057 | 1230 | LNR | LAXMI NAGAR | LGR083 | TG-LGR083A-1 | DT-1 | EK MINAR MASID | 2 | 990 | 19506852 | 1349 | 2019-06-08 | 452 | 1858 | 431 | 1757 | 467 | 1921 | 144 | 270 | 249 | 71 | 126 | 446 | 136% | 107% | 92% | 131% | 10.4517 | Loss 10-20% |  | 896(74.5) |  | 1010(180) | 870(134) | 867(66.5)
1058 | 1230 | LNR | LAXMI NAGAR | LGR083 | TG-LGR083A-2 | DT-2 | EK MINAR MASID | 2 | 990 | 19504438 | 611.7957 | 2019-06-13 23:30 | 196.6333 | 819.6809 | 216.8354 | 904.7626 | 198.3271 | 822.013 | 83.9399 | 208.5 |  |  |  | 0 | 61% | 50% | 53% | 62% | 10.4517 | Loss 10-20% |  | 829(62.5) | 870(122.5) | 853(108) | 788(72)
1059 | 1230 | LNR | LAXMI NAGAR | LGR084 | TG-LGR084A-1 | DT-1 | WEST GURU ANGAD NAGER GALI NO-2 | 1 | 990 | 19502464 | 904 | 2019-06-12 | 329 | 1359 | 268 | 1114 | 307 | 1271 | 215 | 611.5 | 108 | 0.5 |  | 108.5 | 91% | 63% | 61% | 88% | 10.0308 | Loss 10-20% |  |  | 836(77.5) | 823(38)
1060 | 1230 | LNR | LAXMI NAGAR | LGR090 | TG-LGR090A-1 | DT-1 | SCHOOL BLOCK,PARK WALA S/S NEAR MANDIR | 2 | 990 | 19504463 | 968 | 2019-06-10 13:00 | 321 | 1329 | 295 | 1221 | 353 | 1462 | 209 | 545 | 148.5 | 26.5 |  | 175 | 58% | 48% | 98% | 59% | 3.7364 | Loss 0-5% |  | 833(71.5) | 953(180) | 928(116.5) | 826(48)
1061 | 1230 | LNR | LAXMI NAGAR | LGR090 | TG-LGR090A-2 | DT-2 | SCHOOL BLOCK,PARK WALA S/S NEAR MANDIR | 2 | 630 | 19503652 | 617 | 2019-06-03 | 188 | 769 | 186 | 755 | 244 | 996 | 234 | 489.5 | 223 | 7.5 |  | 230.5 | 98% | 67% | 82% | 94% | 3.7364 | Loss 0-5% |  | 566(50.5) | 566(205) | 605(173.5) | 508(51)
1062 | 1230 | LNR | LAXMI NAGAR | LGR093 | TG-LGR093A-1 | DT-1 | SURANA DHARAMSHALA S/S | 2 | 990 | 19504131 | 431 | 2019-06-12 15:30 | 126 | 540 | 137 | 592 | 167 | 720 | 160 | 720 |  |  |  | 0 | 31% | 32% | 43% | 31% | 8.151 | Loss 5-10%
1063 | 1230 | LNR | LAXMI NAGAR | LGR093 | TG-LGR093A-2 | DT-2 | SURANA DHARAMSHALA S/S | 2 | 990 | 19506459 | 828 | 2019-06-30 23:30 | 249 | 1062 | 271 | 1161 | 308 | 1347 | 251 | 664.5 | 55.5 |  |  | 55.5 | 78% | 55% | 63% | 84% | 8.151 | Loss 5-10% |  | 854(42.5) | 879(68.5)
1064 | 1230 | LNR | LAXMI NAGAR | LGR097 | TG-LGR097A-1 | DT-1 | A BLK P,D.VIHAR PARK NR. O/H WATER TANK | 1 | 630 | 19505222 | 550 | 2019-06-11 23:30 | 205 | 833 | 135 | 544 | 211 | 857 | 302 | 552.5 | 167 |  |  | 167 | 87% | 65% | 86% | 87% | 3.7314 | Loss 0-5% |  | 608(65.5) | 589(154) | 557(72)
1065 | 1230 | LNR | LAXMI NAGAR | LGR100 | TG-LGR100A-1 | DT-1 | GYAN KUNJ | 1 | 990 | 19505137 | 1052.5105 | 2019-06-11 01:30 | 352.113 | 1413.0869 | 315.8192 | 1266.8241 | 384.5782 | 1544.4289 | 240.5285 | 672 | 40 | 4.5 | 1 | 45.5 | 106% | 97% | 72% | 92% | 2.9002 | Loss 0-5% |  |  | 756(26)
1066 | 1230 | LNR | LAXMI NAGAR | LGR101 | TG-LGR101A-1 | DT-1 | VEER SAVARKAR BLOCK VIKAS MARG | 1 | 990 | 19504960 | 907 | 2019-06-27 14:00 | 235 | 1071 | 328 | 1506 | 344 | 1597 | 487 | 586.5 | 131.5 | 0.5 |  | 132 | 14% | 19% | 92% | 24% | 6.6538 | Loss 5-10% |  |  | 895(129) | 881(102) | 761(40)
1067 | 1230 | LNR | LAXMI NAGAR | LGR103 | TG-LGR103A-1 | DT-1 | NEW WB BLOCK (NEAR AGGARWAL SWEETS) | 1 | 990 | 19505891 | 910 | 2019-06-30 | 281 | 1163 | 314 | 1318 | 314 | 1307 | 150 | 522.5 | 194 | 3.5 |  | 197.5 | 92% | 63% | 79% | 92% | 7.7886 | Loss 5-10% |  | 892(90.5) | 982(289) | 887(138) | 928(60)
1068 | 1230 | LNR | LAXMI NAGAR | LGR104 | TG-LGR104A-1 | DT-1 | NARAIN NAGAR (NEAR GARHWALI MOHALLA) | 1 | 630 | 19505680 | 521 | 2019-06-29 23:30 | 188 | 773 | 154 | 639 | 178 | 741 | 121 | 655.5 | 61.5 |  |  | 61.5 | 81% | 67% | 65% | 83% | 9.6686 | Loss 5-10% |  |  | 517(77.5) | 521(47)
1069 | 1230 | LNR | LAXMI NAGAR | LGR108 | TG-LGR108A-1 | DT-1 | COMMUNITY CENTER SHAKARPUR | 1 | 630 | 19505626 | 533 | 2019-06-30 23:30 | 185 | 781 | 190 | 801 | 158 | 659 | 133 | 635.5 | 84.5 |  |  | 84.5 | 82% | 57% | 70% | 85% | 5.6641 | Loss 5-10%
1070 | 1230 | LNR | LAXMI NAGAR | PVR008 | TG-PVR008A-1 | DT-1 | DDA FLAT NIRMAN VIHAR:ID | 2 | 990 | 19501093 | 805.617 | 2019-06-01 | 228.2324 | 1003.3517 | 244.8038 | 1087.1956 | 332.5808 | 1474.0097 | 434.8413 | 667.5 | 52.5 |  |  | 52.5 | 81% | 55% | 60% | 81% | 13.5333 | Loss 10-20% |  | 698(207.5) | 774(265.5) | 732(103.5) | 664(182) | 589(81.5)
1071 | 1230 | LNR | LAXMI NAGAR | PVR008 | TG-PVR008A-2 | DT-2 | DDA FLAT NIRMAN VIHAR:ID | 2 | 990 | 19504486 | 857 | 2019-06-11 23:30 | 282 | 1257 | 270 | 1195 | 305 | 1356 | 141 | 610.5 | 109.5 |  |  | 109.5 | 86% | 59% | 63% | 87% | 13.5333 | Loss 10-20% |  |  | 834(66.5)
1072 | 1230 | LNR | MANDAWALI | MAN003 | TG-MAN003A-1 | DT-1 | SOUTH GANESH NAGAR:PM | 1 | 400 | 19505687 | 588 | 2019-06-30 | 183 | 823 | 190 | 864 | 216 | 982 | 143 | 250.5 | 230.5 | 78.5 | 160 | 469 | 147% | 89% | 99% | 135% | 4.4307 | Loss 0-5% | 408(71) | 472(260.5) | 560(467.5) | 557(417.5) |  | 432(150.5)
1073 | 1230 | LNR | MANDAWALI | MAN004 | TG-MAN004A-1 | DT-1 | SOUTH GANESH NAGAR EXTN.:ID | 2 | 990 | 19505658 | 538 | 2019-06-30 | 186 | 851 | 200 | 912 | 152 | 696 | 193 | 719.5 |  |  |  | 0 | 54% | 34% | 40% | 50% | 4.2275 | Loss 0-5%
1074 | 1230 | LNR | MANDAWALI | MAN004 | TG-MAN004A-2 | DT-2 | SOUTH GANESH NAGAR EXTN.:ID | 2 | 630 | 19506133 | 711 | 2019-06-30 | 231 | 1065 | 223 | 1024 | 258 | 1201 | 160 | 523.5 | 131.5 | 54 | 11 | 196.5 | 113% | 67% | 76% | 104% | 4.2275 | Loss 0-5% |  |  | 990(205.5) | 547(61) | 487(28.5)
1075 | 1230 | LNR | MANDAWALI | MAN006 | TG-MAN006A-1 | DT-1 | PANDAV NAGAR D PARK:K | 5 | 990 | 19505744 | 1034 | 2019-06-05 01:00 | 340 | 1441 | 383 | 1639 | 312 | 1335 | 267 | 525.5 | 133 | 50.5 | 10 | 193.5 | 104% | 70% | 74% | 104% | 5.5812 | Loss 5-10% |  | 830(45.5) | 981(129.5) | 923(94) | 779(39.5)
1076 | 1230 | LNR | MANDAWALI | MAN006 | TG-MAN006A-2 | DT-2 | PANDAV NAGAR D PARK:K | 5 | 990 | 19501944 | 965 | 2019-06-05 00:30 | 324 | 1357 | 345 | 1439 | 296 | 1224 | 188 | 538 | 165 | 16 |  | 181 | 97% | 64% | 78% | 97% | 5.5812 | Loss 5-10% | 892(30) |  | 834(68) | 816(44.5) | 809(56.5)
1077 | 1230 | LNR | MANDAWALI | MAN006 | TG-MAN006A-3 | DT-3 | PANDAV NAGAR D PARK:K | 5 | 990 | 19505981 | 917 | 2019-06-07 23:30 | 297 | 1366 | 349 | 1604 | 271 | 1250 | 312 | 594 | 118.5 | 6 |  | 124.5 | 92% | 63% | 73% | 93% | 5.5812 | Loss 5-10% |  | 1210(232.5) | 1299(394.5) | 1213(176) | 1007(175)
1078 | 1230 | LNR | MANDAWALI | MAN006 | TG-MAN006A-4 | DT-4 | PANDAV NAGAR D PARK:K | 5 | 630 | 19502899 | 376.3541 | 2019-06-01 | 134.3932 | 575.6832 | 144.8007 | 626.4359 | 97.1602 | 417.8396 | 188.4183 | 287 |  |  |  | 0 | 60% | 39% | 46% | 58% | 5.5812 | Loss 5-10% |  | 595(89) | 611(106) | 649(136.5) | 546(55.5)
1079 | 1230 | LNR | MANDAWALI | MAN006 | TG-MAN006A-5 | DT-5 | PANDAV NAGAR D PARK:K | 5 | 630 | 19506626 | 423 | 2019-06-02 23:30 | 129 | 535 | 162 | 670 | 132 | 548 | 129 | 719.5 |  |  |  | 0 | 67% | 42% | 56% | 67% | 5.5812 | Loss 5-10%
1080 | 1230 | LNR | MANDAWALI | MAN007 | TG-MAN007A-1 | DT-1 | PANDAV NAGAR S BLOCK:ID | 1 | 990 | 19501803 | 874 | 2019-06-06 03:00 | 274 | 1152 | 287 | 1212 | 314 | 1319 | 146 | 615 | 104.5 |  |  | 104.5 | 88% | 60% | 64% | 88% | 5.4968 | Loss 5-10% |  | 873(42.5) | 902(127) | 892(99) | 784(43)
1081 | 1230 | LNR | MANDAWALI | MAN008 | TG-MAN008A-1 | DT-1 | PANDAV NAGAR S BLOCK NEAR PETROL PUMP:PM | 2 | 990 | 19506364 | 791 | 2019-06-30 23:00 | 256 | 1172 | 287 | 1314 | 249 | 1137 | 162 | 683.5 | 36 |  |  | 36 | 80% | 51% | 61% | 80% | 3.8894 | Loss 0-5% |  |  | 799(50.5)
1082 | 1230 | LNR | MANDAWALI | MAN008 | TG-MAN008A-2 | DT-2 | PANDAV NAGAR S BLOCK NEAR PETROL PUMP:PM | 2 | 630 | 19505534 | 420 | 2019-06-26 23:00 | 131 | 604 | 155 | 718 | 135 | 629 | 104 | 719.5 |  |  |  | 0 | 64% | 42% | 52% | 67% | 3.8894 | Loss 0-5%
1083 | 1230 | LNR | MANDAWALI | MAN009 | TG-MAN009A-1 | DT-1 | J PARK PANDAV NAGAR:K | 1 | 990 | 19502964 | 1094 | 2019-06-29 23:00 | 368 | 1588 | 397 | 1713 | 330 | 1407 | 266 | 489.5 | 139 | 54.5 | 23.5 | 217 | 109% | 68% | 81% | 111% | 3.4241 | Loss 0-5% |  | 1030(97) | 1027(402.5) | 1005(140.5) | 880(87.5)
1084 | 1230 | LNR | MANDAWALI | MAN010 | TG-MAN010A-1 | DT-1 | GANESH NAGAR COM. E BLCK.:PL | 2 | 990 | 19506916 | 1131 | 2019-06-30 | 341 | 1514 | 427 | 1915 | 362 | 1608 | 364 | 338.5 | 101.5 | 40 | 22 | 163.5 | 114% | 71% | 89% | 111% | 4.5931 | Loss 0-5% |  |  |  |  | 1108(177.5) | 951(57)
1085 | 1230 | LNR | MANDAWALI | MAN010 | TG-MAN010A-2 | DT-2 | GANESH NAGAR COM. E BLCK.:PL | 2 | 990 | 19500753 | 1023.2342 | 2019-06-30 00:30 | 334.4389 | 1395.4724 | 352.5955 | 1523.8805 | 336.1998 | 1447.2655 | 111.8951 | 493.5 | 163.5 | 55 | 6 | 224.5 | 103% | 73% | 77% | 102% | 4.5931 | Loss 0-5% | 887(32) | 1214(209) | 1091(203) | 887(109) | 788(61.5)
1086 | 1230 | LNR | MANDAWALI | MAN011 | TG-MAN011A-1 | DT-1 | GANESH NAGAR COM. C BLCK.:PL | 2 | 1600 | 19500759 | 1503.0792 | 2019-06-30 23:30 | 476.6178 | 2165.3617 | 576.61 | 2608.7411 | 449.8514 | 2026.8143 | 526.5071 | 573 | 137.5 | 9 |  | 146.5 | 91% | 62% | 69% | 94% | 3.7274 | Loss 0-5% |  | 1083(97.5) | 1333(413.5) | 1133(273) | 1034(218) | 929(47)
1087 | 1230 | LNR | MANDAWALI | MAN011 | TG-MAN011A-2 | DT-2 | GANESH NAGAR COM. C BLCK.:PL | 2 | 990 | 19504615 | 540 | 2019-06-10 23:30 | 154 | 681 | 182 | 809 | 204 | 913 | 201 | 720 |  |  |  | 0 | 55% | 38% | 44% | 55% | 3.7274 | Loss 0-5%
1088 | 1230 | LNR | MANDAWALI | MAN013 | TG-MAN013A-1 | DT-1 | MANDAWALI A BLOCK SHIV MANDIR MARG:PL | 2 | 990 | 19506457 | 1135 | 2019-06-30 23:30 | 413 | 1753 | 358 | 1510 | 364 | 1524 | 236 | 465.5 | 164 | 65.5 | 23 | 252.5 | 110% | 77% | 82% | 115% | 5.4843 | Loss 5-10% |  |  |  |  | 958(132) | 925(31.5)
1089 | 1230 | LNR | MANDAWALI | MAN013 | TG-MAN013A-2 | DT-2 | MANDAWALI A BLOCK SHIV MANDIR MARG:PL | 2 | 990 | 19502779 | 1242 | 2019-06-29 23:30 | 438 | 1889 | 398 | 1731 | 405 | 1772 | 142 | 426.5 | 168.5 | 44 | 80.5 | 293 | 124% | 85% | 99% | 125% | 5.4843 | Loss 5-10% |  |  |  |  | 991(133.5) | 897(26.5)
1090 | 1230 | LNR | MANDAWALI | MAN016 | TG-MAN016A-1 | DT-1 | MANDAWALI PRIMARY SCHOOL:PL | 3 | 990 | 19506407 | 1132 | 2019-06-29 23:30 | 393 | 1678 | 339 | 1439 | 400 | 1714 | 259 | 405 | 213.5 | 66.5 | 34.5 | 314.5 | 112% | 81% | 92% | 114% | 8.0713 | Loss 5-10% | 799(34.5) | 1143(282.5) | 1290(477)
1091 | 1230 | LNR | MANDAWALI | MAN016 | TG-MAN016A-2 | DT-2 | MANDAWALI PRIMARY SCHOOL:PL | 3 | 990 | 19505523 | 613 | 2019-06-30 23:30 | 226 | 991 | 188 | 822 | 199 | 875 | 150 | 720 |  |  |  | 0 | 61% | 46% | 52% | 62% | 8.0713 | Loss 5-10% |  | 997(105.5) | 1135(257.5) | 1155(187) | 1034(111.5)
1092 | 1230 | LNR | MANDAWALI | MAN016 | TG-MAN016A-3 | DT-3 | MANDAWALI PRIMARY SCHOOL:PL | 3 | 630 | 19506597 | 670 | 2019-06-11 | 209 | 913 | 201 | 881 | 260 | 1143 | 247 | 493 | 180 | 43.5 | 3.5 | 227 | 106% | 84% | 78% | 105% | 8.0713 | Loss 5-10%
1093 | 1230 | LNR | MANDAWALI | MAN017 | TG-MAN017A-1 | DT-1 | SCHOOL KHATTA-1, MANDAWALI:PL | 2 | 990 | 19500781 | 1141.9346 | 2019-06-29 23:30 | 355.0863 | 1542.3112 | 385.3779 | 1680.5981 | 401.4703 | 1750.7756 | 183.7192 | 387.5 | 209 | 78 | 44 | 331 | 114% | 80% | 88% | 115% | 11.9836 | Loss 10-20% |  | 950(107.5) | 1056(224.5) | 1064(221.5) | 992(195.5) | 899(56)
1094 | 1230 | LNR | MANDAWALI | MAN017 | TG-MAN017A-2 | DT-2 | SCHOOL KHATTA-1, MANDAWALI:PL | 2 | 630 | 19505686 | 540 | 2019-06-30 23:30 | 174 | 770 | 179 | 795 | 187 | 825 | 48 | 685 | 33.5 |  |  | 33.5 | 82% | 56% | 58% | 86% | 11.9836 | Loss 10-20% |  | 552(35) | 598(123) | 602(72)
1095 | 1230 | LNR | MANDAWALI | MAN018 | TG-MAN018A-1 | DT-1 | SCHOOL KHATTA-II,MANDAWALI:PM | 1 | 990 | 19500784 | 945.2505 | 2019-06-30 23:30 | 322.5007 | 1399.3783 | 347.5744 | 1529.5476 | 275.1754 | 1197.6125 | 289.6846 | 563.5 | 145 | 10 |  | 155 | 92% | 69% | 76% | 95% | 6.1722 | Loss 5-10% |  |  | 914(105)
1096 | 1230 | LNR | MANDAWALI | MAN019 | TG-MAN019A-1 | DT-1 | MANDAWALI UNCHEPAR;PL | 2 | 990 | 19501990 | 1093 | 2019-06-29 23:30 | 353 | 1547 | 387 | 1699 | 353 | 1528 | 162 | 522.5 | 147 | 38 | 12.5 | 197.5 | 110% | 72% | 76% | 110% | 3.0626 | Loss 0-5% |  | 889(59) | 981(164) | 1032(123.5) | 845(76.5)
1097 | 1230 | LNR | MANDAWALI | MAN019 | TG-MAN019A-2 | DT-2 | MANDAWALI UNCHEPAR;PL | 2 | 630 | 19505664 | 508 | 2019-06-29 23:30 | 182 | 779 | 183 | 786 | 143 | 606 | 177 | 701.5 | 18.5 |  |  | 18.5 | 76% | 60% | 63% | 81% | 3.0626 | Loss 0-5% |  | 533(35.5) | 578(106) | 583(60.5) | 496(27)
1098 | 1230 | LNR | MANDAWALI | MAN021 | TG-MAN021A-1 | DT-1 | MANDAWALI SUBJI MANDI:PL | 2 | 990 | 19504821 | 939 | 2019-06-30 23:00 | 324 | 1402 | 301 | 1309 | 315 | 1369 | 81 | 580 | 133.5 | 6.5 |  | 140 | 91% | 63% | 78% | 95% | 3.9525 | Loss 0-5% |  | 894(80.5) | 1025(221) | 1004(172.5) | 910(124)
1099 | 1230 | LNR | MANDAWALI | MAN021 | TG-MAN021A-2 | DT-2 | MANDAWALI SUBJI MANDI:PL | 2 | 990 | 19504828 | 1069 | 2019-06-29 23:00 | 345 | 1485 | 370 | 1589 | 354 | 1523 | 91 | 426.5 | 253 | 36 | 4 | 293 | 101% | 77% | 90% | 108% | 3.9525 | Loss 0-5%
1100 | 1230 | LNR | MANDAWALI | MAN023 | TG-MAN023A-1 | DT-1 | UTTARY SCHOOL BLOCK:K | 3 | 990 | 19502766 | 1159 | 2019-06-30 23:30 | 407 | 1693 | 384 | 1608 | 368 | 1538 | 134 | 428.5 | 161 | 72.5 | 58 | 291.5 | 112% | 79% | 88% | 117% | 3.8539 | Loss 0-5% |  | 1016(133) | 1056(271) | 1084(244.5) | 1000(220.5) | 838(33)
1101 | 1230 | LNR | MANDAWALI | MAN023 | TG-MAN023A-2 | DT-2 | UTTARY SCHOOL BLOCK:K | 3 | 630 | 19502768 | 720 | 2019-06-29 23:00 | 283 | 1170 | 218 | 911 | 220 | 911 | 259 | 486.5 | 141.5 | 63.5 | 28 | 233 | 102% | 61% | 114% | 114% | 3.8539 | Loss 0-5% |  | 677(200.5) | 758(278.5) | 669(194) | 588(120.5) | 567(75)
1102 | 1230 | LNR | MANDAWALI | MAN023 | TG-MAN023A-3 | DT-3 | UTTARY SCHOOL BLOCK:K | 3 | 630 | 19504321 | 609 | 2019-06-30 23:00 | 222 | 965 | 215 | 937 | 171 | 742 | 210 | 570.5 | 138.5 | 10 |  | 148.5 | 96% | 67% | 79% | 97% | 3.8539 | Loss 0-5%
1103 | 1230 | LNR | MANDAWALI | MAN024 | TG-MAN024A-1 | DT-1 | CHANDERVIHAR SS-1:ID | 2 | 630 | 19500843 | 452.7075 | 2019-06-29 23:00 | 129.538 | 573.5322 | 172.0849 | 765.8088 | 151.0846 | 664.8681 | 166.5856 | 717.5 | 2.5 |  |  | 2.5 | 68% | 45% | 58% | 72% | 5.4734 | Loss 5-10%
1104 | 1230 | LNR | MANDAWALI | MAN024 | TG-MAN024A-2 | DT-2 | CHANDERVIHAR SS-1:ID | 2 | 990 | 19500076 | 1018 | 2019-06-29 23:00 | 354 | 1525 | 325 | 1403 | 339 | 1461 | 105 | 560.5 | 139.5 | 18 | 2 | 159.5 | 95% | 63% | 74% | 103% | 5.4734 | Loss 5-10% |  | 888(44.5) | 1000(156) | 988(111.5) | 1009(141.5) | 828(25)
1105 | 1230 | LNR | MANDAWALI | MAN025 | TG-MAN025A-1 | DT-1 | CHANDERVIHAR SS-II:ID | 2 | 630 | 19500845 | 751 | 2019-06-15 23:00 | 254 | 1085 | 250 | 1063 | 247 | 1057 | 25 | 436 | 183.5 | 63 | 37.5 | 284 | 108% | 79% | 89% | 119% | 4.2908 | Loss 0-5% |  | 662(104) | 723(146.5) | 694(198) | 642(173.5) | 547(33.5)
1106 | 1230 | LNR | MANDAWALI | MAN025 | TG-MAN025A-2 | DT-2 | CHANDERVIHAR SS-II:ID | 2 | 630 | 19504725 | 675 | 2019-06-29 23:00 | 245 | 1072 | 231 | 1004 | 199 | 861 | 186 | 540 | 137 | 35 | 8 | 180 | 102% | 70% | 78% | 107% | 4.2908 | Loss 0-5% |  | 617(51) | 664(106) | 614(130) | 570(91)
1107 | 1230 | LNR | MANDAWALI | MAN026 | TG-MAN026A-1 | DT-1 | WESTVINOD NAGAR NEAR MANGLAM:PL | 3 | 990 | 19506612 | 943 | 2019-06-02 23:30 | 293 | 1232 | 330 | 1392 | 319 | 1345 | 142 | 637 | 75 | 7.5 |  | 82.5 | 92% | 53% | 68% | 95% | 8.8027 | Loss 5-10% |  | 1068(64.5) | 998(103) | 1047(115)
1108 | 1230 | LNR | MANDAWALI | MAN026 | TG-MAN026A-2 | DT-2 | WESTVINOD NAGAR NEAR MANGLAM:PL | 3 | 990 | 19506134 | 1698.2957 | 2019-06-27 00:30 | 553.9903 | 2289.3109 | 568.7532 | 2360.4614 | 575.5522 | 2381.6609 | 83.7865 | 154.5 | 226.5 | 76 | 241 | 543.5 | 172% | 109% | 136% | 165% | 8.8027 | Loss 5-10% | 1119(144) |  | 1573(452.5) |  |  | 1265(295.5)
1109 | 1230 | LNR | MANDAWALI | MAN026 | TG-MAN026A-3 | DT-3 | WESTVINOD NAGAR NEAR MANGLAM:PL | 3 | 990 | 19505743 | 1060 | 2019-06-26 23:00 | 331 | 1380 | 333 | 1382 | 396 | 1650 | 269 | 545.5 | 133 | 33.5 | 7.5 | 174 | 103% | 64% | 100% | 107% | 8.8027 | Loss 5-10% |  | 587(59.5) | 645(116) | 685(131) | 587(67.5)
1110 | 1230 | LNR | MANDAWALI | MAN027 | TG-MAN027A-1 | DT-1 | WESTVINOD NAGAR D BLOCK:ID | 2 | 990 | 19506140 | 742 | 2019-06-29 23:00 | 228 | 967 | 267 | 1135 | 247 | 1055 | 145 | 715.5 | 3.5 |  |  | 3.5 | 71% | 51% | 60% | 75% | 6.5012 | Loss 5-10% |  | 595(86) | 689(169.5) | 662(181) | 594(119)
1111 | 1230 | LNR | MANDAWALI | MAN027 | TG-MAN027A-2 | DT-2 | WESTVINOD NAGAR D BLOCK:ID | 2 | 990 | 19505858 | 1271 | 2019-06-30 23:30 | 421 | 1841 | 446 | 1954 | 404 | 1758 | 170 | 350 | 215 | 74.5 | 80.5 | 370 | 124% | 104% | 98% | 128% | 6.5012 | Loss 5-10% |  | 1055(190) | 1169(257.5) | 1222(337.5) |  | 897(64.5)
1112 | 1230 | LNR | MANDAWALI | MAN029 | TG-MAN029A-1 | DT-1 | A BLOCK WESTVINOD NAGAR | 2 | 990 | 19504659 | 1213 | 2019-06-30 23:30 | 384 | 1682 | 446 | 1966 | 383 | 1685 | 282 | 464.5 | 166 | 55.5 | 33.5 | 255 | 110% | 80% | 85% | 122% | 7.0759 | Loss 5-10% |  | 898(80.5) | 987(154) | 1045(143.5) | 979(84)
1113 | 1230 | LNR | MANDAWALI | MAN029 | TG-MAN029A-2 | DT-2 | A BLOCK WESTVINOD NAGAR | 2 | 990 | 19501888 | 1185 | 2019-06-30 23:30 | 360 | 1530 | 401 | 1700 | 424 | 1813 | 246 | 406.5 | 196.5 | 64.5 | 52 | 313 | 116% | 82% | 92% | 120% | 7.0759 | Loss 5-10% |  | 1159(173) | 1325(252) | 1311(325.5) | 1283(252.5) | 1010(63)
1114 | 1230 | LNR | MANDAWALI | MAN030 | TG-MAN030A-1 | DT-1 | E BLOCK WESTVINOD NAGAR:ID | 2 | 990 | 19505814 | 826.9265 | 2019-06-30 23:00 | 269.7131 | 1166.1252 | 334.0345 | 1470.8048 | 223.1789 | 965.4321 | 440.7431 | 684.5 | 34 |  |  | 34 | 79% | 58% | 66% | 84% | 4.004 | Loss 0-5% |  |  |  | 878(33.5)
1115 | 1230 | LNR | MANDAWALI | MAN030 | TG-MAN030A-2 | DT-2 | E BLOCK WESTVINOD NAGAR:ID | 2 | 990 | 19505463 | 927 | 2019-06-26 23:00 | 272 | 1197 | 353 | 1559 | 301 | 1321 | 319 | 554 | 162 | 2.5 |  | 164.5 | 89% | 68% | 81% | 94% | 4.004 | Loss 0-5% |  | 992(149) | 1106(295.5) | 1183(143) | 882(55.5)
1116 | 1230 | LNR | MANDAWALI | MAN031 | TG-MAN031A-1 | DT-1 | MOHAN BABA MANDIR MANDAWALI:PL | 2 | 990 | 19506135 | 1290 | 2019-06-30 23:30 | 448 | 1956 | 447 | 1951 | 395 | 1723 | 231 | 159 | 257.5 | 114.5 | 188 | 560 | 129% | 103% | 126% | 130% | 9.39 | Loss 5-10% | 862(96) | 976(141) |  |  |  | 950(40)
1117 | 1230 | LNR | MANDAWALI | MAN031 | TG-MAN031A-2 | DT-2 | MOHAN BABA MANDIR MANDAWALI:PL | 2 | 630 | 19504139 | 330 | 2019-06-29 23:00 | 86 | 376 | 137 | 608 | 107 | 470 | 202 | 719.5 |  |  |  | 0 | 49% | 38% | 39% | 52% | 9.39 | Loss 5-10%
1118 | 1230 | LNR | MANDAWALI | MAN032 | TG-MAN032A-1 | DT-1 | SONIYA VIHAR MANDAWALI:PL | 1 | 400 | 19505665 | 430 | 2019-06-11 23:00 | 151 | 683 | 136 | 612 | 143 | 641 | 62 | 329.5 | 273.5 | 101.5 | 15.5 | 390.5 | 106% | 84% | 89% | 107% | 6.2177 | Loss 5-10% |  | 372(187) | 418(338.5) | 433(77) | 412(245.5) | 538(157.5)
1119 | 1230 | LNR | MANDAWALI | MAN033 | TG-MAN033A-1 | DT-1 | B BLOCK MANDAWALI:ID | 3 | 990 | 19506545 | 1105 | 2019-06-30 23:30 | 394 | 1767 | 366 | 1644 | 344 | 1544 | 194 | 479 | 179 | 48 | 13.5 | 240.5 | 104% | 93% | 85% | 112% | 3.6324 | Loss 0-5% |  |  |  |  | 1104(164.5) | 911(46.5)
1120 | 1230 | LNR | MANDAWALI | MAN033 | TG-MAN033A-2 | DT-2 | B BLOCK MANDAWALI:ID | 3 | 990 | 19506320 | 637 | 2019-06-30 23:30 | 199 | 898 | 238 | 1077 | 200 | 901 | 178 | 719.5 |  |  |  | 0 | 58% | 55% | 51% | 64% | 3.6324 | Loss 0-5% |  |  | 838(45.5) | 841(44)
1121 | 1230 | LNR | MANDAWALI | MAN033 | TG-MAN033A-3 | DT-3 | B BLOCK MANDAWALI:ID | 3 | 990 | 19506881 | 330 | 2019-06-30 23:30 | 123 | 540 | 131 | 574 | 76 | 330 | 228 | 719.5 |  |  |  | 0 | 31% | 26% | 25% | 33% | 3.6324 | Loss 0-5%
1122 | 1230 | LNR | MANDAWALI | MAN034 | TG-MAN034A-1 | DT-1 | C BLOCK WESTVINOD NAGAR:PL | 2 | 990 | 19505260 | 1068 | 2019-06-26 23:30 | 368 | 1536 | 326 | 1358 | 374 | 1573 | 200 | 526.5 | 152 | 37 | 4.5 | 193.5 | 106% | 71% | 86% | 108% | 4.471 | Loss 0-5% |  |  | 967(73) | 1011(137.5) | 898(96)
1123 | 1230 | LNR | MANDAWALI | MAN034 | TG-MAN034A-2 | DT-2 | C BLOCK WESTVINOD NAGAR:PL | 2 | 630 | 19506137 | 669 | 2019-06-26 23:00 | 150 | 595 | 245 | 980 | 275 | 1121 | 472 | 506.5 | 21 |  | 0.5 | 21.5 | 82% | 50% | 66% | 106% | 4.471 | Loss 0-5% |  | 639(66) | 694(103.5) | 614(26.5)
1124 | 1230 | LNR | MANDAWALI | MAN037 | TG-MAN037A-1 | DT-1 | SHANKAR MARG MANDAWALI:PL | 1 | 990 | 19506836 | 1290 | 2019-06-30 23:30 | 420 | 1822 | 386 | 1678 | 484 | 2131 | 400 | 395.5 | 159.5 | 60 | 105 | 324.5 | 128% | 85% | 93% | 130% | 4.9787 | Loss 0-5% |  |  | 1277(117) | 1294(179) | 1136(134.5) | 994(52)
1125 | 1230 | LNR | MANDAWALI | MAN038 | TG-MAN038A-1 | DT-1 | KRISHNA PURI MANDAWALI:PL | 1 | 630 | 19504301 | 589 | 2019-06-30 23:30 | 208 | 954 | 192 | 865 | 189 | 855 | 94 | 563.5 | 154.5 | 2 |  | 156.5 | 91% | 68% | 68% | 93% | 10.5314 | Loss 10-20% |  | 563(109.5) | 668(259.5) | 635(212) | 565(147)
1126 | 1230 | LNR | MANDAWALI | MAN039 | TG-MAN039A-1 | DT-1 | ALLAH COLONY MANDAWALI:PL | 1 | 630 | 19506415 | 616 | 2019-06-29 23:30 | 194 | 840 | 212 | 923 | 210 | 913 | 78 | 618.5 | 96 | 5.5 |  | 101.5 | 92% | 87% | 77% | 98% | 9.998 | Loss 5-10% |  |  | 559(61) | 589(69) | 542(43.5)
1127 | 1230 | LNR | MANDAWALI | MAN059 | TG-MAN059A-1 | DT-1 | S/STN.NO-2, PPG CGHS:ID | 1 | 630 | 19501860 | 635 | 2019-06-30 23:00 | 225 | 1040 | 202 | 918 | 208 | 947 | 110 | 503 | 200.5 | 13.5 | 0.5 | 214.5 | 93% | 66% | 83% | 101% | 3.0581 | Loss 0-5% |  |  | 555(94) | 567(71) | 515(33)
1128 | 1230 | LNR | MANDAWALI | MAN212 | TG-MAN212A-1 | DT-1 | RAILWAY COLONY GALI NO. 2:PL | 2 | 990 | 19505555 | 1063 | 2019-06-01 23:00 | 381 | 1715 | 374 | 1681 | 307 | 1386 | 313 | 589 | 91.5 | 28 | 10.5 | 130 | 105% | 84% | 92% | 107% | 6.5533 | Loss 5-10% | 850(68.5) | 1045(285) | 1155(502) |  | 1122(468) | 1007(244.5)
1129 | 1230 | LNR | MANDAWALI | MAN212 | TG-MAN212A-2 | DT-2 | RAILWAY COLONY GALI NO. 2:PL | 2 | 630 | 19506923 | 499 | 2019-06-30 23:00 | 173 | 760 | 183 | 814 | 143 | 637 | 156 | 311 | 13.5 |  |  | 13.5 | 77% | 55% | 59% | 79% | 6.5533 | Loss 5-10%
1130 | 1230 | LNR | MANDAWALI | MAN247 | TG-MAN247A-1 | DT-1 | Budha marg Mandawali | 1 | 990 | 19504474 | 951 | 2019-06-30 23:30 | 348 | 1536 | 321 | 1422 | 282 | 1250 | 250 | 683.5 | 31 | 4 |  | 35 | 94% | 73% | 74% | 96% | 3.3098 | Loss 0-5% |  | 829(43) | 982(167) | 927(131) | 843(68.5)
1131 | 1230 | LNR | MANDAWALI | MAN273 | TG-MAN273A-1 | DT-1 | Ew S/S D-Blk Ramleela Ground Pandav Ngr | 2 | 990 | 19504634 | 904 | 2019-06-30 23:30 | 321 | 1476 | 262 | 1200 | 321 | 1461 | 269 | 604 | 115 | 0.5 |  | 115.5 | 88% | 57% | 70% | 91% | 6.1473 | Loss 5-10% |  | 778(27.5) | 834(87.5) | 823(28.5)
1132 | 1230 | LNR | MANDAWALI | MAN273 | TG-MAN273A-2 | DT-2 | Ew S/S D-Blk Ramleela Ground Pandav Ngr | 2 | 630 | 19505682 | 407 | 2019-06-26 23:30 | 148 | 639 | 139 | 599 | 121 | 519 | 106 | 719.5 |  |  |  | 0 | 63% | 47% | 65% | 65% | 6.1473 | Loss 5-10%
1133 | 1230 | LNR | MANDAWALI | MAN274 | TG-MAN274A-1 | DT-1 | Gnpn Complex, Rob-36 Pandav Nagar | 1 | 630 | 19504788 | 652 | 2019-06-07 23:00 | 225 | 1017 | 211 | 947 | 217 | 973 | 61 | 520 | 153 | 42.5 | 4 | 199.5 | 99% | 67% | 74% | 104% | 4.425 | Loss 0-5% |  | 605(119) | 658(48) | 596(36) | 605(186) | 516(28)
1134 | 1230 | LNR | MANDAWALI | MAN296 | TG-MAN296A-1 | DT-1 | SOUTH GANESH NAGAR (NEAR RAILWAY LINE) | 1 | 630 | 19505316 | 628 | 2019-06-29 23:30 | 211 | 935 | 205 | 915 | 211 | 936 | 21 | 464.5 | 132 | 3 |  | 135 | 98% | 67% | 71% | 100% | 4.8418 | Loss 0-5% |  | 550(74) | 588(168) | 585(84) | 506(61)
1135 | 1230 | LNR | PREET VIHAR | PVR001 | TG-PVR001A-1 | DT-1 | G-II, PREET VIHAR:ID | 2 | 630 | 19503221 | 738 | 2019-06-06 00:30 | 228 | 945 | 275 | 1145 | 235 | 975 | 187 | 534 | 126.5 | 26 | 8.5 | 161 | 117% | 76% | 85% | 109% | 2.6245 | Loss 0-5% |  |  | 565(85.5) | 518(24.5) | 581(25.5)
1136 | 1230 | LNR | PREET VIHAR | PVR001 | TG-PVR001A-2 | DT-2 | G-II, PREET VIHAR:ID | 2 | 990 | 19503213 | 957 | 2019-06-05 02:30 | 319 | 1423 | 308 | 1368 | 330 | 1474 | 92 | 695 |  | 0.5 |  | 0.5 | 97% | 39% | 49% | 58% | 2.6245 | Loss 0-5%
1137 | 1230 | LNR | PREET VIHAR | PVR006 | TG-PVR006A-1 | DT-1 | B BLOCK, PREET VIHAR:ID | 2 | 630 | 19501149 | 208 | 2019-06-03 00:30 | 93 | 419 | 56 | 248 | 59 | 263 | 164 | 720 |  |  |  | 0 | 33% | 23% | 27% | 32% | 3.186 | Loss 0-5%
1138 | 1230 | LNR | PREET VIHAR | PVR006 | TG-PVR006A-2 | DT-2 | B BLOCK, PREET VIHAR:ID | 2 | 630 | 19501150 | 487 | 2019-06-10 23:30 | 172 | 769 | 118 | 519 | 197 | 882 | 322 | 670.5 | 49.5 |  |  | 49.5 | 77% | 58% | 71% | 77% | 3.186 | Loss 0-5%
1139 | 1230 | LNR | PREET VIHAR | PVR009 | TG-PVR009A-1 | DT-1 | EAST GURU ANGAD NAGAR:K | 3 | 630 | 19504643 | 669 | 2019-06-30 23:30 | 211 | 892 | 193 | 833 | 265 | 1134 | 276 | 486 | 148.5 | 32 | 4.5 | 185 | 101% | 70% | 79% | 106% | 4.5107 | Loss 0-5% |  | 660(85.5) | 638(85) | 609(89)
1140 | 1230 | LNR | PREET VIHAR | PVR009 | TG-PVR009A-2 | DT-2 | EAST GURU ANGAD NAGAR:K | 3 | 990 | 19504514 | 1253.9548 | 2019-06-11 22:00 | 325.802 | 1325.0987 | 572.0406 | 2396.0819 | 356.1122 | 1451.0909 | 1013.8755 | 402.5 | 128.5 | 48 | 43.5 | 220 | 107% | 63% | 108% | 127% | 4.5107 | Loss 0-5% |  | 1054(144) |  | 969(29.5) | 980(169)
1141 | 1230 | LNR | PREET VIHAR | PVR009 | TG-PVR009A-3 | DT-3 | EAST GURU ANGAD NAGAR:K | 3 | 990 | 19504811 | 1096 | 2019-06-03 | 325 | 1429 | 401 | 1769 | 370 | 1623 | 295 | 517.5 | 160 | 39.5 | 3 | 202.5 | 111% | 68% | 78% | 102% | 4.5107 | Loss 0-5% |  | 969(52) | 1022(152) | 955(114.5) | 862(80)
1142 | 1230 | LNR | PREET VIHAR | PVR015 | TG-PVR015A-1 | DT-1 | G-I, PREET VIHAR:ID | 2 | 990 | 19501193 | 1017 | 2019-06-10 13:00 | 343 | 1462 | 362 | 1548 | 312 | 1328 | 192 | 423 | 210.5 | 79 | 7.5 | 297 | 62% | 66% | 103% | 73% | 3.7925 | Loss 0-5% |  | 890(96.5) | 976(191) | 967(153.5) | 822(78.5)
1143 | 1230 | LNR | PREET VIHAR | PVR015 | TG-PVR015A-2 | DT-2 | G-I, PREET VIHAR:ID | 2 | 990 | 19506821 | 884 | 2019-06-01 15:30 | 301 | 1289 | 296 | 1277 | 287 | 1224 | 60 | 529.5 | 190 |  |  | 190 | 73% | 52% | 89% | 77% | 3.7925 | Loss 0-5% |  | 812(25) | 919(116) | 851(55)
1144 | 1230 | LNR | PREET VIHAR | PVR018 | TG-PVR018A-1 | DT-1 | C-BLOCK, PREET VIHAR:ID | 3 | 630 | 19501148 | 618 | 2019-06-02 14:00 | 194 | 838 | 236 | 1029 | 188 | 811 | 206 | 583.5 | 134 | 2 |  | 136 | 88% | 70% | 98% | 90% | 7.8937 | Loss 5-10% |  | 504(34) | 499(30.5) | 530(44.5)
1145 | 1230 | LNR | PREET VIHAR | PVR018 | TG-PVR018A-2 | DT-2 | C-BLOCK, PREET VIHAR:ID | 3 | 630 | 19501056 | 483 | 2019-06-01 19:30 | 159 | 702 | 147 | 646 | 178 | 791 | 127 | 690 | 6 |  |  | 6 | 71% | 51% | 77% | 74% | 7.8937 | Loss 5-10%
1146 | 1230 | LNR | PREET VIHAR | PVR018 | TG-PVR018A-3 | DT-3 | C-BLOCK, PREET VIHAR:ID | 3 | 630 | 19505781 | 333 | 2019-06-03 11:30 | 125 | 542 | 114 | 495 | 95 | 407 | 119 | 720 |  |  |  | 0 | 11% | 16% | 53% | 30% | 7.8937 | Loss 5-10%
1147 | 1230 | LNR | PREET VIHAR | PVR019 | TG-PVR019A-1 | DT-1 | NIRMAN VIHAR (NEAR MKT.):ID | 3 | 990 | 19504881 | 802 | 2019-06-11 23:30 | 225 | 970 | 272 | 1150 | 306 | 1342 | 322 | 669.5 | 50 |  |  | 50 | 78% | 49% | 63% | 81% | 5.0685 | Loss 5-10%
1148 | 1230 | LNR | PREET VIHAR | PVR019 | TG-PVR019A-2 | DT-2 | NIRMAN VIHAR (NEAR MKT.):ID | 3 | 990 | 19501146 | 599 | 2019-06-15 15:00 | 179 | 796 | 196 | 892 | 225 | 1015 | 190 | 719.5 |  |  |  | 0 | 55% | 38% | 61% | 58% | 5.0685 | Loss 5-10% |  |  | 779(54)
1149 | 1230 | LNR | PREET VIHAR | PVR019 | TG-PVR019A-3 | DT-3 | NIRMAN VIHAR (NEAR MKT.):ID | 3 | 630 | 19505378 | 406 | 2019-06-11 23:00 | 157 | 694 | 112 | 490 | 138 | 613 | 177 | 717 |  |  |  | 0 | 61% | 49% | 63% | 65% | 5.0685 | Loss 5-10%
1150 | 1230 | LNR | PREET VIHAR | PVR021 | TG-PVR021A-1 | DT-1 | BHARATI ARTIST COLONY:K | 1 | 990 | 19506726 | 1232 | 2019-06-29 14:30 | 430 | 1911 | 426 | 1894 | 376 | 1671 | 232 | 409.5 | 116 | 70 | 122 | 308 | 45% | 48% | 124% | 67% | 4.0596 | Loss 0-5% | 799(44) | 989(176.5) | 1097(237.5) | 1006(178.5)
1151 | 1230 | LNR | PREET VIHAR | PVR026 | TG-PVR026A-1 | DT-1 | B-BLOCK, PREET VIHAR, NEAR MKT.:ID | 1 | 630 | 19503229 | 523 | 2019-06-30 23:00 | 180 | 774 | 191 | 823 | 152 | 646 | 158 | 664 | 56 |  |  | 56 | 81% | 51% | 69% | 83% | 3.9249 | Loss 0-5% |  | 586(99) | 606(179.5) | 571(113)
1152 | 1230 | LNR | PREET VIHAR | PVR067 | TG-PVR067A-1 | DT-1 | Swasthya vihar kiosk Vikas Marg | 2 | 630 | 19502956 | 689 | 2019-06-29 12:30 | 234 | 941 | 241 | 1003 | 213 | 880 | 107 | 476 | 130.5 | 72.5 | 15.5 | 218.5 | 26% | 43% | 109% | 43% | 4.5634 | Loss 0-5% | 511(57) | 636(178) | 695(238.5) | 635(177.5) | 538(61.5) | 537(100.5)
1153 | 1230 | LNR | PREET VIHAR | PVR067 | TG-PVR067A-2 | DT-2 | Swasthya vihar kiosk Vikas Marg | 2 | 630 | 19504801 | 499 | 2019-06-12 17:00 | 198 | 783 | 124 | 485 | 177 | 683 | 263 | 642.5 | 77.5 |  |  | 77.5 | 29% | 32% | 79% | 42% | 4.5634 | Loss 0-5%
1154 | 1230 | LNR | PREET VIHAR | PVR068 | TG-PVR068A-1 | DT-1 | CHITRA VIHAR:ID | 3 | 630 | 19506666 | 528 | 2019-06-30 01:00 | 199 | 814 | 174 | 716 | 155 | 634 | 156 | 692.5 | 26 |  |  | 26 | 84% | 59% | 62% | 76% | 5.0892 | Loss 5-10% |  |  | 511(49.5)
1155 | 1230 | LNR | PREET VIHAR | PVR068 | TG-PVR068A-2 | DT-2 | CHITRA VIHAR:ID | 3 | 630 | 19503203 | 567 | 2019-06-02 22:30 | 238 | 1081 | 199 | 884 | 130 | 573 | 444 | 615.5 | 104 |  |  | 104 | 88% | 56% | 63% | 90% | 5.0892 | Loss 5-10% |  | 552(46) | 564(111) | 535(28.5)
1156 | 1230 | LNR | PREET VIHAR | PVR068 | TG-PVR068A-3 | DT-3 | CHITRA VIHAR:ID | 3 | 630 | 19505782 | 237 | 2019-06-11 23:30 | 70 | 289 | 70 | 290 | 97 | 399 | 109 | 718 |  |  |  | 0 | 36% | 28% | 36% | 38% | 5.0892 | Loss 5-10%
1157 | 1230 | LNR | PREET VIHAR | PVR082 | TG-PVR082A-1 | DT-1 | E-BLK PREET VIHAR(NEAR E-95 PREET VIHAR) | 1 | 630 | 19503740 | 583 | 2019-06-12 | 159 | 690 | 180 | 783 | 244 | 1070 | 343 | 579 | 115.5 | 1.5 |  | 117 | 93% | 58% | 67% | 91% | 3.243 | Loss 0-5% |  | 584(75.5) | 605(154) | 546(61)
1158 | 1240 | MVR | S/STN 8 POCKET C | MV2002 | TG-MV2002A-1 | DT-1 | 15 BLCOK KALYAN PURI:K | 2 | 990 | 19504329 | 527 | 2019-06-27 | 192 | 828 | 183 | 786 | 153 | 652 | 159 | 719 |  |  |  | 0 | 53% | 46% | 52% | 53% | 9.0896 | Loss 5-10%
1159 | 1240 | MVR | S/STN 8 POCKET C | MV2002 | TG-MV2002A-2 | DT-2 | 15 BLCOK KALYAN PURI:K | 2 | 630 | 19505816 | 558 | 2019-06-30 23:00 | 171 | 705 | 137 | 559 | 250 | 1031 | 419 | 640 | 79 |  |  | 79 | 84% | 66% | 78% | 89% | 9.0896 | Loss 5-10% |  |  | 545(63) | 533(40)
1160 | 1240 | MVR | S/STN 8 POCKET C | MV2004 | TG-MV2004A-1 | DT-1 | 13 & 18 BLK,KALYANPURI | 2 | 990 | 19505817 | 956 | 2019-06-09 06:00 | 334 | 1439 | 291 | 1254 | 331 | 1424 | 178 | 420.5 | 290.5 | 7 |  | 297.5 | 93% | 97% | 91% | 92% | 7.936 | Loss 5-10%
1161 | 1240 | MVR | S/STN 8 POCKET C | MV2004 | TG-MV2004A-2 | DT-2 | 13 & 18 BLK,KALYANPURI | 2 | 990 | 19505818 | 808 | 2019-06-09 03:30 | 281 | 1227 | 192 | 839 | 335 | 1482 | 561 | 717 | 0.5 |  |  | 0.5 | 82% | 66% | 51% | 57% | 7.936 | Loss 5-10%
1162 | 1240 | MVR | S/STN 8 POCKET C | MV2005 | TG-MV2005A-1 | DT-1 | 17 BLOCK KLP:PL | 3 | 630 | 19505073 | 355 | 2019-06-02 23:30 | 121 | 519 | 109 | 466 | 125 | 544 | 70 | 679 |  |  |  | 0 | 55% | 51% | 48% | 56% | 18.9815 | Loss 10-20%
1163 | 1240 | MVR | S/STN 8 POCKET C | MV2005 | TG-MV2005A-2 | DT-2 | 17 BLOCK KLP:PL | 3 | 990 | 19502773 | 815 | 2019-06-11 23:30 | 278 | 1252 | 266 | 1196 | 270 | 1215 | 50 | 601 | 119 |  |  | 119 | 80% | 68% | 68% | 82% | 18.9815 | Loss 10-20% |  | 760(32.5) | 823(153.5) | 853(135.5) | 780(70)
1164 | 1240 | MVR | S/STN 8 POCKET C | MV2005 | TG-MV2005A-3 | DT-3 | 17 BLOCK KLP:PL | 3 | 630 | 19505914 | 495 | 2019-06-29 23:30 | 175 | 787 | 169 | 762 | 151 | 676 | 100 | 690.5 | 29.5 |  |  | 29.5 | 76% | 61% | 64% | 79% | 18.9815 | Loss 10-20% |  | 740(165.5) | 715(349.5) | 660(242.5) | 727(153.5)
1165 | 1240 | MVR | S/STN 8 POCKET C | MV2007 | TG-MV2007A-1 | DT-1 | KHP VILLAGE MAIN ROAD:PL | 2 | 630 | 19506237 | 555 | 2019-06-11 23:30 | 152 | 661 | 191 | 818 | 212 | 917 | 224 | 499.5 | 220.5 |  |  | 220.5 | 87% | 69% | 82% | 88% | 19.5724 | Loss 10-20% |  |  | 494(77.5)
1166 | 1240 | MVR | S/STN 8 POCKET C | MV2007 | TG-MV2007A-2 | DT-2 | KHP VILLAGE MAIN ROAD:PL | 2 | 400 | 19504866 | 288 | 2019-06-15 16:00 | 82 | 345 | 108 | 457 | 98 | 411 | 97 | 718.5 | 1.5 |  |  | 1.5 | 59% | 54% | 72% | 68% | 19.5724 | Loss 10-20% |  |  | 310(31) | 326(40)
1167 | 1240 | MVR | S/STN 8 POCKET C | MV2009 | TG-MV2009A-1 | DT-1 | A BLOCK V. NAGAR:PL | 1 | 990 | 19502531 | 934 | 2019-06-30 23:00 | 347 | 1658 | 287 | 1363 | 301 | 1433 | 266 | 587.5 | 128 | 4 |  | 132 | 89% | 57% | 72% | 94% | 3.0145 | Loss 0-5% |  |  | 806(66.5) | 894(76.5) | 778(32.5)
1168 | 1240 | MVR | S/STN 8 POCKET C | MV2010 | TG-MV2010A-1 | DT-1 | E BLOCK V. NAGAR:PL | 3 | 630 | 19503465 | 656 | 2019-06-30 02:00 | 181 | 777 | 205 | 889 | 271 | 1187 | 367 | 573 | 125 | 20.5 | 1.5 | 147 | 104% | 82% | 69% | 73% | 9.1771 | Loss 5-10% |  |  | 654(89.5) |  | 520(48)
1169 | 1240 | MVR | S/STN 8 POCKET C | MV2010 | TG-MV2010A-2 | DT-2 | E BLOCK V. NAGAR:PL | 3 | 990 | 19502553 | 1099 | 2019-06-30 23:00 | 336 | 1513 | 406 | 1836 | 357 | 1596 | 290 | 592 | 86 | 28 | 14 | 128 | 107% | 72% | 82% | 111% | 9.1771 | Loss 5-10% | 1118(91) | 1552(370.5) | 1447(478) | 1344(126) |  | 1109(178)
1170 | 1240 | MVR | S/STN 8 POCKET C | MV2010 | TG-MV2010A-3 | DT-3 | E BLOCK V. NAGAR:PL | 3 | 630 | 19506917 | 350 | 2019-06-30 23:00 | 101 | 436 | 101 | 434 | 147 | 638 | 202 | 439.5 |  |  |  | 0 | 53% | 35% | 42% | 55% | 9.1771 | Loss 5-10%
1171 | 1240 | MVR | S/STN 8 POCKET C | MV2018 | TG-MV2018A-1 | DT-1 | S/S NO. 5 PKT. B :ID | 2 | 630 | 19500735 | 508.838 | 2019-06-30 | 190.6848 | 869.0404 | 155.94 | 715.1899 | 162.2131 | 736.9639 | 144.2018 | 666 | 54 |  |  | 54 | 81% | 51% | 63% | 81% | 9.0414 | Loss 5-10% |  |  | 536(67)
1172 | 1240 | MVR | S/STN 8 POCKET C | MV2018 | TG-MV2018A-2 | DT-2 | S/S NO. 5 PKT. B :ID | 2 | 630 | 19500734 | 448.2426 | 2019-06-11 23:30 | 162.4419 | 722.1565 | 114.0475 | 503.41 | 171.7532 | 760.4409 | 240.1881 | 717.5 | 2.5 |  |  | 2.5 | 69% | 43% | 58% | 71% | 9.0414 | Loss 5-10%
1173 | 1240 | MVR | S/STN 8 POCKET C | MV2025 | TG-MV2025A-1 | DT-1 | S/S NO. 4 PKT-E MVR II:ID | 2 | 400 | 19502103 | 233 | 2019-06-30 23:30 | 85 | 367 | 79 | 341 | 69 | 298 | 61 | 720 |  |  |  | 0 | 52% | 36% | 44% | 58% | 9.4297 | Loss 5-10%
1174 | 1240 | MVR | S/STN 8 POCKET C | MV2025 | TG-MV2025A-2 | DT-2 | S/S NO. 4 PKT-E MVR II:ID | 2 | 630 | 19502109 | 533 | 2019-06-26 23:30 | 153 | 730 | 173 | 823 | 207 | 990 | 229 | 679 | 41 |  |  | 41 | 81% | 50% | 57% | 85% | 9.4297 | Loss 5-10% |  |  | 510(29)
1175 | 1240 | MVR | S/STN 8 POCKET C | MV2034 | TG-MV2034A-1 | DT-1 | D BLOCK GAZIPUR:ID | 2 | 630 | 19502114 | 298 | 2019-06-02 18:00 | 107 | 439 | 118 | 488 | 73 | 297 | 172 | 720 |  |  |  | 0 | 45% | 46% | 47% | 43% | 28.8864 | Loss 20-30%
1176 | 1240 | MVR | S/STN 8 POCKET C | MV2034 | TG-MV2034A-2 | DT-2 | D BLOCK GAZIPUR:ID | 2 | 400 | 19506238 | 332 | 2019-06-25 17:30 | 137 | 556 | 90 | 365 | 105 | 425 | 169 | 661 | 59 |  |  | 59 | 74% | 74% | 83% | 64% | 28.8864 | Loss 20-30% | 393(168.5) | 387(257) | 457(330) | 375(150) | 382(81) | 522(134)
1177 | 1240 | MVR | S/STN 8 POCKET C | MV2036 | TG-MV2036A-1 | DT-1 | DDA JANTA FLAT GAZIPUR:ID | 2 | 630 | 19502536 | 363 | 2019-06-15 18:00 | 99 | 389 | 131 | 513 | 133 | 522 | 129 | 720 |  |  |  | 0 | 41% | 47% | 58% | 40% | 9.0693 | Loss 5-10%
1178 | 1240 | MVR | S/STN 8 POCKET C | MV2036 | TG-MV2036A-2 | DT-2 | DDA JANTA FLAT GAZIPUR:ID | 2 | 990 | 19502496 | 906 | 2019-06-30 | 244 | 1036 | 330 | 1392 | 332 | 1411 | 366 | 555 | 163 | 2 |  | 165 | 91% | 64% | 73% | 91% | 9.0693 | Loss 5-10% |  | 821(55) | 895(159) | 915(126.5) | 813(71)
1179 | 1240 | MVR | S/STN 8 POCKET C | MV2037 | TG-MV2037A-1 | DT-1 | S/S NO. 1 PKT A MVR-II:ID | 1 | 630 | 19502073 | 606 | 2019-06-11 23:30 | 211 | 886 | 202 | 842 | 193 | 807 | 69 | 599.5 | 114 | 6.5 |  | 120.5 | 96% | 61% | 72% | 96% | 4.3259 | Loss 0-5% |  | 538(40) | 576(99.5) | 561(54)
1180 | 1240 | MVR | S/STN 8 POCKET C | MV2041 | TG-MV2041A-1 | DT-1 | S/S NO. 1 KHR COLONY:ID | 2 | 990 | 19502491 | 786 | 2019-06-26 22:30 | 263 | 1082 | 212 | 868 | 310 | 1269 | 347 | 687.5 | 31.5 |  |  | 31.5 | 76% | 67% | 64% | 79% | 3.4545 | Loss 0-5%
1181 | 1240 | MVR | S/STN 8 POCKET C | MV2041 | TG-MV2041A-2 | DT-2 | S/S NO. 1 KHR COLONY:ID | 2 | 400 | 19504469 | 343 | 2019-06-11 03:00 | 84 | 332 | 166 | 659 | 93 | 389 | 302 | 680.5 | 38.5 |  |  | 38.5 | 86% | 71% | 63% | 85% | 3.4545 | Loss 0-5% |  |  | 300(29)
1182 | 1240 | MVR | S/STN 8 POCKET C | MV2043 | TG-MV2043A-1 | DT-1 | S/S -10 BLK KHP. COROM:PL | 2 | 990 | 19502493 | 426 | 2019-06-26 23:00 | 166 | 692 | 133 | 546 | 128 | 530 | 155 | 719.5 |  |  |  | 0 | 42% | 34% | 35% | 43% | 14.1884 | Loss 10-20%
1183 | 1240 | MVR | S/STN 8 POCKET C | MV2043 | TG-MV2043A-2 | DT-2 | S/S -10 BLK KHP. COROM:PL | 2 | 630 | 19505915 | 691 | 2019-06-29 23:30 | 221 | 940 | 248 | 1055 | 222 | 933 | 118 | 288.5 | 302 | 101.5 | 27 | 430.5 | 108% | 93% | 108% | 110% | 14.1884 | Loss 10-20% | 581(100) | 752(399) | 722(476.5) | 727(450.5) |  | 657(139)
1184 | 1240 | MVR | S/STN 8 POCKET C | MV2045 | TG-MV2045A-1 | DT-1 | S/S 8 BLK KHP COLONY:PL | 2 | 630 | 19505911 | 619 | 2019-06-10 10:30 | 226 | 988 | 218 | 950 | 175 | 761 | 211 | 494.5 | 204 | 21.5 |  | 225.5 | 93% | 81% | 98% | 96% | 10.6083 | Loss 10-20% | 770(307) | 827(545) | 853(652) | 1068(686.5)
1185 | 1240 | MVR | S/STN 8 POCKET C | MV2045 | TG-MV2045A-2 | DT-2 | S/S 8 BLK KHP COLONY:PL | 2 | 630 | 19506837 | 259 | 2019-06-02 23:30 | 117 | 477 | 38 | 156 | 104 | 430 | 300 | 720 |  |  |  | 0 | 41% | 33% | 40% | 41% | 10.6083 | Loss 10-20%
1186 | 1240 | MVR | S/STN 8 POCKET C | MV2046 | TG-MV2046A-1 | DT-1 | S/S 10 BLK KHP COLONY (OLD):PL | 1 | 990 | 19502572 | 876 | 2019-06-30 23:30 | 253 | 1031 | 303 | 1253 | 319 | 1324 | 264 | 585 | 134.5 |  |  | 134.5 | 85% | 66% | 73% | 88% | 12.1003 | Loss 10-20% |  |  | 767(41) | 798(35.5)
1187 | 1240 | MVR | S/STN 8 POCKET C | MV2047 | TG-MV2047A-1 | DT-1 | S/S 2 BLK KHP COLONY:ID | 2 | 630 | 19506725 | 750 | 2019-06-06 | 230 | 942 | 258 | 1066 | 262 | 1089 | 137 | 404.5 | 263.5 | 48.5 | 3.5 | 315.5 | 119% | 81% | 87% | 101% | 3.3797 | Loss 0-5% |  | 579(96) | 668(301.5) | 666(298.5) | 603(239) | 593(36.5)
1188 | 1240 | MVR | S/STN 8 POCKET C | MV2047 | TG-MV2047A-2 | DT-2 | S/S 2 BLK KHP COLONY:ID | 2 | 630 | 19505714 | 426 | 2019-06-12 00:30 | 150 | 616 | 113 | 458 | 163 | 664 | 187 | 720 |  |  |  | 0 | 68% | 55% | 57% | 67% | 3.3797 | Loss 0-5%
1189 | 1240 | MVR | S/STN 8 POCKET C | MV2062 | TG-MV2062A-1 | DT-1 | D BLK EAST VINOD NAGAR | 1 | 630 | 19505701 | 620 | 2019-06-30 23:30 | 248 | 1094 | 186 | 813 | 186 | 817 | 279 | 631.5 | 83 | 5.5 |  | 88.5 | 96% | 52% | 75% | 98% | 3.8374 | Loss 0-5%
1190 | 1240 | MVR | S/STN 8 POCKET C | MV2064 | TG-MV2064A-1 | DT-1 | R BLOCK EAST VINOD NGR SPER SHINE | 1 | 990 | 19505715 | 806 | 2019-06-06 | 267 | 1115 | 267 | 1116 | 272 | 1138 | 23 | 663.5 | 56.5 |  |  | 56.5 | 81% | 53% | 69% | 80% | 11.8147 | Loss 10-20% |  |  | 792(25) | 794(25.5)
1191 | 1240 | MVR | SADAR APPARTMENTS | MV1007 | TG-MV1007A-1 | DT-1 | ACHARYA NIKETAN PL/M:PL | 1 | 990 | 19502065 | 754 | 2019-06-13 16:00 | 286 | 1266 | 254 | 1115 | 214 | 940 | 282 | 688 | 32 |  |  | 32 | 25% | 20% | 76% | 54% | 6.4824 | Loss 5-10%
1192 | 1240 | MVR | SADAR APPARTMENTS | MV1008 | TG-MV1008A-1 | DT-1 | ACHARYA NIKETAN:ID | 3 | 990 | 19504354 | 682 | 2019-06-29 16:00 | 186 | 761 | 280 | 1153 | 216 | 888 | 346 | 719.5 |  |  |  | 0 | 62% | 44% | 69% | 62% | 4.5642 | Loss 0-5%
1193 | 1240 | MVR | SADAR APPARTMENTS | MV1008 | TG-MV1008A-2 | DT-2 | ACHARYA NIKETAN:ID | 3 | 990 | 19504284 | 855 | 2019-06-13 17:30 | 297 | 1268 | 308 | 1321 | 249 | 1063 | 237 | 513.5 | 206 |  |  | 206 | 77% | 56% | 86% | 76% | 4.5642 | Loss 0-5% |  | 925(126) | 971(324.5) | 990(242.5) | 865(172)
1194 | 1240 | MVR | SADAR APPARTMENTS | MV1008 | TG-MV1008A-3 | DT-3 | ACHARYA NIKETAN:ID | 3 | 630 | 19505647 | 627 | 2019-06-30 14:30 | 127 | 540 | 348 | 1581 | 152 | 681 | 977 | 439 | 276 | 4.5 |  | 280.5 | 96% | 68% | 100% | 91% | 4.5642 | Loss 0-5% |  |  | 581(107) | 527(53) |  | 595(91.5)
1195 | 1240 | MVR | SADAR APPARTMENTS | MV1009 | TG-MV1009A-1 | DT-1 | SHASHI GARDEN PLM:PL | 2 | 990 | 19502111 | 1297 | 2019-06-30 01:00 | 363 | 1522 | 473 | 2002 | 460 | 1939 | 452 | 373.5 | 184.5 | 63.5 | 98.5 | 346.5 | 131% | 79% | 90% | 131% | 5.7344 | Loss 5-10% |  | 1217(153.5) | 1353(460) |  | 1132(288) | 952(72.5)
1196 | 1240 | MVR | SADAR APPARTMENTS | MV1009 | TG-MV1009A-2 | DT-2 | SHASHI GARDEN PLM:PL | 2 | 990 | 19505279 | 600 | 2019-06-11 | 289 | 1266 | 131 | 567 | 180 | 778 | 621 | 720 |  |  |  | 0 | 61% | 44% | 50% | 59% | 5.7344 | Loss 5-10%
1197 | 1240 | MVR | SADAR APPARTMENTS | MV1018 | TG-MV1018A-1 | DT-1 | S/S-2 PKT-I MVR PH-I:ID | 3 | 630 | 19502099 | 540 | 2019-06-30 23:30 | 158 | 669 | 218 | 923 | 164 | 685 | 247 | 638 | 82 |  |  | 82 | 83% | 74% | 79% | 86% | 6.6913 | Loss 5-10% |  | 569(34) | 541(113.5) | 540(46)
1198 | 1240 | MVR | SADAR APPARTMENTS | MV1018 | TG-MV1018A-2 | DT-2 | S/S-2 PKT-I MVR PH-I:ID | 3 | 630 | 19502100 | 426 | 2019-06-29 23:30 | 170 | 713 | 119 | 506 | 137 | 579 | 182 | 720 |  |  |  | 0 | 67% | 35% | 49% | 68% | 6.6913 | Loss 5-10%
1199 | 1240 | MVR | SADAR APPARTMENTS | MV1018 | TG-MV1018A-3 | DT-3 | S/S-2 PKT-I MVR PH-I:ID | 3 | 630 | 19506269 | 223 | 2019-06-30 23:30 | 91 | 387 | 57 | 239 | 76 | 325 | 129 | 720 |  |  |  | 0 | 34% | 23% | 27% | 35% | 6.6913 | Loss 5-10%
1200 | 1240 | MVR | SADAR APPARTMENTS | MV1023 | TG-MV1023A-1 | DT-1 | S/S-B PKT-2 MVR PH-I:ID | 2 | 630 | 19502096 | 536 | 2019-06-10 23:30 | 206 | 911 | 141 | 628 | 188 | 821 | 250 | 658 | 62 |  |  | 62 | 83% | 49% | 62% | 85% | 6.2483 | Loss 5-10% |  | 521(28.5) | 552(80.5)
1201 | 1240 | MVR | SADAR APPARTMENTS | MV1023 | TG-MV1023A-2 | DT-2 | S/S-B PKT-2 MVR PH-I:ID | 2 | 990 | 19503736 | 511 | 2019-06-29 23:30 | 201 | 855 | 138 | 589 | 173 | 723 | 230 | 696 |  |  |  | 0 | 51% | 31% | 38% | 52% | 6.2483 | Loss 5-10%
1202 | 1240 | MVR | SADAR APPARTMENTS | MV1024 | TG-MV1024A-1 | DT-1 | PARTAP NAGAR PLM:PL | 1 | 990 | 19500719 | 1051 | 2019-06-06 17:30 | 438 | 1804 | 302 | 1229 | 311 | 1268 | 557 | 495.5 | 197 | 24.5 | 1.5 | 223 | 99% | 71% | 106% | 98% | 3.7964 | Loss 0-5% |  |  | 821(72) | 809(30.5)
1203 | 1240 | MVR | SADAR APPARTMENTS | MV1028 | TG-MV1028A-1 | DT-1 | S/S-2 PKT IV MVR PH-1:ID | 2 | 990 | 19502062 | 541 | 2019-06-02 23:30 | 236 | 972 | 130 | 539 | 174 | 712 | 377 | 719 |  |  |  | 0 | 54% | 29% | 39% | 55% | 5.6935 | Loss 5-10%
1204 | 1240 | MVR | SADAR APPARTMENTS | MV1028 | TG-MV1028A-2 | DT-2 | S/S-2 PKT IV MVR PH-1:ID | 2 | 630 | 19502067 | 569 | 2019-06-02 23:30 | 182 | 772 | 206 | 877 | 182 | 776 | 103 | 672.5 | 46.5 | 0.5 |  | 47 | 89% | 50% | 69% | 90% | 5.6935 | Loss 5-10% |  | 553(48.5) | 609(105.5)
1205 | 1240 | MVR | SADAR APPARTMENTS | MV1046 | TG-MV1046A-1 | DT-1 | STN-8 PKT-1 MVR-1(SWITCHING STN) | 2 | 630 | 19500700 | 587.8158 | 2019-06-30 23:00 | 249.0262 | 1124.3224 | 168.7015 | 749.9845 | 170.0881 | 743.2295 | 377.7607 | 617.5 | 99 | 2 |  | 101 | 89% | 57% | 68% | 93% | 4.9963 | Loss 0-5% |  | 527(31.5) | 580(104) | 548(47.5)
1206 | 1240 | MVR | SADAR APPARTMENTS | MV1046 | TG-MV1046A-2 | DT-2 | STN-8 PKT-1 MVR-1(SWITCHING STN) | 2 | 630 | 19504893 | 140 | 2019-06-29 23:30 | 47 | 196 | 35 | 148 | 58 | 246 | 85 | 670.5 |  |  |  | 0 | 22% | 14% | 21% | 22% | 4.9963 | Loss 0-5%
1207 | 1240 | MVR | SADAR APPARTMENTS | MV1058 | TG-MV1058A-1 | DT-1 | CHILLA VILLAGE (OLD):PL | 1 | 990 | 19505242 | 869 | 2019-06-29 00:30 | 324 | 1356 | 220 | 915 | 326 | 1395 | 461 | 635.5 | 83 |  |  | 83 | 88% | 76% | 67% | 78% | 38.5453 | Loss >30% |  |  | 768(70.5) | 790(93.5)
1208 | 1240 | MVR | SADAR APPARTMENTS | MV1074 | TG-MV1074A-1 | DT-1 | ADRESH MOHALLA:PL | 2 | 990 | 19502118 | 827 | 2019-06-02 | 332 | 1370 | 279 | 1136 | 216 | 886 | 419 | 647 | 71.5 |  |  | 71.5 | 83% | 59% | 64% | 80% | 3.6182 | Loss 0-5% |  | 992(154) | 953(212) | 895(102.5) | 793(53.5)
1209 | 1240 | MVR | SADAR APPARTMENTS | MV1074 | TG-MV1074A-2 | DT-2 | ADRESH MOHALLA:PL | 2 | 630 | 19504290 | 602 | 2019-06-30 00:30 | 184 | 823 | 184 | 827 | 234 | 1061 | 237 | 569.5 | 147 | 2.5 |  | 149.5 | 96% | 72% | 69% | 91% | 3.6182 | Loss 0-5% |  |  | 566(120) | 547(73.5) | 486(30.5)
1210 | 1240 | MVR | SADAR APPARTMENTS | MV1075 | TG-MV1075A-1 | DT-1 | SAMASPUR VILLAGE:PL | 3 | 990 | 19504679 | 619 | 2019-06-30 23:30 | 217 | 932 | 189 | 811 | 213 | 913 | 113 | 718 |  |  |  | 0 | 59% | 37% | 50% | 63% | 4.9383 | Loss 0-5%
1211 | 1240 | MVR | SADAR APPARTMENTS | MV1075 | TG-MV1075A-2 | DT-2 | SAMASPUR VILLAGE:PL | 3 | 990 | 19504676 | 830 | 2019-06-30 00:30 | 299 | 1254 | 236 | 986 | 295 | 1238 | 261 | 687 | 33 |  |  | 33 | 84% | 58% | 63% | 82% | 4.9383 | Loss 0-5% |  | 1014(43) | 878(46.5)
1212 | 1240 | MVR | SADAR APPARTMENTS | MV1075 | TG-MV1075A-3 | DT-3 | SAMASPUR VILLAGE:PL | 3 | 990 | 19506676 | 416 | 2019-06-26 23:00 | 118 | 529 | 123 | 550 | 176 | 799 | 260 | 719.5 |  |  |  | 0 | 42% | 27% | 30% | 42% | 4.9383 | Loss 0-5%
1213 | 1240 | MVR | SADAR APPARTMENTS | MV1077 | TG-MV1077A-1 | DT-1 | PATPAR GANJ VILLAGE:ID | 2 | 990 | 19504556 | 974 | 2019-06-30 | 361 | 1576 | 308 | 1334 | 305 | 1330 | 244 | 330.5 | 361.5 | 26.5 |  | 388 | 98% | 73% | 95% | 95% | 3.5524 | Loss 0-5% |  | 933(222) | 986(439.5) | 979(304.5) | 871(172)
1214 | 1240 | MVR | SADAR APPARTMENTS | MV1077 | TG-MV1077A-2 | DT-2 | PATPAR GANJ VILLAGE:ID | 2 | 990 | 19502539 | 571 | 2019-06-02 00:30 | 197 | 827 | 199 | 841 | 175 | 741 | 94 | 716 |  |  |  | 0 | 58% | 43% | 43% | 56% | 3.5524 | Loss 0-5%
1215 | 1240 | MVR | SADAR APPARTMENTS | MV1092 | TG-MV1092A-1 | DT-1 | S.S 1 CGHS MVR PH 1:ID | 3 | 990 | 19502958 | 1000 | 2019-06-11 23:30 | 398 | 1667 | 287 | 1192 | 315 | 1315 | 427 | 548 | 147.5 | 22.5 | 1.5 | 171.5 | 99% | 66% | 74% | 101% | 9.7717 | Loss 5-10% |  | 1065(125.5) | 1157(259) | 1160(267.5) | 912(136.5)
1216 | 1240 | MVR | SADAR APPARTMENTS | MV1092 | TG-MV1092A-2 | DT-2 | S.S 1 CGHS MVR PH 1:ID | 3 | 990 | 19504660 | 612 | 2019-06-26 22:30 | 199 | 908 | 192 | 877 | 221 | 1011 | 122 | 720 |  |  |  | 0 | 59% | 42% | 51% | 62% | 9.7717 | Loss 5-10%
1217 | 1240 | MVR | SADAR APPARTMENTS | MV1092 | TG-MV1092A-3 | DT-3 | S.S 1 CGHS MVR PH 1:ID | 3 | 630 | 19506267 | 741 | 2019-06-26 23:00 | 319 | 1549 | 213 | 1000 | 209 | 995 | 551 | 527.5 | 133.5 | 49 | 10 | 192.5 | 108% | 66% | 90% | 118% | 9.7717 | Loss 5-10%
1218 | 1240 | MVR | SADAR APPARTMENTS | MV1106 | TG-MV1106A-1 | DT-1 | S/S-4 PKT-5 PH-1:ID | 1 | 400 | 19502538 | 385 | 2019-06-26 22:30 | 156 | 678 | 124 | 535 | 105 | 446 | 203 | 663 | 51.5 | 3 |  | 54.5 | 92% | 64% | 64% | 96% | 13.2304 | Loss 10-20% |  | 342(43) | 373(41) | 383(58)
1219 | 1240 | MVR | SADAR APPARTMENTS | MV1107 | TG-MV1107A-1 | DT-1 | NEW S/S SHASHIGARDEN:PLM | 3 | 630 | 19502516 | 446 | 2019-06-26 22:30 | 143 | 634 | 145 | 643 | 158 | 702 | 64 | 719 | 1 |  |  | 1 | 68% | 44% | 56% | 71% | 16.6018 | Loss 10-20%
1220 | 1240 | MVR | SADAR APPARTMENTS | MV1107 | TG-MV1107A-2 | DT-2 | NEW S/S SHASHIGARDEN:PLM | 3 | 630 | 19502512 | 685 | 2019-06-26 23:30 | 213 | 881 | 265 | 1101 | 207 | 856 | 233 | 183 | 342.5 | 162.5 | 30 | 535 | 108% | 95% | 89% | 109% | 16.6018 | Loss 10-20% |  | 629(57.5) | 665(492) | 677(228) | 616(59) | 614(280.5)
1221 | 1240 | MVR | SADAR APPARTMENTS | MV1107 | TG-MV1107A-3 | DT-3 | NEW S/S SHASHIGARDEN:PLM | 3 | 630 | 19505731 | 569 | 2019-06-26 23:30 | 186 | 776 | 177 | 748 | 206 | 868 | 108 | 550 | 169 | 1 |  | 170 | 87% | 70% | 77% | 90% | 16.6018 | Loss 10-20% |  | 554(39.5) | 521(111) | 525(89.5) | 503(36)
1222 | 1240 | MVR | SADAR APPARTMENTS | MV1117 | TG-MV1117A-1 | DT-1 | STN-4 CHILLA VIL NR DDA FLAT | 1 | 630 | 19505536 | 531 | 2019-06-10 02:00 | 175 | 761 | 153 | 649 | 204 | 883 | 202 | 556 | 164 |  |  | 164 | 84% | 84% | 77% | 82% | 46.7507 | Loss >30% |  | 1043(39) | 532(162.5) | 545(175) | 542(125.5)
1223 | 1240 | MVR | TRILOKPURI | TKP003 | TG-TKP003A-1 | DT-1 | 7 BLOCK TKP:K | 2 | 990 | 19505097 | 873 | 2019-06-26 23:00 | 304 | 1292 | 262 | 1116 | 306 | 1311 | 186 | 589 | 130.5 |  |  | 130.5 | 88% | 69% | 73% | 88% | 3.1243 | Loss 0-5% |  |  | 790(52.5) | 1125(179)
1224 | 1240 | MVR | TRILOKPURI | TKP003 | TG-TKP003A-2 | DT-2 | 7 BLOCK TKP:K | 2 | 630 | 19505810 | 535 | 2019-06-07 19:00 | 190 | 797 | 166 | 691 | 179 | 749 | 91 | 668 | 51.5 |  |  | 51.5 | 65% | 72% | 85% | 66% | 3.1243 | Loss 0-5% |  |  | 498(32) |  | 500(26)
1225 | 1240 | MVR | TRILOKPURI | TKP005 | TG-TKP005A-1 | DT-1 | 10 BLOCK TKP:PL | 2 | 400 | 19505993 | 360 | 2019-06-22 20:00 | 141 | 591 | 111 | 463 | 108 | 446 | 138 | 608.5 | 111 | 0.5 |  | 111.5 | 80% | 72% | 90% | 85% | 9.7355 | Loss 5-10% |  |  | 347(35.5) | 363(26.5)
1226 | 1240 | MVR | TRILOKPURI | TKP005 | TG-TKP005A-2 | DT-2 | 10 BLOCK TKP:PL | 2 | 630 | 19504673 | 434 | 2019-06-27 00:30 | 122 | 499 | 168 | 688 | 144 | 591 | 164 | 720 |  |  |  | 0 | 69% | 54% | 52% | 68% | 9.7355 | Loss 5-10%
1227 | 1240 | MVR | TRILOKPURI | TKP006 | TG-TKP006A-1 | DT-1 | 18 BLOCK TKP:PL:ID | 2 | 630 | 19505763 | 567 | 2019-06-30 23:30 | 182 | 818 | 186 | 827 | 198 | 898 | 77 | 528.5 | 191 | 0.5 |  | 191.5 | 89% | 73% | 80% | 90% | 8.5464 | Loss 5-10% |  | 528(35) | 616(177) | 589(155) | 542(95)
1228 | 1240 | MVR | TRILOKPURI | TKP006 | TG-TKP006A-2 | DT-2 | 18 BLOCK TKP:PL:ID | 2 | 100 | 19506209 | 126 | 2019-06-09 19:30 | 47 | 207 | 0 | 0 | 79 | 362 | 315 | 719.5 |  |  | 0.5 | 0.5 | 38% | 37% | 126% | 49% | 8.5464 | Loss 5-10%
1229 | 1240 | MVR | TRILOKPURI | TKP007 | TG-TKP007A-1 | DT-1 | 13 BLOCK TKP:ID | 2 | 630 | 19500453 | 647 | 2019-06-30 01:00 | 221 | 960 | 194 | 839 | 233 | 1018 | 158 | 560 | 156.5 | 2.5 | 1 | 160 | 103% | 78% | 76% | 93% | 9.5923 | Loss 5-10% |  | 507(34) | 544(130) | 551(141.5) | 503(86.5)
1230 | 1240 | MVR | TRILOKPURI | TKP007 | TG-TKP007A-2 | DT-2 | 13 BLOCK TKP:ID | 2 | 990 | 19506208 | 916 | 2019-06-30 01:00 | 395 | 1711 | 258 | 1122 | 263 | 1125 | 587 | 642.5 | 77 | 0.5 |  | 77.5 | 93% | 72% | 72% | 85% | 9.5923 | Loss 5-10% |  | 985(90.5) | 911(181.5) | 933(177.5) | 841(117.5)
1231 | 1240 | MVR | TRILOKPURI | TKP008 | TG-TKP008A-1 | DT-1 | 23 BLOCK TKP:PL | 2 | 990 | 19504151 | 944 | 2019-06-26 23:00 | 326 | 1360 | 310 | 1301 | 308 | 1280 | 72 | 540 | 172 | 8 |  | 180 | 91% | 74% | 72% | 95% | 4.5654 | Loss 0-5% |  | 853(34) | 908(145.5) | 905(154.5) | 822(79.5)
1232 | 1240 | MVR | TRILOKPURI | TKP008 | TG-TKP008A-2 | DT-2 | 23 BLOCK TKP:PL | 2 | 630 | 19504155 | 709 | 2019-06-12 06:00 | 246 | 1012 | 206 | 850 | 257 | 1069 | 197 | 437 | 271.5 | 10.5 | 1 | 283 | 95% | 112% | 92% | 94% | 4.5654 | Loss 0-5% |  | 513(60) | 590(218) | 578(202.5) | 521(142)
1233 | 1240 | MVR | TRILOKPURI | TKP012 | TG-TKP012A-1 | DT-1 | 26 BLOCK TKP:ID | 2 | 990 | 19506805 | 889 | 2019-06-27 06:00 | 295 | 1295 | 302 | 1308 | 292 | 1258 | 45 | 659.5 | 60.5 |  |  | 60.5 | 83% | 90% | 75% | 85% | 11.9696 | Loss 10-20% |  |  | 791(33)
1234 | 1240 | MVR | TRILOKPURI | TKP012 | TG-TKP012A-2 | DT-2 | 26 BLOCK TKP:ID | 2 | 990 | 19506214 | 871 | 2019-06-27 06:00 | 332 | 1411 | 237 | 994 | 302 | 1297 | 373 | 715.5 | 4.5 |  |  | 4.5 | 79% | 88% | 71% | 80% | 11.9696 | Loss 10-20%
1235 | 1240 | MVR | TRILOKPURI | TKP013 | TG-TKP013A-1 | DT-1 | 134 WORK CENTER:ID | 2 | 630 | 19505258 | 535 | 2019-06-26 00:30 | 217 | 899 | 144 | 590 | 174 | 725 | 268 | 672 | 48 |  |  | 48 | 85% | 81% | 70% | 78% | 11.2278 | Loss 10-20% |  |  | 504(43) | 508(30)
1236 | 1240 | MVR | TRILOKPURI | TKP013 | TG-TKP013A-2 | DT-2 | 134 WORK CENTER:ID | 2 | 630 | 19504315 | 367 | 2019-06-03 00:30 | 112 | 462 | 107 | 449 | 147 | 616 | 161 | 720 |  |  |  | 0 | 58% | 50% | 47% | 58% | 11.2278 | Loss 10-20%
1237 | 1240 | MVR | TRILOKPURI | TKP014 | TG-TKP014A-1 | DT-1 | 320 EWS CHILLA DDA FLAT,TKP | 1 | 630 | 19506913 | 516.4526 | 2019-06-30 23:30 | 168.6874 | 735.47 | 166.1172 | 732.1808 | 181.648 | 797.5063 | 63.7446 | 681 | 39 |  |  | 39 | 78% | 63% | 60% | 82% | 2.6459 | Loss 0-5%
1238 | 1240 | MVR | TRILOKPURI | TKP016 | TG-TKP016A-1 | DT-1 | 31 BLOCK TKP:K | 2 | 630 | 19504812 | 784 | 2019-06-30 23:00 | 229 | 1007 | 287 | 1293 | 269 | 1214 | 255 | 180.5 | 282 | 101 | 156.5 | 539.5 | 124% | 104% | 99% | 124% | 6.4787 | Loss 5-10% |  |  | 515(108) | 531(81)
1239 | 1240 | MVR | TRILOKPURI | TKP016 | TG-TKP016A-2 | DT-2 | 31 BLOCK TKP:K | 2 | 990 | 19506213 | 696 | 2019-06-05 23:00 | 239 | 1033 | 225 | 967 | 232 | 997 | 57 | 719.5 | 0.5 |  |  | 0.5 | 68% | 70% | 60% | 70% | 6.4787 | Loss 5-10% |  | 930(81.5) | 1043(244.5) | 958(87.5) | 873(43)
1240 | 1240 | MVR | TRILOKPURI | TKP018 | TG-TKP018A-1 | DT-1 | 28 BLOCK TKP:PL | 2 | 990 | 19506682 | 837 | 2019-06-27 06:00 | 301 | 1283 | 259 | 1118 | 278 | 1186 | 144 | 694 | 25 |  |  | 25 | 78% | 85% | 72% | 76% | 3.5227 | Loss 0-5%
1241 | 1240 | MVR | TRILOKPURI | TKP018 | TG-TKP018A-2 | DT-2 | 28 BLOCK TKP:PL | 2 | 990 | 19504189 | 708 | 2019-06-29 23:00 | 197 | 816 | 240 | 1013 | 271 | 1133 | 277 | 713 | 3.5 |  |  | 3.5 | 71% | 71% | 56% | 71% | 3.5227 | Loss 0-5%
1242 | 1240 | MVR | TRILOKPURI | TKP020 | TG-TKP020A-1 | DT-1 | KOTLA VILLAGE:PL | 2 | 990 | 19504356 | 695 | 2019-06-12 00:30 | 267 | 1136 | 201 | 853 | 227 | 965 | 247 | 714.5 | 0.5 |  |  | 0.5 | 70% | 49% | 57% | 63% | 25.8551 | Loss 20-30% |  |  | 748(26) | 765(27.5)
1243 | 1240 | MVR | TRILOKPURI | TKP020 | TG-TKP020A-2 | DT-2 | KOTLA VILLAGE:PL | 2 | 630 | 19505256 | 651 | 2019-06-12 00:30 | 191 | 819 | 244 | 1050 | 215 | 918 | 201 | 385 | 311.5 | 18 | 0.5 | 330 | 103% | 79% | 89% | 98% | 25.8551 | Loss 20-30% |  | 582(147) | 681(344) | 615(309.5) | 584(212)
1244 | 1240 | MVR | TRILOKPURI | TKP023 | TG-TKP023A-1 | DT-1 | 17 BLOCK TKP:PL | 2 | 990 | 19502505 | 1079 | 2019-06-03 02:00 | 343 | 1449 | 333 | 1410 | 402 | 1694 | 266 | 447 | 187.5 | 67 | 15.5 | 270 | 109% | 77% | 81% | 104% | 6.449 | Loss 5-10% |  | 907(109.5) | 1049(168) | 1086(271) | 949(83.5) | 795(30)
1245 | 1240 | MVR | TRILOKPURI | TKP023 | TG-TKP023A-2 | DT-2 | 17 BLOCK TKP:PL | 2 | 630 | 19505648 | 722 | 2019-06-03 | 274 | 1235 | 261 | 1183 | 187 | 840 | 372 | 538 | 134 | 35.5 | 9.5 | 179 | 115% | 75% | 73% | 104% | 6.449 | Loss 5-10% |  | 587(80) | 692(199.5) | 629(150.5) | 614(104.5)
1246 | 1240 | MVR | TRILOKPURI | TKP024 | TG-TKP024A-1 | DT-1 | 2 BLOCK TKP:PL | 2 | 630 | 19505548 | 764 | 2019-06-09 | 245 | 1182 | 239 | 1145 | 281 | 1361 | 200 | 603.5 | 75.5 | 33.5 | 5 | 114 | 121% | 80% | 87% | 101% | 4.7514 | Loss 0-5% |  | 739(160.5) | 707(320) | 665(306) | 640(281) | 556(59)
1247 | 1240 | MVR | TRILOKPURI | TKP024 | TG-TKP024A-2 | DT-2 | 2 BLOCK TKP:PL | 2 | 990 | 19502552 | 737 | 2019-06-12 00:30 | 238 | 1078 | 257 | 1166 | 242 | 1093 | 81 | 715.5 | 1.5 |  |  | 1.5 | 74% | 54% | 55% | 70% | 4.7514 | Loss 0-5%
1248 | 1240 | MVR | TRILOKPURI | TKP025 | TG-TKP025A-1 | DT-1 | 15 BLOCK TKP:PL | 1 | 630 | 19502486 | 562 | 2019-06-26 23:30 | 208 | 882 | 165 | 701 | 189 | 799 | 157 | 554 | 166 |  |  | 166 | 89% | 77% | 65% | 89% | 9.822 | Loss 5-10% |  | 486(32) | 524(173) | 522(120.5) | 503(51)
1249 | 1240 | MVR | TRILOKPURI | TKP027 | TG-TKP027A-1 | DT-1 | 11&12 BLOCK TRILOK TRILOK PURI | 2 | 630 | 19505745 | 597 | 2019-06-22 20:00 | 175 | 750 | 219 | 935 | 203 | 871 | 163 | 568.5 | 150.5 | 0.5 |  | 151 | 87% | 75% | 95% | 87% | 3.4944 | Loss 0-5% |  |  | 621(64.5) | 636(48)
1250 | 1240 | MVR | TRILOKPURI | TKP027 | TG-TKP027A-2 | DT-2 | 11&12 BLOCK TRILOK TRILOK PURI | 2 | 630 | 19506211 | 570 | 2019-06-03 15:30 | 179 | 831 | 218 | 1003 | 172 | 804 | 187 | 705.5 | 14 | 0.5 |  | 14.5 | 73% | 79% | 90% | 76% | 3.4944 | Loss 0-5%
1251 | 1240 | MVR | TRILOKPURI | TKP030 | TG-TKP030A-1 | DT-1 | KOTLA VILLAGE NEW | 1 | 630 | 19504357 | 675 | 2019-06-13 23:30 | 226 | 962 | 223 | 946 | 226 | 965 | 17 | 224 | 153.5 | 43 | 21.5 | 218 | 107% | 85% | 89% | 107% | 6.3206 | Loss 5-10%
1252 | 1240 | MVR | TRILOKPURI | TKP032 | TG-TKP032A-1 | DT-1 | NEW 28 BLOCK TRILOKPURI | 1 | 630 | 19506216 | 647 | 2019-06-27 06:00 | 203 | 828 | 220 | 891 | 224 | 927 | 86 | 538 | 176.5 | 4.5 | 1 | 182 | 102% | 103% | 88% | 99% | 5.5413 | Loss 5-10% |  | 555(68) | 759(176) | 578(128)
1253 | 1241 | MV3 | MVR-III | VSE004 | TG-VSE004A-1 | DT-1 | S/STN 5 A2 PKT MVR-III:ID | 2 | 400 | 19506007 | 227 | 2019-06-03 01:00 | 86 | 372 | 72 | 314 | 68 | 295 | 70 | 719 |  |  |  | 0 | 57% | 30% | 34% | 53% | 3.0953 | Loss 0-5%
1254 | 1241 | MV3 | MVR-III | VSE004 | TG-VSE004A-2 | DT-2 | S/STN 5 A2 PKT MVR-III:ID | 2 | 400 | 19503533 | 440 | 2019-06-03 01:00 | 172 | 781 | 165 | 744 | 103 | 455 | 309 | 587 | 109 | 21 | 2 | 132 | 110% | 53% | 70% | 102% | 3.0953 | Loss 0-5% |  | 345(30) | 387(98) | 403(72)
1255 | 1241 | MV3 | MVR-III | VSE008 | TG-VSE008A-1 | DT-1 | S/STN 9 A2 PKT MVR - III:ID | 2 | 990 | 19505180 | 347 | 2019-06-03 01:30 | 77 | 339 | 159 | 703 | 111 | 487 | 317 | 719 |  |  |  | 0 | 35% | 19% | 26% | 33% | 4.1941 | Loss 0-5%
1256 | 1241 | MV3 | MVR-III | VSE008 | TG-VSE008A-2 | DT-2 | S/STN 9 A2 PKT MVR - III:ID | 2 | 630 | 19502404 | 550 | 2019-06-29 23:30 | 175 | 728 | 215 | 908 | 160 | 666 | 218 | 676 | 43 |  |  | 43 | 87% | 47% | 62% | 87% | 4.1941 | Loss 0-5% |  |  | 546(49)
1257 | 1241 | MV3 | MVR-III | VSE011 | TG-VSE011A-1 | DT-1 | S/STN B5 DDA JANTA FLATE:ID | 1 | 400 | 19506212 | 369 | 2019-06-30 23:00 | 109 | 442 | 142 | 578 | 119 | 486 | 120 | 622.5 | 95 | 2.5 |  | 97.5 | 92% | 48% | 72% | 92% | 2.8602 | Loss 0-5% |  |  | 348(68) | 378(76.5)
1258 | 1241 | MV3 | MVR-III | VSE012 | TG-VSE012A-1 | DT-1 | S/STN 3 B-7 DDA JANTA FLAT:ID | 2 | 400 | 19502420 | 477 | 2019-06-30 22:30 | 197 | 833 | 104 | 433 | 176 | 751 | 366 | 517.5 | 131 | 48.5 | 23 | 202.5 | 109% | 56% | 89% | 119% | 4.3101 | Loss 0-5% |  | 385(87) |  |  | 385(123.5)
1259 | 1241 | MV3 | MVR-III | VSE012 | TG-VSE012A-2 | DT-2 | S/STN 3 B-7 DDA JANTA FLAT:ID | 2 | 400 | 19503538 | 283 | 2019-06-30 23:30 | 98 | 411 | 80 | 334 | 105 | 444 | 97 | 718.5 | 1.5 |  |  | 1.5 | 67% | 34% | 51% | 71% | 4.3101 | Loss 0-5%
1260 | 1241 | MV3 | MVR-III | VSE014 | TG-VSE014A-1 | DT-1 | S/STN C-1 PKT DDA JANTA FLAT:ID | 1 | 630 | 19506899 | 527 | 2019-06-02 | 211 | 873 | 143 | 593 | 173 | 718 | 243 | 642.5 | 76.5 |  |  | 76.5 | 84% | 57% | 72% | 83% | 7.006 | Loss 5-10% |  |  | 506(49.5)
1261 | 1241 | MV3 | MVR-III | VSE015 | TG-VSE015A-1 | DT-1 | S/STN C-2 PKT DDA JANTA FLAT:ID | 1 | 630 | 19502405 | 661 | 2019-06-30 23:00 | 226 | 949 | 242 | 1025 | 193 | 819 | 181 | 496 | 177.5 | 40.5 | 6 | 224 | 102% | 70% | 87% | 105% | 6.3715 | Loss 5-10% |  | 595(83) | 607(208) | 681(155) | 549(86)
1262 | 1241 | MV3 | MVR-III | VSE036 | TG-VSE036A-1 | DT-1 | SUBJI MANDI HARIJAN BASTI KNODLI:K | 2 | 990 | 19506914 | 1208 | 2019-06-02 23:30 | 358 | 1615 | 453 | 2059 | 396 | 1770 | 390 | 373.5 | 286 | 46.5 | 5.5 | 338 | 100% | 81% | 89% | 122% | 12.9457 | Loss 10-20% | 788(26.5) | 1093(311.5) | 1216(577.5) | 1225(524) | 1071(328.5) | 768(25)
1264 | 1241 | MV3 | MVR-III | VSE037 | TG-VSE037A-1 | DT-1 | KNODLI VILL. PANCHYAT GHAR:PL | 1 | 990 | 19502838 | 794 | 2019-06-29 22:30 | 199 | 859 | 357 | 1550 | 238 | 1010 | 630 | 655 | 63 |  |  | 63 | 77% | 69% | 72% | 80% | 16.0114 | Loss 10-20% |  |  | 876(197.5) | 886(54.5) | 866(92)
1265 | 1241 | MV3 | MVR-III | VSE039 | TG-VSE039A-1 | DT-1 | KNODLI INDAL PUBLIC SCHOOL:PM | 1 | 400 | 19506640 | 433 | 2019-06-30 22:30 | 152 | 632 | 163 | 676 | 118 | 483 | 175 | 205.5 | 387 | 114.5 | 12.5 | 514 | 102% | 93% | 93% | 108% | 20.3023 | Loss 20-30% | 334(42.5) | 420(376.5) | 386(447) | 378(286)
1266 | 1241 | MV3 | MVR-III | VSE042 | TG-VSE042A-1 | DT-1 | B-BLK RAJBIR COLONY:PL | 2 | 990 | 19502732 | 763 | 2019-06-11 23:00 | 212 | 912 | 286 | 1256 | 265 | 1160 | 307 | 688 | 31.5 |  |  | 31.5 | 76% | 67% | 65% | 77% | 11.3691 | Loss 10-20%
1267 | 1241 | MV3 | MVR-III | VSE042 | TG-VSE042A-2 | DT-2 | B-BLK RAJBIR COLONY:PL | 2 | 630 | 19505311 | 462 | 2019-06-09 | 111 | 451 | 154 | 640 | 197 | 802 | 305 | 719 | 0.5 |  |  | 0.5 | 73% | 45% | 57% | 59% | 11.3691 | Loss 10-20%
1268 | 1241 | MV3 | MVR-III | VSE045 | TG-VSE045A-1 | DT-1 | GHARAOLI VILL. OLD:PL | 1 | 630 | 19502849 | 504 | 2019-06-13 23:00 | 175 | 731 | 151 | 624 | 177 | 724 | 104 | 606.5 | 112.5 |  |  | 112.5 | 79% | 71% | 70% | 80% | 17.1142 | Loss 10-20%
1269 | 1241 | MV3 | MVR-III | VSE046 | TG-VSE046A-1 | DT-1 | GHARAOLI VILL. NEW:PL | 1 | 990 | 19502842 | 785 | 2019-06-13 23:00 | 270 | 1108 | 241 | 998 | 274 | 1146 | 133 | 632 | 87.5 |  |  | 87.5 | 77% | 69% | 72% | 79% | 11.469 | Loss 10-20% |  | 858(111) | 893(270.5) | 827(53.5) | 760(26.5)
1270 | 1241 | MV3 | MVR-III | VSE142 | TG-VSE142A-1 | DT-1 | STN 3 GHAROLI DAIRY CL MVR PH-3:ID | 2 | 990 | 19504841 | 1052 | 2019-06-30 23:30 | 333 | 1416 | 334 | 1440 | 385 | 1680 | 253 | 463.5 | 194 | 55 | 7.5 | 256.5 | 104% | 66% | 89% | 106% | 4.8702 | Loss 0-5% |  | 958(116.5) | 1033(287) | 1020(207) | 1010(161)
1271 | 1241 | MV3 | MVR-III | VSE142 | TG-VSE142A-2 | DT-2 | STN 3 GHAROLI DAIRY CL MVR PH-3:ID | 2 | 630 | 19502831 | 522 | 2019-06-11 23:30 | 189 | 764 | 158 | 636 | 175 | 713 | 111 | 645 | 75 |  |  | 75 | 82% | 56% | 77% | 83% | 4.8702 | Loss 0-5%
1272 | 1241 | MV3 | MVR-III | VSE143 | TG-VSE143A-1 | DT-1 | STN 4 GHAROLI DAIRY CL MVR PH-3:ID | 2 | 990 | 19503159 | 1001 | 2019-06-02 23:00 | 425 | 1830 | 273 | 1147 | 303 | 1298 | 621 | 533.5 | 154 | 29.5 | 1 | 184.5 | 99% | 72% | 87% | 101% | 6.3496 | Loss 5-10% |  |  | 975(172.5) | 966(198) | 1000(142)
1273 | 1241 | MV3 | MVR-III | VSE143 | TG-VSE143A-2 | DT-2 | STN 4 GHAROLI DAIRY CL MVR PH-3:ID | 2 | 630 | 19502843 | 666 | 2019-06-30 23:00 | 231 | 1013 | 213 | 934 | 222 | 974 | 68 | 535 | 136.5 | 39.5 | 7.5 | 183.5 | 103% | 72% | 95% | 106% | 6.3496 | Loss 5-10%
1274 | 1241 | MV3 | MVR-III | VSE163 | TG-VSE163A-1 | DT-1 | S/S-2 C-BLK HARIZAN BASTI,MULLA CLY:PL | 1 | 630 | 19506207 | 719 | 2019-06-02 23:30 | 250 | 1121 | 232 | 1049 | 238 | 1067 | 65 | 292 | 344 | 80 | 4 | 428 | 101% | 91% | 106% | 114% | 7.6876 | Loss 5-10% |  |  |  |  | 612(302)
1275 | 1241 | MV3 | NEW ASHOK NAGAR | VSE103 | TG-VSE103A-1 | DT-1 | ABLK NEW ASHOK NAGAR:ID | 2 | 990 | 19500836 | 1020.3621 | 2019-06-30 23:30 | 341.4279 | 1514.7642 | 311.9477 | 1378.3478 | 366.9866 | 1631.4866 | 219.4457 | 390.5 | 267.5 | 59.5 | 2.5 | 329.5 | 99% | 78% | 84% | 103% | 5.0648 | Loss 5-10% |  | 936(103) | 1055(285.5) | 982(253.5) | 928(161)
1276 | 1241 | MV3 | NEW ASHOK NAGAR | VSE103 | TG-VSE103A-2 | DT-2 | ABLK NEW ASHOK NAGAR:ID | 2 | 630 | 19500873 | 506.9606 | 2019-06-02 22:30 | 154.4813 | 704.7824 | 191.0069 | 876.9429 | 161.4724 | 730.5454 | 160.8341 | 619.5 | 100.5 |  |  | 100.5 | 80% | 63% | 74% | 80% | 5.0648 | Loss 5-10% |  |  | 528(61) | 500(71)
1277 | 1241 | MV3 | NEW ASHOK NAGAR | VSE104 | TG-VSE104A-1 | DT-1 | ABLK (LOOP) NEW ASHOK NAGAR:ID | 2 | 990 | 19505992 | 1143 | 2019-06-26 22:30 | 361 | 1633 | 395 | 1757 | 387 | 1730 | 113 | 159 | 374 | 123 | 64 | 561 | 111% | 88% | 103% | 115% | 3.9427 | Loss 0-5% | 816(33) | 1106(321) | 1149(635) | 1124(598) | 1081(517.5) | 955(192)
1278 | 1241 | MV3 | NEW ASHOK NAGAR | VSE104 | TG-VSE104A-2 | DT-2 | ABLK (LOOP) NEW ASHOK NAGAR:ID | 2 | 990 | 19505532 | 650 | 2019-06-26 22:30 | 236 | 1077 | 209 | 945 | 204 | 932 | 139 | 720 |  |  |  | 0 | 64% | 54% | 53% | 66% | 3.9427 | Loss 0-5%
1279 | 1241 | MV3 | NEW ASHOK NAGAR | VSE105 | TG-VSE105A-1 | DT-1 | B BLK NEW ASHOK NAGAR:ID | 2 | 990 | 19506128 | 948 | 2019-06-09 23:30 | 289 | 1315 | 375 | 1707 | 284 | 1288 | 406 | 635.5 | 81 | 3.5 |  | 84.5 | 94% | 71% | 86% | 96% | 5.5377 | Loss 5-10% |  |  | 776(47) | 778(35)
1280 | 1241 | MV3 | NEW ASHOK NAGAR | VSE105 | TG-VSE105A-2 | DT-2 | B BLK NEW ASHOK NAGAR:ID | 2 | 990 | 19505427 | 765 | 2019-06-30 | 243 | 1078 | 264 | 1176 | 258 | 1167 | 94 | 689 | 31 |  |  | 31 | 77% | 58% | 68% | 77% | 5.5377 | Loss 5-10% |  |  | 751(28)
1281 | 1241 | MV3 | NEW ASHOK NAGAR | VSE106 | TG-VSE106A-1 | DT-1 | B1 BLK NEW ASHOK NAGAR:ID | 2 | 630 | 19500875 | 403.8376 | 2019-06-13 23:30 | 114.2968 | 493.9788 | 139.65 | 609.6122 | 149.8908 | 650.3985 | 140.5378 | 719.5 |  |  |  | 0 | 62% | 49% | 52% | 64% | 5.5782 | Loss 5-10% |  | 619(155.5) | 1113(634) | 1228(601.5) | 679(82)
1282 | 1241 | MV3 | NEW ASHOK NAGAR | VSE106 | TG-VSE106A-2 | DT-2 | B1 BLK NEW ASHOK NAGAR:ID | 2 | 990 | 19505221 | 900 | 2019-06-30 | 266 | 1222 | 310 | 1420 | 323 | 1479 | 233 | 535 | 184 | 0.5 |  | 184.5 | 91% | 80% | 75% | 89% | 5.5782 | Loss 5-10%
1283 | 1241 | MV3 | NEW ASHOK NAGAR | VSE107 | TG-VSE107A-1 | DT-1 | B2 BLK NEW ASHOK NAGAR:ID | 2 | 990 | 19500797 | 1222.6722 | 2019-06-30 | 383.9311 | 1699.8631 | 426.4464 | 1913.4313 | 412.2947 | 1871.175 | 195.8887 | 250 | 325.5 | 95.5 | 48.5 | 469.5 | 124% | 88% | 92% | 110% | 3.7303 | Loss 0-5% | 846(35) | 1275(315.5) | 1015(339.5) | 1073(282.5) | 1024(224) | 823(30)
1284 | 1241 | MV3 | NEW ASHOK NAGAR | VSE107 | TG-VSE107A-2 | DT-2 | B2 BLK NEW ASHOK NAGAR:ID | 2 | 990 | 19500303 | 1005 | 2019-06-30 01:30 | 336 | 1477 | 292 | 1291 | 377 | 1681 | 338 | 531.5 | 185 | 1 | 1 | 187 | 101% | 71% | 76% | 88% | 3.7303 | Loss 0-5% |  |  | 859(188.5) | 868(103.5) | 824(53)
1285 | 1241 | MV3 | NEW ASHOK NAGAR | VSE108 | TG-VSE108A-1 | DT-1 | C2 BLK NEW ASHOK NAGAR:ID | 2 | 990 | 19500837 | 846.8837 | 2019-06-01 | 338.9342 | 1475.102 | 261.9922 | 1142.5242 | 245.9573 | 1065.119 | 377.2835 | 715 | 5 |  |  | 5 | 86% | 67% | 60% | 69% | 4.6568 | Loss 0-5%
1286 | 1241 | MV3 | NEW ASHOK NAGAR | VSE108 | TG-VSE108A-2 | DT-2 | C2 BLK NEW ASHOK NAGAR:ID | 2 | 630 | 19506902 | 708 | 2019-06-29 23:30 | 234 | 1037 | 222 | 968 | 252 | 1101 | 115 | 376 | 227.5 | 81.5 | 34.5 | 343.5 | 112% | 82% | 84% | 112% | 4.6568 | Loss 0-5% |  | 562(59.5) | 518(112.5) | 552(116) | 488(39)
1287 | 1241 | MV3 | NEW ASHOK NAGAR | VSE109 | TG-VSE109A-1 | DT-1 | C3 BLK NEW ASHOK NAGAR:ID | 2 | 630 | 19506026 | 916 | 2019-06-13 23:00 | 307 | 1330 | 329 | 1439 | 280 | 1206 | 202 | 417.5 | 159 | 37.5 | 98 | 294.5 | 141% | 139% | 131% | 145% | 3.8299 | Loss 0-5% |  |  | 541(139.5) | 556(105.5) | 521(46)
1288 | 1241 | MV3 | NEW ASHOK NAGAR | VSE109 | TG-VSE109A-2 | DT-2 | C3 BLK NEW ASHOK NAGAR:ID | 2 | 990 | 19506757 | 842 | 2019-06-29 23:30 | 284 | 1244 | 233 | 1017 | 325 | 1444 | 370 | 687 | 31.5 |  |  | 31.5 | 82% | 59% | 63% | 85% | 3.8299 | Loss 0-5%
1289 | 1241 | MV3 | NEW ASHOK NAGAR | VSE110 | TG-VSE110A-1 | DT-1 | C4 BLK NEW ASHOK NAGAR:ID | 2 | 630 | 19505530 | 728 | 2019-06-12 | 233 | 1013 | 259 | 1141 | 237 | 1032 | 119 | 437 | 220 | 36 | 27 | 283 | 116% | 85% | 91% | 115% | 4.6547 | Loss 0-5% |  | 518(44.5) | 561(79)
1290 | 1241 | MV3 | NEW ASHOK NAGAR | VSE110 | TG-VSE110A-2 | DT-2 | C4 BLK NEW ASHOK NAGAR:ID | 2 | 990 | 19505232 | 662 | 2019-06-11 01:00 | 161 | 730 | 183 | 820 | 319 | 1453 | 682 | 720 |  |  |  | 0 | 67% | 52% | 54% | 65% | 4.6547 | Loss 0-5%
1291 | 1241 | MV3 | NEW ASHOK NAGAR | VSE111 | TG-VSE111A-1 | DT-1 | C5 BLK NEW ASHOK NAGAR:ID | 2 | 990 | 19500846 | 927.2653 | 2019-06-26 23:00 | 285.326 | 1230.7024 | 284.4857 | 1215.0237 | 357.4536 | 1543.3427 | 320.7672 | 650.5 | 63.5 | 2 |  | 65.5 | 87% | 73% | 75% | 94% | 5.6564 | Loss 5-10% | 531(35.5)
1292 | 1241 | MV3 | NEW ASHOK NAGAR | VSE111 | TG-VSE111A-2 | DT-2 | C5 BLK NEW ASHOK NAGAR:ID | 2 | 630 | 19500850 | 688.7085 | 2019-06-13 23:30 | 219.9498 | 920.4074 | 231.2776 | 977.2153 | 237.4812 | 1000.5107 | 71.3665 | 352.5 | 253.5 | 77 | 36.5 | 367 | 108% | 89% | 88% | 109% | 5.6564 | Loss 5-10% |  | 642(259.5) | 650(531) | 616(46) | 635(480) | 553(34)
1293 | 1241 | MV3 | NEW ASHOK NAGAR | VSE112 | TG-VSE112A-1 | DT-1 | D BLK NEW ASHOK NAGAR:ID | 2 | 990 | 19506911 | 629 | 2019-06-30 23:30 | 200 | 881 | 239 | 1060 | 190 | 846 | 199 | 720 |  |  |  | 0 | 62% | 50% | 55% | 64% | 6.5989 | Loss 5-10%
1294 | 1241 | MV3 | NEW ASHOK NAGAR | VSE112 | TG-VSE112A-2 | DT-2 | D BLK NEW ASHOK NAGAR:ID | 2 | 990 | 19505544 | 937 | 2019-06-30 23:00 | 283 | 1312 | 353 | 1651 | 301 | 1418 | 301 | 508.5 | 207 | 4.5 |  | 211.5 | 89% | 74% | 78% | 95% | 6.5989 | Loss 5-10% |  |  |  |  | 819(38.5)
1295 | 1241 | MV3 | NEW ASHOK NAGAR | VSE113 | TG-VSE113A-1 | DT-1 | E1 BLK NEW ASHOK NAGAR:ID | 2 | 990 | 19505322 | 774 | 2019-06-02 23:30 | 269 | 1142 | 290 | 1214 | 215 | 901 | 284 | 677 | 41.5 |  |  | 41.5 | 77% | 66% | 66% | 78% | 4.4917 | Loss 0-5% |  | 1028(313) | 1048(398)
1296 | 1241 | MV3 | NEW ASHOK NAGAR | VSE113 | TG-VSE113A-2 | DT-2 | E1 BLK NEW ASHOK NAGAR:ID | 2 | 630 | 19506488 | 365 | 2019-06-28 23:30 | 117 | 482 | 115 | 472 | 134 | 554 | 78 | 720 |  |  |  | 0 | 57% | 52% | 50% | 58% | 4.4917 | Loss 0-5%
1297 | 1241 | MV3 | NEW ASHOK NAGAR | VSE114 | TG-VSE114A-1 | DT-1 | E2 BLK NEW ASHOK NAGAR:ID | 2 | 630 | 19505994 | 1034.8665 | 2019-06-27 21:30 | 327.6259 | 1390.3664 | 380.7403 | 1656.5451 | 326.5002 | 1425.5784 | 250.4362 | 375 | 288 | 41.5 | 14.5 | 344 | 118% | 88% | 116% | 164% | 7.4756 | Loss 5-10% |  | 597(160.5) | 681(529) | 711(565) | 754(525.5) | 606(155)
1298 | 1241 | MV3 | NEW ASHOK NAGAR | VSE114 | TG-VSE114A-2 | DT-2 | E2 BLK NEW ASHOK NAGAR:ID | 2 | 400 | 19505522 | 513 | 2019-06-30 23:00 | 170 | 769 | 181 | 822 | 162 | 733 | 78 | 251 | 307.5 | 66.5 | 94.5 | 468.5 | 124% | 100% | 104% | 128% | 7.4756 | Loss 5-10%
1299 | 1241 | MV3 | VASUNDHARA ENCLAVE | VSE031 | TG-VSE031A-1 | DT-1 | S/STN 9 MIXED HOUSING MVR III:ID | 2 | 990 | 19502440 | 728 | 2019-06-30 23:30 | 290 | 1263 | 236 | 1015 | 202 | 857 | 354 | 713 | 7 |  |  | 7 | 72% | 50% | 57% | 74% | 3.926 | Loss 0-5%
1300 | 1241 | MV3 | VASUNDHARA ENCLAVE | VSE031 | TG-VSE031A-2 | DT-2 | S/STN 9 MIXED HOUSING MVR III:ID | 2 | 630 | 19506129 | 629 | 2019-06-30 03:00 | 260 | 1119 | 179 | 750 | 190 | 801 | 347 | 628 | 90.5 | 1.5 |  | 92 | 100% | 57% | 66% | 92% | 3.926 | Loss 0-5% |  | 517(33) | 535(88) | 565(36)
1301 | 1241 | MV3 | VASUNDHARA ENCLAVE | VSE035 | TG-VSE035A-1 | DT-1 | S/STN D-BLK NEW KNODLI:ID | 2 | 400 | 19505444 | 187 | 2019-06-02 18:30 | 77 | 314 | 56 | 230 | 54 | 224 | 87 | 719.5 |  |  |  | 0 | 38% | 36% | 47% | 40% | 5.4137 | Loss 5-10% |  |  |  |  | 306(28)
1302 | 1241 | MV3 | VASUNDHARA ENCLAVE | VSE035 | TG-VSE035A-2 | DT-2 | S/STN D-BLK NEW KNODLI:ID | 2 | 400 | 19505985 | 377 | 2019-06-13 22:30 | 111 | 442 | 142 | 564 | 124 | 491 | 107 | 356.5 | 361 | 2 |  | 363 | 91% | 68% | 89% | 94% | 5.4137 | Loss 5-10%
1303 | 1241 | MV3 | VASUNDHARA ENCLAVE | VSE048 | TG-VSE048A-1 | DT-1 | DALLUPURA VILL. DURGA PARK:ID | 2 | 990 | 19505213 | 800 | 2019-06-14 00:30 | 227 | 953 | 211 | 895 | 363 | 1558 | 636 | 679 | 40 |  |  | 40 | 81% | 67% | 73% | 76% | 30.429 | Loss >30% |  | 1025(98.5) | 949(228) | 1038(251.5) | 1005(63.5)
1304 | 1241 | MV3 | VASUNDHARA ENCLAVE | VSE048 | TG-VSE048A-2 | DT-2 | DALLUPURA VILL. DURGA PARK:ID | 2 | 630 | 19505346 | 856 | 2019-06-30 12:30 | 248 | 1012 | 296 | 1222 | 312 | 1287 | 249 | 519 | 198.5 |  | 1.5 | 200 | 81% | 75% | 136% | 102% | 30.429 | Loss >30% |  | 701(237) | 586(82) | 675(62.5)
1305 | 1241 | MV3 | VASUNDHARA ENCLAVE | VSE172 | TG-VSE172A-1 | DT-1 | DALLUPURA HARIZAN BASTI SUB STN. | 3 | 630 | 19500842 | 618.4301 | 2019-06-30 22:30 | 236.7289 | 1032.3531 | 198.3688 | 869.4286 | 183.3324 | 789.2052 | 214.5939 | 377.5 | 325 | 17 |  | 342 | 90% | 86% | 92% | 98% | 38.9217 | Loss >30% |  |  | 500(38.5) | 489(59.5) |  | 571(57)
1306 | 1241 | MV3 | VASUNDHARA ENCLAVE | VSE172 | TG-VSE172A-2 | DT-2 | DALLUPURA HARIZAN BASTI SUB STN. | 3 | 630 | 19505698 | 570 | 2019-06-21 23:00 | 164 | 670 | 164 | 663 | 242 | 997 | 331 | 570.5 | 148.5 | 0.5 |  | 149 | 84% | 71% | 87% | 91% | 38.9217 | Loss >30% |  | 608(227.5) | 653(453) | 581(167)
1307 | 1241 | MV3 | VASUNDHARA ENCLAVE | VSE172 | TG-VSE172A-3 | DT-3 | DALLUPURA HARIZAN BASTI SUB STN. | 3 | 630 | 19505589 | 444 | 2019-06-13 11:00 | 124 | 541 | 154 | 680 | 165 | 723 | 165 | 719.5 | 0.5 |  |  | 0.5 | 64% | 58% | 70% | 65% | 38.9217 | Loss >30% |  | 562(88) | 598(248) | 742(376) | 833(345) | 582(95)
1308 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM001 | TG-YAM001A-1 | DT-1 | C-4 YAMUNA VIHAR:PL | 1 | 990 | 19506333 | 1005 | 2019-06-11 23:30 | 316 | 1339 | 264 | 1112 | 425 | 1825 | 632 | 635 | 80 | 3 | 0.5 | 83.5 | 86% | 62% | 63% | 101% | 5.6558 | Loss 5-10% |  | 949(69) | 1031(172) | 814(36)
1309 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM003 | TG-YAM003A-1 | DT-1 | C-6, YAMUNA VIHAR:PG | 2 | 990 | 19503253 | 1093 | 2019-06-12 | 341 | 1454 | 360 | 1518 | 393 | 1663 | 186 | 565.5 | 91.5 | 40.5 | 21.5 | 153.5 | 110% | 58% | 74% | 109% | 6.5689 | Loss 5-10% |  | 1057(96) | 1125(186) | 1016(122) | 891(89)
1310 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM003 | TG-YAM003A-2 | DT-2 | C-6, YAMUNA VIHAR:PG | 2 | 990 | 19503252 | 967 | 2019-06-29 23:30 | 396 | 1691 | 314 | 1325 | 257 | 1088 | 526 | 687.5 | 28 | 4.5 |  | 32.5 | 97% | 58% | 64% | 98% | 6.5689 | Loss 5-10%
1311 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM005 | TG-YAM005A-1 | DT-1 | C-7, YAMUNA VIHAR:ID | 2 | 630 | 19500622 | 385 | 2019-06-11 23:30 | 143 | 588 | 140 | 581 | 102 | 534 | 51 | 720 |  |  |  | 0 | 61% | 49% | 53% | 61% | 6.986 | Loss 5-10%
1312 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM005 | TG-YAM005A-2 | DT-2 | C-7, YAMUNA VIHAR:ID | 2 | 990 | 19506506 | 1024.4402 | 2019-06-12 | 382.7983 | 1627.2672 | 301.5334 | 1259.7486 | 340.1085 | 1429.748 | 318.5777 | 580.5 | 127 | 10.5 | 1.5 | 139 | 103% | 88% | 94% | 103% | 6.986 | Loss 5-10%
1313 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM006 | TG-YAM006A-1 | DT-1 | C-7/2, YAMUNA VIHAR:ID | 2 | 400 | 19500646 | 102.2563 | 2019-06-13 16:00 | 20.9633 | 86.6395 | 52.5082 | 219.3051 | 28.7848 | 118.4025 | 119.98 | 718 |  |  |  | 0 | 17% | 18% | 26% | 18% | 6.986 | Loss 5-10% |  | 388(92) | 459(256) | 443(181) | 382(73)
1314 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM006 | TG-YAM006A-2 | DT-2 | C-7/2, YAMUNA VIHAR:ID | 2 | 630 | 19502948 | 552 | 2019-06-12 00:30 | 213 | 908 | 156 | 672 | 183 | 750 | 208 | 628 | 90 |  |  | 90 | 88% | 53% | 70% | 87% | 6.986 | Loss 5-10% |  | 628(55.5) | 706(162) | 589(100.5)
1315 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM007 | TG-YAM007A-1 | DT-1 | C-8 YAMUNA VIHAR:ID | 3 | 990 | 19503237 | 960 | 2019-06-30 23:30 | 313 | 1287 | 336 | 1392 | 311 | 1285 | 106 | 663 | 51.5 | 5 |  | 56.5 | 94% | 56% | 67% | 97% | 10.0918 | Loss 10-20% |  | 1501(165.5) | 910(79.5) | 870(49)
1316 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM007 | TG-YAM007A-2 | DT-2 | C-8 YAMUNA VIHAR:ID | 3 | 990 | 19503239 | 745 | 2019-06-30 23:00 | 205 | 835 | 267 | 1096 | 273 | 1126 | 278 | 699 | 20.5 |  |  | 20.5 | 75% | 47% | 61% | 75% | 10.0918 | Loss 10-20% |  | 895(46.5) | 884(88) | 810(30)
1317 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM007 | TG-YAM007A-3 | DT-3 | C-8 YAMUNA VIHAR:ID | 3 | 630 | 19506256 | 441 | 2019-06-07 00:30 | 122 | 519 | 169 | 720 | 150 | 626 | 174 | 719.5 |  |  |  | 0 | 70% | 34% | 38% | 59% | 10.0918 | Loss 10-20% |  |  | 625(49) | 575(58.5)
1318 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM008 | TG-YAM008A-1 | DT-1 | C-11 YAMUNA VIHAR:ID | 2 | 630 | 19500554 | 525 | 2019-06-30 00:30 | 180 | 704 | 209 | 830 | 135 | 529 | 262 | 694.5 | 25 |  |  | 25 | 83% | 56% | 58% | 80% | 9.1291 | Loss 5-10%
1319 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM008 | TG-YAM008A-2 | DT-2 | C-11 YAMUNA VIHAR:ID | 2 | 990 | 19500543 | 772 | 2019-06-03 | 340 | 1482 | 259 | 1116 | 173 | 740 | 642 | 709 | 10.5 |  |  | 10.5 | 78% | 55% | 61% | 74% | 9.1291 | Loss 5-10% |  |  | 796(31.5)
1320 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM009 | TG-YAM009A-1 | DT-1 | C-12, YAMUNA VIHAR:ID | 2 | 990 | 19501815 | 488 | 2019-06-09 00:30 | 183 | 775 | 149 | 638 | 156 | 667 | 125 | 719 |  |  |  | 0 | 49% | 34% | 38% | 49% | 7.1641 | Loss 5-10%
1321 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM009 | TG-YAM009A-2 | DT-2 | C-12, YAMUNA VIHAR:ID | 2 | 400 | 19505309 | 368 | 2019-06-12 | 167 | 749 | 104 | 453 | 97 | 428 | 309 | 613.5 | 104.5 | 1 |  | 105.5 | 92% | 84% | 78% | 92% | 7.1641 | Loss 5-10% |  | 322(36.5) | 420(127.5) | 347(65.5)
1322 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM011 | TG-YAM011A-1 | DT-1 | B-2 YAMUNA VIHAR:PL | 1 | 990 | 19503247 | 918 | 2019-06-29 23:00 | 370 | 1608 | 304 | 1309 | 244 | 1055 | 479 | 573 | 139 | 8 |  | 147 | 92% | 57% | 73% | 93% | 3.668 | Loss 0-5% |  | 842(34.5) | 949(114.5) | 899(59.5)
1323 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM012 | TG-YAM012A-1 | DT-1 | B-4 YAMUNA VIHAR:ID | 2 | 990 | 19506327 | 593 | 2019-06-30 23:30 | 197 | 835 | 205 | 866 | 191 | 811 | 48 | 719 |  |  |  | 0 | 58% | 37% | 46% | 60% | 7.6872 | Loss 5-10%
1324 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM012 | TG-YAM012A-2 | DT-2 | B-4 YAMUNA VIHAR:ID | 2 | 990 | 19503453 | 1044 | 2019-06-10 01:30 | 348 | 1376 | 386 | 1548 | 310 | 1235 | 272 | 523.5 | 160 | 31 | 2 | 193 | 105% | 61% | 76% | 99% | 7.6872 | Loss 5-10% |  | 957(36.5) |  | 968(46.5) | 889(95)
1325 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM015 | TG-YAM015A-1 | DT-1 | PUMPING STATION BHAJAN PURA :ID | 1 | 990 | 19504082 | 1166 | 2019-06-01 22:30 | 412 | 1677 | 386 | 1565 | 368 | 1501 | 155 | 282.5 | 294 | 105.5 | 36.5 | 436 | 113% | 73% | 106% | 118% | 6.4079 | Loss 5-10% |  | 1209(310.5) | 1280(303) | 848(114.5) | 809(31.5)
1326 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM017 | TG-YAM017A-1 | DT-1 | C-BLOCK GALI NO7 BHAJAN PURA:PL | 1 | 1600 | 19502144 | 1608 | 2019-06-01 00:30 | 495 | 2096 | 452 | 1919 | 661 | 2819 | 826 | 609.5 | 99 | 6 | 0.5 | 105.5 | 100% | 69% | 67% | 91% | 15.1465 | Loss 10-20% |  |  |  | 1179(168) | 1173(317.5) | 993(76)
1327 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM018 | TG-YAM018A-1 | DT-1 | K-BLOCK GHONDA:ID | 3 | 990 | 19503720 | 358.9012 | 2019-06-05 23:30 | 158.5136 | 619.7749 | 114.8278 | 444.9655 | 85.5598 | 328.9117 | 253.6022 | 166.5 |  |  |  | 0 | 36% | 27% | 28% | 36% | 7.067 | Loss 5-10% |  | 868(96.5) | 1210(263) | 1194(260) | 1171(139)
1328 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM018 | TG-YAM018A-2 | DT-2 | K-BLOCK GHONDA:ID | 3 | 630 | 19506573 | 607 | 2019-06-16 03:00 | 233 | 937 | 213 | 856 | 161 | 647 | 259 | 684 | 24 | 3.5 |  | 27.5 | 96% | 77% | 70% | 94% | 7.067 | Loss 5-10% |  |  |  |  | 666(202) | 593(146.5)
1329 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM018 | TG-YAM018A-3 | DT-3 | K-BLOCK GHONDA:ID | 3 | 630 | 19506826 | 1148.6508 | 2019-06-10 00:30 | 422.1685 | 1785.5963 | 415.9515 | 1762.1332 | 310.5307 | 1283.8744 | 490.4115 | 344.5 | 93 | 28 | 221.5 | 342.5 | 182% | 175% | 130% | 177% | 7.067 | Loss 5-10%
1330 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM019 | TG-YAM019A-1 | DT-1 | DISPENSERY BHAJAN PURA:PL | 2 | 990 | 19502203 | 1465 | 2019-06-01 01:00 | 446 | 1860 | 480 | 2000 | 538 | 2239 | 332 | 188 | 265.5 | 77.5 | 174 | 517 | 148% | 114% | 116% | 139% | 7.0042 | Loss 5-10% |  |  | 1381(471) | 1346(398) | 1150(228.5) | 977(94)
1331 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM019 | TG-YAM019A-2 | DT-2 | DISPENSERY BHAJAN PURA:PL | 2 | 990 | 19506331 | 1158 | 2019-06-01 01:00 | 372 | 1426 | 388 | 1499 | 398 | 1528 | 91 | 436.5 | 171.5 | 54.5 | 42.5 | 268.5 | 117% | 103% | 95% | 115% | 7.0042 | Loss 5-10% | 679(49.5) |  |  |  | 803(28)
1332 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM020 | TG-YAM020A-1 | DT-1 | D-BLOCK, SANJAY MOHALLA:K | 2 | 990 | 19505851 | 908 | 2019-06-30 00:30 | 289 | 1147 | 304 | 1199 | 314 | 1251 | 90 | 559.5 | 156.5 | 1.5 |  | 158 | 92% | 72% | 80% | 90% | 6.2749 | Loss 5-10%
1333 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM020 | TG-YAM020A-2 | DT-2 | D-BLOCK, SANJAY MOHALLA:K | 2 | 630 | 19506598 | 761 | 2019-06-01 01:00 | 222 | 897 | 328 | 1354 | 212 | 862 | 475 | 706 | 4 | 2 | 2.5 | 8.5 | 121% | 91% | 85% | 60% | 6.2749 | Loss 5-10% | [5 empty] | 543(34)
1334 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM021 | TG-YAM021A-1 | DT-1 | NOOR-E-ILLAHI:K | 3 | 990 | 19505649 | 708 | 2019-06-02 21:00 | 234 | 958 | 225 | 929 | 249 | 1031 | 91 | 718 | 0.5 |  |  | 0.5 | 70% | 61% | 66% | 71% | 13.0353 | Loss 10-20%
1335 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM021 | TG-YAM021A-2 | DT-2 | NOOR-E-ILLAHI:K | 3 | 990 | 19500192 | 1344 | 2019-06-11 01:30 | 450 | 1882 | 428 | 1773 | 466 | 1943 | 149 | 22.5 | 249.5 | 187 | 259 | 695.5 | 136% | 118% | 127% | 130% | 13.0353 | Loss 10-20% | 852(148) | 1104(559.5) | 1016(485.5) | 923(381.5) | 845(221.5)
1336 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM021 | TG-YAM021A-3 | DT-3 | NOOR-E-ILLAHI:K | 3 | 990 | 19502220 | 890 | 2019-06-11 02:00 | 323 | 1360 | 250 | 1033 | 317 | 1327 | 312 | 579.5 | 137 |  |  | 137 | 90% | 74% | 84% | 84% | 13.0353 | Loss 10-20% |  | 985(189.5) | 1059(606.5) | 1099(537) | 912(391) | 806(69.5)
1337 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM025 | TG-YAM025A-1 | DT-1 | GHONDA CHOWK:K | 4 | 630 | 19505509 | 535 | 2019-06-29 12:00 | 173 | 703 | 184 | 753 | 178 | 731 | 43 | 686.5 | 31.5 |  |  | 31.5 | 56% | 50% | 85% | 59% | 8.7219 | Loss 5-10% | 571(164.5) | 605(210.5) | 586(161) | 612(224) | 642(109.5) | 522(28)
1338 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM025 | TG-YAM025A-2 | DT-2 | GHONDA CHOWK:K | 4 | 990 | 19504714 | 865 | 2019-06-29 16:00 | 294 | 1222 | 315 | 1294 | 257 | 1060 | 208 | 566.5 | 151.5 |  |  | 151.5 | 85% | 67% | 87% | 86% | 8.7219 | Loss 5-10% |  | 957(225.5) | 930(262.5) | 911(208) | 859(130)
1339 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM025 | TG-YAM025A-3 | DT-3 | GHONDA CHOWK:K | 4 | 990 | 19503250 | 983 | 2019-06-01 23:30 | 353 | 1488 | 348 | 1501 | 282 | 1187 | 308 | 364 | 331.5 | 23 |  | 354.5 | 96% | 90% | 99% | 99% | 8.7219 | Loss 5-10% |  | 934(238.5) | 966(437) | 988(386) | 893(275.5) | 810(122.5)
1340 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM025 | TG-YAM025A-4 | DT-4 | GHONDA CHOWK:K | 4 | 630 | 19505878 | 383 | 2019-06-30 14:30 | 83 | 351 | 113 | 467 | 187 | 830 | 433 | 718.5 |  |  |  | 0 | 57% | 53% | 61% | 58% | 8.7219 | Loss 5-10%
1341 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM027 | TG-YAM027A-1 | DT-1 | CHET RAM MAUJ PUR:PL | 3 | 990 | 19502189 | 1340 | 2019-06-30 03:00 | 495 | 2107 | 382 | 1612 | 463 | 1956 | 439 | 174.5 | 297.5 | 100.5 | 137 | 535 | 135% | 119% | 118% | 133% | 13.3986 | Loss 10-20% | 906(45) |  |  |  | 1193(436) | 937(72.5)
1342 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM027 | TG-YAM027A-2 | DT-2 | CHET RAM MAUJ PUR:PL | 3 | 990 | 19502235 | 1332 | 2019-06-30 03:30 | 391 | 1649 | 491 | 2100 | 451 | 1907 | 392 | 168.5 | 324.5 | 101 | 115 | 540.5 | 135% | 112% | 116% | 129% | 13.3986 | Loss 10-20% | 873(29.5) | 1108(355.5) | 1251(537.5) | 1034(39)
1343 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM027 | TG-YAM027A-3 | DT-3 | CHET RAM MAUJ PUR:PL | 3 | 630 | 19505259 | 672 | 2019-06-11 01:00 | 221 | 988 | 219 | 957 | 232 | 1022 | 57 | 515 | 168.5 | 23 | 2.5 | 194 | 107% | 88% | 81% | 101% | 13.3986 | Loss 10-20%
1344 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM028 | TG-YAM028A-1 | DT-1 | SUBJI MANDI-1 MAUJ PUR | 1 | 1600 | 19506745 | 1717 | 2019-06-30 01:30 | 582 | 2515 | 607 | 2592 | 528 | 2265 | 296 | 528.5 | 149 | 31.5 | 5 | 185.5 | 107% | 72% | 88% | 102% | 18.449 | Loss 10-20% | 795(31.5) | 1083(396.5) | 1349(612) |  | 1309(666.5) | 1006(392.5)
1345 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM030 | TG-YAM030A-1 | DT-1 | BABU RAM CHOWK MAUJ PUR:PL | 2 | 990 | 19502197 | 750 | 2019-06-02 16:30 | 252 | 1051 | 243 | 998 | 255 | 1063 | 60 | 713 | 3.5 |  |  | 3.5 | 67% | 56% | 76% | 67% | 14.7313 | Loss 10-20% |  | 833(57.5) | 892(165) | 925(248) | 919(177.5)
1346 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM030 | TG-YAM030A-2 | DT-2 | BABU RAM CHOWK MAUJ PUR:PL | 2 | 990 | 19503728 | 761 | 2019-06-29 23:30 | 261 | 1091 | 239 | 1005 | 260 | 1099 | 91 | 679.5 | 37 |  |  | 37 | 75% | 57% | 76% | 77% | 14.7313 | Loss 10-20% |  | 752(24.5) | 804(62) | 796(45) | 791(55.5)
1347 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM031 | TG-YAM031A-1 | DT-1 | SANDHYA PUBLIC SCHOOL:PL | 2 | 990 | 19504743 | 1043 | 2019-06-29 17:30 | 366 | 1657 | 347 | 1573 | 330 | 1497 | 139 | 344 | 333 | 32 | 8 | 373 | 91% | 77% | 105% | 96% | 15.8772 | Loss 10-20% |  |  |  | 995(157.5) | 866(214.5) | 768(55)
1348 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM031 | TG-YAM031A-2 | DT-2 | SANDHYA PUBLIC SCHOOL:PL | 2 | 400 | 19505485 | 375 | 2019-06-03 15:00 | 79 | 326 | 128 | 536 | 167 | 701 | 326 | 584.5 | 132.5 | 1 |  | 133.5 | 90% | 79% | 94% | 92% | 15.8772 | Loss 10-20% | 489(545) | 654(738.5) | 717(669.5) | 746(547) | 361(234.5)
1349 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM033 | TG-YAM033A-1 | DT-1 | SUBHASH MOHALLA NO-1:PL | 1 | 990 | 19506704 | 1213 | 2019-06-05 23:30 | 441 | 1818 | 405 | 1653 | 367 | 1495 | 280 | 261 | 304.5 | 72 | 81.5 | 458 | 120% | 86% | 99% | 123% | 9.9227 | Loss 5-10% |  |  | 986(91.5) | 1001(143.5)
1350 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM034 | TG-YAM034A-1 | DT-1 | SUBHASH MOHALLA NO.-2:PL | 3 | 990 | 19500611 | 935.594 | 2019-06-01 23:00 | 311.6341 | 1272.2355 | 299.8014 | 1215.9371 | 324.1585 | 1308.621 | 80.8817 | 493 | 218 | 7 |  | 225 | 94% | 83% | 81% | 95% | 8.7048 | Loss 5-10% |  | 786(41.5) | 813(113.5) | 818(103.5)
1351 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM034 | TG-YAM034A-2 | DT-2 | SUBHASH MOHALLA NO.-2:PL | 3 | 990 | 19502153 | 1036 | 2019-06-11 00:30 | 355 | 1397 | 306 | 1195 | 375 | 1484 | 257 | 382.5 | 279 | 52.5 | 4.5 | 336 | 105% | 86% | 83% | 104% | 8.7048 | Loss 5-10% |  |  | 784(75) | 769(46)
1352 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM034 | TG-YAM034A-3 | DT-3 | SUBHASH MOHALLA NO.-2:PL | 3 | 400 | 19506006 | 371 | 2019-06-28 04:00 | 160 | 652 | 160 | 669 | 51 | 207 | 454 | 718 |  | 0.5 |  | 0.5 | 93% | 51% | 62% | 62% | 8.7048 | Loss 5-10%
1353 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM036 | TG-YAM036A-1 | DT-1 | VIJAY PARK KIOSK:K | 2 | 630 | 19505577 | 670 | 2019-06-27 00:30 | 132 | 555 | 201 | 868 | 337 | 1426 | 764 | 450.5 | 217 | 42.5 | 5.5 | 265 | 106% | 92% | 98% | 100% | 11.7499 | Loss 10-20% |  | 577(151) | 746(350) | 673(222.5) | 577(136.5)
1354 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM036 | TG-YAM036A-2 | DT-2 | VIJAY PARK KIOSK:K | 2 | 990 | 19505778 | 1279 | 2019-06-30 00:30 | 498 | 2000 | 450 | 1787 | 331 | 1301 | 620 | 100 | 254 | 59.5 | 28 | 341.5 | 129% | 87% | 101% | 114% | 11.7499 | Loss 10-20% |  | 987(292.5) | 1205(507) | 1032(437) | 942(334) | 765(58)
1355 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM038 | TG-YAM038A-1 | DT-1 | VIJAY PARK SHIV SADHAN MANDIR:PL | 1 | 990 | 19505446 | 1068 | 2019-06-12 | 456 | 1773 | 255 | 1014 | 356 | 1409 | 657 | 370.5 | 274 | 61 | 13.5 | 348.5 | 108% | 88% | 96% | 105% | 5.102 | Loss 5-10% |  |  | 962(137) | 1034(175) | 885(121.5)
1356 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM039 | TG-YAM039A-1 | DT-1 | VIJAY PARK NEAR NURSARY:PL | 2 | 630 | 19505323 | 806 | 2019-06-29 01:30 | 278 | 1180 | 276 | 1165 | 253 | 1058 | 115 | 345.5 | 220 | 69.5 | 80.5 | 370 | 128% | 85% | 95% | 118% | 15.164 | Loss 10-20% |  | 687(153.5) | 890(293.5) | 701(247.5) | 653(212) | 517(29)
1357 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM039 | TG-YAM039A-2 | DT-2 | VIJAY PARK NEAR NURSARY:PL | 2 | 400 | 19505873 | 459 | 2019-06-01 01:00 | 141 | 568 | 171 | 701 | 147 | 597 | 121 | 624.5 | 69.5 | 9 | 12.5 | 91 | 115% | 82% | 89% | 111% | 15.164 | Loss 10-20% | 389(51) | 430(161.5) | 456(286.5) | 438(367.5) | 399(292.5) | 358(44)
1358 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM041 | TG-YAM041A-1 | DT-1 | NALA NO.4 MAUJPUR:PL | 2 | 990 | 19503438 | 1171 | 2019-06-12 | 376 | 1502 | 423 | 1668 | 373 | 1481 | 177 | 376 | 248.5 | 60.5 | 33.5 | 342.5 | 118% | 68% | 93% | 115% | 16.8893 | Loss 10-20% |  | 926(96.5) | 1398(406) |  | 793(50.5) | 799(26.5)
1359 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM041 | TG-YAM041A-2 | DT-2 | NALA NO.4 MAUJPUR:PL | 2 | 630 | 19505866 | 719 | 2019-06-12 | 304 | 1228 | 192 | 748 | 223 | 890 | 426 | 531 | 144 | 38 | 4.5 | 186.5 | 114% | 64% | 89% | 102% | 16.8893 | Loss 10-20% |  |  |  |  | 551(36.5)
1360 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM042 | TG-YAM042A-1 | DT-1 | SETH BHAGWAN DAS MAUJ PUR:PL | 1 | 990 | 19506033 | 937 | 2019-06-12 00:30 | 255 | 1028 | 396 | 1625 | 286 | 1148 | 546 | 569.5 | 146 | 3.5 |  | 149.5 | 95% | 67% | 80% | 92% | 8.6529 | Loss 5-10% |  | 906(59.5) | 1127(159.5) | 1032(100.5)
1361 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM043 | TG-YAM043A-1 | DT-1 | CRESENT PUBLIC SCHOOL MAUJ PUR:PL | 2 | 990 | 19503717 | 1026 | 2019-06-30 03:30 | 336 | 1358 | 390 | 1578 | 300 | 1200 | 329 | 598.5 | 106.5 | 10.5 | 0.5 | 117.5 | 104% | 86% | 83% | 95% | 15.0808 | Loss 10-20% |  | 901(47)
1362 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM043 | TG-YAM043A-2 | DT-2 | CRESENT PUBLIC SCHOOL MAUJ PUR:PL | 2 | 630 | 19506512 | 704 | 2019-06-03 | 251 | 1142 | 223 | 994 | 229 | 1041 | 132 | 393 | 241.5 | 68.5 | 13 | 323 | 112% | 96% | 93% | 109% | 15.0808 | Loss 10-20%
1363 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM044 | TG-YAM044A-1 | DT-1 | ZAMALO KA BAGH MAUJ PUR:PL | 2 | 990 | 19505148 | 289 | 2019-06-28 12:00 | 61 | 241 | 144 | 574 | 84 | 337 | 296 | 719.5 |  |  |  | 0 | 16% | 15% | 29% | 16% | 9.7778 | Loss 5-10%
1364 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM044 | TG-YAM044A-2 | DT-2 | ZAMALO KA BAGH MAUJ PUR:PL | 2 | 990 | 19505170 | 988 | 2019-06-02 02:00 | 322 | 1365 | 401 | 1699 | 265 | 1097 | 522 | 459 | 230 | 30 |  | 260 | 100% | 86% | 90% | 96% | 9.7778 | Loss 5-10% |  |  | 1067(380.5) | 913(326) | 858(202.5)
1365 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM045 | TG-YAM045A-1 | DT-1 | VIJAY MOHALLA GALI NO 11:PL | 1 | 990 | 19503437 | 1061 | 2019-06-03 03:00 | 356 | 1487 | 347 | 1456 | 358 | 1519 | 55 | 316.5 | 336.5 | 47.5 | 18 | 402 | 107% | 96% | 88% | 93% | 8.6791 | Loss 5-10% | 913(118.5) | 1233(635) | 1357(524) | 1045(542) | 975(378.5) | 870(60)
1366 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM048 | TG-YAM048A-1 | DT-1 | C- 9 YAMUNA VIHAR:PG | 1 | 990 | 19504378 | 1178 | 2019-06-11 03:30 | 351 | 1375 | 509 | 2016 | 318 | 1263 | 704 | 455.5 | 152 | 62.5 | 49 | 263.5 | 119% | 86% | 81% | 115% | 6.4358 | Loss 5-10% | 854(28.5) | 1086(162.5) | 962(148) | 959(86) | 819(63.5)
1367 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM053 | TG-YAM053A-1 | DT-1 | MOHANPURI NO-2 OUTSIDE SCHOOL | 2 | 630 | 19504374 | 773 | 2019-06-11 | 254 | 1115 | 289 | 1276 | 231 | 1020 | 225 | 246 | 358 | 64.5 | 51 | 473.5 | 123% | 83% | 97% | 114% | 9.2308 | Loss 5-10% |  | 622(299.5) | 661(294.5) | 632(163) | 611(262) | 513(37.5)
1368 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM053 | TG-YAM053A-2 | DT-2 | MOHANPURI NO-2 OUTSIDE SCHOOL | 2 | 400 | 19506332 | 370 | 2019-06-05 13:30 | 110 | 511 | 132 | 613 | 128 | 594 | 94 | 717 | 2.5 | 0.5 |  | 3 | 69% | 59% | 93% | 69% | 9.2308 | Loss 5-10% |  |  | 535(367.5) | 486(369)
1369 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM054 | TG-YAM054A-1 | DT-1 | SUBHASH MOHALLA NO.-3:PL | 2 | 990 | 19502226 | 871 | 2019-06-30 23:00 | 308 | 1241 | 297 | 1199 | 266 | 1076 | 149 | 595 | 123 |  |  | 123 | 88% | 71% | 73% | 88% | 9.0717 | Loss 5-10% |  |  | 776(55.5) | 792(29.5)
1370 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM054 | TG-YAM054A-2 | DT-2 | SUBHASH MOHALLA NO.-3:PL | 2 | 630 | 19502194 | 470 | 2019-06-30 | 131 | 565 | 176 | 760 | 163 | 700 | 173 | 701 | 16.5 |  |  | 16.5 | 75% | 54% | 55% | 74% | 9.0717 | Loss 5-10%
1371 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM060 | TG-YAM060A-1 | DT-1 | C-1, YVR NEAR ANAND SAGAR | 1 | 630 | 19506311 | 710 | 2019-06-14 11:30 | 237 | 972 | 227 | 928 | 246 | 1002 | 64 | 467.5 | 127 | 91.5 | 34 | 252.5 | 73% | 63% | 113% | 76% | 4.5252 | Loss 0-5% |  | 540(54) | 683(249) | 649(212.5) | 591(89)
1372 | 1250 | YVR | GHONDA | GHO001 | TG-GHO001A-1 | DT-1 | A BLOCK BHAJANPURA GALI NO. -3:PL | 1 | 990 | 19504886 | 898 | 2019-06-30 00:30 | 287 | 1205 | 356 | 1499 | 254 | 1059 | 388 | 609 | 110 | 0.5 |  | 110.5 | 91% | 53% | 61% | 90% | 6.372 | Loss 5-10% |  | 896(80.5) | 987(180.5) | 948(111.5) | 823(69.5)
1373 | 1250 | YVR | GHONDA | GHO002 | TG-GHO002A-1 | DT-1 | B BLOCK BHAJANPURA:K | 3 | 990 | 19501767 | 1101 | 2019-06-08 14:00 | 356 | 1492 | 372 | 1589 | 373 | 1583 | 94 | 405 | 149 | 44 | 12.5 | 205.5 | 106% | 81% | 111% | 111% | 11.4238 | Loss 10-20% | 823(24) | 1133(194.5) | 1202(426.5) | 964(216.5) | 902(111)
1374 | 1250 | YVR | GHONDA | GHO002 | TG-GHO002A-2 | DT-2 | B BLOCK BHAJANPURA:K | 3 | 990 | 19506334 | 1265.9065 | 2019-06-29 23:00 | 445.525 | 1989.6617 | 405.0761 | 1791.5796 | 415.3053 | 1848.2655 | 176.6956 | 372 | 236 | 54 | 42 | 332 | 120% | 99% | 122% | 128% | 11.4238 | Loss 10-20% |  |  |  | 868(34) | 956(45.5)
1375 | 1250 | YVR | GHONDA | GHO002 | TG-GHO002A-3 | DT-3 | B BLOCK BHAJANPURA:K | 3 | 990 | 19504179 | 1251 | 2019-06-02 23:30 | 421 | 1821 | 413 | 1779 | 417 | 1802 | 36 | 515.5 | 152.5 | 18.5 | 18.5 | 189.5 | 126% | 81% | 98% | 126% | 11.4238 | Loss 10-20% |  | 1010(163) | 1242(403.5) | 1059(237.5) | 1019(187)
1376 | 1250 | YVR | GHONDA | GHO003 | TG-GHO003A-1 | DT-1 | D BLOCK BHAJANPURA:K | 3 | 990 | 19503712 | 1020 | 2019-06-29 23:30 | 360 | 1530 | 318 | 1355 | 343 | 1447 | 152 | 531.5 | 144.5 | 39.5 | 4.5 | 188.5 | 102% | 73% | 74% | 103% | 19.5469 | Loss 10-20% |  |  | 1439(632.5) | 1431(434.5)
1377 | 1250 | YVR | GHONDA | GHO003 | TG-GHO003A-2 | DT-2 | D BLOCK BHAJANPURA:K | 3 | 990 | 19504884 | 1023 | 2019-06-29 23:30 | 328 | 1397 | 382 | 1640 | 313 | 1321 | 289 | 525 | 183 | 10.5 | 1 | 194.5 | 102% | 72% | 79% | 103% | 19.5469 | Loss 10-20% |  |  |  |  | 878(85.5) | 843(102.5)
1378 | 1250 | YVR | GHONDA | GHO003 | TG-GHO003A-3 | DT-3 | D BLOCK BHAJANPURA:K | 3 | 990 | 19501785 | 1020 | 2019-06-30 02:00 | 324 | 1366 | 342 | 1443 | 354 | 1492 | 110 | 562.5 | 151.5 | 5 | 0.5 | 157 | 103% | 85% | 74% | 78% | 19.5469 | Loss 10-20% | 819(84.5) | 960(339) | 813(51) | 794(34.5) | 896(128.5) | 874(67.5)
1379 | 1250 | YVR | GHONDA | GHO006 | TG-GHO006A-1 | DT-1 | SOUTH GAMRI KIOSK:K | 2 | 990 | 19505178 | 546 | 2019-06-11 19:00 | 155 | 660 | 213 | 906 | 179 | 768 | 213 | 720 |  |  |  | 0 | 49% | 42% | 55% | 50% | 11.8158 | Loss 10-20% |  |  | 841(57)
1380 | 1250 | YVR | GHONDA | GHO006 | TG-GHO006A-2 | DT-2 | SOUTH GAMRI KIOSK:K | 2 | 990 | 19505655 | 898 | 2019-06-29 23:00 | 291 | 1259 | 270 | 1175 | 337 | 1474 | 267 | 576.5 | 142 | 1.5 |  | 143.5 | 88% | 71% | 88% | 91% | 11.8158 | Loss 10-20% |  |  | 910(58) | 1140(173.5) | 880(134)
1381 | 1250 | YVR | GHONDA | GHO007 | TG-GHO007A-1 | DT-1 | GAMRHI VILLAGE:PL | 2 | 630 | 19502639 | 599 | 2019-06-30 00:30 | 196 | 830 | 176 | 747 | 228 | 965 | 191 | 639 | 70.5 | 5.5 |  | 76 | 95% | 75% | 73% | 93% | 33.7815 | Loss >30% |  | 533(59) | 598(128.5) | 517(39.5)
1382 | 1250 | YVR | GHONDA | GHO007 | TG-GHO007A-2 | DT-2 | GAMRHI VILLAGE:PL | 2 | 990 | 19506047 | 922 | 2019-06-01 | 296 | 1295 | 306 | 1331 | 320 | 1390 | 83 | 471.5 | 242.5 | 4 |  | 246.5 | 93% | 77% | 86% | 94% | 33.7815 | Loss >30% | 760(33) | 918(225) | 978(483) | 960(434.5) | 921(309.5) | 851(142.5)
1383 | 1250 | YVR | GHONDA | GHO008 | TG-GHO008A-1 | DT-1 | GAMRI KIOSK:K | 1 | 1600 | 19506830 | 1217 | 2019-06-11 23:30 | 362 | 1489 | 394 | 1645 | 462 | 1918 | 376 | 687.5 | 31.5 |  |  | 31.5 | 76% | 72% | 67% | 76% | 23.4899 | Loss 20-30% | 974(430.5) | 1253(694) | 1367(645)
1384 | 1250 | YVR | GHONDA | GHO009 | TG-GHO009A-1 | DT-1 | ARVIND NAGAR PRIMARY SCHOOL GAUTAM VIHAR:PL | 3 | 990 | 19506005 | 969 | 2019-06-12 | 366 | 1489 | 289 | 1173 | 314 | 1268 | 281 | 551.5 | 154.5 | 11 |  | 165.5 | 98% | 75% | 74% | 97% | 24.6905 | Loss 20-30%
1385 | 1250 | YVR | GHONDA | GHO009 | TG-GHO009A-2 | DT-2 | ARVIND NAGAR PRIMARY SCHOOL GAUTAM VIHAR:PL | 3 | 990 | 19501821 | 680 | 2019-06-11 23:00 | 231 | 1009 | 177 | 761 | 271 | 1172 | 358 | 717 |  |  |  | 0 | 68% | 56% | 56% | 69% | 24.6905 | Loss 20-30% |  | 813(36) | 1046(163.5) | 924(67.5) | 770(26)
1386 | 1250 | YVR | GHONDA | GHO009 | TG-GHO009A-3 | DT-3 | ARVIND NAGAR PRIMARY SCHOOL GAUTAM VIHAR:PL | 3 | 630 | 19506522 | 297 | 2019-06-11 | 98 | 406 | 46 | 190 | 153 | 635 | 386 | 717.5 |  |  |  | 0 | 47% | 33% | 36% | 46% | 24.6905 | Loss 20-30%
1387 | 1250 | YVR | GHONDA | GHO010 | TG-GHO010A-1 | DT-1 | GAUTAM VIHAR KIOSK:K | 2 | 990 | 19501769 | 1072 | 2019-06-10 23:30 | 305 | 1214 | 350 | 1412 | 417 | 1680 | 405 | 130 | 444.5 | 113.5 | 30.5 | 588.5 | 107% | 92% | 97% | 108% | 13.4553 | Loss 10-20% | 825(58) | 1060(480) | 1163(620) | 1033(575.5) | 975(325) | 838(131.5)
1388 | 1250 | YVR | GHONDA | GHO010 | TG-GHO010A-2 | DT-2 | GAUTAM VIHAR KIOSK:K | 2 | 990 | 19505118 | 871 | 2019-06-09 23:30 | 289 | 1172 | 292 | 1181 | 289 | 1169 | 11 | 558.5 | 160 |  |  | 160 | 87% | 78% | 74% | 88% | 13.4553 | Loss 10-20% | 820(51) | 1079(371.5) | 1100(414.5) | 804(100.5) | 752(36)
1389 | 1250 | YVR | GHONDA | GHO011 | TG-GHO011A-1 | DT-1 | JAI PRAKASH NO-1:PL | 1 | 990 | 19501819 | 957 | 2019-06-29 23:30 | 326 | 1438 | 332 | 1478 | 299 | 1325 | 137 | 572.5 | 140.5 | 5 |  | 145.5 | 92% | 69% | 75% | 97% | 6.0258 | Loss 5-10% |  | 978(213.5) | 1101(574.5) | 1023(540.5) | 1045(422) | 810(99)
1390 | 1250 | YVR | GHONDA | GHO012 | TG-GHO012A-1 | DT-1 | JAI PRAKASH NO-2:PL | 1 | 990 | 19506116 | 1043 | 2019-06-29 23:30 | 283 | 1262 | 389 | 1749 | 371 | 1671 | 452 | 293 | 366.5 | 51.5 | 7 | 425 | 102% | 80% | 84% | 105% | 12.1486 | Loss 10-20% |  |  | 767(25) | 788(41.5)
1391 | 1250 | YVR | GHONDA | GHO013 | TG-GHO013A-1 | DT-1 | KARTAR NAGAR HOTEL WALA:PL | 1 | 990 | 19501723 | 1116 | 2019-06-10 23:30 | 378 | 1634 | 344 | 1471 | 394 | 1711 | 213 | 211 | 384.5 | 73 | 51 | 508.5 | 109% | 83% | 93% | 113% | 20.0801 | Loss 20-30% |  |  | 1266(665) | 1335(665) | 1229(598.5) | 1056(412)
1392 | 1250 | YVR | GHONDA | GHO014 | TG-GHO014A-1 | DT-1 | 3.5 PUSTA KARTAR NAGAR:K | 2 | 630 | 19505486 | 700 | 2019-06-29 23:30 | 219 | 922 | 230 | 968 | 251 | 1063 | 125 | 124 | 91.5 | 19.5 | 12.5 | 123.5 | 109% | 81% | 92% | 111% | 5.3389 | Loss 5-10% | [5 empty] | 612(62.5)
1393 | 1250 | YVR | GHONDA | GHO014 | TG-GHO014A-2 | DT-2 | 3.5 PUSTA KARTAR NAGAR:K | 2 | 630 | 19504173 | 555 | 2019-06-29 23:30 | 175 | 737 | 206 | 878 | 174 | 734 | 142 | 651.5 | 63 |  |  | 63 | 85% | 68% | 75% | 88% | 5.3389 | Loss 5-10%
1394 | 1250 | YVR | GHONDA | GHO015 | TG-GHO015A-1 | DT-1 | JAGJEET NAGAR KIOSK:K | 3 | 990 | 19506721 | 1021 | 2019-06-29 23:30 | 360 | 1465 | 312 | 1264 | 349 | 1420 | 183 | 412 | 259 | 40.5 | 4 | 303.5 | 103% | 96% | 94% | 103% | 5.4038 | Loss 5-10% | 1077(496) | 1358(566.5) | 1480(654) | 1111(542.5) | 1027(446) | 1069(118)
1395 | 1250 | YVR | GHONDA | GHO015 | TG-GHO015A-2 | DT-2 | JAGJEET NAGAR KIOSK:K | 3 | 990 | 19506046 | 1237 | 2019-06-01 07:30 | 368 | 1510 | 414 | 1693 | 456 | 1879 | 320 | 159 | 390 | 110 | 59.5 | 559.5 | 120% | 125% | 108% | 120% | 5.4038 | Loss 5-10% | 853(80.5) | 1168(215.5)
1396 | 1250 | YVR | GHONDA | GHO015 | TG-GHO015A-3 | DT-3 | JAGJEET NAGAR KIOSK:K | 3 | 990 | 19506495 | 927 | 2019-06-06 00:30 | 316 | 1396 | 289 | 1283 | 322 | 1437 | 138 | 579 | 135 | 1.5 |  | 136.5 | 94% | 68% | 79% | 91% | 5.4038 | Loss 5-10%
1397 | 1250 | YVR | GHONDA | GHO016 | TG-GHO016A-1 | DT-1 | 3 RD JAGJEET NAGAR :PL | 1 | 990 | 19506707 | 904 | 2019-06-25 18:30 | 290 | 1222 | 248 | 1029 | 365 | 1554 | 460 | 614 | 100.5 | 0.5 |  | 101 | 88% | 77% | 91% | 87% | 7.2109 | Loss 5-10%
1398 | 1250 | YVR | GHONDA | GHO017 | TG-GHO017A-1 | DT-1 | VIJAY COLONY:PL | 1 | 990 | 19505799 | 1398 | 2019-06-30 | 511 | 2325 | 481 | 2251 | 406 | 1841 | 452 | 549 | 163 | 5 | 2 | 170 | 141% | 83% | 83% | 101% | 7.8147 | Loss 5-10%
1399 | 1250 | YVR | GHONDA | GHO018 | TG-GHO018A-1 | DT-1 | USMANPUR PUSTA NO-2:PL | 2 | 630 | 19506644 | 544 | 2019-06-15 16:00 | 127 | 535 | 291 | 1198 | 126 | 524 | 669 | 563.5 | 153 |  |  | 153 | 83% | 65% | 86% | 85% | 24.4679 | Loss 20-30% |  | 546(151) | 538(89.5) | 541(268.5)
1400 | 1250 | YVR | GHONDA | GHO018 | TG-GHO018A-2 | DT-2 | USMANPUR PUSTA NO-2:PL | 2 | 630 | 19504176 | 546 | 2019-06-27 23:30 | 153 | 668 | 138 | 605 | 255 | 1121 | 488 | 604 | 113.5 |  |  | 113.5 | 84% | 68% | 75% | 87% | 24.4679 | Loss 20-30% |  |  | 484(27)
1401 | 1250 | YVR | GHONDA | GHO019 | TG-GHO019A-1 | DT-1 | KHADDEY WALI MASJID:PM | 1 | 630 | 19506336 | 935 | 2019-06-22 01:30 | 315 | 1341 | 340 | 1456 | 279 | 1189 | 233 | 20.5 | 197 | 166 | 335 | 698 | 148% | 120% | 144% | 147% | 10.1807 | Loss 10-20% | [5 empty] | 792(363)
1402 | 1250 | YVR | GHONDA | GHO020 | TG-GHO020A-1 | DT-1 | MONI BABA MANDIR:K | 3 | 990 | 19504129 | 1086 | 2019-06-30 23:30 | 419 | 1906 | 309 | 1379 | 358 | 1613 | 457 | 354 | 258 | 80 | 27.5 | 365.5 | 107% | 89% | 91% | 110% | 7.6924 | Loss 5-10% |  |  |  |  | 1044(49) | 941(70)
1403 | 1250 | YVR | GHONDA | GHO020 | TG-GHO020A-2 | DT-2 | MONI BABA MANDIR:K | 3 | 630 | 19500582 | 836.1671 | 2019-06-29 23:30 | 213.0083 | 893.0792 | 318.2256 | 1360.4617 | 304.9332 | 1288.4318 | 435.8546 | 183.5 | 310.5 | 84 | 140.5 | 535 | 133% | 94% | 99% | 133% | 7.6924 | Loss 5-10% |  | 929(125.5) | 1450(458) | 897(706) | 822(691.5) | 729(367)
1404 | 1250 | YVR | GHONDA | GHO020 | TG-GHO020A-3 | DT-3 | MONI BABA MANDIR:K | 3 | 990 | 19506337 | 1022.5369 | 2019-06-29 23:00 | 311.7354 | 1382.0507 | 393.8928 | 1799.9124 | 316.9087 | 1422.8382 | 399.0345 | 516 | 159.5 | 41 | 2.5 | 203 | 100% | 75% | 81% | 103% | 7.6924 | Loss 5-10% |  | 590(36) | 527(26.5)
1405 | 1250 | YVR | GHONDA | GHO021 | TG-GHO021A-1 | DT-1 | R BLOCK BRAHAMPURI:PL | 1 | 990 | 19505894 | 861 | 2019-06-11 00:30 | 217 | 924 | 372 | 1619 | 272 | 1153 | 614 | 562.5 | 155.5 |  |  | 155.5 | 87% | 85% | 86% | 85% | 10.9312 | Loss 10-20%
1406 | 1250 | YVR | GHONDA | GHO023 | TG-GHO023A-1 | DT-1 | BRAMPURI NO-6 NEAR MANDIR:PL | 1 | 990 | 19502174 | 942 | 2019-06-03 | 314 | 1328 | 302 | 1270 | 327 | 1367 | 84 | 337 | 368.5 | 14.5 |  | 383 | 95% | 80% | 88% | 95% | 26.7926 | Loss 20-30% | 910(355) | 924(350) | 983(500.5) | 947(471) | 902(392) | 846(148)
1407 | 1250 | YVR | GHONDA | GHO024 | TG-GHO024A-1 | DT-1 | X BL BRAHAMPURI RAMNIWAS WALA:PL | 3 | 990 | 19506904 | 943 | 2019-06-09 23:30 | 383 | 1674 | 291 | 1269 | 268 | 1149 | 476 | 478.5 | 230.5 | 9.5 |  | 240 | 92% | 89% | 83% | 95% | 10.1778 | Loss 10-20% |  | 821(53) | 1021(158) | 856(95.5) | 821(84)
1408 | 1250 | YVR | GHONDA | GHO024 | TG-GHO024A-2 | DT-2 | X BL BRAHAMPURI RAMNIWAS WALA:PL | 3 | 990 | 19503177 | 433 | 2019-06-29 23:00 | 188 | 793 | 123 | 513 | 121 | 508 | 283 | 719.5 |  |  |  | 0 | 41% | 38% | 42% | 44% | 10.1778 | Loss 10-20%
1409 | 1250 | YVR | GHONDA | GHO024 | TG-GHO024A-3 | DT-3 | X BL BRAHAMPURI RAMNIWAS WALA:PL | 3 | 630 | 19506049 | 452 | 2019-06-29 23:00 | 168 | 726 | 128 | 551 | 156 | 675 | 157 | 717.5 | 2 |  |  | 2 | 69% | 57% | 70% | 72% | 10.1778 | Loss 10-20% | 417(43) | 450(426.5) | 789(308.5)
1410 | 1250 | YVR | GHONDA | GHO025 | TG-GHO025A-1 | DT-1 | X BL BRAHAMPURI KHATTEY WALA:PL | 2 | 990 | 19503713 | 896 | 2019-06-29 22:30 | 330 | 1467 | 269 | 1198 | 297 | 1304 | 234 | 482 | 79 | 0.5 |  | 79.5 | 85% | 64% | 79% | 90% | 16.5691 | Loss 10-20%
1411 | 1250 | YVR | GHONDA | GHO025 | TG-GHO025A-2 | DT-2 | X BL BRAHAMPURI KHATTEY WALA:PL | 2 | 630 | 19506248 | 487 | 2019-06-11 13:00 | 186 | 701 | 168 | 639 | 133 | 501 | 177 | 710 | 1 |  |  | 1 | 66% | 67% | 77% | 66% | 16.5691 | Loss 10-20% |  |  |  | 726(253.5) | 662(361) | 659(111)
1412 | 1250 | YVR | GHONDA | GHO026 | TG-GHO026A-1 | DT-1 | X BL BRAHAMPURI BHISHAM WALA:PL | 1 | 990 | 19504986 | 963 | 2019-06-29 23:00 | 299 | 1198 | 324 | 1352 | 340 | 1412 | 191 | 531 | 177 | 10.5 |  | 187.5 | 94% | 71% | 76% | 97% | 4.6979 | Loss 0-5% |  | 818(50) | 893(153.5) | 884(130) | 875(68)
1415 | 1250 | YVR | GHONDA | GHO035 | TG-GHO035A-1 | DT-1 | BALLU KA TUBEWELL | 1 | 990 | 19504732 | 875 | 2019-06-29 23:00 | 269 | 1179 | 332 | 1465 | 274 | 1212 | 272 | 595 | 123.5 |  |  | 123.5 | 87% | 73% | 72% | 88% | 15.9877 | Loss 10-20% |  |  | 854(96) | 791(55) | 777(32)
1416 | 1250 | YVR | GHONDA | GHO038 | TG-GHO038A-1 | DT-1 | MAIN BRAHMPURI RD GALI NO.7:PM | 1 | 990 | 19504532 | 932 | 2019-06-03 00:30 | 208 | 870 | 367 | 1549 | 357 | 1522 | 666 | 515 | 191 | 12.5 |  | 203.5 | 94% | 77% | 80% | 92% | 15.0867 | Loss 10-20% |  | 1010(219) | 1003(389) | 987(391.5) | 987(221.5) | 812(89)
1417 | 1250 | YVR | GHONDA | GHO040 | TG-GHO040A-1 | DT-1 | MAIN BRAHMPURI RD GALI NO.19:PM | 1 | 630 | 19506050 | 774 | 2019-06-30 01:30 | 239 | 1016 | 244 | 1032 | 291 | 1243 | 219 | 151 | 409 | 111 | 48 | 568 | 123% | 103% | 108% | 112% | 5.9512 | Loss 5-10% | 680(349.5) | 834(706) | 887(713.5) | 817(732.5) | 777(741)
1418 | 1250 | YVR | GHONDA | GHO041 | TG-GHO041A-1 | DT-1 | MAIN BRAHMPURI RD GALI NO. 24 | 1 | 400 | 19505946 | 317 | 2019-06-01 17:00 | 125 | 516 | 93 | 403 | 99 | 428 | 103 | 682 | 37.5 |  |  | 37.5 | 74% | 72% | 79% | 70% | 6.1509 | Loss 5-10% |  | 315(25.5) | 339(64.5) | 320(89.5)
1419 | 1250 | YVR | GHONDA | GHO042 | TG-GHO042A-1 | DT-1 | MAIN BRAHMPURI RD GALI NO. 23:PM | 1 | 990 | 19505995 | 1071 | 2019-06-26 02:00 | 362 | 1477 | 390 | 1583 | 320 | 1304 | 244 | 239 | 372 | 85.5 | 16 | 473.5 | 108% | 100% | 104% | 104% | 16.1339 | Loss 10-20% | 604(92) | 916(353.5) | 932(326.5) | 930(406)
1420 | 1250 | YVR | GHONDA | GHO054 | TG-GHO054A-1 | DT-1 | D-BLOCK GAMRI EXTR S/ST | 2 | 990 | 19505519 | 636 | 2019-06-14 19:30 | 202 | 836 | 239 | 1006 | 195 | 820 | 179 | 719.5 |  |  |  | 0 | 61% | 52% | 64% | 64% | 39.99 | Loss >30%
1421 | 1250 | YVR | GHONDA | GHO054 | TG-GHO054A-2 | DT-2 | D-BLOCK GAMRI EXTR S/ST | 2 | 630 | 19505777 | 642 | 2019-06-30 06:30 | 130 | 517 | 274 | 1104 | 237 | 979 | 536 | 493.5 | 212 | 10 | 1 | 223 | 101% | 102% | 91% | 98% | 39.99 | Loss >30% | [5 empty] | 504(30)
1422 | 1250 | YVR | GHONDA | GHO056 | TG-GHO056A-1 | DT-1 | A BLOCK BHAJANPURA GALI NO. -2:P/M | 1 | 630 | 19506048 | 662 | 2019-06-30 14:30 | 306 | 1429 | 136 | 611 | 220 | 971 | 710 | 593.5 | 119 | 4.5 | 2.5 | 126 | 102% | 62% | 105% | 103% | 10.8644 | Loss 10-20% |  |  | 681(100.5) | 716(36)
1423 | 1250 | YVR | GHONDA | YAM032 | TG-YAM032A-1 | DT-1 | GAMRI ROAD PUMP HOUSE:PL | 2 | 630 | 19505578 | 438 | 2019-06-10 23:00 | 123 | 510 | 216 | 911 | 99 | 411 | 459 | 720 |  |  |  | 0 | 69% | 55% | 55% | 69% | 44.8804 | Loss >30% |  | 635(411) | 683(616) | 675(620.5) | 603(368.5)
1424 | 1250 | YVR | GHONDA | YAM032 | TG-YAM032A-2 | DT-2 | GAMRI ROAD PUMP HOUSE:PL | 2 | 990 | 19505820 | 949 | 2019-06-12 12:00 | 361 | 1458 | 347 | 1419 | 242 | 958 | 482 | 611 | 108 | 1 |  | 109 | 74% | 74% | 96% | 80% | 44.8804 | Loss >30%
1425 | 1250 | YVR | NEW SEELAMPUR | SLM010 | TG-SLM010A-1 | DT-1 | RISHI KARDOM MARG:PL | 1 | 990 | 19503434 | 778 | 2019-06-30 | 188 | 803 | 361 | 1561 | 229 | 962 | 692 | 691 | 28 |  |  | 28 | 79% | 69% | 72% | 78% | 18.7756 | Loss 10-20% |  | 843(91.5) | 861(207.5)
1426 | 1250 | YVR | NEW SEELAMPUR | SLM011 | TG-SLM011A-1 | DT-1 | BRAHMPURI NO-I:PL | 2 | 990 | 19506454 | 881 | 2019-06-26 18:00 | 332 | 1363 | 298 | 1203 | 251 | 1024 | 293 | 448.5 | 148.5 |  |  | 148.5 | 82% | 73% | 89% | 80% | 31.8886 | Loss >30% |  |  |  | 1184(169) | 991(220) | 827(62.5)
1428 | 1250 | YVR | NEW SEELAMPUR | SLM013 | TG-SLM013A-1 | DT-1 | OUTSIDE KOTHI ZAFRABAD:PL | 2 | 990 | 19502308 | 821 | 2019-06-30 03:00 | 213 | 852 | 307 | 1229 | 301 | 1194 | 361 | 681.5 | 37 |  |  | 37 | 83% | 72% | 74% | 80% | 16.6384 | Loss 10-20% |  | 836(115.5) | 883(218) | 839(195) | 831(131.5)
1429 | 1250 | YVR | NEW SEELAMPUR | SLM013 | TG-SLM013A-2 | DT-2 | OUTSIDE KOTHI ZAFRABAD:PL | 2 | 630 | 19506525 | 335 | 2019-06-30 01:00 | 60 | 236 | 88 | 348 | 187 | 745 | 464 | 718.5 |  |  |  | 0 | 53% | 44% | 44% | 49% | 16.6384 | Loss 10-20%
1430 | 1250 | YVR | NEW SEELAMPUR | SLM014 | TG-SLM014A-1 | DT-1 | INSIDE KOTHI ZAFRABAD:PL | 2 | 990 | 19503430 | 537 | 2019-06-01 21:30 | 139 | 584 | 244 | 1021 | 154 | 647 | 409 | 720 |  |  |  | 0 | 54% | 46% | 53% | 54% | 33.7557 | Loss >30%
1431 | 1250 | YVR | NEW SEELAMPUR | SLM014 | TG-SLM014A-2 | DT-2 | INSIDE KOTHI ZAFRABAD:PL | 2 | 990 | 19503729 | 882 | 2019-06-30 00:30 | 320 | 1321 | 246 | 1009 | 316 | 1310 | 307 | 606 | 114 |  |  | 114 | 89% | 76% | 79% | 86% | 33.7557 | Loss >30% |  | 871(152.5) | 921(311.5) | 848(209) | 801(141.5)
1432 | 1250 | YVR | NEW SEELAMPUR | SLM015 | TG-SLM015A-1 | DT-1 | KHATTA ROAD NO 66 ZAFRABAD:PL | 2 | 990 | 19505169 | 847 | 2019-06-30 | 249 | 1004 | 299 | 1191 | 299 | 1194 | 188 | 265 | 59.5 |  |  | 59.5 | 86% | 78% | 78% | 84% | 49.9148 | Loss >30% |  |  | 1137(46.5) | 884(215.5) | 892(168) | 767(37)
1433 | 1250 | YVR | NEW SEELAMPUR | SLM015 | TG-SLM015A-2 | DT-2 | KHATTA ROAD NO 66 ZAFRABAD:PL | 2 | 990 | 19506711 | 983 | 2019-06-29 23:30 | 335 | 1329 | 323 | 1282 | 325 | 1315 | 42 | 495.5 | 208 | 15.5 |  | 223.5 | 98% | 87% | 92% | 99% | 49.9148 | Loss >30% | 988(254.5) | 1027(165.5) | 895(32.5) | 1033(394) | 1165(484.5) | 1023(325)
1434 | 1250 | YVR | NEW SEELAMPUR | SLM016 | TG-SLM016A-1 | DT-1 | OUTSIDE SCHOOL ZAFRABAD:PL | 2 | 990 | 19505290 | 775 | 2019-06-03 01:00 | 254 | 1081 | 221 | 931 | 301 | 1306 | 327 | 683 | 36 |  |  | 36 | 78% | 67% | 75% | 75% | 27.0774 | Loss 20-30% |  |  |  |  | 901(192.5) | 928(189)
1435 | 1250 | YVR | NEW SEELAMPUR | SLM016 | TG-SLM016A-2 | DT-2 | OUTSIDE SCHOOL ZAFRABAD:PL | 2 | 990 | 19505654 | 648 | 2019-06-29 17:00 | 123 | 477 | 345 | 1353 | 180 | 699 | 789 | 719.5 |  |  |  | 0 | 55% | 48% | 65% | 54% | 27.0774 | Loss 20-30%
1436 | 1250 | YVR | NEW SEELAMPUR | SLM017 | TG-SLM017A-1 | DT-1 | NALA NO 1 SEELAMPUR:PL | 3 | 990 | 19505092 | 633 | 2019-06-03 01:30 | 220 | 891 | 212 | 853 | 202 | 821 | 61 | 717.5 |  |  |  | 0 | 64% | 46% | 61% | 57% | 38.2424 | Loss >30% | [5 empty] | 786(35)
1437 | 1250 | YVR | NEW SEELAMPUR | SLM017 | TG-SLM017A-2 | DT-2 | NALA NO 1 SEELAMPUR:PL | 3 | 990 | 19505652 | 787 | 2019-06-29 23:30 | 285 | 1279 | 229 | 1019 | 273 | 1219 | 236 | 665 | 52 |  |  | 52 | 79% | 68% | 76% | 80% | 38.2424 | Loss >30% |  | 940(226.5) | 981(309) | 819(201) | 812(157)
1438 | 1250 | YVR | NEW SEELAMPUR | SLM017 | TG-SLM017A-3 | DT-3 | NALA NO 1 SEELAMPUR:PL | 3 | 630 | 19506702 | 494 | 2019-06-11 07:00 | 166 | 672 | 177 | 720 | 151 | 609 | 96 | 718 | 0.5 |  |  | 0.5 | 35% | 78% | 35% | 34% | 38.2424 | Loss >30%
1439 | 1250 | YVR | NEW SEELAMPUR | SLM018 | TG-SLM018A-1 | DT-1 | SBI WELCOME:ID | 3 | 990 | 19506718 | 917 | 2019-06-01 23:00 | 310 | 1253 | 291 | 1167 | 316 | 1257 | 88 | 507.5 | 205.5 | 3 |  | 208.5 | 90% | 86% | 92% | 93% | 12.0079 | Loss 10-20% |  |  |  |  | 963(103) | 919(34)
1440 | 1250 | YVR | NEW SEELAMPUR | SLM018 | TG-SLM018A-2 | DT-2 | SBI WELCOME:ID | 3 | 990 | 19505886 | 826 | 2019-06-07 15:30 | 383 | 1592 | 359 | 1450 | 84 | 334 | 1194 | 715 | 0.5 |  |  | 0.5 | 62% | 59% | 83% | 58% | 12.0079 | Loss 10-20% |  | 1085(110.5) | 903(242.5) | 936(204) | 963(166.5)
1441 | 1250 | YVR | NEW SEELAMPUR | SLM018 | TG-SLM018A-3 | DT-3 | SBI WELCOME:ID | 3 | 630 | 19506642 | 355 | 2019-06-01 22:00 | 129 | 513 | 117 | 461 | 109 | 435 | 69 | 716.5 |  |  |  | 0 | 54% | 48% | 52% | 56% | 12.0079 | Loss 10-20%
1442 | 1250 | YVR | NEW SEELAMPUR | SLM019 | TG-SLM019A-1 | DT-1 | PHOTO CHOCK WELCOME:PL | 3 | 990 | 19505807 | 1242 | 2019-06-24 20:30 | 415 | 1747 | 428 | 1789 | 398 | 1655 | 118 | 703.5 | 12.5 |  | 0.5 | 13 | 80% | 62% | 125% | 76% | 32.3349 | Loss >30% |  | 830(65)
1443 | 1250 | YVR | NEW SEELAMPUR | SLM019 | TG-SLM019A-2 | DT-2 | PHOTO CHOCK WELCOME:PL | 3 | 990 | 19505086 | 1005 | 2019-06-30 00:30 | 327 | 1403 | 319 | 1359 | 360 | 1532 | 156 | 600 | 113 | 2 | 0.5 | 115.5 | 102% | 78% | 81% | 89% | 32.3349 | Loss >30% |  | 880(186.5) | 947(181.5) | 885(147.5) | 851(86.5)
1444 | 1250 | YVR | NEW SEELAMPUR | SLM019 | TG-SLM019A-3 | DT-3 | PHOTO CHOCK WELCOME:PL | 3 | 630 | 19506059 | 420 | 2019-06-20 19:30 | 175 | 703 | 102 | 409 | 143 | 575 | 255 | 716.5 |  |  |  | 0 | 61% | 48% | 67% | 60% | 32.3349 | Loss >30%
1445 | 1250 | YVR | NEW SEELAMPUR | SLM020 | TG-SLM020A-1 | DT-1 | Z-2 BLOCK WELCOME:PL | 2 | 630 | 19506530 | 447 | 2019-06-30 22:30 | 153 | 693 | 154 | 705 | 140 | 631 | 69 | 719.5 | 0.5 |  |  | 0.5 | 63% | 68% | 58% | 71% | 12.6212 | Loss 10-20%
1446 | 1250 | YVR | NEW SEELAMPUR | SLM020 | TG-SLM020A-2 | DT-2 | Z-2 BLOCK WELCOME:PL | 2 | 990 | 19500583 | 916 | 2019-06-01 00:30 | 298 | 1284 | 276 | 1184 | 342 | 1476 | 257 | 649 | 69.5 | 1 |  | 70.5 | 93% | 76% | 76% | 84% | 12.6212 | Loss 10-20% |  | 823(76) | 849(123.5) | 820(94) | 812(33.5)
1447 | 1250 | YVR | NEW SEELAMPUR | SLM021 | TG-SLM021A-1 | DT-1 | KABOOTER MARKET WELCOME:ID | 3 | 990 | 19506754 | 606 | 2019-06-01 01:00 | 236 | 966 | 195 | 784 | 176 | 711 | 227 | 720 |  |  |  | 0 | 61% | 60% | 60% | 60% | 21.5762 | Loss 20-30%
1448 | 1250 | YVR | NEW SEELAMPUR | SLM021 | TG-SLM021A-2 | DT-2 | KABOOTER MARKET WELCOME:ID | 3 | 990 | 19500609 | 1084 | 2019-06-03 01:30 | 397 | 1701 | 272 | 1148 | 415 | 1797 | 607 | 370.5 | 300.5 | 37 | 12 | 349.5 | 109% | 98% | 100% | 104% | 21.5762 | Loss 20-30% |  |  |  |  | 931(31.5)
1449 | 1250 | YVR | NEW SEELAMPUR | SLM021 | TG-SLM021A-3 | DT-3 | KABOOTER MARKET WELCOME:ID | 3 | 630 | 19505892 | 468 | 2019-06-03 | 177 | 719 | 175 | 719 | 116 | 473 | 247 | 707 | 13 |  |  | 13 | 74% | 64% | 70% | 73% | 21.5762 | Loss 20-30% |  |  |  | 509(26.5)
1450 | 1250 | YVR | NEW SEELAMPUR | SLM044 | TG-SLM044A-1 | DT-1 | CHAUHAN BANGAR GALI NO 10:PL | 5 | 990 | 19505063 | 515 | 2019-06-28 18:00 | 155 | 636 | 200 | 827 | 160 | 657 | 182 | 715.5 |  |  |  | 0 | 49% | 52% | 52% | 50% | 33.6837 | Loss >30%
1451 | 1250 | YVR | NEW SEELAMPUR | SLM044 | TG-SLM044A-2 | DT-2 | CHAUHAN BANGAR GALI NO 10:PL | 5 | 990 | 19502301 | 658 | 2019-06-02 | 254 | 1072 | 219 | 916 | 184 | 763 | 268 | 716.5 |  |  |  | 0 | 66% | 58% | 63% | 65% | 33.6837 | Loss >30%
1452 | 1250 | YVR | NEW SEELAMPUR | SLM044 | TG-SLM044A-3 | DT-3 | CHAUHAN BANGAR GALI NO 10:PL | 5 | 990 | 19502234 | 864 | 2019-06-02 00:30 | 314 | 1401 | 233 | 1019 | 317 | 1351 | 360 | 388.5 | 78 |  |  | 78 | 87% | 77% | 80% | 86% | 33.6837 | Loss >30% |  | 880(231.5) | 948(289) | 847(253) | 889(193) | 784(55.5)
1453 | 1250 | YVR | NEW SEELAMPUR | SLM044 | TG-SLM044A-4 | DT-4 | CHAUHAN BANGAR GALI NO 10:PL | 5 | 990 | 19504045 | 810 | 2019-06-01 23:30 | 255 | 1052 | 271 | 1115 | 283 | 1187 | 117 | 704 | 13 |  |  | 13 | 80% | 69% | 68% | 82% | 33.6837 | Loss >30% |  | 995(318.5) | 1015(133) | 785(88.5) | 784(53.5)
1454 | 1250 | YVR | NEW SEELAMPUR | SLM044 | TG-SLM044A-5 | DT-5 | CHAUHAN BANGAR GALI NO 10:PL | 5 | 990 | 19505205 | 791 | 2019-06-30 | 268 | 1171 | 254 | 1116 | 269 | 1178 | 59 | 699.5 | 17 |  |  | 17 | 80% | 75% | 73% | 76% | 33.6837 | Loss >30% |  |  | 831(124) | 861(111) | 835(101)
1455 | 1250 | YVR | NEW SEELAMPUR | SLM056 | TG-SLM056A-1 | DT-1 | OPP MAZAR BRAHMPURI ROAD:PM | 1 | 400 | 19506254 | 409 | 2019-06-30 03:30 | 128 | 546 | 146 | 629 | 135 | 585 | 72 | 450 | 258.5 | 10 | 1 | 269.5 | 102% | 84% | 91% | 98% | 34.6216 | Loss >30%
1456 | 1250 | YVR | NEW SEELAMPUR | SLM057 | TG-SLM057A-1 | DT-1 | CHAUHAN BANGAR GALI NO 5:PL | 2 | 990 | 19505374 | 967 | 2019-06-01 00:30 | 283 | 1193 | 352 | 1517 | 332 | 1429 | 290 | 508 | 202.5 | 7 |  | 209.5 | 98% | 81% | 85% | 94% | 28.7906 | Loss 20-30% |  | 951(229.5) | 1140(349) | 1078(297.5) | 834(213) | 816(46)
1457 | 1250 | YVR | NEW SEELAMPUR | SLM057 | TG-SLM057A-2 | DT-2 | CHAUHAN BANGAR GALI NO 5:PL | 2 | 630 | 19506438 | 423 | 2019-06-29 23:00 | 173 | 691 | 188 | 767 | 61 | 242 | 492 | 718 |  |  |  | 0 | 65% | 60% | 59% | 67% | 28.7906 | Loss 20-30%
1458 | 1250 | YVR | NEW SEELAMPUR | SLM060 | TG-SLM060A-1 | DT-1 | JANTA COLONY NO-2 | 1 | 400 | 19506052 | 342 | 2019-06-01 03:00 | 104 | 416 | 99 | 405 | 139 | 555 | 144 | 659.5 | 60.5 |  |  | 60.5 | 86% | 74% | 85% | 80% | 35.0115 | Loss >30% | 384(59) | 354(78) |  |  |  | 381(117.5)
1459 | 1250 | YVR | NEW SEELAMPUR | SLM061 | TG-SLM061A-1 | DT-1 | JANTA COLONY NO-3 | 1 | 630 | 19505809 | 591 | 2019-06-02 18:30 | 225 | 912 | 185 | 759 | 181 | 743 | 162 | 688 | 28.5 | 0.5 |  | 29 | 76% | 70% | 94% | 77% | 38.4575 | Loss >30%
1460 | 1250 | YVR | NEW SEELAMPUR | SLM073 | TG-SLM073A-1 | DT-1 | ARORA BLDG GALI-24 CHAUHAN | 1 | 630 | 19506061 | 534 | 2019-06-30 03:30 | 169 | 660 | 197 | 780 | 168 | 665 | 117 | 666 | 53 |  |  | 53 | 85% | 71% | 74% | 78% | 35.7816 | Loss >30% |  | 546(156) | 769(310.5) | 547(202) | 549(116)
1461 | 1250 | YVR | SHASTRI PARK | SLM001 | TG-SLM001A-1 | DT-1 | USMAN PUR KIOSK:K | 2 | 990 | 19502886 | 935 | 2019-06-27 23:00 | 314 | 1340 | 293 | 1248 | 327 | 1402 | 134 | 482.5 | 232.5 | 1.5 |  | 234 | 88% | 72% | 81% | 94% | 15.2261 | Loss 10-20% |  | 748(25.5) | 785(68) | 790(60.5) | 787(46)
1462 | 1250 | YVR | SHASTRI PARK | SLM001 | TG-SLM001A-2 | DT-2 | USMAN PUR KIOSK:K | 2 | 630 | 19506418 | 751 | 2019-06-14 | 209 | 911 | 269 | 1189 | 272 | 1188 | 277 | 420.5 | 197 | 53.5 | 45.5 | 296 | 119% | 80% | 94% | 116% | 15.2261 | Loss 10-20% | 638(65.5) | 823(448) | 853(659.5) | 822(667) | 767(631.5) | 635(247)
1463 | 1250 | YVR | SHASTRI PARK | SLM005 | TG-SLM005A-1 | DT-1 | GAUTAM PURI NO.1:PL | 1 | 990 | 19506608 | 1018 | 2019-06-03 14:30 | 309 | 1299 | 353 | 1465 | 356 | 1501 | 186 | 359 | 326 | 32 | 3 | 361 | 101% | 87% | 103% | 101% | 5.1853 | Loss 5-10% |  | 918(210.5) | 960(439.5) |  |  | 968(37.5)
1464 | 1250 | YVR | SHASTRI PARK | SLM007 | TG-SLM007A-1 | DT-1 | BHAGAT SINGH MOHALLA:PL | 1 | 990 | 19504172 | 858 | 2019-06-30 23:00 | 281 | 1231 | 282 | 1241 | 295 | 1294 | 59 | 614 | 103 |  |  | 103 | 85% | 58% | 70% | 87% | 5.5783 | Loss 5-10% |  | 811(34.5) | 856(100.5) | 832(48.5)
1465 | 1250 | YVR | SHASTRI PARK | SLM027 | TG-SLM027A-1 | DT-1 | H BLOCK SEELAMPUR:PL | 2 | 990 | 19505107 | 764 | 2019-06-29 23:30 | 278 | 1160 | 229 | 948 | 258 | 1089 | 187 | 686.5 | 33.5 |  |  | 33.5 | 77% | 65% | 66% | 77% | 17.9051 | Loss 10-20% |  |  | 849(43.5)
1466 | 1250 | YVR | SHASTRI PARK | SLM027 | TG-SLM027A-2 | DT-2 | H BLOCK SEELAMPUR:PL | 2 | 400 | 19505146 | 209 | 2019-06-21 12:30 | 77 | 354 | 67 | 304 | 65 | 297 | 53 | 719.5 |  |  |  | 0 | 32% | 39% | 52% | 40% | 17.9051 | Loss 10-20%
1467 | 1250 | YVR | SHASTRI PARK | SLM034 | TG-SLM034A-1 | DT-1 | RAJU WALA SHASTRI PARK:PL | 1 | 990 | 19505879 | 803 | 2019-06-29 23:30 | 260 | 1123 | 304 | 1294 | 239 | 1033 | 230 | 666 | 53 |  |  | 53 | 79% | 70% | 69% | 81% | 7.9029 | Loss 5-10% |  |  | 1062(48) | 784(29)
1468 | 1250 | YVR | SHASTRI PARK | SLM086 | TG-SLM086A-1 | DT-1 | ENGG COLL GAUTAM PUR NO-3:PL | 2 | 630 | 19503150 | 418 | 2019-06-30 23:00 | 108 | 448 | 136 | 568 | 175 | 726 | 242 | 720 |  |  |  | 0 | 65% | 46% | 63% | 66% | 4.4451 | Loss 0-5% |  |  | 494(51.5)
1469 | 1250 | YVR | SHASTRI PARK | SLM086 | TG-SLM086A-2 | DT-2 | ENGG COLL GAUTAM PUR NO-3:PL | 2 | 630 | 19505880 | 487 | 2019-06-29 23:30 | 165 | 713 | 160 | 689 | 162 | 693 | 22 | 679 | 41 |  |  | 41 | 77% | 59% | 72% | 77% | 4.4451 | Loss 0-5%
1471 | 1251 | KWR | GOKUL PURI | KWL001 | TG-KWL001A-1 | DT-1 | RAJEEV GANDHI NAGAR GALI NO.-3:ID | 2 | 630 | 19506907 | 664 | 2019-06-10 21:30 | 206 | 824 | 234 | 963 | 224 | 916 | 122 | 591 | 118.5 | 6 | 2 | 126.5 | 104% | 83% | 103% | 105% | 11.8949 | Loss 10-20%
1472 | 1251 | KWR | GOKUL PURI | KWL001 | TG-KWL001A-2 | DT-2 | RAJEEV GANDHI NAGAR GALI NO.-3:ID | 2 | 630 | 19505431 | 495 | 2019-06-02 | 232 | 933 | 175 | 703 | 88 | 343 | 515 | 714.5 | 3 |  |  | 3 | 79% | 61% | 77% | 74% | 11.8949 | Loss 10-20%
1473 | 1251 | KWR | GOKUL PURI | KWL003 | TG-KWL003A-1 | DT-1 | RAJEEV GANDHI NAGAR GALI NO.-15:ID | 2 | 990 | 19505388 | 833 | 2019-06-03 14:30 | 278 | 1269 | 284 | 1343 | 271 | 1252 | 84 | 713 | 5 |  |  | 5 | 71% | 79% | 84% | 81% | 7.8682 | Loss 5-10%
1474 | 1251 | KWR | GOKUL PURI | KWL003 | TG-KWL003A-2 | DT-2 | RAJEEV GANDHI NAGAR GALI NO.-15:ID | 2 | 990 | 19504934 | 882.7997 | 2019-06-01 23:30 | 329.2282 | 1360.672 | 235.1079 | 956.2287 | 318.4636 | 1317.435 | 384.6517 | 37 | 107 |  |  | 107 | 88% | 79% | 85% | 89% | 7.8682 | Loss 5-10% |  | 833(125.5) | 872(325) | 849(190.5) | 801(92.5)
1475 | 1251 | KWR | GOKUL PURI | KWL004 | TG-KWL004A-1 | DT-1 | RAJEEV GANDHI NAGAR GALI NO.-21:ID | 2 | 990 | 19504064 | 784 | 2019-06-30 | 243 | 969 | 240 | 956 | 300 | 1208 | 245 | 655 | 64.5 |  |  | 64.5 | 79% | 74% | 74% | 79% | 6.7925 | Loss 5-10%
1476 | 1251 | KWR | GOKUL PURI | KWL004 | TG-KWL004A-2 | DT-2 | RAJEEV GANDHI NAGAR GALI NO.-21:ID | 2 | 630 | 19506671 | 443 | 2019-06-13 14:00 | 145 | 590 | 136 | 552 | 163 | 667 | 102 | 719 | 0.5 |  |  | 0.5 | 69% | 70% | 70% | 65% | 6.7925 | Loss 5-10%
1477 | 1251 | KWR | GOKUL PURI | KWL005 | TG-KWL005A-1 | DT-1 | D BLOCK BHAGRATHI VIHAR:PL | 2 | 630 | 19500546 | 545 | 2019-06-02 08:00 | 154 | 628 | 203 | 823 | 188 | 768 | 174 | 619.5 | 99.5 |  |  | 99.5 | 84% | 87% | 71% | 82% | 7.9448 | Loss 5-10% |  | 538(24.5) | 613(56.5) | 498(42.5) | 493(25.5)
1478 | 1251 | KWR | GOKUL PURI | KWL005 | TG-KWL005A-2 | DT-2 | D BLOCK BHAGRATHI VIHAR:PL | 2 | 630 | 19505241 | 300 | 2019-06-03 14:30 | 99 | 429 | 107 | 471 | 94 | 412 | 53 | 719.5 |  |  |  | 0 | 39% | 43% | 48% | 40% | 7.9448 | Loss 5-10%
1479 | 1251 | KWR | GOKUL PURI | KWL014 | TG-KWL014A-1 | DT-1 | D BL BRIJPURI GALI NO. 10:ID | 1 | 630 | 19500566 | 529 | 2019-06-29 23:00 | 211 | 852 | 188 | 738 | 131 | 525 | 288 | 670 | 50 |  |  | 50 | 83% | 70% | 70% | 84% | 5.751 | Loss 5-10% |  |  | 500(48.5) | 495(37.5)
1480 | 1251 | KWR | GOKUL PURI | KWL019 | TG-KWL019A-1 | DT-1 | A BLK G N 2 BHAGIRATHI VIHAR NO-II :ID | 2 | 630 | 19506448 | 515 | 2019-06-30 | 184 | 720 | 177 | 684 | 154 | 592 | 115 | 665 | 54.5 |  |  | 54.5 | 82% | 76% | 77% | 80% | 5.4688 | Loss 5-10%
1481 | 1251 | KWR | GOKUL PURI | KWL019 | TG-KWL019A-2 | DT-2 | A BLK G N 2 BHAGIRATHI VIHAR NO-II :ID | 2 | 630 | 19505765 | 558 | 2019-06-29 23:30 | 184 | 738 | 228 | 925 | 146 | 580 | 299 | 582 | 137 |  |  | 137 | 88% | 86% | 87% | 89% | 5.4688 | Loss 5-10% |  |  | 523(41) | 549(47.5)
1482 | 1251 | KWR | GOKUL PURI | KWL027 | TG-KWL027A-1 | DT-1 | A BLOCK BRIJ PURI:ID | 2 | 630 | 19500627 | 643 | 2019-06-10 23:30 | 298 | 1293 | 228 | 992 | 116 | 486 | 706 | 577.5 | 127 | 13 | 1 | 141 | 100% | 71% | 86% | 102% | 6.2381 | Loss 5-10% | 518(36.5) | 686(389) | 650(104.5) | 764(495.5) |  | 554(96)
1483 | 1251 | KWR | GOKUL PURI | KWL027 | TG-KWL027A-2 | DT-2 | A BLOCK BRIJ PURI:ID | 2 | 630 | 19506307 | 379 | 2019-06-27 18:30 | 84 | 341 | 134 | 572 | 162 | 683 | 302 | 720 |  |  |  | 0 | 51% | 44% | 60% | 52% | 6.2381 | Loss 5-10%
1484 | 1251 | KWR | GOKUL PURI | KWL028 | TG-KWL028A-1 | DT-1 | B BLOCK BRIJ PURI:ID | 1 | 990 | 19505234 | 925 | 2019-06-10 01:00 | 259 | 1110 | 279 | 1194 | 388 | 1688 | 541 | 554 | 159.5 | 6.5 |  | 166 | 93% | 83% | 88% | 92% | 5.6254 | Loss 5-10% |  | 872(30.5) | 875(104.5) | 890(79.5) | 825(31.5)
1485 | 1251 | KWR | GOKUL PURI | KWL039 | TG-KWL039A-1 | DT-1 | GANGA VIHAR NO-1:ID | 2 | 990 | 19504447 | 739 | 2019-06-25 23:30 | 216 | 892 | 257 | 1059 | 265 | 1103 | 192 | 714.5 | 5.5 |  |  | 5.5 | 74% | 64% | 63% | 75% | 5.791 | Loss 5-10% |  | 1123(248.5) | 1262(469.5) | 1232(388) | 1251(298.5)
1486 | 1251 | KWR | GOKUL PURI | KWL039 | TG-KWL039A-2 | DT-2 | GANGA VIHAR NO-1:ID | 2 | 990 | 19500982 | 956 | 2019-06-25 23:30 | 412 | 1691 | 272 | 1098 | 272 | 1115 | 585 | 561.5 | 146 | 12.5 |  | 158.5 | 96% | 83% | 71% | 97% | 5.791 | Loss 5-10% |  | 671(156.5) | 717(372) | 704(276) | 701(181.5)
1487 | 1251 | KWR | GOKUL PURI | KWL040 | TG-KWL040A-1 | DT-1 | GANGA VIHAR NO-2:ID | 2 | 990 | 19501736 | 1126 | 2019-06-30 07:30 | 398 | 1520 | 377 | 1378 | 351 | 1337 | 166 | 378.5 | 244.5 | 68.5 | 25.5 | 338.5 | 106% | 114% | 96% | 108% | 7.2668 | Loss 5-10% | 914(38.5) | 1229(373.5) | 1410(150.5) | 952(48) | 1148(131)
1488 | 1251 | KWR | GOKUL PURI | KWL040 | TG-KWL040A-2 | DT-2 | GANGA VIHAR NO-2:ID | 2 | 990 | 19503794 | 1153 | 2019-06-08 23:30 | 282 | 1139 | 457 | 1903 | 414 | 1699 | 685 | 306 | 319 | 65.5 | 26.5 | 411 | 109% | 73% | 105% | 116% | 7.2668 | Loss 5-10% |  | 949(188) |  | 1027(99.5) | 1187(419.5) | 917(92.5)
1489 | 1251 | KWR | GOKUL PURI | KWL044 | TG-KWL044A-1 | DT-1 | GALI NO.3 OLD MUSTAFABAD:ID | 2 | 990 | 19502319 | 866 | 2019-06-02 07:00 | 334 | 1409 | 240 | 1006 | 292 | 1221 | 349 | 543.5 | 172 |  |  | 172 | 82% | 88% | 81% | 83% | 14.4156 | Loss 10-20% |  |  | 774(88.5) | 794(50.5)
1490 | 1251 | KWR | GOKUL PURI | KWL044 | TG-KWL044A-2 | DT-2 | GALI NO.3 OLD MUSTAFABAD:ID | 2 | 400 | 19501040 | 373 | 2019-06-29 23:30 | 136 | 566 | 119 | 496 | 117 | 481 | 79 | 320.5 | 393.5 | 2 |  | 395.5 | 91% | 93% | 90% | 93% | 14.4156 | Loss 10-20% |  | 354(144) | 357(420.5) | 389(394.5) | 334(127.5)
1491 | 1251 | KWR | GOKUL PURI | KWL052 | TG-KWL052A-1 | DT-1 | B BLOCK GOKUL PURI:PL | 1 | 630 | 19503799 | 538 | 2019-06-02 23:00 | 214 | 942 | 139 | 598 | 185 | 804 | 299 | 599 | 121 |  |  | 121 | 84% | 65% | 67% | 85% | 6.3099 | Loss 5-10%
1492 | 1251 | KWR | GOKUL PURI | KWL053 | TG-KWL053A-1 | DT-1 | JAWHAR NAGAR NO.-1:PL | 2 | 990 | 19506012 | 894 | 2019-06-24 14:30 | 224 | 937 | 335 | 1412 | 334 | 1406 | 472 | 708.5 | 11 | 0.5 |  | 11.5 | 39% | 41% | 90% | 18% | 6.6515 | Loss 5-10%
1493 | 1251 | KWR | GOKUL PURI | KWL053 | TG-KWL053A-2 | DT-2 | JAWHAR NAGAR NO.-1:PL | 2 | 990 | 19504953 | 1037 | 2019-06-24 12:00 | 346 | 1461 | 338 | 1428 | 354 | 1488 | 52 | 535.5 | 134.5 | 47.5 | 2 | 184 | 31% | 57% | 105% | 31% | 6.6515 | Loss 5-10% | 910(136.5) | 962(167) | 1010(173.5) | 1051(188.5) | 1083(221.5) | 1185(251)
1494 | 1251 | KWR | GOKUL PURI | KWL077 | TG-KWL077A-1 | DT-1 | SAMPAT NAGAR 1:ID | 2 | 630 | 19505662 | 342 | 2019-06-30 00:30 | 84 | 340 | 124 | 501 | 133 | 540 | 184 | 719 |  |  |  | 0 | 54% | 47% | 50% | 49% | 8.972 | Loss 5-10%
1495 | 1251 | KWR | GOKUL PURI | KWL077 | TG-KWL077A-2 | DT-2 | SAMPAT NAGAR 1:ID | 2 | 400 | 19505301 | 413 | 2019-06-30 | 156 | 655 | 130 | 547 | 126 | 528 | 118 | 238.5 | 389 | 87.5 | 4.5 | 481 | 103% | 97% | 100% | 102% | 8.972 | Loss 5-10% | 379(156) | 525(552) |  | 383(179) | 371(92)
1496 | 1251 | KWR | GOKUL PURI | KWL101 | TG-KWL101A-1 | DT-1 | MANSINGH NAGAR GALI NO. 16:ID | 2 | 630 | 19503017 | 500 | 2019-06-29 23:00 | 159 | 644 | 132 | 532 | 209 | 844 | 274 | 687.5 | 30.5 |  |  | 30.5 | 78% | 71% | 77% | 79% | 5.6675 | Loss 5-10% |  | 638(427)
1497 | 1251 | KWR | GOKUL PURI | KWL101 | TG-KWL101A-2 | DT-2 | MANSINGH NAGAR GALI NO. 16:ID | 2 | 990 | 19506035 | 804 | 2019-06-03 14:00 | 345 | 1602 | 278 | 1268 | 181 | 838 | 663 | 707.5 | 8.5 |  |  | 8.5 | 72% | 69% | 81% | 72% | 5.6675 | Loss 5-10% | 380(83) | 1220(543)
1498 | 1251 | KWR | GOKUL PURI | KWL103 | TG-KWL103A-1 | DT-1 | MAJOR MALHOTRA FARM HOUSE:PM | 1 | 100 | 19506634 | 85 | 2019-06-28 12:00 | 11 | 44 | 30 | 122 | 44 | 182 | 120 | 649.5 | 70.5 |  |  | 70.5 | 55% | 55% | 85% | 59% | 2.6432 | Loss 0-5%
1499 | 1251 | KWR | GOKUL PURI | KWL107 | TG-KWL107A-1 | DT-1 | JOHRIPUR GUJARMAL MOHALLA:PL | 1 | 990 | 19506817 | 934 | 2019-06-27 15:30 | 325 | 1503 | 305 | 1368 | 304 | 1391 | 125 | 668.5 | 49.5 | 0.5 |  | 50 | 39% | 45% | 94% | 40% | 7.491 | Loss 5-10% | 843(33.5) | 853(51) |  | 902(80.5) | 851(44.5) | 875(59.5)
1500 | 1251 | KWR | GOKUL PURI | KWL162 | TG-KWL162A-1 | DT-1 | JAIN COMPLEX JOHIRIPUR:PM | 1 | 100 | 19506636 | 87 | 2019-06-12 03:30 | 33 | 135 | 26 | 105 | 28 | 111 | 28 | 666.5 | 49.5 |  |  | 49.5 | 87% | 59% | 77% | 82% | 2.1297 | Loss 0-5% |  |  | 79(31.5)
1501 | 1251 | KWR | GOKUL PURI | KWL237 | TG-KWL237A-1 | DT-1 | SHANI BAZAR ROAD JOHRI PUR :PM | 1 | 630 | 19505924 | 905 | 2019-06-29 12:00 | 289 | 1325 | 292 | 1356 | 324 | 1488 | 150 | 551.5 | 150.5 | 14 | 1.5 | 166 | 63% | 68% | 144% | 67% | 5.8425 | Loss 5-10% | 681(197) | 701(200) | 826(195) | 727(190.5) | 769(221.5) | 748(228.5)
1502 | 1251 | KWR | GOKUL PURI | KWL243 | TG-KWL243A-1 | DT-1 | G & H BLK MUSTAFABAD GALI NO. 18:ID | 2 | 990 | 19505960 | 1101 | 2019-06-02 05:30 | 392 | 1669 | 396 | 1692 | 314 | 1323 | 359 | 293.5 | 395 | 29.5 | 2 | 426.5 | 111% | 86% | 107% | 103% | 6.5849 | Loss 5-10% |  | 1062(132.5) | 1046(384.5) | 1094(256.5) | 1042(135.5)
1503 | 1251 | KWR | GOKUL PURI | KWL243 | TG-KWL243A-2 | DT-2 | G & H BLK MUSTAFABAD GALI NO. 18:ID | 2 | 990 | 19505215 | 889 | 2019-06-02 06:00 | 280 | 1209 | 249 | 1075 | 361 | 1569 | 442 | 714.5 | 5.5 |  |  | 5.5 | 71% | 90% | 84% | 71% | 6.5849 | Loss 5-10%
1504 | 1251 | KWR | GOKUL PURI | KWL246 | TG-KWL246A-1 | DT-1 | C BLOCK BRIJ PURI:ID | 1 | 990 | 19505514 | 985 | 2019-06-03 14:00 | 326 | 1578 | 344 | 1617 | 315 | 1491 | 111 | 478.5 | 220.5 | 21 |  | 241.5 | 95% | 95% | 99% | 97% | 4.6852 | Loss 0-5% |  | 1020(54) | 998(168) | 1221(140) | 1028(69.5)
1505 | 1251 | KWR | GOKUL PURI | KWL331 | TG-KWL331A-1 | DT-1 | GALI NO.5 JAWAHAR NAGAR P/M | 1 | 990 | 19504775 | 935 | 2019-06-22 16:00 | 310 | 1350 | 309 | 1332 | 315 | 1363 | 27 | 583.5 | 128 | 3 |  | 131 | 44% | 57% | 94% | 40% | 12.9229 | Loss 10-20% | 883(123.5) | 842(82.5) |  | 906(87) | 802(43.5) | 886(96)
1506 | 1251 | KWR | GOKUL PURI | KWL344 | TG-KWL344A-1 | DT-1 | MAIN ROAD MCD SCHOOL JOHRI PUR | 1 | 990 | 19505304 | 1164 | 2019-06-29 15:00 | 405 | 1827 | 384 | 1720 | 375 | 1689 | 125 | 509.5 | 153 | 38.5 | 16.5 | 208 | 42% | 52% | 118% | 46% | 10.2229 | Loss 10-20% | 997(170.5) | 1114(214) |  | 1171(241) | 1199(214) | 1128(167)
1507 | 1251 | KWR | GOKUL PURI | KWL349 | TG-KWL349A-1 | DT-1 | G BLK GANGA VIHAR(SHAMSHAAN GHAT) | 2 | 630 | 19506686 | 566 | 2019-06-11 23:00 | 191 | 795 | 181 | 750 | 194 | 803 | 50 | 608 | 112 |  |  | 112 | 88% | 74% | 76% | 90% | 3.8389 | Loss 0-5%
1508 | 1251 | KWR | GOKUL PURI | KWL349 | TG-KWL349A-2 | DT-2 | G BLK GANGA VIHAR(SHAMSHAAN GHAT) | 2 | 630 | 19506762 | 231 | 2019-06-11 23:00 | 64 | 268 | 78 | 321 | 89 | 369 | 88 | 720 |  |  |  | 0 | 35% | 25% | 28% | 37% | 3.8389 | Loss 0-5%
1509 | 1251 | KWR | KARAWAL NAGAR | KWL010 | TG-KWL010A-1 | DT-1 | MUKUND VIHAR "A" BLK:ID | 1 | 630 | 19500537 | 598 | 2019-06-12 17:00 | 194 | 868 | 207 | 923 | 198 | 884 | 49 | 513.5 | 199.5 | 2 |  | 201.5 | 86% | 71% | 95% | 85% | 6.9589 | Loss 5-10% |  | 635(157.5) | 620(278) | 604(152.5) | 593(221.5) | 557(88)
1510 | 1251 | KWR | KARAWAL NAGAR | KWL013 | TG-KWL013A-1 | DT-1 | C BLK MUKUND VIHAR GALI NO. 9:ID | 1 | 1600 | 19505641 | 1944 | 2019-06-02 05:30 | 665 | 2676 | 591 | 2390 | 689 | 2810 | 371 | 483 | 205 | 21.5 | 2 | 228.5 | 122% | 82% | 103% | 101% | 13.461 | Loss 10-20% |  | 1037(233) | 1103(509) | 1284(434.5) | 1096(403.5) | 824(174.5)
1511 | 1251 | KWR | KARAWAL NAGAR | KWL031 | TG-KWL031A-1 | DT-1 | PREM NAGAR S/STN :ID | 2 | 630 | 19505231 | 637 | 2019-06-12 00:30 | 219 | 959 | 208 | 915 | 211 | 912 | 46 | 609 | 102 | 1.5 | 0.5 | 104 | 101% | 81% | 85% | 90% | 4.424 | Loss 0-5%
1512 | 1251 | KWR | KARAWAL NAGAR | KWL031 | TG-KWL031A-2 | DT-2 | PREM NAGAR S/STN :ID | 2 | 630 | 19505925 | 332 | 2019-06-22 18:30 | 97 | 432 | 84 | 374 | 150 | 673 | 275 | 714 |  |  |  | 0 | 46% | 35% | 53% | 41% | 4.424 | Loss 0-5%
1513 | 1251 | KWR | KARAWAL NAGAR | KWL033 | TG-KWL033A-1 | DT-1 | MAHALAXMI ENCLAVE:ID | 2 | 990 | 19506283 | 880 | 2019-06-11 22:00 | 330 | 1431 | 272 | 1190 | 279 | 1219 | 227 | 657.5 | 61.5 |  |  | 61.5 | 81% | 75% | 75% | 89% | 10.4578 | Loss 10-20% |  | 901(81) | 956(243.5) | 1119(172.5) | 905(97.5)
1514 | 1251 | KWR | KARAWAL NAGAR | KWL033 | TG-KWL033A-2 | DT-2 | MAHALAXMI ENCLAVE:ID | 2 | 630 | 19500685 | 567.545 | 2019-06-12 | 192.0934 | 822.8459 | 196.3834 | 835.4606 | 179.0683 | 765.5434 | 64.5412 | 664.5 | 53.5 | 0.5 |  | 54 | 90% | 77% | 71% | 87% | 10.4578 | Loss 10-20%
1515 | 1251 | KWR | KARAWAL NAGAR | KWL046 | TG-KWL046A-1 | DT-1 | C C KARAWAL NAGAR S/STN. NO. 2:I/D | 2 | 990 | 19500592 | 933 | 2019-06-26 15:30 | 334 | 1431 | 304 | 1317 | 295 | 1269 | 143 | 602.5 | 113 | 3 |  | 116 | 46% | 40% | 94% | 47% | 14.591 | Loss 10-20% | 778(35) | 894(121.5) |  | 784(39) | 813(84) | 824(28.5)
1516 | 1251 | KWR | KARAWAL NAGAR | KWL046 | TG-KWL046A-2 | DT-2 | C C KARAWAL NAGAR S/STN. NO. 2:I/D | 2 | 990 | 19500664 | 769 | 2019-06-03 14:30 | 230 | 1004 | 281 | 1240 | 258 | 1138 | 206 | 704 | 14.5 |  |  | 14.5 | 37% | 52% | 78% | 38% | 14.591 | Loss 10-20% |  |  |  | 814(58.5)
1517 | 1251 | KWR | KARAWAL NAGAR | KWL056 | TG-KWL056A-1 | DT-1 | KARWAL NAGAR NO.-1 DAL MILL:PL | 2 | 990 | 19505998 | 867 | 2019-06-28 16:00 | 291 | 1329 | 275 | 1250 | 300 | 1364 | 102 | 673.5 | 46 |  |  | 46 | 47% | 46% | 88% | 50% | 10.2339 | Loss 10-20%
1518 | 1251 | KWR | KARAWAL NAGAR | KWL056 | TG-KWL056A-2 | DT-2 | KARWAL NAGAR NO.-1 DAL MILL:PL | 2 | 990 | 19506728 | 929.3679 | 2019-06-01 12:00 | 293.9679 | 1276.2345 | 296.9879 | 1298.7053 | 338.4121 | 1485.3058 | 198.7907 | 585.5 | 133 | 1 |  | 134 | 53% | 54% | 94% | 55% | 10.2339 | Loss 10-20% | 1017(165) | 1106(187.5) | 975(152.5) | 986(168.5) | 968(148.5) | 1004(172)
1519 | 1251 | KWR | KARAWAL NAGAR | KWL058 | TG-KWL058A-1 | DT-1 | KARWAL NAGAR NO.-4:PL | 2 | 990 | 19504901 | 775 | 2019-06-27 15:00 | 264 | 1127 | 266 | 1137 | 245 | 1042 | 91 | 681.5 | 38 |  |  | 38 | 26% | 40% | 78% | 31% | 14.8878 | Loss 10-20% | 1028(163) | 1119(203.5) |  |  | 988(182)
1520 | 1251 | KWR | KARAWAL NAGAR | KWL058 | TG-KWL058A-2 | DT-2 | KARWAL NAGAR NO.-4:PL | 2 | 990 | 19503507 | 850 | 2019-06-28 16:00 | 278 | 1180 | 272 | 1151 | 300 | 1277 | 114 | 616.5 | 102.5 |  |  | 102.5 | 35% | 41% | 86% | 43% | 14.8878 | Loss 10-20% |  |  |  | 807(33.5) | 910(75.5) | 896(119)
1521 | 1251 | KWR | KARAWAL NAGAR | KWL059 | TG-KWL059A-1 | DT-1 | KARWAL NAGAR NO.-5 SBI KWR:PL | 3 | 990 | 19500596 | 1087.1146 | 2019-06-27 16:30 | 431.2797 | 1884.5518 | 337.7799 | 1492.4881 | 318.0551 | 1387.0091 | 454.0861 | 570.5 | 129 | 16.5 | 2 | 147.5 | 30% | 51% | 110% | 32% | 14.3272 | Loss 10-20% | 1042(173) | 1158(213.5) | 1129(183.5) | 1250(228.5) | 1212(177) | 984(154)
1522 | 1251 | KWR | KARAWAL NAGAR | KWL059 | TG-KWL059A-2 | DT-2 | KARWAL NAGAR NO.-5 SBI KWR:PL | 3 | 990 | 19502963 | 823 | 2019-06-03 14:30 | 262 | 1162 | 269 | 1202 | 292 | 1310 | 133 | 625.5 | 93.5 |  |  | 93.5 | 54% | 68% | 83% | 52% | 14.3272 | Loss 10-20% | 865(80) | 942(112) | 1053(211.5) | 1015(153.5) | 1120(232.5) | 1158(294)
1523 | 1251 | KWR | KARAWAL NAGAR | KWL059 | TG-KWL059A-3 | DT-3 | KARWAL NAGAR NO.-5 SBI KWR:PL | 3 | 990 | 19505348 | 823 | 2019-06-29 11:00 | 285 | 1232 | 275 | 1183 | 262 | 1132 | 87 | 672 | 47 |  |  | 47 | 33% | 43% | 83% | 38% | 14.3272 | Loss 10-20%
1524 | 1251 | KWR | KARAWAL NAGAR | KWL100 | TG-KWL100A-1 | DT-1 | SAHID BHAGAT SINGH CLY GALI NO 16:ID | 1 | 630 | 19506759 | 616 | 2019-06-02 07:00 | 194 | 840 | 187 | 811 | 236 | 1022 | 198 | 538.5 | 172.5 | 7 |  | 179.5 | 97% | 98% | 96% | 92% | 6.9448 | Loss 5-10% |  |  | 518(27)
1525 | 1251 | KWR | KARAWAL NAGAR | KWL264 | TG-KWL264A-1 | DT-1 | WEST KAMAL VIHAR (HVDS) INDUT. AREA:PM | 1 | 400 | 19505888 | 393 | 2019-06-30 14:30 | 148 | 669 | 112 | 508 | 134 | 605 | 140 | 638.5 | 73.5 | 3.5 |  | 77 | 57% | 44% | 98% | 55% | 2.9268 | Loss 0-5% | [5 empty] | 415(47.5)
1526 | 1251 | KWR | KARAWAL NAGAR | KWL287 | TG-KWL287A-1 | DT-1 | BABU NAGAR 1 GALI NO. 5:ID | 1 | 630 | 19506284 | 575 | 2019-06-14 11:00 | 181 | 795 | 200 | 878 | 194 | 849 | 73 | 613 | 104.5 | 0.5 |  | 105 | 83% | 88% | 91% | 79% | 8.2377 | Loss 5-10% |  |  |  | 585(32.5)
1527 | 1251 | KWR | KARAWAL NAGAR | KWL296 | TG-KWL296A-1 | DT-1 | SAHID BHAGAT SINGH CLY GALI NO 6:ID | 1 | 990 | 19500671 | 863.5283 | 2019-06-30 23:30 | 291.338 | 1285.9764 | 295.9745 | 1301.1584 | 276.2158 | 1219.2267 | 75.4945 | 621.5 | 97 |  |  | 97 | 83% | 72% | 74% | 87% | 6.3234 | Loss 5-10% |  |  | 991(43) | 833(37)
1528 | 1251 | KWR | SONIA VIHAR | KWL016 | TG-KWL016A-1 | DT-1 | CHANDU NAGAR:ID | 2 | 990 | 19500597 | 596 | 2019-06-11 00:30 | 232 | 993 | 189 | 794 | 176 | 749 | 225 | 714 |  |  |  | 0 | 60% | 44% | 49% | 57% | 3.6533 | Loss 0-5%
1529 | 1251 | KWR | SONIA VIHAR | KWL016 | TG-KWL016A-2 | DT-2 | CHANDU NAGAR:ID | 2 | 400 | 19505302 | 422 | 2019-06-10 22:00 | 143 | 580 | 131 | 538 | 148 | 615 | 67 | 570.5 | 144 | 1.5 | 1 | 146.5 | 95% | 80% | 87% | 106% | 3.6533 | Loss 0-5%
1530 | 1251 | KWR | SONIA VIHAR | KWL017 | TG-KWL017A-1 | DT-1 | E BLOCK KHAJOORI GALI NO. 3:ID | 2 | 630 | 19506119 | 465 | 2019-06-18 00:30 | 94 | 380 | 165 | 674 | 206 | 830 | 396 | 719.5 | 0.5 |  |  | 0.5 | 74% | 51% | 62% | 70% | 5.4279 | Loss 5-10%
1531 | 1251 | KWR | SONIA VIHAR | KWL017 | TG-KWL017A-2 | DT-2 | E BLOCK KHAJOORI GALI NO. 3:ID | 2 | 990 | 19505644 | 892 | 2019-06-30 23:00 | 305 | 1346 | 282 | 1226 | 304 | 1342 | 118 | 635.5 | 84 | 0.5 |  | 84.5 | 81% | 61% | 76% | 90% | 5.4279 | Loss 5-10% |  |  | 951(46.5) | 827(36.5)
1532 | 1251 | KWR | SONIA VIHAR | KWL018 | TG-KWL018A-1 | DT-1 | F BLOCK KHAJOORI GALI NO. 11&13:ID | 2 | 990 | 19504694 | 973 | 2019-06-02 22:30 | 319 | 1353 | 341 | 1463 | 313 | 1317 | 131 | 387.5 | 321 | 10.5 |  | 331.5 | 92% | 76% | 89% | 98% | 6.2874 | Loss 5-10% | 763(44.5) | 798(27.5) | 839(78.5) | 927(224.5) | 878(150)
1533 | 1251 | KWR | SONIA VIHAR | KWL018 | TG-KWL018A-2 | DT-2 | F BLOCK KHAJOORI GALI NO. 11&13:ID | 2 | 630 | 19502248 | 544 | 2019-06-03 15:30 | 155 | 677 | 224 | 988 | 166 | 724 | 290 | 549.5 | 169.5 |  |  | 169.5 | 80% | 62% | 86% | 80% | 6.2874 | Loss 5-10% |  | 656(434.5) | 697(468) | 577(190.5)
1534 | 1251 | KWR | SONIA VIHAR | KWL022 | TG-KWL022A-1 | DT-1 | B-II BLOCK NEHRU VIHAR GALI NO. 6:ID | 1 | 630 | 19506820 | 933 | 2019-06-28 14:30 | 336 | 1412 | 305 | 1272 | 292 | 1217 | 174 | 17 | 319 | 217 | 167 | 703 | 119% | 110% | 148% | 120% | 8.5328 | Loss 5-10% |  | 504(59.5) | 494(29) | 529(112) | 502(58.5)
1535 | 1251 | KWR | SONIA VIHAR | KWL026 | TG-KWL026A-1 | DT-1 | E-1, NEHRU VIHAR:ID | 1 | 990 | 19505257 | 891 | 2019-06-11 22:30 | 270 | 1221 | 308 | 1399 | 312 | 1414 | 186 | 647 | 73 |  |  | 73 | 89% | 82% | 82% | 90% | 3.4253 | Loss 0-5% |  |  | 873(27.5)
1536 | 1251 | KWR | SONIA VIHAR | KWL060 | TG-KWL060A-1 | DT-1 | C BLOCK KHAJORI MAIN MARKET | 3 | 990 | 19506447 | 869.5479 | 2019-06-13 23:00 | 236.4072 | 974.5939 | 367.6768 | 1527.8487 | 265.4639 | 1115.7695 | 497.911 | 650.5 | 67 |  |  | 67 | 87% | 61% | 73% | 88% | 4.7355 | Loss 0-5% |  | 923(87.5) | 1020(218.5) | 1086(169) | 920(125)
1537 | 1251 | KWR | SONIA VIHAR | KWL060 | TG-KWL060A-2 | DT-2 | C BLOCK KHAJORI MAIN MARKET | 3 | 990 | 19502298 | 786 | 2019-06-27 01:00 | 252 | 1009 | 234 | 936 | 301 | 1210 | 246 | 703 | 15.5 |  |  | 15.5 | 79% | 51% | 57% | 76% | 4.7355 | Loss 0-5% |  |  |  |  | 771(28)
1538 | 1251 | KWR | SONIA VIHAR | KWL060 | TG-KWL060A-3 | DT-3 | C BLOCK KHAJORI MAIN MARKET | 3 | 630 | 19506413 | 647 | 2019-06-12 | 199 | 825 | 261 | 1079 | 187 | 769 | 286 | 505.5 | 164 | 47 | 1.5 | 212.5 | 103% | 75% | 98% | 102% | 4.7355 | Loss 0-5%
1539 | 1251 | KWR | SONIA VIHAR | KWL061 | TG-KWL061A-1 | DT-1 | FATMA NURSARY CHAND BAGH MRD WZB ROAD:PL | 1 | 990 | 19502590 | 875 | 2019-06-30 23:30 | 299 | 1223 | 282 | 1151 | 294 | 1203 | 64 | 496 | 222.5 |  |  | 222.5 | 88% | 77% | 82% | 88% | 8.5864 | Loss 5-10% |  | 784(33.5) | 790(99) | 846(100.5) | 783(50)
1540 | 1251 | KWR | SONIA VIHAR | KWL063 | TG-KWL063A-1 | DT-1 | VILLAGE SABHAPUR:PM | 1 | 630 | 19502302 | 758 | 2019-06-09 23:00 | 293 | 1297 | 211 | 918 | 255 | 1125 | 329 | 304 | 266 | 95.5 | 48 | 409.5 | 115% | 86% | 95% | 120% | 10.8069 | Loss 10-20% |  |  |  | 738(119) | 735(442) | 674(192)
1541 | 1251 | KWR | SONIA VIHAR | KWL064 | TG-KWL064A-1 | DT-1 | SHERPUR CHOWK:PL | 2 | 990 | 19505767 | 784 | 2019-06-26 12:00 | 254 | 1111 | 268 | 1167 | 262 | 1143 | 48 | 710 | 9.5 |  |  | 9.5 | 39% | 48% | 79% | 45% | 14.5623 | Loss 10-20% | 1025(180.5) | 903(197.5)
1542 | 1251 | KWR | SONIA VIHAR | KWL064 | TG-KWL064A-2 | DT-2 | SHERPUR CHOWK:PL | 2 | 630 | 19506395 | 624 | 2019-06-24 15:30 | 200 | 841 | 223 | 946 | 201 | 852 | 100 | 583 | 117 | 20 |  | 137 | 58% | 82% | 99% | 58% | 14.5623 | Loss 10-20% |  |  | 665(167.5) | 671(130.5) | 665(206.5)
1543 | 1251 | KWR | SONIA VIHAR | KWL069 | TG-KWL069A-1 | DT-1 | DAYAL PUR 1 TANKI MAIN ROAD DAYAL PUR:PL | 3 | 630 | 19506842 | 435 | 2019-06-15 20:00 | 131 | 562 | 156 | 675 | 148 | 634 | 99 | 720 |  |  |  | 0 | 61% | 44% | 69% | 66% | 10.9717 | Loss 10-20%
1544 | 1251 | KWR | SONIA VIHAR | KWL069 | TG-KWL069A-2 | DT-2 | DAYAL PUR 1 TANKI MAIN ROAD DAYAL PUR:PL | 3 | 630 | 19506601 | 564 | 2019-06-11 22:30 | 154 | 651 | 165 | 695 | 246 | 1089 | 418 | 641 | 79 |  |  | 79 | 80% | 65% | 80% | 90% | 10.9717 | Loss 10-20% |  |  | 475(32.5)
1545 | 1251 | KWR | SONIA VIHAR | KWL069 | TG-KWL069A-3 | DT-3 | DAYAL PUR 1 TANKI MAIN ROAD DAYAL PUR:PL | 3 | 630 | 19506880 | 384 | 2019-06-01 15:00 | 93 | 406 | 151 | 652 | 140 | 614 | 230 | 720 |  |  |  | 0 | 44% | 41% | 61% | 56% | 10.9717 | Loss 10-20%
1546 | 1251 | KWR | SONIA VIHAR | KWL070 | TG-KWL070A-1 | DT-1 | B BLK GALI NO. 9, CHAND BAGH:ID | 2 | 630 | 19500570 | 584 | 2019-06-02 23:30 | 196 | 859 | 225 | 994 | 164 | 715 | 242 | 476 | 238.5 | 4.5 |  | 243 | 93% | 76% | 87% | 93% | 11.9171 | Loss 10-20% |  | 533(70) | 549(206) | 535(91.5) | 539(49.5)
1547 | 1251 | KWR | SONIA VIHAR | KWL070 | TG-KWL070A-2 | DT-2 | B BLK GALI NO. 9, CHAND BAGH:ID | 2 | 990 | 19505139 | 884 | 2019-06-02 15:00 | 307 | 1390 | 302 | 1372 | 276 | 1239 | 142 | 706 | 13 |  |  | 13 | 87% | 80% | 89% | 87% | 11.9171 | Loss 10-20%
1548 | 1251 | KWR | SONIA VIHAR | KWL072 | TG-KWL072A-1 | DT-1 | VILLAGE KHAJOORI NR.SCHOOL:PL | 1 | 630 | 19504805 | 601 | 2019-06-12 15:00 | 253 | 1061 | 174 | 721 | 174 | 720 | 340 | 466.5 | 251 | 1.5 |  | 252.5 | 86% | 64% | 95% | 86% | 18.023 | Loss 10-20% |  | 517(74.5) |  | 579(165) | 538(79)
1549 | 1251 | KWR | SONIA VIHAR | KWL076 | TG-KWL076A-1 | DT-1 | A BL MAIN ROAD DAYALPUR:PL | 1 | 990 | 19506896 | 988 | 2019-06-16 02:00 | 353 | 1486 | 286 | 1185 | 349 | 1457 | 287 | 540.5 | 168.5 | 7 |  | 175.5 | 100% | 69% | 88% | 94% | 13.0986 | Loss 10-20% |  | 838(24) | 822(83) | 897(86) | 886(63)
1550 | 1251 | KWR | SONIA VIHAR | KWL079 | TG-KWL079A-1 | DT-1 | B BLK SADAT PUR GALI NO. 8:ID | 1 | 400 | 19504409 | 369 | 2019-06-29 23:00 | 141 | 631 | 112 | 491 | 115 | 508 | 132 | 578 | 139.5 | 2.5 |  | 142 | 91% | 59% | 72% | 92% | 2.9931 | Loss 0-5%
1551 | 1251 | KWR | SONIA VIHAR | KWL080 | TG-KWL080A-1 | DT-1 | BIHARI PUR VILLNR. NLA KHJURI PUST RD:PL | 1 | 990 | 19506903 | 842 | 2019-06-30 14:30 | 309 | 1384 | 257 | 1170 | 276 | 1266 | 186 | 663.5 | 56 |  |  | 56 | 78% | 64% | 85% | 78% | 20.6627 | Loss 20-30% |  |  | 784(24)
1552 | 1251 | KWR | SONIA VIHAR | KWL083 | TG-KWL083A-1 | DT-1 | L BLK SADAT PUR:ID | 1 | 990 | 19500560 | 893.8565 | 2019-06-30 | 286.146 | 1304.1016 | 295.6431 | 1344.5655 | 312.0675 | 1416.2997 | 98.4163 | 661.5 | 58 | 0.5 |  | 58.5 | 90% | 70% | 68% | 90% | 6.5996 | Loss 5-10%
1553 | 1251 | KWR | SONIA VIHAR | KWL085 | TG-KWL085A-1 | DT-1 | B BLK PUSTA 1 SONIA VIHAR GALI NO 1 | 1 | 630 | 19506042 | 589 | 2019-06-08 09:30 | 176 | 745 | 202 | 854 | 210 | 883 | 126 | 616 | 89.5 | 1 |  | 90.5 | 90% | 92% | 93% | 90% | 7.1229 | Loss 5-10% |  |  |  | 611(728)
1554 | 1251 | KWR | SONIA VIHAR | KWL093 | TG-KWL093A-1 | DT-1 | CHAUHAN PATTI PUSTA VILL SONIA VIHAR:PL | 1 | 630 | 19506301 | 714 | 2019-06-29 22:30 | 218 | 952 | 262 | 1154 | 234 | 1025 | 177 | 347 | 328 | 33.5 | 3.5 | 365 | 100% | 99% | 103% | 113% | 7.2728 | Loss 5-10% |  | 652(76) | 722(256.5) | 726(276.5) |  | 592(31.5)
1555 | 1251 | KWR | SONIA VIHAR | KWL096 | TG-KWL096A-1 | DT-1 | B-I, NEHRU VIHAR:ID | 1 | 990 | 19500614 | 1166 | 2019-06-29 23:00 | 389 | 1610 | 380 | 1576 | 397 | 1648 | 62 | 313.5 | 268 | 78 | 60 | 406 | 116% | 86% | 89% | 118% | 7.9336 | Loss 5-10% |  | 969(168.5) | 1043(328) | 1098(285)
1556 | 1251 | KWR | SONIA VIHAR | KWL113 | TG-KWL113A-1 | DT-1 | SONIA VIHAR "B" BLK GALI NO-27 | 1 | 400 | 19506291 | 524 | 2019-06-10 05:00 | 193 | 808 | 181 | 756 | 150 | 616 | 172 | 128 | 519.5 | 58.5 | 6.5 | 584.5 | 131% | 95% | 102% | 113% | 7.5588 | Loss 5-10%
1557 | 1251 | KWR | SONIA VIHAR | KWL115 | TG-KWL115A-1 | DT-1 | C 1 KHAJOORI GALI NO. 24:PM | 1 | 400 | 19502314 | 439 | 2019-06-02 23:00 | 152 | 636 | 89 | 365 | 198 | 832 | 406 | 299.5 | 307.5 | 84 | 29 | 420.5 | 107% | 86% | 94% | 110% | 4.8874 | Loss 0-5%
1558 | 1251 | KWR | SONIA VIHAR | KWL119 | TG-KWL119A-1 | DT-1 | F BLK DAYAL PUR : ID | 1 | 630 | 19503341 | 500 | 2019-06-29 23:30 | 213 | 952 | 139 | 614 | 148 | 664 | 316 | 674 | 46 |  |  | 46 | 79% | 61% | 69% | 79% | 11.7189 | Loss 10-20%
1559 | 1251 | KWR | SONIA VIHAR | KWL121 | TG-KWL121A-1 | DT-1 | JEEVAN JYOTI SCHOOL SADAT PUR : ID | 2 | 630 | 19506411 | 276 | 2019-06-11 23:00 | 114 | 512 | 81 | 368 | 81 | 361 | 148 | 720 |  |  |  | 0 | 42% | 26% | 32% | 44% | 5.9491 | Loss 5-10%
1560 | 1251 | KWR | SONIA VIHAR | KWL121 | TG-KWL121A-2 | DT-2 | JEEVAN JYOTI SCHOOL SADAT PUR : ID | 2 | 990 | 19500551 | 1161.4047 | 2019-06-27 | 414.5778 | 1811.5699 | 392.1803 | 1725.8417 | 354.6466 | 1563.8355 | 217.9078 | 383.5 | 192.5 | 64.5 | 79.5 | 336.5 | 117% | 79% | 92% | 117% | 5.9491 | Loss 5-10% |  | 895(96.5) | 1061(200) | 980(141)
1561 | 1251 | KWR | SONIA VIHAR | KWL127 | TG-KWL127A-1 | DT-1 | NIKKA PLASTIC TUKMEERPUR VILLAGE:PM | 1 | 400 | 19505123 | 501 | 2019-06-17 20:00 | 165 | 662 | 166 | 674 | 169 | 683 | 18 | 487 | 130.5 | 32 | 67.5 | 230 | 117% | 117% | 125% | 116% | 29.45 | Loss 20-30% | 446(400.5) | 564(513.5) | 716(242) | 374(116.5) | 397(256.5) | 415(414)
1562 | 1251 | KWR | SONIA VIHAR | KWL145 | TG-KWL145A-1 | DT-1 | SHRI RAM COLONY B BLK RAMLILA GROUND | 1 | 400 | 19506532 | 487.9528 | 2019-06-30 14:30 | 196.3645 | 800.2791 | 110.7378 | 443.377 | 180.8505 | 734.5673 | 329.0053 | 439.5 | 266.5 | 9.5 | 2.5 | 278.5 | 120% | 103% | 122% | 98% | 10.6186 | Loss 10-20% |  |  |  | 490(132.5) | 414(155.5)
1563 | 1251 | KWR | SONIA VIHAR | KWL146 | TG-KWL146A-1 | DT-1 | C BLK SHRI RAM COLONY :PLM | 1 | 630 | 19506504 | 697.4431 | 2019-06-14 06:00 | 155.4979 | 636.4779 | 299.0081 | 1262.3832 | 242.9371 | 1014.5206 | 545.944 | 286.5 | 417.5 | 11.5 | 1.5 | 430.5 | 93% | 111% | 103% | 98% | 10.0862 | Loss 10-20% |  |  |  | 640(422) | 694(258)
1564 | 1251 | KWR | SONIA VIHAR | KWL147 | TG-KWL147A-1 | DT-1 | SHRI RAM COLONY D BLK:PLM | 1 | 630 | 19506716 | 788 | 2019-06-30 01:30 | 259 | 1094 | 301 | 1302 | 228 | 968 | 292 | 554.5 | 162.5 | 0.5 | 1.5 | 164.5 | 125% | 111% | 120% | 86% | 3.6386 | Loss 0-5% |  | 468(26) |  | 524(78.5) | 477(53)
1565 | 1251 | KWR | SONIA VIHAR | KWL154 | TG-KWL154A-1 | DT-1 | SHRI RAM CLY E BLK GN 3 NR MASJID :PM | 1 | 400 | 19504596 | 388 | 2019-06-02 15:00 | 124 | 530 | 122 | 519 | 143 | 614 | 89 | 296.5 | 385 | 37 |  | 422 | 94% | 85% | 97% | 95% | 13.0373 | Loss 10-20% |  | 355(287.5) | 376(229.5) | 396(477) | 401(315) | 351(129.5)
1566 | 1251 | KWR | SONIA VIHAR | KWL157 | TG-KWL157A-1 | DT-1 | D BLOCK GALI NO 2 DAYAL PUR | 2 | 990 | 19504362 | 972 | 2019-06-28 23:00 | 292 | 1180 | 341 | 1386 | 339 | 1374 | 200 | 526 | 180 | 13 |  | 193 | 98% | 81% | 90% | 98% | 7.3168 | Loss 5-10% |  |  | 861(91) | 852(59)
1567 | 1251 | KWR | SONIA VIHAR | KWL157 | TG-KWL157A-2 | DT-2 | D BLOCK GALI NO 2 DAYAL PUR | 2 | 630 | 19505019 | 639 | 2019-06-11 23:00 | 191 | 819 | 214 | 917 | 235 | 1004 | 160 | 614 | 96 | 6.5 | 0.5 | 103 | 97% | 68% | 73% | 101% | 7.3168 | Loss 5-10%
1568 | 1251 | KWR | SONIA VIHAR | KWL158 | TG-KWL158A-1 | DT-1 | D-3 NEHRU VIHAR : ID | 2 | 990 | 19500584 | 874 | 2019-06-10 23:00 | 250 | 1056 | 339 | 1438 | 285 | 1192 | 336 | 504 | 215.5 |  |  | 215.5 | 88% | 73% | 79% | 88% | 7.1995 | Loss 5-10% | 758(28.5) | 1035(361.5) | 927(255.5) | 1021(479.5) | 911(324) | 767(42.5)
1569 | 1251 | KWR | SONIA VIHAR | KWL158 | TG-KWL158A-2 | DT-2 | D-3 NEHRU VIHAR : ID | 2 | 990 | 19505769 | 813 | 2019-06-28 23:00 | 335 | 1490 | 199 | 881 | 279 | 1248 | 531 | 704 | 15.5 |  |  | 15.5 | 79% | 67% | 73% | 82% | 7.1995 | Loss 5-10% |  | 607(30) | 785(385) | 597(64)
1570 | 1251 | KWR | SONIA VIHAR | KWL234 | TG-KWL234A-1 | DT-1 | B BLK SHRI RAM COLONY :PL | 1 | 990 | 19506536 | 1156 | 2019-06-30 01:30 | 424 | 1808 | 445 | 1885 | 287 | 1202 | 648 | 533 | 184 | 1 | 1 | 186 | 117% | 100% | 114% | 87% | 14.3165 | Loss 10-20% |  | 829(104) |  | 927(52) | 916(110.5)
1571 | 1251 | KWR | SONIA VIHAR | KWL235 | TG-KWL235A-1 | DT-1 | A BLK SHRI RAM CLY NEAR GALI 26:PL | 1 | 630 | 19505324 | 755 | 2019-06-30 01:30 | 277 | 1189 | 210 | 887 | 268 | 1146 | 283 | 638 | 78.5 |  | 1.5 | 80 | 120% | 103% | 116% | 82% | 7.6651 | Loss 5-10% |  | 545(62) |  | 594(105) | 715(42.5)
1572 | 1251 | KWR | SONIA VIHAR | KWL249 | TG-KWL249A-1 | DT-1 | A BLOCK SHRI RAM CLY. NEAR SERVICE RD:PL | 1 | 630 | 19506533 | 739 | 2019-06-30 | 207 | 870 | 304 | 1307 | 228 | 964 | 398 | 465.5 | 252.5 | 0.5 | 0.5 | 253.5 | 117% | 83% | 91% | 90% | 10.0142 | Loss 10-20% |  | 513(79) |  | 623(53) | 515(95.5)
1573 | 1251 | KWR | SONIA VIHAR | KWL251 | TG-KWL251A-1 | DT-1 | A BLK KHAJOORI:PL | 1 | 630 | 19505294 | 747 | 2019-06-01 05:00 | 227 | 923 | 284 | 1159 | 236 | 968 | 217 | 669.5 | 49.5 |  | 0.5 | 50 | 119% | 60% | 80% | 81% | 12.4516 | Loss 10-20%
1574 | 1251 | KWR | SONIA VIHAR | KWL292 | TG-KWL292A-1 | DT-1 | E BLOCK CHAND BAGH:PL | 1 | 630 | 19506537 | 810 | 2019-06-30 01:30 | 242 | 1030 | 280 | 1194 | 289 | 1244 | 194 | 109 | 410.5 | 112.5 | 87.5 | 610.5 | 129% | 118% | 125% | 118% | 11.2623 | Loss 10-20% | 488(26) | 616(358) |  | 683(179)
1575 | 1251 | KWR | SONIA VIHAR | KWL295 | TG-KWL295A-1 | DT-1 | K BLK SADAT PUR EXT. GALI NO. 51:ID | 1 | 990 | 19500647 | 876 | 2019-06-09 23:00 | 265 | 1156 | 302 | 1322 | 308 | 1366 | 192 | 581.5 | 138.5 |  |  | 138.5 | 85% | 62% | 73% | 88% | 5.0709 | Loss 5-10% |  | 886(98) |  | 988(254) | 946(188.5) | 752(29.5)
1576 | 1251 | KWR | SONIA VIHAR | KWL297 | TG-KWL297A-1 | DT-1 | B BLK SHRI RAM COLONY SAITAN CHOWK:PL | 1 | 990 | 19506034 | 1222 | 2019-06-15 07:30 | 493 | 2032 | 393 | 1595 | 337 | 1358 | 592 | 169.5 | 463.5 | 74 | 11 | 548.5 | 106% | 123% | 115% | 106% | 8.4841 | Loss 5-10% | 694(165.5) |  |  |  | 901(30)
1577 | 1251 | KWR | SONIA VIHAR | KWL298 | TG-KWL298A-1 | DT-1 | Delhi Police Training Center:PM | 1 | 400 | 19506396 | 460 | 2019-06-18 04:00 | 162 | 623 | 151 | 576 | 147 | 567 | 53 | 382 | 307.5 | 26.5 | 3 | 337 | 115% | 80% | 114% | 91% | 2.5361 | Loss 0-5% |  |  |  | 384(108.5) | 363(140)
1578 | 1260 | NNG | C-4 NANDNAGRI | NGR006 | TG-NGR006A-1 | DT-1 | JANTA FLAT S/S NO.1 GTB ENCLAVE:ID | 3 | 990 | 19505505 | 956.1592 | 2019-06-30 23:30 | 314.798 | 1386.409 | 276.0916 | 1206.6412 | 365.2696 | 1618.9593 | 358.0519 | 609.5 | 105.5 | 3.5 |  | 109 | 93% | 55% | 63% | 97% | 6.4544 | Loss 5-10% |  | 917(71) | 926(101.5) | 958(55)
1579 | 1260 | NNG | C-4 NANDNAGRI | NGR006 | TG-NGR006A-2 | DT-2 | JANTA FLAT S/S NO.1 GTB ENCLAVE:ID | 3 | 630 | 19506194 | 734 | 2019-06-18 02:00 | 318 | 1273 | 285 | 1172 | 130 | 509 | 720 | 719 |  |  | 0.5 | 0.5 | 116% | 38% | 44% | 59% | 6.4544 | Loss 5-10% |  | 519(25)
1580 | 1260 | NNG | C-4 NANDNAGRI | NGR006 | TG-NGR006A-3 | DT-3 | JANTA FLAT S/S NO.1 GTB ENCLAVE:ID | 3 | 630 | 19506507 | 385 | 2019-06-29 23:30 | 114 | 466 | 96 | 391 | 175 | 716 | 295 | 720 |  |  |  | 0 | 60% | 38% | 45% | 61% | 6.4544 | Loss 5-10%
1581 | 1260 | NNG | C-4 NANDNAGRI | NGR007 | TG-NGR007A-1 | DT-1 | JANTA FLAT S/S NO.2 GTB ENCLAVE:ID | 3 | 630 | 19505795 | 525 | 2019-06-30 23:30 | 174 | 736 | 217 | 939 | 134 | 570 | 321 | 658 | 61.5 |  |  | 61.5 | 83% | 51% | 58% | 83% | 5.62 | Loss 5-10% |  |  | 493(25.5)
1582 | 1260 | NNG | C-4 NANDNAGRI | NGR007 | TG-NGR007A-2 | DT-2 | JANTA FLAT S/S NO.2 GTB ENCLAVE:ID | 3 | 630 | 19505794 | 593 | 2019-06-03 | 164 | 687 | 186 | 786 | 244 | 1049 | 324 | 616 | 102.5 | 1.5 |  | 104 | 94% | 53% | 64% | 94% | 5.62 | Loss 5-10% |  | 528(30.5) | 602(109) | 602(65) | 506(28)
1583 | 1260 | NNG | C-4 NANDNAGRI | NGR007 | TG-NGR007A-3 | DT-3 | JANTA FLAT S/S NO.2 GTB ENCLAVE:ID | 3 | 630 | 19505801 | 518 | 2019-06-12 00:30 | 218 | 944 | 114 | 480 | 186 | 788 | 409 | 681 | 38.5 |  |  | 38.5 | 82% | 48% | 61% | 82% | 5.62 | Loss 5-10% |  |  | 535(44.5)
1584 | 1260 | NNG | C-4 NANDNAGRI | NGR008 | TG-NGR008A-1 | DT-1 | JANTA FLAT S/S NO.3 GTB ENCLAVE:ID | 2 | 990 | 19505360 | 752 | 2019-06-30 23:30 | 202 | 849 | 267 | 1140 | 283 | 1193 | 321 | 688.5 | 31 |  |  | 31 | 76% | 52% | 55% | 76% | 8.9519 | Loss 5-10%
1585 | 1260 | NNG | C-4 NANDNAGRI | NGR008 | TG-NGR008A-2 | DT-2 | JANTA FLAT S/S NO.3 GTB ENCLAVE:ID | 2 | 990 | 19505177 | 926 | 2019-06-30 00:30 | 222 | 910 | 303 | 1264 | 401 | 1678 | 666 | 634 | 84.5 | 1 |  | 85.5 | 94% | 56% | 63% | 88% | 8.9519 | Loss 5-10% |  |  | 990(79.5) | 823(34)
1586 | 1260 | NNG | C-4 NANDNAGRI | NGR014 | TG-NGR014A-1 | DT-1 | I.J K BLOCK SUNDER NAGARI:K | 2 | 990 | 19502680 | 876 | 2019-06-11 23:00 | 267 | 1129 | 303 | 1289 | 306 | 1293 | 162 | 503.5 | 215.5 |  |  | 215.5 | 88% | 81% | 76% | 88% | 5.7344 | Loss 5-10% |  | 791(55.5) | 834(171.5) | 877(134.5) | 757(51)
1587 | 1260 | NNG | C-4 NANDNAGRI | NGR014 | TG-NGR014A-2 | DT-2 | I.J K BLOCK SUNDER NAGARI:K | 2 | 990 | 19505808 | 719 | 2019-06-28 23:30 | 227 | 956 | 213 | 906 | 279 | 1187 | 259 | 295 | 6.5 |  |  | 6.5 | 72% | 58% | 63% | 73% | 5.7344 | Loss 5-10%
1588 | 1260 | NNG | C-4 NANDNAGRI | NGR015 | TG-NGR015A-1 | DT-1 | MN BLOCK SUNDER NAGARI:K | 3 | 630 | 19502676 | 287 | 2019-06-11 | 68 | 281 | 121 | 503 | 99 | 413 | 194 | 719.5 |  |  |  | 0 | 46% | 39% | 40% | 45% | 15.9324 | Loss 10-20%
1589 | 1260 | NNG | C-4 NANDNAGRI | NGR015 | TG-NGR015A-2 | DT-2 | MN BLOCK SUNDER NAGARI:K | 3 | 630 | 19506466 | 555 | 2019-06-11 | 176 | 740 | 169 | 708 | 209 | 880 | 158 | 547 | 172.5 |  |  | 172.5 | 88% | 74% | 77% | 87% | 15.9324 | Loss 10-20% |  |  |  | 515(31)
1590 | 1260 | NNG | C-4 NANDNAGRI | NGR015 | TG-NGR015A-3 | DT-3 | MN BLOCK SUNDER NAGARI:K | 3 | 630 | 19502650 | 332 | 2019-06-10 22:30 | 106 | 453 | 87 | 376 | 139 | 605 | 202 | 719.5 |  |  |  | 0 | 51% | 42% | 49% | 53% | 15.9324 | Loss 10-20%
1591 | 1260 | NNG | C-4 NANDNAGRI | NGR016 | TG-NGR016A-1 | DT-1 | E-1 NAND NAGARI PK WALA GAGAN CINEMA:PL | 1 | 630 | 19505497 | 553 | 2019-06-14 16:00 | 142 | 595 | 199 | 849 | 211 | 913 | 291 | 634.5 | 85.5 |  |  | 85.5 | 84% | 70% | 88% | 83% | 3.5431 | Loss 0-5% |  |  | 673(37) | 529(81)
1592 | 1260 | NNG | C-4 NANDNAGRI | NGR018 | TG-NGR018A-1 | DT-1 | E-4 NAND NAGARI:ID | 3 | 630 | 19506221 | 635 | 2019-06-08 00:30 | 234 | 1020 | 226 | 980 | 175 | 748 | 254 | 502 | 195.5 | 20 | 0.5 | 216 | 101% | 82% | 93% | 99% | 5.9363 | Loss 5-10% | 510(33) | 616(213) | 697(250) | 677(208.5) | 532(130.5)
1593 | 1260 | NNG | C-4 NANDNAGRI | NGR018 | TG-NGR018A-2 | DT-2 | E-4 NAND NAGARI:ID | 3 | 630 | 19506220 | 631 | 2019-06-29 23:00 | 206 | 865 | 250 | 1067 | 175 | 740 | 285 | 681.5 | 36 |  | 0.5 | 36.5 | 82% | 75% | 80% | 100% | 5.9363 | Loss 5-10% |  |  |  | 580(29)
1594 | 1260 | NNG | C-4 NANDNAGRI | NGR018 | TG-NGR018A-3 | DT-3 | E-4 NAND NAGARI:ID | 3 | 630 | 19506699 | 631 | 2019-06-08 21:00 | 193 | 846 | 223 | 985 | 215 | 938 | 122 | 537.5 | 178 | 2 | 0.5 | 180.5 | 91% | 84% | 92% | 100% | 5.9363 | Loss 5-10% |  | 575(97.5) | 588(276) | 526(127) | 489(48)
1595 | 1260 | NNG | C-4 NANDNAGRI | NGR019 | TG-NGR019A-1 | DT-1 | JAGAT PURI EXT.NO.1:ID | 1 | 990 | 19505917 | 883 | 2019-06-11 23:30 | 293 | 1205 | 340 | 1390 | 250 | 1017 | 323 | 583.5 | 136.5 |  |  | 136.5 | 89% | 65% | 69% | 89% | 5.6822 | Loss 5-10% |  | 984(39) | 836(111.5) | 865(72)
1596 | 1260 | NNG | C-4 NANDNAGRI | NGR020 | TG-NGR020A-1 | DT-1 | JAGAT PURI EXT.NO.2:ID | 1 | 990 | 19502686 | 755 | 2019-06-11 23:00 | 313 | 1292 | 265 | 1085 | 176 | 723 | 498 | 695 | 25 |  |  | 25 | 76% | 54% | 56% | 76% | 4.9826 | Loss 0-5%
1597 | 1260 | NNG | C-4 NANDNAGRI | NGR021 | TG-NGR021A-1 | DT-1 | A-4 NAND NAGARI:ID | 3 | 630 | 19504975 | 460 | 2019-06-30 23:00 | 204 | 858 | 127 | 543 | 129 | 565 | 304 | 712.5 | 6 |  |  | 6 | 72% | 62% | 63% | 73% | 8.6786 | Loss 5-10%
1598 | 1260 | NNG | C-4 NANDNAGRI | NGR021 | TG-NGR021A-2 | DT-2 | A-4 NAND NAGARI:ID | 3 | 990 | 19505803 | 789 | 2019-06-30 00:30 | 315 | 1331 | 214 | 890 | 259 | 1077 | 384 | 642.5 | 75 |  |  | 75 | 80% | 70% | 79% | 79% | 8.6786 | Loss 5-10%
1599 | 1260 | NNG | C-4 NANDNAGRI | NGR021 | TG-NGR021A-3 | DT-3 | A-4 NAND NAGARI:ID | 3 | 990 | 19505342 | 805 | 2019-06-14 15:00 | 313 | 1442 | 167 | 758 | 325 | 1463 | 695 | 683.5 | 34.5 |  |  | 34.5 | 75% | 65% | 81% | 75% | 8.6786 | Loss 5-10%
1600 | 1260 | NNG | C-4 NANDNAGRI | NGR022 | TG-NGR022A-1 | DT-1 | B-4 NAND NAGARI AKHADA WALA :ID | 4 | 990 | 19502143 | 592 | 2019-06-29 23:30 | 216 | 911 | 209 | 872 | 166 | 687 | 207 | 720 |  |  |  | 0 | 59% | 53% | 50% | 60% | 4.4724 | Loss 0-5%
1601 | 1260 | NNG | C-4 NANDNAGRI | NGR022 | TG-NGR022A-2 | DT-2 | B-4 NAND NAGARI AKHADA WALA :ID | 4 | 990 | 19503369 | 683 | 2019-06-30 23:30 | 203 | 837 | 218 | 895 | 262 | 1081 | 221 | 720 |  |  |  | 0 | 68% | 66% | 61% | 69% | 4.4724 | Loss 0-5% | 598(64.5) | 640(339.5) | 722(526.5) | 772(571.5) | 660(462.5) | 596(296)
1602 | 1260 | NNG | C-4 NANDNAGRI | NGR022 | TG-NGR022A-3 | DT-3 | B-4 NAND NAGARI AKHADA WALA :ID | 4 | 630 | 19505435 | 526 | 2019-06-01 23:00 | 168 | 704 | 216 | 913 | 142 | 586 | 287 | 693 | 27 |  |  | 27 | 76% | 66% | 67% | 84% | 4.4724 | Loss 0-5%
1603 | 1260 | NNG | C-4 NANDNAGRI | NGR022 | TG-NGR022A-4 | DT-4 | B-4 NAND NAGARI AKHADA WALA :ID | 4 | 630 | 19506004 | 501 | 2019-06-29 23:30 | 170 | 725 | 194 | 839 | 137 | 598 | 209 | 671.5 | 48 |  |  | 48 | 78% | 64% | 71% | 80% | 4.4724 | Loss 0-5% |  |  | 525(40)
1604 | 1260 | NNG | C-4 NANDNAGRI | NGR023 | TG-NGR023A-1 | DT-1 | C BLOCK COMPLAINT CENTRE NNG:ID | 4 | 990 | 19502651 | 609 | 2019-06-29 23:30 | 204 | 855 | 223 | 949 | 182 | 763 | 161 | 720 |  |  |  | 0 | 61% | 57% | 61% | 62% | 8.2969 | Loss 5-10%
1605 | 1260 | NNG | C-4 NANDNAGRI | NGR023 | TG-NGR023A-2 | DT-2 | C BLOCK COMPLAINT CENTRE NNG:ID | 4 | 990 | 19505918 | 869 | 2019-06-30 | 296 | 1316 | 280 | 1250 | 294 | 1294 | 59 | 643.5 | 76 |  |  | 76 | 88% | 68% | 76% | 81% | 8.2969 | Loss 5-10% |  |  | 879(38)
1606 | 1260 | NNG | C-4 NANDNAGRI | NGR023 | TG-NGR023A-3 | DT-3 | C BLOCK COMPLAINT CENTRE NNG:ID | 4 | 630 | 19502635 | 585 | 2019-06-29 23:30 | 203 | 838 | 197 | 805 | 185 | 766 | 63 | 532.5 | 183.5 | 3 |  | 186.5 | 92% | 73% | 73% | 93% | 8.2969 | Loss 5-10% |  | 519(51.5) | 595(186.5) | 556(143.5) | 544(77.5)
1607 | 1260 | NNG | C-4 NANDNAGRI | NGR023 | TG-NGR023A-4 | DT-4 | C BLOCK COMPLAINT CENTRE NNG:ID | 4 | 630 | 19505379 | 431 | 2019-06-11 22:30 | 140 | 615 | 101 | 436 | 191 | 837 | 348 | 720 |  |  |  | 0 | 66% | 56% | 65% | 68% | 8.2969 | Loss 5-10%
1608 | 1260 | NNG | C-4 NANDNAGRI | NGR030 | TG-NGR030A-1 | DT-1 | MANDOLI S/S-4 (PANI KI TANKI) :PL | 2 | 990 | 19506090 | 838 | 2019-06-12 01:00 | 282 | 1137 | 252 | 1014 | 305 | 1235 | 192 | 665.5 | 49.5 |  |  | 49.5 | 85% | 60% | 73% | 80% | 10.2836 | Loss 10-20%
1609 | 1260 | NNG | C-4 NANDNAGRI | NGR030 | TG-NGR030A-2 | DT-2 | MANDOLI S/S-4 (PANI KI TANKI) :PL | 2 | 400 | 19506385 | 235 | 2019-06-13 10:00 | 84 | 337 | 88 | 352 | 63 | 251 | 94 | 716.5 |  |  |  | 0 | 26% | 35% | 59% | 27% | 10.2836 | Loss 10-20%
1610 | 1260 | NNG | C-4 NANDNAGRI | NGR035 | TG-NGR035A-1 | DT-1 | MANDOLI EXTN.NO.1,GALI NO.-9:ID | 2 | 400 | 19502142 | 388 | 2019-06-02 21:30 | 155 | 702 | 116 | 521 | 117 | 524 | 179 | 614 | 96 | 9 |  | 105 | 94% | 75% | 86% | 97% | 8.9484 | Loss 5-10% |  | 403(157) | 419(287) | 410(147) |  | 318(27)
1611 | 1260 | NNG | C-4 NANDNAGRI | NGR035 | TG-NGR035A-2 | DT-2 | MANDOLI EXTN.NO.1,GALI NO.-9:ID | 2 | 990 | 19506611 | 874 | 2019-06-10 22:00 | 307 | 1305 | 236 | 996 | 331 | 1418 | 378 | 621 | 97.5 |  |  | 97.5 | 83% | 80% | 88% | 88% | 8.9484 | Loss 5-10%
1612 | 1260 | NNG | C-4 NANDNAGRI | NGR044 | TG-NGR044A-1 | DT-1 | SAFAI KARAMCHARI NAND NAGARI-E BLK:ID | 1 | 400 | 19503383 | 336 | 2019-06-09 23:00 | 112 | 500 | 124 | 549 | 100 | 445 | 90 | 592.5 | 127.5 |  |  | 127.5 | 83% | 60% | 62% | 84% | 5.4694 | Loss 5-10% |  |  | 327(69) | 310(24)
1613 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1002 | TG-LO1002A-1 | DT-1 | B-BLOCK MEET NAGAR:ID | 2 | 990 | 19505636 | 968.3635 | 2019-06-11 01:00 | 239.9317 | 1005.9609 | 421.3517 | 1775.2335 | 307.0801 | 1288.0338 | 674.0583 | 621 | 82 | 2.5 |  | 84.5 | 98% | 73% | 82% | 89% | 8.8071 | Loss 5-10% |  | 498(42) | 645(180) | 606(80.5) | 519(37.5)
1614 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1002 | TG-LO1002A-2 | DT-2 | B-BLOCK MEET NAGAR:ID | 2 | 990 | 19502162 | 754 | 2019-06-29 23:30 | 223 | 923 | 282 | 1169 | 249 | 1024 | 214 | 700.5 | 7 |  |  | 7 | 73% | 57% | 66% | 76% | 8.8071 | Loss 5-10% |  | 653(162.5) | 748(334)
1615 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1009 | TG-LO1009A-1 | DT-1 | GOKUL PUR VILL NO.KAPOOR WALA PETROL:PL | 3 | 990 | 19506309 | 770 | 2019-06-26 15:30 | 234 | 1015 | 265 | 1151 | 271 | 1170 | 146 | 683 | 35 |  |  | 35 | 43% | 37% | 78% | 45% | 7.8914 | Loss 5-10% |  | 884(79) | 914(132.5) | 957(170.5) | 958(148.5) | 891(145.5)
1616 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1009 | TG-LO1009A-2 | DT-2 | GOKUL PUR VILL NO.KAPOOR WALA PETROL:PL | 3 | 630 | 19500607 | 307.7469 | 2019-06-29 14:00 | 80.2314 | 342.3281 | 137.0345 | 586.4193 | 90.481 | 387.2003 | 225.0358 | 718 |  |  |  | 0 | 26% | 24% | 49% | 27% | 7.8914 | Loss 5-10%
1617 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1009 | TG-LO1009A-3 | DT-3 | GOKUL PUR VILL NO.KAPOOR WALA PETROL:PL | 3 | 630 | 19506226 | 235 | 2019-06-12 18:00 | 64 | 254 | 93 | 366 | 78 | 306 | 97 | 718.5 |  |  |  | 0 | 37% | 31% | 37% | 36% | 7.8914 | Loss 5-10%
1618 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1017 | TG-LO1017A-1 | DT-1 | E JYOTI NAGAR BEHAIND JOYATI NURSING:ID | 4 | 630 | 19502178 | 578 | 2019-06-30 01:30 | 143 | 624 | 209 | 923 | 226 | 1002 | 345 | 580.5 | 48 | 0.5 |  | 48.5 | 92% | 66% | 61% | 84% | 7.002 | Loss 5-10% |  | 716(130) | 797(236) | 706(156) | 581(107)
1619 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1017 | TG-LO1017A-2 | DT-2 | E JYOTI NAGAR BEHAIND JOYATI NURSING:ID | 4 | 990 | 19504503 | 1223 | 2019-06-11 23:30 | 299 | 1281 | 407 | 1753 | 517 | 2254 | 843 | 409 | 108.5 | 28 | 29 | 165.5 | 120% | 73% | 95% | 124% | 7.002 | Loss 5-10%
1620 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1017 | TG-LO1017A-3 | DT-3 | E JYOTI NAGAR BEHAIND JOYATI NURSING:ID | 4 | 990 | 19502206 | 1003 | 2019-06-30 01:30 | 394 | 1696 | 354 | 1507 | 255 | 1076 | 551 | 590 | 113 | 9.5 | 0.5 | 123 | 101% | 71% | 67% | 97% | 7.002 | Loss 5-10%
1621 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1017 | TG-LO1017A-4 | DT-4 | E JYOTI NAGAR BEHAIND JOYATI NURSING:ID | 4 | 630 | 19506358 | 587 | 2019-06-30 01:00 | 166 | 690 | 219 | 922 | 202 | 850 | 206 | 661.5 | 53.5 | 1 |  | 54.5 | 93% | 63% | 80% | 84% | 7.002 | Loss 5-10%
1622 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1024 | TG-LO1024A-1 | DT-1 | EAST OF LONI ROAD,MIG,S/STN-7:ID | 2 | 400 | 19502176 | 365 | 2019-06-03 02:30 | 112 | 481 | 114 | 485 | 139 | 598 | 115 | 650 | 69 | 0.5 |  | 69.5 | 91% | 46% | 61% | 89% | 4.112 | Loss 0-5% |  |  |  | 327(26.5)
1623 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1024 | TG-LO1024A-2 | DT-2 | EAST OF LONI ROAD,MIG,S/STN-7:ID | 2 | 400 | 19502202 | 335 | 2019-06-11 23:30 | 146 | 617 | 95 | 404 | 93 | 401 | 215 | 652 | 68 |  |  | 68 | 83% | 45% | 67% | 84% | 4.112 | Loss 0-5% |  | 395(76) | 465(149) | 332(25.5)
1624 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1028 | TG-LO1028A-1 | DT-1 | D-BLOCK ASHOK NAGAR GALI NO-3:ID | 3 | 990 | 19503018 | 950 | 2019-06-30 | 381 | 1641 | 319 | 1392 | 250 | 1096 | 472 | 682.5 | 29.5 | 4.5 |  | 34 | 96% | 65% | 70% | 96% | 5.9352 | Loss 5-10%
1625 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1028 | TG-LO1028A-2 | DT-2 | D-BLOCK ASHOK NAGAR GALI NO-3:ID | 3 | 630 | 19503472 | 549 | 2019-06-10 23:30 | 170 | 759 | 178 | 800 | 201 | 892 | 118 | 619 | 97.5 |  |  | 97.5 | 85% | 61% | 69% | 87% | 5.9352 | Loss 5-10%
1626 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1028 | TG-LO1028A-3 | DT-3 | D-BLOCK ASHOK NAGAR GALI NO-3:ID | 3 | 990 | 19504095 | 941 | 2019-06-10 23:30 | 334 | 1502 | 324 | 1446 | 283 | 1246 | 233 | 617 | 94 | 5.5 |  | 99.5 | 93% | 65% | 71% | 95% | 5.9352 | Loss 5-10% |  | 804(32.5)
1627 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1029 | TG-LO1029A-1 | DT-1 | B-BLOCK ASHOK NAGAR SCHOOL WALA:K | 3 | 990 | 19506195 | 1128.7818 | 2019-06-01 01:30 | 384.6673 | 1712.1435 | 386.7725 | 1691.1785 | 357.342 | 1571.0103 | 131.9062 | 556 | 135.5 | 19 | 3.5 | 158 | 114% | 82% | 79% | 99% | 4.1572 | Loss 0-5% |  | 931(47) | 1067(122.5) | 897(54)
1628 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1029 | TG-LO1029A-2 | DT-2 | B-BLOCK ASHOK NAGAR SCHOOL WALA:K | 3 | 630 | 19502179 | 595 | 2019-06-30 02:00 | 144 | 616 | 245 | 1057 | 207 | 890 | 386 | 437 | 60 | 2.5 |  | 62.5 | 94% | 72% | 68% | 88% | 4.1572 | Loss 0-5% |  | 775(217) | 822(230) | 742(220.5) | 651(179) | 642(50)
1629 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1029 | TG-LO1029A-3 | DT-3 | B-BLOCK ASHOK NAGAR SCHOOL WALA:K | 3 | 990 | 19502205 | 1145 | 2019-06-12 00:30 | 408 | 1689 | 281 | 1157 | 455 | 1898 | 662 | 544.5 | 120 | 34.5 | 14.5 | 169 | 116% | 102% | 76% | 107% | 4.1572 | Loss 0-5% |  |  | 836(24) | 915(26)
1630 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1031 | TG-LO1031A-1 | DT-1 | HARDEV PURI NO.1:ID | 1 | 990 | 19502158 | 805 | 2019-06-11 | 198 | 857 | 356 | 1584 | 251 | 1124 | 637 | 642.5 | 52 |  |  | 52 | 81% | 54% | 70% | 81% | 14.1886 | Loss 10-20%
1631 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1032 | TG-LO1032A-1 | DT-1 | HARDEVPURI NO.2 ( JOSHI WALA):PL | 1 | 990 | 19506310 | 1146 | 2019-06-29 23:00 | 375 | 1697 | 464 | 2148 | 306 | 1378 | 670 | 470 | 142.5 | 43 | 35 | 220.5 | 114% | 78% | 89% | 116% | 5.6375 | Loss 5-10% |  |  | 1301(238) | 1366(245) | 1037(153)
1632 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1033 | TG-LO1033A-1 | DT-1 | E-1 BLK ASHOK NAGAR.KANCH WALA NR S BHAWAN:K | 2 | 630 | 19504098 | 587 | 2019-06-03 01:30 | 223 | 879 | 235 | 948 | 130 | 515 | 403 | 606.5 | 111 | 2.5 |  | 113.5 | 93% | 69% | 72% | 91% | 12.964 | Loss 10-20% |  |  |  |  | 489(26)
1633 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1033 | TG-LO1033A-2 | DT-2 | E-1 BLK ASHOK NAGAR.KANCH WALA NR S BHAWAN:K | 2 | 630 | 19505663 | 490 | 2019-06-02 23:00 | 160 | 676 | 175 | 736 | 155 | 640 | 84 | 685.5 | 33 |  |  | 33 | 76% | 54% | 55% | 78% | 12.964 | Loss 10-20%
1634 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1034 | TG-LO1034A-1 | DT-1 | ASHOK NAGAR NO EXTN NO 1 KACHCHI CLY:PL | 2 | 630 | 19503619 | 437 | 2019-06-29 23:30 | 178 | 796 | 117 | 522 | 142 | 625 | 240 | 716 |  |  |  | 0 | 67% | 50% | 51% | 69% | 3.8141 | Loss 0-5%
1635 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1034 | TG-LO1034A-2 | DT-2 | ASHOK NAGAR NO EXTN NO 1 KACHCHI CLY:PL | 2 | 630 | 19505269 | 711 | 2019-06-10 23:30 | 186 | 850 | 201 | 900 | 324 | 1534 | 660 | 488 | 174.5 | 35.5 | 18 | 228 | 113% | 77% | 100% | 113% | 3.8141 | Loss 0-5% |  | 569(70) | 624(185) | 627(62.5) | 519(47.5)
1636 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1035 | TG-LO1035A-1 | DT-1 | NATHU COLONY:K | 2 | 990 | 19506177 | 912 | 2019-06-11 23:30 | 248 | 1090 | 324 | 1443 | 340 | 1541 | 411 | 621 | 94 | 0.5 |  | 94.5 | 87% | 69% | 72% | 92% | 5.0527 | Loss 5-10%
1637 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1035 | TG-LO1035A-2 | DT-2 | NATHU COLONY:K | 2 | 990 | 19504782 | 690 | 2019-06-11 23:30 | 233 | 1036 | 255 | 1145 | 202 | 880 | 231 | 718.5 |  |  |  | 0 | 66% | 45% | 53% | 70% | 5.0527 | Loss 5-10% |  |  | 820(89.5) | 806(29.5)
1638 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1043 | TG-LO1043A-1 | DT-1 | LALITA MANDIR ASHOK NAGAR D BLK:PL | 1 | 990 | 19502640 | 907 | 2019-06-26 23:30 | 319 | 1378 | 324 | 1408 | 264 | 1144 | 250 | 588.5 | 125 | 1 |  | 126 | 90% | 68% | 69% | 92% | 5.4957 | Loss 5-10% |  |  | 865(80) | 855(47.5)
1639 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1045 | TG-LO1045A-1 | DT-1 | HARIJAN BASTI, AKHADA EAST GOKAL PUR:PL | 2 | 990 | 19505674 | 879 | 2019-06-01 10:30 | 297 | 1284 | 292 | 1257 | 290 | 1252 | 30 | 650 | 69 |  |  | 69 | 51% | 62% | 89% | 49% | 25.1555 | Loss 20-30%
1640 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1045 | TG-LO1045A-2 | DT-2 | HARIJAN BASTI, AKHADA EAST GOKAL PUR:PL | 2 | 630 | 19505673 | 478 | 2019-06-20 16:30 | 152 | 624 | 158 | 654 | 168 | 688 | 55 | 717 | 2.5 |  |  | 2.5 | 68% | 70% | 76% | 59% | 25.1555 | Loss 20-30% | 797(229.5) | 659(85) | 737(75) | 689(123) | 759(116) | 685(78.5)
1641 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1047 | TG-LO1047A-1 | DT-1 | D-1 ASHOK NAGAR WAZIRA BAD ROAD:PL | 1 | 630 | 19505923 | 725 | 2019-06-02 18:30 | 206 | 895 | 283 | 1219 | 237 | 1051 | 281 | 498 | 163 | 32.5 | 19.5 | 215 | 111% | 93% | 115% | 115% | 4.363 | Loss 0-5% | 660(33) | 747(291.5) | 764(470) | 728(198.5) | 597(129)
1642 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1053 | TG-LO1053A-1 | DT-1 | D 1/1 BLK ASHOK NAGAR DP :PL | 1 | 990 | 19505926 | 928 | 2019-06-29 23:30 | 394 | 1684 | 302 | 1281 | 232 | 981 | 611 | 660.5 | 54.5 | 1 |  | 55.5 | 91% | 74% | 79% | 94% | 6.744 | Loss 5-10%
1643 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1055 | TG-LO1055A-1 | DT-1 | LONI BORDER S/S NO-1 | 1 | 630 | 19505051 | 653 | 2019-06-10 22:30 | 272 | 1185 | 206 | 871 | 175 | 755 | 385 | 535 | 166 | 5 | 0.5 | 171.5 | 92% | 85% | 98% | 104% | 25.6375 | Loss 20-30% |  |  | 625(72.5) | 594(44)
1644 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1056 | TG-LO1056A-1 | DT-1 | LONI BORDER S/S NO-2 | 1 | 630 | 19503678 | 875 | 2019-06-18 17:30 | 357 | 1543 | 240 | 1023 | 279 | 1166 | 466 | 174.5 | 451.5 | 46.5 | 13.5 | 511.5 | 101% | 114% | 139% | 117% | 36.826 | Loss >30% | 615(43) | 589(164.5) | 793(390) | 770(334.5) | 847(279) | 816(112.5)
1645 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1060 | TG-LO1060A-1 | DT-1 | DURGA PURI MAIN GALI - 10:ID | 3 | 630 | 19505223 | 897.5917 | 2019-06-08 02:00 | 336.1458 | 1603.2901 | 265.3966 | 1236.1852 | 296.0493 | 1392.649 | 319.0741 | 450.5 | 130.5 | 45.5 | 42.5 | 218.5 | 142% | 84% | 93% | 114% | 5.8835 | Loss 5-10% |  | 666(129.5) | 712(229) | 673(168.5) | 630(127)
1646 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1060 | TG-LO1060A-2 | DT-2 | DURGA PURI MAIN GALI - 10:ID | 3 | 990 | 19506308 | 1286 | 2019-06-08 01:30 | 307 | 1392 | 465 | 2154 | 514 | 2263 | 822 | 324.5 | 293.5 | 62 | 37 | 392.5 | 130% | 70% | 101% | 117% | 5.8835 | Loss 5-10%
1647 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1060 | TG-LO1060A-3 | DT-3 | DURGA PURI MAIN GALI - 10:ID | 3 | 630 | 19502695 | 491 | 2019-06-30 00:30 | 142 | 612 | 176 | 768 | 173 | 755 | 150 | 713.5 | 4 |  |  | 4 | 78% | 47% | 54% | 73% | 5.8835 | Loss 5-10%
1648 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1061 | TG-LO1061A-1 | DT-1 | JAGAT PURI MAIN:PL | 2 | 630 | 19503373 | 603 | 2019-06-11 23:00 | 174 | 741 | 225 | 964 | 204 | 873 | 194 | 605 | 110.5 | 2.5 |  | 113 | 89% | 62% | 69% | 96% | 4.2091 | Loss 0-5% | 584(54.5) | 762(340) | 608(90) | 529(41.5)
1649 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1061 | TG-LO1061A-2 | DT-2 | JAGAT PURI MAIN:PL | 2 | 630 | 19506558 | 936.9566 | 2019-06-11 19:30 | 336.9131 | 1386.8161 | 248.7815 | 1032.8027 | 351.262 | 1486.6975 | 413.1115 | 556 | 154 | 3.5 | 1 | 158.5 | 119% | 71% | 149% | 99% | 4.2091 | Loss 0-5%
1650 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1063 | TG-LO1063A-1 | DT-1 | JAG JIVAN NAGAR:PL | 1 | 990 | 19506222 | 1078 | 2019-06-06 00:30 | 322 | 1419 | 418 | 1857 | 338 | 1510 | 400 | 577 | 128.5 | 8.5 | 2 | 139 | 109% | 75% | 74% | 94% | 10.0496 | Loss 10-20% |  | 863(41) | 970(91.5) | 801(28)
1651 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1066 | TG-LO1066A-1 | DT-1 | CHANDER LOK:PL | 1 | 990 | 19505936 | 1182.4515 | 2019-06-30 01:00 | 360.6617 | 1579.0102 | 475.0448 | 2102.8987 | 346.7449 | 1504.8386 | 564.6399 | 431.5 | 192.5 | 49 | 44.5 | 286 | 119% | 73% | 94% | 117% | 11.0792 | Loss 10-20% |  | 987(88.5) | 1090(205) | 998(134.5) | 979(99.5)
1652 | 1260 | NNG | SUDAMA PURI | LO2004 | TG-LO2004A-1 | DT-1 | JYOTI COLONY NO.1:K | 2 | 630 | 19506079 | 874 | 2019-06-11 00:30 | 295 | 1306 | 249 | 1085 | 330 | 1457 | 324 | 386 | 192.5 | 51.5 | 89 | 333 | 139% | 79% | 101% | 130% | 9.3425 | Loss 5-10% | 666(46.5) | 1028(330.5) | 933(546) |  | 625(95)
1653 | 1260 | NNG | SUDAMA PURI | LO2004 | TG-LO2004A-2 | DT-2 | JYOTI COLONY NO.1:K | 2 | 400 | 19505874 | 402 | 2019-06-11 01:00 | 186 | 802 | 94 | 395 | 122 | 515 | 362 | 603 | 111.5 | 4 | 0.5 | 116 | 100% | 62% | 61% | 97% | 9.3425 | Loss 5-10% |  | 400(80.5) | 426(165)
1654 | 1260 | NNG | SUDAMA PURI | LO2006 | TG-LO2006A-1 | DT-1 | JYOTI COLONY NO.3:K | 2 | 990 | 19504914 | 644 | 2019-06-29 23:30 | 258 | 1091 | 164 | 689 | 222 | 931 | 351 | 636.5 |  |  |  | 0 | 65% | 44% | 48% | 65% | 7.8995 | Loss 5-10%
1655 | 1260 | NNG | SUDAMA PURI | LO2006 | TG-LO2006A-2 | DT-2 | JYOTI COLONY NO.3:K | 2 | 630 | 19506078 | 689 | 2019-06-12 00:30 | 283 | 1176 | 199 | 814 | 207 | 854 | 344 | 632 | 69 | 15 | 3 | 87 | 109% | 69% | 83% | 102% | 7.8995 | Loss 5-10%
1656 | 1260 | NNG | SUDAMA PURI | LO2007 | TG-LO2007A-1 | DT-1 | AMBEDKAR PARK:PL | 2 | 990 | 19506615 | 974 | 2019-06-10 23:00 | 344 | 1494 | 437 | 1859 | 193 | 819 | 914 | 585.5 | 121 | 10.5 |  | 131.5 | 95% | 66% | 76% | 98% | 7.6514 | Loss 5-10% | 913(24.5) |  | 1386(102) | 1073(104.5)
1657 | 1260 | NNG | SUDAMA PURI | LO2007 | TG-LO2007A-2 | DT-2 | AMBEDKAR PARK:PL | 2 | 630 | 19506514 | 774 | 2019-06-11 01:00 | 262 | 1120 | 293 | 1233 | 218 | 916 | 279 | 489 | 135 | 50.5 | 42.5 | 228 | 123% | 71% | 87% | 113% | 7.6514 | Loss 5-10%
1658 | 1260 | NNG | SUDAMA PURI | LO2009 | TG-LO2009A-1 | DT-1 | SHIV MANDIR 100 FT. RD:PL | 2 | 990 | 19506076 | 746 | 2019-06-01 | 227 | 985 | 299 | 1402 | 220 | 953 | 434 | 569 | 9.5 |  |  | 9.5 | 75% | 52% | 65% | 74% | 7.0932 | Loss 5-10% |  |  | 838(32.5)
1659 | 1260 | NNG | SUDAMA PURI | LO2009 | TG-LO2009A-2 | DT-2 | SHIV MANDIR 100 FT. RD:PL | 2 | 400 | 19506549 | 405 | 2019-06-10 23:00 | 167 | 721 | 123 | 519 | 116 | 496 | 215 | 566.5 | 130.5 | 21 | 0.5 | 152 | 95% | 69% | 77% | 101% | 7.0932 | Loss 5-10%
1660 | 1260 | NNG | SUDAMA PURI | LO2012 | TG-LO2012A-1 | DT-1 | BABAR PUR VILLAGE:PL | 2 | 630 | 19502729 | 525 | 2019-06-11 23:30 | 140 | 589 | 181 | 772 | 203 | 869 | 246 | 641 | 78 |  |  | 78 | 82% | 65% | 69% | 83% | 21.0092 | Loss 20-30% | 636(147) | 638(264.5)
1661 | 1260 | NNG | SUDAMA PURI | LO2012 | TG-LO2012A-2 | DT-2 | BABAR PUR VILLAGE:PL | 2 | 990 | 19504911 | 655 | 2019-06-10 23:30 | 256 | 1131 | 217 | 959 | 182 | 786 | 299 | 719 |  |  |  | 0 | 64% | 54% | 50% | 66% | 21.0092 | Loss 20-30%
1662 | 1260 | NNG | SUDAMA PURI | LO2013 | TG-LO2013A-1 | DT-1 | MAHA DEVI SCHOOL:PL | 2 | 630 | 19502715 | 716 | 2019-06-03 | 263 | 1160 | 217 | 961 | 236 | 1053 | 172 | 549 | 121.5 | 37 | 11 | 169.5 | 114% | 76% | 74% | 108% | 6.8494 | Loss 5-10% |  | 628(85.5) | 670(211.5) | 672(150) | 585(108)
1663 | 1260 | NNG | SUDAMA PURI | LO2013 | TG-LO2013A-2 | DT-2 | MAHA DEVI SCHOOL:PL | 2 | 630 | 19502722 | 550 | 2019-06-29 00:30 | 131 | 562 | 207 | 905 | 212 | 928 | 355 | 683.5 | 33 |  |  | 33 | 87% | 62% | 72% | 82% | 6.8494 | Loss 5-10%
1664 | 1260 | NNG | SUDAMA PURI | LO2016 | TG-LO2016A-1 | DT-1 | SUDAMA PURI NO.3:PL | 1 | 990 | 19506468 | 992.4833 | 2019-06-27 00:30 | 275.2841 | 1161.2912 | 279.1033 | 1187.7747 | 438.0959 | 1848.194 | 674.0513 | 511.5 | 187 | 19 | 0.5 | 206.5 | 100% | 69% | 84% | 96% | 8.2144 | Loss 5-10% |  |  | 871(98.5) | 877(76.5) | 851(99)
1665 | 1260 | NNG | SUDAMA PURI | LO2018 | TG-LO2018A-1 | DT-1 | SUDAMAPURI NO. 4:PL | 1 | 400 | 19506829 | 481 | 2019-06-09 23:30 | 178 | 755 | 130 | 552 | 174 | 735 | 194 | 360.5 | 209.5 | 65 | 84 | 358.5 | 119% | 86% | 89% | 120% | 6.1208 | Loss 5-10% |  | 314(28) |  | 399(38) |  | 349(36)
1666 | 1260 | NNG | SUDAMA PURI | LO2020 | TG-LO2020A-1 | DT-1 | BALBIR NAGAR EXT.:PL | 2 | 990 | 19504551 | 1475 | 2019-06-11 00:30 | 451 | 1824 | 478 | 1967 | 546 | 2289 | 412 | 236.5 | 217 | 96 | 165.5 | 478.5 | 149% | 87% | 131% | 145% | 5.8898 | Loss 5-10% |  | 1201(203) | 1199(417.5) | 1239(291) | 1014(214) | 862(34)
1667 | 1260 | NNG | SUDAMA PURI | LO2020 | TG-LO2020A-2 | DT-2 | BALBIR NAGAR EXT.:PL | 2 | 630 | 19506261 | 473 | 2019-06-12 | 131 | 515 | 220 | 879 | 122 | 481 | 382 | 712 | 3 |  |  | 3 | 75% | 48% | 67% | 70% | 5.8898 | Loss 5-10% |  | 787(150.5) | 824(264.5) | 795(190) | 655(141.5)
1668 | 1260 | NNG | SUDAMA PURI | LO2021 | TG-LO2021A-1 | DT-1 | D BLOCK KABIR NAGAR(SHAMSHAN GHAT) | 3 | 990 | 19505805 | 972 | 2019-06-01 23:30 | 368 | 1557 | 310 | 1294 | 294 | 1235 | 296 | 628.5 | 82.5 | 7.5 |  | 90 | 98% | 79% | 89% | 98% | 11.5993 | Loss 10-20% |  |  | 799(30.5)
1669 | 1260 | NNG | SUDAMA PURI | LO2021 | TG-LO2021A-2 | DT-2 | D BLOCK KABIR NAGAR(SHAMSHAN GHAT) | 3 | 630 | 19505296 | 513 | 2019-06-26 13:00 | 174 | 715 | 150 | 617 | 189 | 777 | 139 | 702.5 | 16.5 |  |  | 16.5 | 78% | 66% | 81% | 80% | 11.5993 | Loss 10-20% |  | 844(258) | 902(306) | 1140(81.5) | 562(64)
1670 | 1260 | NNG | SUDAMA PURI | LO2021 | TG-LO2021A-3 | DT-3 | D BLOCK KABIR NAGAR(SHAMSHAN GHAT) | 3 | 630 | 19506074 | 270 | 2019-06-29 23:30 | 96 | 400 | 109 | 457 | 65 | 271 | 166 | 719 |  |  |  | 0 | 42% | 37% | 42% | 43% | 11.5993 | Loss 10-20%
1671 | 1260 | NNG | SUDAMA PURI | LO2023 | TG-LO2023A-1 | DT-1 | A BLOCK KABIR NAGAR:ID | 3 | 990 | 19502671 | 975 | 2019-06-01 | 331 | 1301 | 356 | 1417 | 288 | 1144 | 237 | 506.5 | 200.5 | 12.5 |  | 213 | 98% | 84% | 82% | 96% | 13.2709 | Loss 10-20% |  | 950(173.5) | 1019(210) | 827(41.5) | 864(82)
1672 | 1260 | NNG | SUDAMA PURI | LO2023 | TG-LO2023A-2 | DT-2 | A BLOCK KABIR NAGAR:ID | 3 | 990 | 19503249 | 554 | 2019-06-01 17:00 | 196 | 835 | 189 | 805 | 169 | 722 | 101 | 720 |  |  |  | 0 | 46% | 41% | 56% | 49% | 13.2709 | Loss 10-20%
1673 | 1260 | NNG | SUDAMA PURI | LO2023 | TG-LO2023A-3 | DT-3 | A BLOCK KABIR NAGAR:ID | 3 | 630 | 19505875 | 325 | 2019-06-29 11:00 | 98 | 407 | 104 | 429 | 123 | 510 | 94 | 719.5 |  |  |  | 0 | 14% | 22% | 52% | 15% | 13.2709 | Loss 10-20% |  |  | 551(60.5) | 578(62) | 537(70.5) | 559(115.5)
1674 | 1260 | NNG | SUDAMA PURI | LO2025 | TG-LO2025A-1 | DT-1 | B-BLOCK KABIR NAGAR:ID | 2 | 990 | 19506075 | 816 | 2019-06-01 | 300 | 1291 | 242 | 1037 | 274 | 1174 | 220 | 692 | 27 |  |  | 27 | 82% | 71% | 78% | 79% | 13.3839 | Loss 10-20% |  | 879(116.5) | 908(131.5) | 788(36.5)
1675 | 1260 | NNG | SUDAMA PURI | LO2025 | TG-LO2025A-2 | DT-2 | B-BLOCK KABIR NAGAR:ID | 2 | 990 | 19502720 | 761 | 2019-06-01 22:00 | 305 | 1328 | 204 | 891 | 252 | 1075 | 380 | 710.5 | 9 |  |  | 9 | 74% | 62% | 71% | 77% | 13.3839 | Loss 10-20%
1676 | 1260 | NNG | SUDAMA PURI | LO2026 | TG-LO2026A-1 | DT-1 | C BLOCK KABIR NAGAR | 2 | 990 | 19502709 | 960 | 2019-06-01 01:00 | 351 | 1503 | 292 | 1308 | 317 | 1355 | 176 | 558 | 150 | 9.5 |  | 159.5 | 97% | 81% | 95% | 95% | 12.6474 | Loss 10-20% | 808(37) | 1128(202) | 1185(401) | 1091(419) | 1047(310) | 842(92)
1677 | 1260 | NNG | SUDAMA PURI | LO2026 | TG-LO2026A-2 | DT-2 | C BLOCK KABIR NAGAR | 2 | 990 | 19502707 | 683 | 2019-06-01 17:30 | 183 | 745 | 260 | 1062 | 240 | 973 | 283 | 717 |  |  |  | 0 | 61% | 53% | 69% | 59% | 12.6474 | Loss 10-20% | 790(35.5) | 975(299) | 1090(275) | 998(285.5)
1678 | 1260 | NNG | SUDAMA PURI | LO2028 | TG-LO2028A-1 | DT-1 | HARIJAN BASTI WEST JYOTI NARAR:ID | 2 | 630 | 19502724 | 622 | 2019-06-29 23:30 | 234 | 985 | 190 | 795 | 197 | 822 | 178 | 543 | 153 | 24 |  | 177 | 97% | 68% | 71% | 99% | 6.1603 | Loss 5-10% |  |  | 599(53) | 639(100) | 510(47.5)
1679 | 1260 | NNG | SUDAMA PURI | LO2028 | TG-LO2028A-2 | DT-2 | HARIJAN BASTI WEST JYOTI NARAR:ID | 2 | 400 | 19502719 | 467 | 2019-06-11 00:30 | 95 | 398 | 187 | 817 | 186 | 807 | 414 | 469 | 131 | 56.5 | 63.5 | 251 | 117% | 78% | 81% | 116% | 6.1603 | Loss 5-10% | 405(39) | 613(310) | 543(186) | 452(140.5) | 354(88.5)
1680 | 1260 | NNG | SUDAMA PURI | LO2029 | TG-LO2029A-1 | DT-1 | KARDAM MARG KHET WALA:-PL | 2 | 630 | 19506176 | 441 | 2019-06-08 01:30 | 171 | 765 | 146 | 641 | 124 | 550 | 187 | 718 | 0.5 |  |  | 0.5 | 70% | 38% | 53% | 65% | 7.7449 | Loss 5-10%
1681 | 1260 | NNG | SUDAMA PURI | LO2029 | TG-LO2029A-2 | DT-2 | KARDAM MARG KHET WALA:-PL | 2 | 990 | 19506895 | 1018 | 2019-06-11 23:00 | 291 | 1264 | 425 | 1883 | 302 | 1302 | 601 | 567.5 | 126.5 | 23 | 1 | 150.5 | 98% | 57% | 78% | 103% | 7.7449 | Loss 5-10% |  |  | 1041(111) | 937(55.5)
1682 | 1260 | NNG | SUDAMA PURI | LO2030 | TG-LO2030A-1 | DT-1 | KARDAM PURI AZAD CHOWK:-ID | 2 | 990 | 19506684 | 892 | 2019-06-01 | 253 | 1062 | 343 | 1453 | 296 | 1236 | 339 | 615.5 | 104 | 0.5 |  | 104.5 | 90% | 73% | 82% | 87% | 13.4219 | Loss 10-20% |  | 782(36) | 804(27.5) | 932(53) | 790(33.5)
1683 | 1260 | NNG | SUDAMA PURI | LO2030 | TG-LO2030A-2 | DT-2 | KARDAM PURI AZAD CHOWK:-ID | 2 | 990 | 19506490 | 696 | 2019-06-02 02:00 | 226 | 911 | 242 | 972 | 228 | 906 | 64 | 719.5 | 0.5 |  |  | 0.5 | 70% | 57% | 64% | 68% | 13.4219 | Loss 10-20%
1684 | 1260 | NNG | SUDAMA PURI | LO2031 | TG-LO2031A-1 | DT-1 | NEW KARDAMPURI NO 1 GALI NO -4:PL | 1 | 630 | 19506465 | 603 | 2019-06-29 23:30 | 176 | 784 | 259 | 1183 | 168 | 699 | 448 | 501.5 | 193 | 14.5 |  | 207.5 | 96% | 82% | 91% | 96% | 9.041 | Loss 5-10% |  |  |  |  | 595(67)
1685 | 1260 | NNG | SUDAMA PURI | LO2032 | TG-LO2032A-1 | DT-1 | NORTH CHAJJUPUR:ID | 2 | 990 | 19502700 | 1029 | 2019-06-11 02:00 | 337 | 1402 | 310 | 1286 | 382 | 1599 | 275 | 559.5 | 132 | 23 | 3.5 | 158.5 | 104% | 63% | 72% | 101% | 7.9983 | Loss 5-10% |  | 1002(82.5) | 983(149.5) | 989(105) | 830(64.5)
1686 | 1260 | NNG | SUDAMA PURI | LO2032 | TG-LO2032A-2 | DT-2 | NORTH CHAJJUPUR:ID | 2 | 990 | 19505766 | 757 | 2019-06-08 01:30 | 255 | 1156 | 257 | 1175 | 246 | 1113 | 55 | 716.5 | 0.5 |  |  | 0.5 | 77% | 42% | 68% | 70% | 7.9983 | Loss 5-10% |  | 551(116.5) | 634(368) | 545(46.5) | 520(104.5)
1687 | 1260 | NNG | SUDAMA PURI | LO2041 | TG-LO2041A-1 | DT-1 | West Jyoti Ngr(Beh. Gopal Nur Home):-PL | 2 | 990 | 19506073 | 900 | 2019-06-11 00:30 | 354 | 1474 | 295 | 1232 | 251 | 1046 | 372 | 649 | 70.5 | 0.5 |  | 71 | 91% | 50% | 70% | 89% | 5.5294 | Loss 5-10% |  | 1177(29.5) | 983(91.5) | 1045(34.5)
1688 | 1260 | NNG | SUDAMA PURI | LO2041 | TG-LO2041A-2 | DT-2 | West Jyoti Ngr(Beh. Gopal Nur Home):-PL | 2 | 990 | 19506072 | 667 | 2019-06-11 00:30 | 259 | 1086 | 181 | 746 | 227 | 949 | 296 | 720 |  |  |  | 0 | 67% | 38% | 52% | 63% | 5.5294 | Loss 5-10%
1689 | 1260 | NNG | SUDAMA PURI | LO2044 | TG-LO2044A-1 | DT-1 | CNG STATION LONI ROAD:PM | 2 | 400 | 19503385 | 16 | 2019-06-14 03:30 | 6 | 25 | 3 | 11 | 7 | 29 | 17 | 720 |  |  |  | 0 | 4% | 3% | 4% | 4% | 5.4597 | Loss 5-10%
1690 | 1260 | NNG | SUDAMA PURI | LO2044 | TG-LO2044A-2 | DT-2 | CNG STATION LONI ROAD:PM | 2 | 400 | 19506633 | 355 | 2019-06-04 06:00 | 118 | 481 | 118 | 482 | 119 | 489 | 8 | 666.5 | 52.5 |  |  | 52.5 | 87% | 89% | 87% | 83% | 5.4597 | Loss 5-10%
1691 | 1260 | NNG | SUDAMA PURI | LO2046 | TG-LO2046A-1 | DT-1 | SUDAMAPURI S/S- 5 Nr. BABARPUR BUS TERM. | 1 | 630 | 19505667 | 886 | 2019-06-08 01:30 | 312 | 1364 | 250 | 1077 | 324 | 1419 | 319 | 425.5 | 209.5 | 67.5 | 14.5 | 291.5 | 141% | 82% | 87% | 107% | 17.3868 | Loss 10-20% | 611(31.5) | 769(276) | 836(451.5) | 725(219.5) | 567(130.5)

## Overloaded SSTN Peak Load
[7 empty] | KVA | [7 empty] | Peak Loading June 2019
Sr.No. | SDO | DIVISION | ZONE | SSTN SAP CODE | SSTN NAME | NO OF DTs In Sstn | DT-1 | DT-2 | DT-3 | DT-4 | DT-5 | DT-6 | DT-7 | DT-8 | DT-1 | DT-2 | DT-3 | DT-4 | DT-5 | DT-6 | DT-7 | DT-8 | DT-8
1 | 1110 | CCK | HAMILTON ROAD | HAM003 | HAMILTON ROAD STN:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 47%; Peak Loading June 2019 DT-2: 82%
2 | 1110 | CCK | HAMILTON ROAD | HAM009 | CHABBI GANJ:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 98%
3 | 1110 | CCK | HAMILTON ROAD | HAM017 | KASHMERE GATE POLICE THANA:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 77%
4 | 1110 | CCK | HAMILTON ROAD | HAM034 | YAMUNA BAZAR GHAT DELHI 6 | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 147%
5 | 1110 | CCK | LAHORI GATE | LHR001 | MOHALLA NIHARIYAN:K | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 101%; Peak Loading June 2019 DT-2: 53%
6 | 1110 | CCK | LAHORI GATE | LHR003 | MOHALLA SHAHGANJ:K | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 89%; Peak Loading June 2019 DT-2: 77%
7 | 1110 | CCK | LAHORI GATE | LHR015 | ZEENAT MAHAL:K | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 89%; Peak Loading June 2019 DT-2: 32%
8 | 1110 | CCK | LAHORI GATE | LHR017 | LAL QUAN:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 110%
9 | 1110 | CCK | LAHORI GATE | LHR018 | BARSHABULLA:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 85%; Peak Loading June 2019 DT-2: 117%
10 | 1110 | CCK | LAHORI GATE | LHR019 | CHARKHE WALAN:PL | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 70%; Peak Loading June 2019 DT-2: 83%
11 | 1110 | CCK | LAHORI GATE | LHR023 | JOGIWARA:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 100%; Peak Loading June 2019 DT-2: 91%; Peak Loading June 2019 DT-3: 70%
12 | 1110 | CCK | LAHORI GATE | LHR024 | PANDIT BROS:K | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 82%; Peak Loading June 2019 DT-2: 88%
13 | 1110 | CCK | LAHORI GATE | LHR025 | CYCLE STAND:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 74%; Peak Loading June 2019 DT-2: 92%
14 | 1110 | CCK | LAHORI GATE | LHR026 | OLD KRISHNA MARKET:ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 82%
15 | 1110 | CCK | LAHORI GATE | LHR027 | NEW KRISHNA MKT:ID | 2 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 95%
16 | 1110 | CCK | LAHORI GATE | LHR032 | HAVELI HYDERQULI:PM | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 83%
17 | 1110 | CCK | LAHORI GATE | LHR034 | KATRA BARYIAN PLINTH:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 95%
18 | 1110 | CCK | LAHORI GATE | LHR043 | GADODIA KIOSK:K | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 96%
19 | 1110 | CCK | LAHORI GATE | LHR046 | LAL DARWAZA:PM | 2 | KVA DT-1: 400; KVA DT-2: 400; Peak Loading June 2019 DT-1: 83%; Peak Loading June 2019 DT-2: 65%
20 | 1110 | CCK | LAHORI GATE | LHR047 | LAMBI GALI:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 89%
21 | 1110 | CCK | LAHORI GATE | LHR048 | P.S HAUZ QUAZI:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 54%; Peak Loading June 2019 DT-2: 90%; Peak Loading June 2019 DT-3: 75%
22 | 1110 | CCK | LAHORI GATE | LHR051 | NEW HAUZ QUAZI:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 46%; Peak Loading June 2019 DT-2: 63%; Peak Loading June 2019 DT-3: 110%
23 | 1110 | CCK | LAHORI GATE | LHR054 | HAMDARD:ID | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 84%
24 | 1110 | CCK | LAHORI GATE | LHR055 | GALI KASIM JAAN:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 98%; Peak Loading June 2019 DT-2: 94%
25 | 1110 | CCK | LAHORI GATE | LHR056 | GALI HASHMUDDIN:PKG | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 115%
26 | 1110 | CCK | TOWN HALL | THL004 | KATRA KUSHAL RAI:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 74%; Peak Loading June 2019 DT-2: 89%; Peak Loading June 2019 DT-3: 71%
27 | 1110 | CCK | TOWN HALL | THL006 | NEW LAJPAT RAI MKT:ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 87%
28 | 1110 | CCK | TOWN HALL | THL007 | MALIWARA : PKG | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 83%
29 | 1110 | CCK | TOWN HALL | THL010 | KUCHHA NALWA:PKG | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 95%
30 | 1110 | CCK | TOWN HALL | THL014 | KUMAR CINEMA:PKG | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 85%
31 | 1110 | CCK | TOWN HALL | THL015 | MAHARASHTRA BANK:PKG | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 90%
32 | 1110 | CCK | TOWN HALL | THL019 | KINARI BAZAR:PM | 2 | KVA DT-1: 400; KVA DT-2: 400; Peak Loading June 2019 DT-1: 96%; Peak Loading June 2019 DT-2: 93%
33 | 1110 | CCK | TOWN HALL | THL020 | DIWAN HALL:PM | 3 | KVA DT-1: 400; KVA DT-2: 400; KVA DT-3: 400; Peak Loading June 2019 DT-1: 86%; Peak Loading June 2019 DT-2: 35%; Peak Loading June 2019 DT-3: 93%
34 | 1110 | CCK | TOWN HALL | THL021 | TIKONA PARK:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 71%; Peak Loading June 2019 DT-2: 79%
35 | 1110 | CCK | TOWN HALL | THL025 | SHRI RAM:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 85%
36 | 1110 | CCK | TOWN HALL | THL028 | MOTI BAZAR:PKG | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 78%
37 | 1110 | CCK | TOWN HALL | THL029 | GALI PARATHE:PKG | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 78%
38 | 1110 | CCK | TOWN HALL | THL035 | CHARHAT:PKG | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 88%
39 | 1120 | DRG | DARYAGANJ | DRY007 | BACHHO KA GHAR:PKG | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 46%; Peak Loading June 2019 DT-2: 92%
40 | 1120 | DRG | DARYAGANJ | DRY011 | DARYA GANJ KOTWALI:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 92%
41 | 1120 | DRG | DARYAGANJ | DRY035 | VIKRAM NAGAR:PACKAGE S/STN | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 52%; Peak Loading June 2019 DT-2: 81%
42 | 1120 | DRG | DARYAGANJ | DRY089 | GHATA MASJID:PG | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 96%
43 | 1120 | DRG | JAMA MASJID | HAU001 | 84 GHANTA:K | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 107%; Peak Loading June 2019 DT-2: 105%; Peak Loading June 2019 DT-3: 99%
44 | 1120 | DRG | JAMA MASJID | HAU003 | DDA HOUSING COMP.TURKMAN GATE:ID | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 630; Peak Loading June 2019 DT-1: 73%; Peak Loading June 2019 DT-2: 80%; Peak Loading June 2019 DT-3: 73%; Peak Loading June 2019 DT-4: 58%
45 | 1120 | DRG | JAMA MASJID | HAU006 | GALI DAKOTAN:PM | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 91%
46 | 1120 | DRG | JAMA MASJID | HAU008 | GALI SHANKAR:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 97%; Peak Loading June 2019 DT-2: 111%
47 | 1120 | DRG | JAMA MASJID | HAU010 | HAMMATGARH:K | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 50%; Peak Loading June 2019 DT-2: 79%
48 | 1120 | DRG | JAMA MASJID | HAU011 | RAJ ENGINEERING:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 82%; Peak Loading June 2019 DT-2: 77%
49 | 1120 | DRG | JAMA MASJID | HAU012 | SARAK PREM NARAIN:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 105%
50 | 1120 | DRG | JAMA MASJID | HAU014 | BARSHABULLA:ID DRG | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 98%
51 | 1120 | DRG | JAMA MASJID | HAU015 | NEW HAUZ QUAZI:ID DRG | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 95%
52 | 1120 | DRG | JAMA MASJID | JMS001 | BULIBULI KHANA:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 89%; Peak Loading June 2019 DT-2: 99%
53 | 1120 | DRG | JAMA MASJID | JMS002 | CHANDNI MAHAL:ID | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 630; Peak Loading June 2019 DT-1: 64%; Peak Loading June 2019 DT-2: 127%; Peak Loading June 2019 DT-3: 29%; Peak Loading June 2019 DT-4: 128%
54 | 1120 | DRG | JAMA MASJID | JMS003 | CHANDNI MAHAL [K]:K | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 110%
55 | 1120 | DRG | JAMA MASJID | JMS004 | DELHI GATE TELEPHONE EXCHANGE PM:K | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 110%; Peak Loading June 2019 DT-2: 147%
56 | 1120 | DRG | JAMA MASJID | JMS006 | GANJ MEER KHAN:PM | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 125%
57 | 1120 | DRG | JAMA MASJID | JMS008 | GIRDHAR PANNA:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 72%; Peak Loading June 2019 DT-2: 79%; Peak Loading June 2019 DT-3: 123%
58 | 1120 | DRG | JAMA MASJID | JMS010 | JAMA MASJID:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 47%; Peak Loading June 2019 DT-2: 58%; Peak Loading June 2019 DT-3: 82%
59 | 1120 | DRG | JAMA MASJID | JMS013 | KASTURBA P/M:PM | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 79%
60 | 1120 | DRG | JAMA MASJID | JMS015 | KUCHA CHELAN-2:PL | 3 | KVA DT-1: 990; KVA DT-2: 400; KVA DT-3: 990; Peak Loading June 2019 DT-1: 101%; Peak Loading June 2019 DT-2: 107%; Peak Loading June 2019 DT-3: 135%
61 | 1120 | DRG | JAMA MASJID | JMS017 | KUCHA DAKHINI RAI:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 109%; Peak Loading June 2019 DT-2: 83%
62 | 1120 | DRG | JAMA MASJID | JMS018 | MOHALLA QUABRISTAN:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 92%
63 | 1120 | DRG | JAMA MASJID | JMS019 | MOTHER DAIRY:K | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 101%
64 | 1120 | DRG | JAMA MASJID | JMS021 | NEW DUJANA HOUSE 8 PANEL:ID | 8 | 990 | 990 | 990 | 990 | 990 | 990 | 990 | 990 | 55% | 59% | 82% | 103% | 109% | 84% | 72% | 824 | 83%
65 | 1120 | DRG | JAMA MASJID | JMS022 | OLD DUJANA:K | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 119%; Peak Loading June 2019 DT-2: 101%
66 | 1120 | DRG | JAMA MASJID | JMS023 | SHEESH MAHAL:K | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 101%; Peak Loading June 2019 DT-2: 85%
67 | 1120 | DRG | JAMA MASJID | JMS024 | SSA ROAD:PL:PG | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 105%; Peak Loading June 2019 DT-2: 94%
68 | 1120 | DRG | JAMA MASJID | JMS025 | TIRAHA BAIRAM KHAN:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 82%; Peak Loading June 2019 DT-2: 142%
69 | 1120 | DRG | JAMA MASJID | JMS026 | URDU BAZAR:PG | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 108%; Peak Loading June 2019 DT-2: 99%; Peak Loading June 2019 DT-3: 55%
70 | 1120 | DRG | JAMA MASJID | JMS033 | HOTEL BROADWAY:K | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 990; Peak Loading June 2019 DT-1: 102%; Peak Loading June 2019 DT-2: 81%; Peak Loading June 2019 DT-3: 110%; Peak Loading June 2019 DT-4: 52%
71 | 1120 | DRG | MINTO ROAD | MRD012 | KOTLA RD.:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 85%
72 | 1120 | DRG | MINTO ROAD | MRD073 | SHAKOOR KI DANDI P/M | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 93%
73 | 1130 | PHG | B G ROAD | BGR003 | GALI BAHUJI: PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 88%
74 | 1130 | PHG | B G ROAD | BGR004 | MODEL BASTI:PL | 2 | KVA DT-1: 400; KVA DT-2: 990; Peak Loading June 2019 DT-1: 55%; Peak Loading June 2019 DT-2: 81%
75 | 1130 | PHG | B G ROAD | BGR005 | CHIMNI MIL PL/M:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 87%; Peak Loading June 2019 DT-2: 85%
76 | 1130 | PHG | B G ROAD | BGR013 | FOOTA ROAD KIOSK:K | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 101%
77 | 1130 | PHG | B G ROAD | BGR016 | GALI NEEM WALI:K | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 86%
78 | 1130 | PHG | B G ROAD | BGR020 | AHATA KIDARA UNIT I:PM | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 116%
79 | 1130 | PHG | B G ROAD | BGR021 | FILMISTAN:ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 77%
80 | 1130 | PHG | B G ROAD | BGR022 | B. G. ROAD COMP CTR:ID | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 630; Peak Loading June 2019 DT-1: 55%; Peak Loading June 2019 DT-2: 55%; Peak Loading June 2019 DT-3: 63%; Peak Loading June 2019 DT-4: 81%
81 | 1130 | PHG | B G ROAD | BGR027 | JHABBAR MAL P/M:PKG | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 91%
82 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN007 | CHUNA MANDI:ID | 5 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 990; KVA DT-5: 990; Peak Loading June 2019 DT-1: 60%; Peak Loading June 2019 DT-2: 67%; Peak Loading June 2019 DT-3: 92%; Peak Loading June 2019 DT-4: 59%; Peak Loading June 2019 DT-5: 71%
83 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN008 | GALI NALWA:K | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 79%
84 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN009 | KRISHNA MKT. (K):K | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 104%
85 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN015 | LADOO GHATI:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 105%
86 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN016 | 6: TOOTI PL/M:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 78%; Peak Loading June 2019 DT-2: 83%
87 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN020 | BASANT ROAD:K | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 88%; Peak Loading June 2019 DT-2: 45%
88 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN022 | GALI MANTOLA:PL | 3 | KVA DT-1: 630; KVA DT-2: 630; KVA DT-3: 990; Peak Loading June 2019 DT-1: 86%; Peak Loading June 2019 DT-2: 72%; Peak Loading June 2019 DT-3: 50%
89 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN023 | DARIBA PAN KIOSK:K | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 73%; Peak Loading June 2019 DT-2: 59%; Peak Loading June 2019 DT-3: 90%
90 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN025 | PHG DISP.:ID | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 630; Peak Loading June 2019 DT-1: 50%; Peak Loading June 2019 DT-2: 45%; Peak Loading June 2019 DT-3: 108%; Peak Loading June 2019 DT-4: 146%
91 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | CHN026 | GALI SCHOOL WALI:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 92%; Peak Loading June 2019 DT-2: 99%
92 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM001 | HANUMAN MANDIR:PL | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 94%; Peak Loading June 2019 DT-2: 85%
93 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM003 | KILA KADAM SHARIF:PG | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 82%
94 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM010 | MCD PARK:PG | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 80%; Peak Loading June 2019 DT-2: 68%; Peak Loading June 2019 DT-3: 92%
95 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM011 | YOG MAYA:PG | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 87%
96 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM025 | CHARA MANDI:K | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 73%; Peak Loading June 2019 DT-2: 88%
97 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM026 | BAGICHI ALLUDDIN:K | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 76%; Peak Loading June 2019 DT-2: 81%
98 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM027 | ARP QUARTERS.:K | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 62%; Peak Loading June 2019 DT-2: 86%
99 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM029 | JHANDEWALAN P/M:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 83%
100 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM030 | KABIR BASTI:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 80%
101 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM031 | GALI NO. 5 MULTANI DHANDA:PKG | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 98%
102 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM035 | AARAKASHA ROAD:PKG | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 102%; Peak Loading June 2019 DT-2: 92%
103 | 1130 | PHG | CHUNA MANDI & RAM NAGAR | RAM044 | DB GUPTA ROAD BUS STOP | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 120%
104 | 1130 | PHG | PP QUARTERS | PPQ001 | RAILWAY BOOKING P/M:PL | 2 | KVA DT-1: 990; KVA DT-2: 400; Peak Loading June 2019 DT-1: 72%; Peak Loading June 2019 DT-2: 92%
105 | 1130 | PHG | PP QUARTERS | PPQ003 | KHURSHEED MARKET:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 400; Peak Loading June 2019 DT-1: 82%; Peak Loading June 2019 DT-2: 61%; Peak Loading June 2019 DT-3: 66%
106 | 1130 | PHG | PP QUARTERS | PPQ005 | 12 TOOTI CHOWK:PKG | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 98%; Peak Loading June 2019 DT-2: 63%
107 | 1130 | PHG | PP QUARTERS | PPQ006 | WEST END CINEMA:ID | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 81%; Peak Loading June 2019 DT-2: 156%
108 | 1130 | PHG | PP QUARTERS | PPQ012 | A K TANKI P/M:ID | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 400; Peak Loading June 2019 DT-1: 52%; Peak Loading June 2019 DT-2: 51%; Peak Loading June 2019 DT-3: 63%; Peak Loading June 2019 DT-4: 82%
109 | 1130 | PHG | PP QUARTERS | PPQ015 | OLD QASAB PURA:K | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 78%; Peak Loading June 2019 DT-2: 54%
110 | 1130 | PHG | PP QUARTERS | PPQ023 | NARIAN MARKET:K | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 92%; Peak Loading June 2019 DT-2: 57%
111 | 1140 | SRD | CHHAPARWALAN | CPW032 | JOSHI ROAD KIOSK:K | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 88%; Peak Loading June 2019 DT-2: 65%
112 | 1140 | SRD | CHHAPARWALAN | CPW035 | AJMAL KHAN KIOSK | 2 | KVA DT-1: 990; KVA DT-2: 400; Peak Loading June 2019 DT-1: 57%; Peak Loading June 2019 DT-2: 79%
113 | 1140 | SRD | CHHAPARWALAN | CPW037 | 53 BLOCK RAMJAS ROAD:K | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 93%
114 | 1140 | SRD | CHHAPARWALAN | CPW038 | 61 BLOCK RAMJAS ROAD PL/M:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 81%
115 | 1140 | SRD | CHHAPARWALAN | KKW001 | NANAK HOTEL K. BAGH:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 104%
116 | 1140 | SRD | CHHAPARWALAN | KKW002 | MASJID WALA K. BAGH.:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 101%
117 | 1140 | SRD | CHHAPARWALAN | KKW003 | ELAHI BUX:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 84%; Peak Loading June 2019 DT-2: 64%
118 | 1140 | SRD | CHHAPARWALAN | KKW004 | BIRLA FLATS K. BAGH:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 85%; Peak Loading June 2019 DT-2: 85%
119 | 1140 | SRD | CHHAPARWALAN | KKW010 | POLICE QTR. K. BAGH:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 75%; Peak Loading June 2019 DT-2: 36%; Peak Loading June 2019 DT-3: 50%
120 | 1140 | SRD | CHHAPARWALAN | KKW013 | PO NO. 1 K. BAGH:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 83%; Peak Loading June 2019 DT-2: 83%
121 | 1140 | SRD | CHHAPARWALAN | KKW017 | PO NO. 5 K. BAGH:PG | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 90%
122 | 1140 | SRD | CHHAPARWALAN | KKW018 | H S ROAD BASEMENT:ID | 6 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 630; KVA DT-5: 630; Peak Loading June 2019 DT-1: 96%; Peak Loading June 2019 DT-2: 82%; Peak Loading June 2019 DT-3: 100%; Peak Loading June 2019 DT-4: 37%; Peak Loading June 2019 DT-5: 35%
123 | 1140 | SRD | CHHAPARWALAN | RJN030 | SP.MUKERJI MKT. FAIZ RD. P/M NO. 2:PL | 2 | KVA DT-1: 990; KVA DT-2: 400; Peak Loading June 2019 DT-1: 68%; Peak Loading June 2019 DT-2: 98%
124 | 1140 | SRD | CHHAPARWALAN | RJN037 | 2E JHANDEWALAN PL/M(PARK):PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 86%; Peak Loading June 2019 DT-2: 41%; Peak Loading June 2019 DT-3: 69%
125 | 1140 | SRD | CHHAPARWALAN | RJN041 | JHANDENWALAN NO. 1:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 82%; Peak Loading June 2019 DT-2: 54%
126 | 1140 | SRD | PUSA ROAD | KKW006 | SATBHRAWA (K) STN.:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 62%; Peak Loading June 2019 DT-2: 80%
127 | 1140 | SRD | PUSA ROAD | KKW007 | SHASTRI PARK (INDOOR):ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 83%; Peak Loading June 2019 DT-2: 59%; Peak Loading June 2019 DT-3: 75%
128 | 1140 | SRD | PUSA ROAD | KKW008 | JESSA RAM HOSPITAL PACKAGE S/STN | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 16%; Peak Loading June 2019 DT-2: 16%; Peak Loading June 2019 DT-3: 116%
129 | 1140 | SRD | PUSA ROAD | KKW020 | 39, BEEDEN PURA (W):PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 64%; Peak Loading June 2019 DT-2: 81%
130 | 1140 | SRD | PUSA ROAD | KKW025 | 8 C WEA KAROL BAGH JASSA RAM | 2 | KVA DT-1: 990; KVA DT-2: 400; Peak Loading June 2019 DT-1: 102%; Peak Loading June 2019 DT-2: 101%
131 | 1140 | SRD | PUSA ROAD | KKW028 | H.S.RD. KHATTAWAL K. BAGH:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 97%; Peak Loading June 2019 DT-2: 92%
132 | 1140 | SRD | PUSA ROAD | KKW030 | NALA WALA H. S. RD.:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 79%
133 | 1140 | SRD | PUSA ROAD | KKW031 | 13 BLK WEA K. BAGH:PACKAGE S/STN | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 630; Peak Loading June 2019 DT-1: 58%; Peak Loading June 2019 DT-2: 87%; Peak Loading June 2019 DT-3: 42%; Peak Loading June 2019 DT-4: 78%
134 | 1140 | SRD | PUSA ROAD | KKW032 | 5WEA K BAGH KIOSK:PACKAGE S/STN | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 70%; Peak Loading June 2019 DT-2: 90%; Peak Loading June 2019 DT-3: 57%
135 | 1140 | SRD | PUSA ROAD | KKW037 | 26 BEEDEN PURA P.L RD.:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 98%
136 | 1140 | SRD | PUSA ROAD | KKW039 | 40 REGER PURA P/M:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 96%
137 | 1140 | SRD | PUSA ROAD | KKW046 | PUSA RD. CAMP CENTRE:ID | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 990; Peak Loading June 2019 DT-1: 88%; Peak Loading June 2019 DT-2: 97%; Peak Loading June 2019 DT-3: 77%; Peak Loading June 2019 DT-4: 103%
138 | 1140 | SRD | PUSA ROAD | KKW049 | R. K. DASS-1 K. BAGH:K | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 119%; Peak Loading June 2019 DT-2: 82%
139 | 1140 | SRD | PUSA ROAD | KKW050 | R.K.DASS-1/2 K. BAGH:K | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 79%; Peak Loading June 2019 DT-2: 70%
140 | 1140 | SRD | PUSA ROAD | KKW059 | BAPU BHAWAN S/ST.:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 86%
141 | 1140 | SRD | PUSA ROAD | KKW067 | 5 BLOCK WEA KAROL BAGH KIOSK | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 94%; Peak Loading June 2019 DT-2: 111%; Peak Loading June 2019 DT-3: 41%
142 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | EPN003 | 21 BLK. O. R. NAGAR:K | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 93%; Peak Loading June 2019 DT-2: 51%; Peak Loading June 2019 DT-3: 92%
143 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN006 | TIKONA PARK BAZAR MARG:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 93%; Peak Loading June 2019 DT-2: 80%; Peak Loading June 2019 DT-3: 94%
144 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN007 | BAZAR MARG (K):K | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 59%; Peak Loading June 2019 DT-2: 111%
145 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN011 | SALWAN SCHOOL OLD:PL | 4 | KVA DT-1: 990; KVA DT-2: 630; KVA DT-3: 990; KVA DT-4: 630; Peak Loading June 2019 DT-1: 99%; Peak Loading June 2019 DT-2: 62%; Peak Loading June 2019 DT-3: 66%; Peak Loading June 2019 DT-4: 58%
146 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN012 | SALWAN SCHOOL NEW:K | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 94%; Peak Loading June 2019 DT-2: 23%; Peak Loading June 2019 DT-3: 72%
147 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN013 | SETHI PETROL PUMP:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 57%; Peak Loading June 2019 DT-2: 117%; Peak Loading June 2019 DT-3: 27%
148 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN019 | SRD BUILDING OFFICE:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 88%; Peak Loading June 2019 DT-2: 27%
149 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN023 | NPL MULTI STORIES:ID | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 81%
150 | 1140 | SRD | R BLOCK NEW RAJENDER NAGAR | RJN081 | HANDIWALA ORN : K | 3 | KVA DT-1: 990; KVA DT-2: 630; KVA DT-3: 630; Peak Loading June 2019 DT-1: 103%; Peak Loading June 2019 DT-2: 94%; Peak Loading June 2019 DT-3: 117%
151 | 1141 | PNR | KIKARWALAN | PNR002 | SABZIWALA P.S RD. K. BAGH:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 67%; Peak Loading June 2019 DT-2: 63%; Peak Loading June 2019 DT-3: 82%
152 | 1141 | PNR | KIKARWALAN | PNR003 | H.S. RD.P/M BAPA NGR:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 93%; Peak Loading June 2019 DT-2: 105%
153 | 1141 | PNR | KIKARWALAN | PNR005 | 17 B DEV NGR. K. BAGH:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 87%; Peak Loading June 2019 DT-2: 59%; Peak Loading June 2019 DT-3: 58%
154 | 1141 | PNR | KIKARWALAN | PNR006 | 11 B DEV NGR. A.S RD.:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 52%; Peak Loading June 2019 DT-2: 89%; Peak Loading June 2019 DT-3: 50%
155 | 1141 | PNR | KIKARWALAN | PNR007 | 13-B DEV NAGAR K. BAGH:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 82%
156 | 1141 | PNR | KIKARWALAN | PNR008 | 14-B MCD QTR. P.L. RD.:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 112%; Peak Loading June 2019 DT-2: 84%
157 | 1141 | PNR | KIKARWALAN | PNR010 | MILITARY ROAD (K):PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 87%; Peak Loading June 2019 DT-2: 88%
158 | 1141 | PNR | KIKARWALAN | PNR012 | TANK RD. KHATTA S/ST.:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 121%; Peak Loading June 2019 DT-2: 105%
159 | 1141 | PNR | KIKARWALAN | PNR013 | TANK RD .BOOSTER PUMP:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 103%; Peak Loading June 2019 DT-2: 96%; Peak Loading June 2019 DT-3: 86%
160 | 1141 | PNR | KIKARWALAN | PNR015 | KRISHNA TIRATH DEV NAGAR | 2 | KVA DT-1: 990; KVA DT-2: 1600; Peak Loading June 2019 DT-1: 100%; Peak Loading June 2019 DT-2: 91%
161 | 1141 | PNR | KIKARWALAN | PNR016 | REGER PURA ZONAL OFF INDOOR S/ST:ID | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 87%; Peak Loading June 2019 DT-2: 88%
162 | 1141 | PNR | KIKARWALAN | PNR125 | MILITARY ROAD S/ST. NO. 3:PM | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 91%
163 | 1141 | PNR | KIKARWALAN | PNR155 | VIJAY CHOWK | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 94%
164 | 1141 | PNR | KIKARWALAN | PNR157 | 10-B, RAJENDRAPLACE | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 80%
165 | 1141 | PNR | PATEL NAGAR | PNR018 | FARID PURI KIOSK:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 62%; Peak Loading June 2019 DT-2: 88%
166 | 1141 | PNR | PATEL NAGAR | PNR019 | FARID PURI NO.1 | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 100%
167 | 1141 | PNR | PATEL NAGAR | PNR020 | FARID PURI P/M NO. 2:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 117%
168 | 1141 | PNR | PATEL NAGAR | PNR021 | RAJASTHANI COLONY P/M-1:PM | 2 | KVA DT-1: 400; KVA DT-2: 400; Peak Loading June 2019 DT-1: 86%; Peak Loading June 2019 DT-2: 110%
169 | 1141 | PNR | PATEL NAGAR | PNR028 | 12 BLOCK E.P. NAGAR P/M:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 54%; Peak Loading June 2019 DT-2: 84%
170 | 1141 | PNR | PATEL NAGAR | PNR029 | 10 BLOCK E. P. NAGAR (K):PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 64%; Peak Loading June 2019 DT-2: 104%; Peak Loading June 2019 DT-3: 60%
171 | 1141 | PNR | PATEL NAGAR | PNR032 | 22 BLOCK W.P. NAGAR:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 87%; Peak Loading June 2019 DT-2: 85%
172 | 1141 | PNR | PATEL NAGAR | PNR043 | BALJIT NGR. BARAT GHAR:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 113%; Peak Loading June 2019 DT-2: 88%
173 | 1141 | PNR | PATEL NAGAR | PNR044 | BALJIT NAGAR AGGARWAL SWEET P/M:PM | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 109%
174 | 1141 | PNR | PATEL NAGAR | PNR047 | SHADI PUR DTC DEPOT:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 42%; Peak Loading June 2019 DT-2: 126%
175 | 1141 | PNR | PATEL NAGAR | PNR048 | BALJIT NAGAR SCHOOLWALA TR.1:PM | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 144%; Peak Loading June 2019 DT-2: 130%
176 | 1141 | PNR | PATEL NAGAR | PNR049 | BALJIT NAGAR JANTA PARK:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 106%; Peak Loading June 2019 DT-2: 104%
177 | 1141 | PNR | PATEL NAGAR | PNR050 | BALJIT NAGAR P/M J. WALAN CHOWK:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 114%; Peak Loading June 2019 DT-2: 77%
178 | 1141 | PNR | PATEL NAGAR | PNR051 | DAV MULTAN:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 87%; Peak Loading June 2019 DT-2: 97%; Peak Loading June 2019 DT-3: 98%
179 | 1141 | PNR | PATEL NAGAR | PNR052 | MUFFATLAL:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 83%
180 | 1141 | PNR | PATEL NAGAR | PNR054 | POLICE STN. W.P.NAGAR:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 120%; Peak Loading June 2019 DT-2: 92%
181 | 1141 | PNR | PATEL NAGAR | PNR056 | F&G BLOCK W.P. NAGAR:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 96%; Peak Loading June 2019 DT-2: 48%
182 | 1141 | PNR | PATEL NAGAR | PNR057 | S- BLOCK W.P. NAGAR:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 62%; Peak Loading June 2019 DT-2: 103%; Peak Loading June 2019 DT-3: 81%
183 | 1141 | PNR | PATEL NAGAR | PNR059 | BALJIT NGR. NO. 1 (DOGWALA):PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 97%; Peak Loading June 2019 DT-2: 115%
184 | 1141 | PNR | PATEL NAGAR | PNR062 | NALA (K) W.P. NAGAR:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 112%
185 | 1141 | PNR | PATEL NAGAR | PNR063 | Z-BLOCK, W.P. NAGAR:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 88%
186 | 1141 | PNR | PATEL NAGAR | PNR064 | D-BLOCK, W.P. NAGAR P/M:PM | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 97%
187 | 1141 | PNR | PATEL NAGAR | PNR066 | WEST PATEL NAGAR INDOOR:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 72%; Peak Loading June 2019 DT-2: 118%
188 | 1141 | PNR | PATEL NAGAR | PNR067 | 30 BLOCK WEST PATEL NAGAR:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 66%; Peak Loading June 2019 DT-2: 85%
189 | 1141 | PNR | PATEL NAGAR | PNR094 | 29 BLOCK W.P. NAGAR:PL | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 68%; Peak Loading June 2019 DT-2: 96%
190 | 1141 | PNR | PATEL NAGAR | PNR131 | HOLI CHOWK PATEL NAGAR | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 83%
191 | 1141 | PNR | PATEL NAGAR | PNR134 | NEPALI MANDIR BALJIT NAGAR | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 78%
192 | 1141 | PNR | PATEL NAGAR | PNR152 | 25 BLK WEST PATEL NAGAR | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 139%; Peak Loading June 2019 DT-2: 83%
193 | 1141 | PNR | PATEL NAGAR | PNR153 | ROAD NO-20 BALJEET NAGAR | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 128%; Peak Loading June 2019 DT-2: 100%
194 | 1141 | PNR | SARAI ROHILLA | PNR096 | DHAL WALA GALI NO-6 | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 80%; Peak Loading June 2019 DT-2: 21%
195 | 1141 | PNR | SARAI ROHILLA | PNR099 | K. PAHAR G. NO. 8 S/ST-7:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 76%
196 | 1141 | PNR | SARAI ROHILLA | PNR100 | K. PAHR G. NO. 9:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 103%
197 | 1141 | PNR | SARAI ROHILLA | PNR101 | S/STN NO.15 GALI NO.8 KALA PAHAR | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 82%; Peak Loading June 2019 DT-2: 100%
198 | 1141 | PNR | SARAI ROHILLA | PNR102 | NAGARWALA GHATTI RD.:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 105%
199 | 1141 | PNR | SARAI ROHILLA | PNR104 | ZONAL OFF. K. PAHAR:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 54%; Peak Loading June 2019 DT-2: 84%
200 | 1141 | PNR | SARAI ROHILLA | PNR105 | POLICE POST K. PAHAR:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 79%
201 | 1141 | PNR | SARAI ROHILLA | PNR106 | TIN MKT. K. PAHAR:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 68%; Peak Loading June 2019 DT-2: 113%
202 | 1141 | PNR | SARAI ROHILLA | PNR107 | BANGALI DHABA K. PAHAR:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 91%
203 | 1141 | PNR | SARAI ROHILLA | PNR110 | G. NO. 11 BABU RAM K. PAHAR:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 83%
204 | 1141 | PNR | SARAI ROHILLA | PNR113 | SARAI ROHILLA:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 92%
205 | 1141 | PNR | SARAI ROHILLA | PNR114 | KAMAL (K) K.PAHAR:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 94%
206 | 1141 | PNR | SARAI ROHILLA | PNR116 | GALI NO.1 NANAKWALA:PL | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 57%; Peak Loading June 2019 DT-2: 79%
207 | 1141 | PNR | SARAI ROHILLA | PNR120 | SOHAN SINGH K.PAHAR:PL | 3 | KVA DT-1: 630; KVA DT-2: 630; KVA DT-3: 630; Peak Loading June 2019 DT-1: 95%; Peak Loading June 2019 DT-2: 56%; Peak Loading June 2019 DT-3: 90%
208 | 1141 | PNR | SARAI ROHILLA | PNR121 | KHANNA S/STN, K.PAHAR:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 85%
209 | 1141 | PNR | SARAI ROHILLA | PNR127 | MILITARY RD. P/M S/ST:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 64%; Peak Loading June 2019 DT-2: 101%
210 | 1141 | PNR | SARAI ROHILLA | PNR129 | GALI-4 POST OFFICE ANAND PARBAT | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 80%
211 | 1141 | PNR | SARAI ROHILLA | PNR130 | TAULUI WALA PATEL NAGAR | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 87%
212 | 1141 | PNR | SARAI ROHILLA | PNR138 | RIWA GALI NO-4 | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 81%
213 | 1141 | PNR | SARAI ROHILLA | PNR139 | POST OFFICE P/M GALI NO-2 | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 84%
214 | 1141 | PNR | SARAI ROHILLA | PNR141 | TIKONA PARK GODODIA ROAD | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 112%
215 | 1141 | PNR | SARAI ROHILLA | PNR149 | HR. ROAD ANAND PARVAT | 2 | KVA DT-1: 630; KVA DT-2: 400; Peak Loading June 2019 DT-1: 103%; Peak Loading June 2019 DT-2: 88%
216 | 1141 | PNR | SARAI ROHILLA | PNR165 | Booster Pump Nai basti( Rajiv Vatika ) | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 84%
217 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI038 | D-BLK VIVEK VIHAR PLM:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 57%; Peak Loading June 2019 DT-2: 87%
218 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI039 | PRATAP KHAND:ID | 3 | KVA DT-1: 630; KVA DT-2: 400; KVA DT-3: 630; Peak Loading June 2019 DT-1: 59%; Peak Loading June 2019 DT-2: 69%; Peak Loading June 2019 DT-3: 79%
219 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI061 | C-BLK VIVEK VIHAR(PARK WALA):PG | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 51%; Peak Loading June 2019 DT-2: 91%
220 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI062 | JANTA QTR. VIVEK VIHAR:PL | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 93%; Peak Loading June 2019 DT-2: 50%
221 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI063 | MAHILA COLLEGE VIVEK VIHAR:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 72%; Peak Loading June 2019 DT-2: 88%
222 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI064 | SHIVA KHAND:PL | 2 | KVA DT-1: 630; KVA DT-2: 400; Peak Loading June 2019 DT-1: 87%; Peak Loading June 2019 DT-2: 53%
223 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI074 | C-BLK DSIDC JLM COLONY:ID | 2 | KVA DT-1: 400; KVA DT-2: 400; Peak Loading June 2019 DT-1: 101%; Peak Loading June 2019 DT-2: 48%
224 | 1210 | KKD | B-BLOCK VIVEK VIHAR | JHI126 | A-BLK VIVEK VIHAR PH-2 | 2 | KVA DT-1: 990; KVA DT-2: 400; Peak Loading June 2019 DT-1: 82%; Peak Loading June 2019 DT-2: 75%
225 | 1210 | KKD | B-BLOCK VIVEK VIHAR | VNG002 | YOJNA VIHAR C-BLOCK:ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 93%
226 | 1210 | KKD | B-BLOCK VIVEK VIHAR | VNG048 | SURAJ MAL VIHAR C-BLOCK:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 87%; Peak Loading June 2019 DT-2: 75%; Peak Loading June 2019 DT-3: 81%
227 | 1210 | KKD | B-BLOCK VIVEK VIHAR | VNG104 | YOJANA VIHAR B-BLOCK:ID | 2 | KVA DT-1: 990; KVA DT-2: 400; Peak Loading June 2019 DT-1: 39%; Peak Loading June 2019 DT-2: 87%
228 | 1210 | KKD | B-BLOCK VIVEK VIHAR | VNG115 | SURAJ MAL VIHAR B-BLOCK:PG | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 105%
229 | 1210 | KKD | JWALA NAGAR | VNG007 | RAMA BLOCK(BABU RAM SCHOOL):K | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 73%; Peak Loading June 2019 DT-2: 94%
230 | 1210 | KKD | JWALA NAGAR | VNG010 | ANAJ MANDI:K | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 63%; Peak Loading June 2019 DT-2: 96%
231 | 1210 | KKD | JWALA NAGAR | VNG011 | DELHI GATE:K | 2 | KVA DT-1: 990; KVA DT-2: 400; Peak Loading June 2019 DT-1: 80%; Peak Loading June 2019 DT-2: 72%
232 | 1210 | KKD | JWALA NAGAR | VNG013 | BIHARI COLONY:K | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 99%; Peak Loading June 2019 DT-2: 86%; Peak Loading June 2019 DT-3: 106%
233 | 1210 | KKD | JWALA NAGAR | VNG017 | MUKESH NAGAR:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 99%; Peak Loading June 2019 DT-2: 69%
234 | 1210 | KKD | JWALA NAGAR | VNG018 | TEL MILL:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 98%
235 | 1210 | KKD | JWALA NAGAR | VNG022 | 4-POLE PANDAV ROAD:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 86%
236 | 1210 | KKD | JWALA NAGAR | VNG025 | MAHAVIR BLOCK:PL | 2 | KVA DT-1: 400; KVA DT-2: 400; Peak Loading June 2019 DT-1: 97%; Peak Loading June 2019 DT-2: 77%
237 | 1210 | KKD | JWALA NAGAR | VNG026 | DALAI MOHALLA:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 80%
238 | 1210 | KKD | JWALA NAGAR | VNG027 | SHALIMAR PARK:K | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 99%; Peak Loading June 2019 DT-2: 59%
239 | 1210 | KKD | JWALA NAGAR | VNG028 | MANI RAM MANDIR:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 126%; Peak Loading June 2019 DT-2: 81%; Peak Loading June 2019 DT-3: 103%
240 | 1210 | KKD | JWALA NAGAR | VNG029 | IDGAH BHOLA NATH NAGAR:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 117%
241 | 1210 | KKD | JWALA NAGAR | VNG030 | TELEWARA:PM | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 87%
242 | 1210 | KKD | JWALA NAGAR | VNG031 | TEJAB MILL:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 95%; Peak Loading June 2019 DT-2: 63%; Peak Loading June 2019 DT-3: 80%
243 | 1210 | KKD | JWALA NAGAR | VNG032 | MAHA RAM MOHALLA:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 52%; Peak Loading June 2019 DT-2: 87%
244 | 1210 | KKD | JWALA NAGAR | VNG036 | BHOLA NATH NAGAR:K | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 82%; Peak Loading June 2019 DT-2: 81%; Peak Loading June 2019 DT-3: 106%
245 | 1210 | KKD | JWALA NAGAR | VNG037 | PATHAN PURA:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 118%
246 | 1210 | KKD | JWALA NAGAR | VNG038 | AGGARWAL BHAWAN:PM | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 81%; Peak Loading June 2019 DT-2: 76%
247 | 1210 | KKD | JWALA NAGAR | VNG064 | HALKANA KUNA NO-1:K | 4 | KVA DT-1: 630; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 630; Peak Loading June 2019 DT-1: 86%; Peak Loading June 2019 DT-2: 49%; Peak Loading June 2019 DT-3: 69%; Peak Loading June 2019 DT-4: 126%
248 | 1210 | KKD | JWALA NAGAR | VNG090 | GALI NO-10 VISHWAS NAGAR:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 27%; Peak Loading June 2019 DT-2: 93%
249 | 1210 | KKD | JWALA NAGAR | VNG111 | BIHARI COLONY EXT.;PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 45%; Peak Loading June 2019 DT-2: 89%
250 | 1210 | KKD | JWALA NAGAR | VNG158 | CIVIL HOSPITAL SHAHDARA S/STN | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 92%
251 | 1210 | KKD | JWALA NAGAR | VNG177 | TELIWARA PARK NEAR GURUDWARA :OD | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 81%
252 | 1210 | KKD | SAINI ENCLAVE | VNG012 | LSC MKT A-BLK SURAJ MAL VIHAR:ID | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 87%; Peak Loading June 2019 DT-2: 31%
253 | 1210 | KKD | SAINI ENCLAVE | VNG019 | ASHOKA NIKETAN:PG | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 85%
254 | 1210 | KKD | SAINI ENCLAVE | VNG035 | KARKAR DOOMA VILLAGE:PM | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 97%
255 | 1210 | KKD | SAINI ENCLAVE | VNG053 | ANAND VIHAR C-BLOCK:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 37%; Peak Loading June 2019 DT-2: 97%; Peak Loading June 2019 DT-3: 75%
256 | 1210 | KKD | SAINI ENCLAVE | VNG070 | AGCR ENCLAVE:ID | 3 | KVA DT-1: 990; KVA DT-2: 630; KVA DT-3: 990; Peak Loading June 2019 DT-1: 43%; Peak Loading June 2019 DT-2: 84%; Peak Loading June 2019 DT-3: 47%
257 | 1210 | KKD | SAINI ENCLAVE | VNG071 | HARGOVIND ENCLAVE:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 84%; Peak Loading June 2019 DT-2: 78%; Peak Loading June 2019 DT-3: 114%
258 | 1210 | KKD | SAINI ENCLAVE | VNG073 | DELHI ADMN FLATS:ID | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 90%; Peak Loading June 2019 DT-2: 74%
259 | 1210 | KKD | SAINI ENCLAVE | VNG076 | SURYA NIKETAN:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 76%; Peak Loading June 2019 DT-2: 106%; Peak Loading June 2019 DT-3: 58%
260 | 1210 | KKD | SAINI ENCLAVE | VNG078 | RAM VIHAR:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 46%; Peak Loading June 2019 DT-2: 49%; Peak Loading June 2019 DT-3: 78%
261 | 1210 | KKD | SAINI ENCLAVE | VNG081 | ANAND VIHAR A-BLOCK:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 55%; Peak Loading June 2019 DT-2: 83%; Peak Loading June 2019 DT-3: 57%
262 | 1210 | KKD | SAINI ENCLAVE | VNG099 | L.S.C SAINI ENCLAVE:ID | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 28%; Peak Loading June 2019 DT-2: 89%
263 | 1210 | KKD | SAINI ENCLAVE | VNG103 | DAYANAND VIHAR 2:ID | 3 | KVA DT-1: 630; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 67%; Peak Loading June 2019 DT-2: 58%; Peak Loading June 2019 DT-3: 90%
264 | 1210 | KKD | SAINI ENCLAVE | VNG109 | SURAJ MAL VIHAR A-BLOCK:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 36%; Peak Loading June 2019 DT-2: 88%
265 | 1210 | KKD | SAINI ENCLAVE | VNG131 | MANAK VIHAR (VIGYAN LOK) | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 84%; Peak Loading June 2019 DT-2: 22%
266 | 1210 | KKD | SAINI ENCLAVE | VNG133 | D BLOCK ANAND VIHAR | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 121%
267 | 1210 | KKD | SAINI ENCLAVE | VNG147 | AGCR ENCLAVE:PKG STN | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 88%
268 | 1211 | GTR | E&F DILSHAD GARDEN | DGN069 | A-BLOCK JHILMIL INDILSHAD AREA:ID | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 990; Peak Loading June 2019 DT-1: 76%; Peak Loading June 2019 DT-2: 86%; Peak Loading June 2019 DT-3: 110%; Peak Loading June 2019 DT-4: 90%
269 | 1211 | GTR | E&F DILSHAD GARDEN | DGN071 | B-BLK COMPLAINT CENTER JLM IND AREA:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 96%; Peak Loading June 2019 DT-2: 78%; Peak Loading June 2019 DT-3: 114%
270 | 1211 | GTR | E&F DILSHAD GARDEN | DGN072 | PREM ICE FACTORY:ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 103%
271 | 1211 | GTR | E&F DILSHAD GARDEN | DGN073 | SARDAR ALUMINIUM:ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 92%
272 | 1211 | GTR | E&F DILSHAD GARDEN | DGN077 | SANSAR:K | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 81%; Peak Loading June 2019 DT-2: 88%; Peak Loading June 2019 DT-3: 114%
273 | 1211 | GTR | E&F DILSHAD GARDEN | DGN080 | SITA FLATS,DILSHAD GARDEN:ID | 3 | KVA DT-1: 630; KVA DT-2: 630; KVA DT-3: 630; Peak Loading June 2019 DT-1: 72%; Peak Loading June 2019 DT-2: 87%; Peak Loading June 2019 DT-3: 58%
274 | 1211 | GTR | E&F DILSHAD GARDEN | DGN081 | DILSHAD GDN S/STN-4:ID | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; KVA DT-4: 990; Peak Loading June 2019 DT-1: 71%; Peak Loading June 2019 DT-2: 76%; Peak Loading June 2019 DT-3: 99%; Peak Loading June 2019 DT-4: 89%
275 | 1211 | GTR | E&F DILSHAD GARDEN | DGN083 | R.BLK DILSHAD GARDEN S/S NO-1:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 46%; Peak Loading June 2019 DT-2: 88%
276 | 1211 | GTR | E&F DILSHAD GARDEN | DGN085 | A-PKT,DILSHAD GDN:ID | 3 | KVA DT-1: 630; KVA DT-2: 630; KVA DT-3: 630; Peak Loading June 2019 DT-1: 89%; Peak Loading June 2019 DT-2: 80%; Peak Loading June 2019 DT-3: 31%
277 | 1211 | GTR | E&F DILSHAD GARDEN | DGN091 | O&P PKT DILSHAD GARDEN:ID | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 103%; Peak Loading June 2019 DT-2: 93%
278 | 1211 | GTR | E&F DILSHAD GARDEN | DGN092 | Q-POCKET DILSHAD GARDEN:ID | 2 | KVA DT-1: 630; KVA DT-2: 400; Peak Loading June 2019 DT-1: 46%; Peak Loading June 2019 DT-2: 93%
279 | 1211 | GTR | E&F DILSHAD GARDEN | DGN098 | OLD SEEMAPURI (BUS STOP):ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 400; Peak Loading June 2019 DT-1: 92%; Peak Loading June 2019 DT-2: 55%; Peak Loading June 2019 DT-3: 65%
280 | 1211 | GTR | E&F DILSHAD GARDEN | DGN099 | POLICE STATION OLD SEEMAPURI:ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 77%
281 | 1211 | GTR | E&F DILSHAD GARDEN | DGN101 | B-BLK DSIDC SHED JLM IA NO-3:ID | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 63%; Peak Loading June 2019 DT-2: 120%
282 | 1211 | GTR | E&F DILSHAD GARDEN | DGN103 | A BLK TAHIRPUR(JLM IND AREA) S/STN-1:ID | 3 | KVA DT-1: 630; KVA DT-2: 630; KVA DT-3: 630; Peak Loading June 2019 DT-1: 90%; Peak Loading June 2019 DT-2: 107%; Peak Loading June 2019 DT-3: 75%
283 | 1211 | GTR | E&F DILSHAD GARDEN | DGN104 | A BLK TAHIRPUR(JLM IND AREA) S/STN-3:ID | 4 | KVA DT-1: 630; KVA DT-2: 630; KVA DT-3: 630; KVA DT-4: 630; Peak Loading June 2019 DT-1: 101%; Peak Loading June 2019 DT-2: 92%; Peak Loading June 2019 DT-3: 67%; Peak Loading June 2019 DT-4: 83%
284 | 1211 | GTR | E&F DILSHAD GARDEN | DGN107 | B BLK OPP SWAHNEY IND.:PL | 3 | KVA DT-1: 990; KVA DT-2: 630; KVA DT-3: 630; Peak Loading June 2019 DT-1: 88%; Peak Loading June 2019 DT-2: 71%; Peak Loading June 2019 DT-3: 50%
285 | 1211 | GTR | E&F DILSHAD GARDEN | DGN109 | B-34 JLM INDUSTRIAL AREA | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 110%
286 | 1211 | GTR | E&F DILSHAD GARDEN | DGN112 | DAMODAR PARK,DILSHAD GARDEN:PL | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 990; Peak Loading June 2019 DT-1: 133%; Peak Loading June 2019 DT-2: 106%; Peak Loading June 2019 DT-3: 134%; Peak Loading June 2019 DT-4: 86%
287 | 1211 | GTR | E&F DILSHAD GARDEN | DGN114 | JHULFE BENGAL S/S NO. 2:PL | 3 | KVA DT-1: 630; KVA DT-2: 630; KVA DT-3: 990; Peak Loading June 2019 DT-1: 125%; Peak Loading June 2019 DT-2: 81%; Peak Loading June 2019 DT-3: 116%
288 | 1211 | GTR | E&F DILSHAD GARDEN | DGN116 | E-BLK NEW SEEMA PURI:PL | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 102%; Peak Loading June 2019 DT-2: 79%
289 | 1211 | GTR | E&F DILSHAD GARDEN | DGN124 | G.T ROAD SEEMA PURI BORDER:PM | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 101%
290 | 1211 | GTR | E&F DILSHAD GARDEN | DGN125 | NEW SEEMAPURI DDA FLAT:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 79%; Peak Loading June 2019 DT-2: 100%
291 | 1211 | GTR | E&F DILSHAD GARDEN | DGN128 | JULFE BENGAL S/S NO.I | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 86%; Peak Loading June 2019 DT-2: 119%; Peak Loading June 2019 DT-3: 144%
292 | 1211 | GTR | E&F DILSHAD GARDEN | DGN130 | LOCAL SHOPPING CENTER DILSHAD GARDEN:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 87%; Peak Loading June 2019 DT-2: 78%
293 | 1211 | GTR | E&F DILSHAD GARDEN | DGN132 | E&F PKT. DILSHAD GARDEN:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 87%; Peak Loading June 2019 DT-2: 43%
294 | 1211 | GTR | E&F DILSHAD GARDEN | DGN133 | B-BLOCK OLD SEEMAPURI :PL | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; KVA DT-4: 630; Peak Loading June 2019 DT-1: 34%; Peak Loading June 2019 DT-2: 53%; Peak Loading June 2019 DT-3: 61%; Peak Loading June 2019 DT-4: 104%
295 | 1211 | GTR | E&F DILSHAD GARDEN | DGN134 | TAHIRPUR SARAI:PM | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 111%
296 | 1211 | GTR | E&F DILSHAD GARDEN | DGN135 | KHERA VILLAGE:PM | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 93%
297 | 1211 | GTR | E&F DILSHAD GARDEN | DGN141 | B-BLK DILSHAD CLY:PM | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 62%; Peak Loading June 2019 DT-2: 104%; Peak Loading June 2019 DT-3: 23%
298 | 1211 | GTR | E&F DILSHAD GARDEN | DGN147 | SATISH STEEL ROLLING MILL:ID | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 81%; Peak Loading June 2019 DT-2: 71%
299 | 1211 | GTR | E&F DILSHAD GARDEN | DGN162 | F-BLOCK DILSHAD COLONY:ID | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 630; Peak Loading June 2019 DT-1: 92%; Peak Loading June 2019 DT-2: 81%; Peak Loading June 2019 DT-3: 115%; Peak Loading June 2019 DT-4: 70%
300 | 1211 | GTR | E&F DILSHAD GARDEN | DGN190 | NEW POLICE BOTH DILSHAD CLY | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 101%
301 | 1211 | GTR | E&F DILSHAD GARDEN | DGN197 | C- BLK DILSHAD COLONY SSTN NO.-2:PL | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 92%; Peak Loading June 2019 DT-2: 49%
302 | 1211 | GTR | E&F DILSHAD GARDEN | DGN207 | SHANKAR KE DP,A-BLK.JLM IA. | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 97%
303 | 1211 | GTR | E&F DILSHAD GARDEN | DGN225 | Oberai compound | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 105%; Peak Loading June 2019 DT-2: 110%
304 | 1211 | GTR | E&F DILSHAD GARDEN | DGN228 | A-BLK DILSHAD COLONY | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 106%
305 | 1211 | GTR | E&F DILSHAD GARDEN | DGN232 | DSIDC SUBSTATION NO-2 | 4 | KVA DT-1: 630; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 990; Peak Loading June 2019 DT-1: 111%; Peak Loading June 2019 DT-2: 99%; Peak Loading June 2019 DT-3: 133%; Peak Loading June 2019 DT-4: 97%
306 | 1211 | GTR | E&F DILSHAD GARDEN | DGN233 | G Block Dilshad Colony ( Park Wala) | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 120%
307 | 1211 | GTR | E&F DILSHAD GARDEN | DGN237 | B-42 JHILMIL IND AREA NEARRAILWAY LINE | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 92%; Peak Loading June 2019 DT-2: 90%
308 | 1211 | GTR | E&F DILSHAD GARDEN | DGN249 | Police Booth A BLK JLM IA | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 97%
309 | 1211 | GTR | E&F DILSHAD GARDEN | DGN252 | RAILWAY LINE IN FRONT OF B-43 JHILMIL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 115%
310 | 1211 | GTR | E&F DILSHAD GARDEN | DGN254 | DAMODAR PARK S/S NO. 2 | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 78%; Peak Loading June 2019 DT-2: 133%
311 | 1211 | GTR | GT ROAD SHAHDRA | DGN032 | J-Block MS Park Package Near Dispensary | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 100%
312 | 1211 | GTR | GT ROAD SHAHDRA | DGN038 | MOTI RAM ROAD G.T.ROAD FLYOVER S/STN | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 32%; Peak Loading June 2019 DT-2: 85%
313 | 1211 | GTR | GT ROAD SHAHDRA | DGN039 | MANSAROVER PARK MOTHER DAIRY | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 92%; Peak Loading June 2019 DT-2: 87%; Peak Loading June 2019 DT-3: 74%
314 | 1211 | GTR | GT ROAD SHAHDRA | DGN042 | MOTI RAM PEER WALA S/STN | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 29%; Peak Loading June 2019 DT-2: 94%
315 | 1211 | GTR | GT ROAD SHAHDRA | DGN044 | JAISWAL MARG:PM | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 87%; Peak Loading June 2019 DT-2: 80%
316 | 1211 | GTR | GT ROAD SHAHDRA | DGN045 | MANDOLI ROAD:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 93%; Peak Loading June 2019 DT-2: 66%
317 | 1211 | GTR | GT ROAD SHAHDRA | DGN046 | RAM NAGAR SCHOOL:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 150%; Peak Loading June 2019 DT-2: 60%
318 | 1211 | GTR | GT ROAD SHAHDRA | DGN047 | BHAGWANPUR KHERA NO-1:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 101%
319 | 1211 | GTR | GT ROAD SHAHDRA | DGN049 | BHAGWANPUR KHERA NO-3:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 107%
320 | 1211 | GTR | GT ROAD SHAHDRA | DGN050 | NEW MODERN SHAHDRA NO I GALI NO 13:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 98%; Peak Loading June 2019 DT-2: 56%
321 | 1211 | GTR | GT ROAD SHAHDRA | DGN051 | NEW MODERN SHAHDARA NO 2 GALI NO7,8 | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 96%; Peak Loading June 2019 DT-2: 113%
322 | 1211 | GTR | GT ROAD SHAHDRA | DGN052 | SUBHASH MARG NEW MODERN SHAHDARA:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 72%; Peak Loading June 2019 DT-2: 96%
323 | 1211 | GTR | GT ROAD SHAHDRA | DGN074 | RAJ ENGG.COMPOUND | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 108%; Peak Loading June 2019 DT-2: 74%
324 | 1211 | GTR | GT ROAD SHAHDRA | DGN075 | PAPER PRODUCT | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 104%; Peak Loading June 2019 DT-2: 78%
325 | 1211 | GTR | GT ROAD SHAHDRA | DGN105 | SHAMBU NATH COMP.(F.COL):ID | 5 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 990; KVA DT-5: 1600; Peak Loading June 2019 DT-1: 120%; Peak Loading June 2019 DT-2: 92%; Peak Loading June 2019 DT-3: 103%; Peak Loading June 2019 DT-4: 86%; Peak Loading June 2019 DT-5: 75%
326 | 1211 | GTR | GT ROAD SHAHDRA | DGN110 | VERMA CASTLE:PL | 6 | 990 | 990 | 630 | 630 | 990 | 990 |  |  | 116% | 98% | 88% | 111% | 113% | 100%
327 | 1211 | GTR | GT ROAD SHAHDRA | DGN111 | FRIENDS COLONY GALI NO.1 | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 89%; Peak Loading June 2019 DT-2: 67%; Peak Loading June 2019 DT-3: 88%
328 | 1211 | GTR | GT ROAD SHAHDRA | DGN120 | GALI NO.3 FRIENDS COLONY:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 102%; Peak Loading June 2019 DT-2: 43%
329 | 1211 | GTR | GT ROAD SHAHDRA | DGN127 | GALI NO.1B FRIENDS COLONY:PL | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 630; Peak Loading June 2019 DT-1: 84%; Peak Loading June 2019 DT-2: 90%; Peak Loading June 2019 DT-3: 95%; Peak Loading June 2019 DT-4: 71%
330 | 1211 | GTR | GT ROAD SHAHDRA | DGN129 | FRIENDS COLONY GALI NO-5-6 NEAR RLY.LINE:PM | 6 | 990 | 990 | 990 | 990 | 990 | 990 |  |  | 72% | 121% | 77% | 114% | 58% | 111%
331 | 1211 | GTR | GT ROAD SHAHDRA | DGN131 | GALI NO.1A FRIENDS COLONY UNDER FLYOVER: PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 115%; Peak Loading June 2019 DT-2: 88%
332 | 1211 | GTR | GT ROAD SHAHDRA | DGN178 | HANSRAJ COMPOUND S/STN | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; KVA DT-4: 990; Peak Loading June 2019 DT-1: 99%; Peak Loading June 2019 DT-2: 72%; Peak Loading June 2019 DT-3: 111%; Peak Loading June 2019 DT-4: 92%
333 | 1211 | GTR | GT ROAD SHAHDRA | DGN198 | GALI NO-1 METRO PARKING SS-2 | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 119%; Peak Loading June 2019 DT-2: 109%; Peak Loading June 2019 DT-3: 100%
334 | 1211 | GTR | GT ROAD SHAHDRA | DGN231 | GALI NO-1 RAILWAY LINE FRIENDS COLONY | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 93%; Peak Loading June 2019 DT-2: 110%
335 | 1211 | GTR | GT ROAD SHAHDRA | DGN236 | 1B Friends colony near railway line. | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 90%
336 | 1211 | GTR | GT ROAD SHAHDRA | DGN255 | GALI NO. 00 FRIENDS COLONY(THAKUR WALA) | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 98%
337 | 1211 | GTR | ZAFFRABAD | DGN001 | ZAFRABAD AE OFFICE | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 93%
338 | 1211 | GTR | ZAFFRABAD | DGN002 | ZAFRABAD CONSTRUCTION OFFICE:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 54%; Peak Loading June 2019 DT-2: 102%; Peak Loading June 2019 DT-3: 48%
339 | 1211 | GTR | ZAFFRABAD | DGN003 | NAV DURGA MANDIR | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 83%; Peak Loading June 2019 DT-2: 110%; Peak Loading June 2019 DT-3: 81%
340 | 1211 | GTR | ZAFFRABAD | DGN004 | GORAKH PARK NALA (ASHOK WALA) | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 87%
341 | 1211 | GTR | ZAFFRABAD | DGN008 | SUBHASH PARK CHAND RAM | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 108%
342 | 1211 | GTR | ZAFFRABAD | DGN009 | SUBHASH PARK ICE FACTORY | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 97%; Peak Loading June 2019 DT-2: 82%
343 | 1211 | GTR | ZAFFRABAD | DGN010 | PANCH SHEEL PARK (JHULE WALA):K | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 108%; Peak Loading June 2019 DT-2: 121%; Peak Loading June 2019 DT-3: 74%
344 | 1211 | GTR | ZAFFRABAD | DGN011 | H-BLOCK NAVEEN SHAHDARA:PL | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 630; Peak Loading June 2019 DT-1: 82%; Peak Loading June 2019 DT-2: 63%; Peak Loading June 2019 DT-3: 87%; Peak Loading June 2019 DT-4: 106%
345 | 1211 | GTR | ZAFFRABAD | DGN012 | MOHAN PARK | 2 | KVA DT-1: 990; KVA DT-2: 400; Peak Loading June 2019 DT-1: 107%; Peak Loading June 2019 DT-2: 112%
346 | 1211 | GTR | ZAFFRABAD | DGN013 | K-BLOCK NAVEEN SHAHDARA:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 64%; Peak Loading June 2019 DT-2: 79%
347 | 1211 | GTR | ZAFFRABAD | DGN014 | LONI ROAD KHATTEWALA:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 66%; Peak Loading June 2019 DT-2: 99%
348 | 1211 | GTR | ZAFFRABAD | DGN018 | R. BLOCK NAVEEN SHAHDARA:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 69%; Peak Loading June 2019 DT-2: 76%
349 | 1211 | GTR | ZAFFRABAD | DGN019 | KABOOL NAGAR KIOSK | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 96%; Peak Loading June 2019 DT-2: 62%
350 | 1211 | GTR | ZAFFRABAD | DGN020 | KABOOL NAGAR MOTHER DAIRY:PL | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 52%; Peak Loading June 2019 DT-2: 98%
351 | 1211 | GTR | ZAFFRABAD | DGN021 | KABOOL NAGAR RAIN BASERA:PM | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 100%; Peak Loading June 2019 DT-2: 59%
352 | 1211 | GTR | ZAFFRABAD | DGN022 | SHAHI MOHALLA:K | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 630; Peak Loading June 2019 DT-1: 88%; Peak Loading June 2019 DT-2: 98%; Peak Loading June 2019 DT-3: 64%; Peak Loading June 2019 DT-4: 87%
353 | 1211 | GTR | ZAFFRABAD | DGN023 | SHIVAJI PARK ARYA SAMAJ MANDIR | 1 | KVA DT-1: 1600; Peak Loading June 2019 DT-1: 101%
354 | 1211 | GTR | ZAFFRABAD | DGN024 | GORAKH PARK HANUMAN MANDIR PM | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 91%
355 | 1211 | GTR | ZAFFRABAD | DGN025 | GORAKH PARK KISOK:K | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 630; Peak Loading June 2019 DT-1: 74%; Peak Loading June 2019 DT-2: 98%; Peak Loading June 2019 DT-3: 69%; Peak Loading June 2019 DT-4: 108%
356 | 1211 | GTR | ZAFFRABAD | DGN026 | BALBIR NAGA NALA GALI NO.14:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 110%; Peak Loading June 2019 DT-2: 77%
357 | 1211 | GTR | ZAFFRABAD | DGN027 | BALBIR NAGAR NALA GALI NO. 16:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 119%
358 | 1211 | GTR | ZAFFRABAD | DGN028 | BALBIR NAGAR NALA GALI.4 GORAKH PUR:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 96%; Peak Loading June 2019 DT-2: 96%
359 | 1211 | GTR | ZAFFRABAD | DGN029 | BEHAL GALI | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 123%
360 | 1211 | GTR | ZAFFRABAD | DGN030 | BALBIR NAGAR EXTN. 60 F ROAD:PM:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 117%; Peak Loading June 2019 DT-2: 133%
361 | 1211 | GTR | ZAFFRABAD | DGN031 | BALBIR NAGAR SCHOOL:K | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 134%; Peak Loading June 2019 DT-2: 99%; Peak Loading June 2019 DT-3: 107%
362 | 1211 | GTR | ZAFFRABAD | DGN034 | LONI ROAD TIKONA PARK:PL | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 91%; Peak Loading June 2019 DT-2: 81%
363 | 1211 | GTR | ZAFFRABAD | DGN053 | EAST ROHTAS NAGAR:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 109%; Peak Loading June 2019 DT-2: 49%
364 | 1220 | KNR | GAGAN VIHAR | JAG001 | ARAM PARK:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 142%
365 | 1220 | KNR | GAGAN VIHAR | JAG002 | BEDI MKT:ID | 3 | KVA DT-1: 990; KVA DT-2: 1600; KVA DT-3: 990; Peak Loading June 2019 DT-1: 103%; Peak Loading June 2019 DT-2: 144%; Peak Loading June 2019 DT-3: 107%
366 | 1220 | KNR | GAGAN VIHAR | JAG003 | BALDEV PARK:K | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 67%; Peak Loading June 2019 DT-2: 92%
367 | 1220 | KNR | GAGAN VIHAR | JAG004 | BALDEV PARK(PARK WALA):PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 77%; Peak Loading June 2019 DT-2: 102%
368 | 1220 | KNR | GAGAN VIHAR | JAG005 | BRIJPURI:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 109%
369 | 1220 | KNR | GAGAN VIHAR | JAG006 | CHANDER NAGAR:ID | 2 | KVA DT-1: 1600; KVA DT-2: 990; Peak Loading June 2019 DT-1: 56%; Peak Loading June 2019 DT-2: 99%
370 | 1220 | KNR | GAGAN VIHAR | JAG008 | GAGAN VIHAR:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 71%; Peak Loading June 2019 DT-2: 90%; Peak Loading June 2019 DT-3: 81%
371 | 1220 | KNR | GAGAN VIHAR | JAG009 | GAGAN VIHAR EXT:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 71%; Peak Loading June 2019 DT-2: 141%
372 | 1220 | KNR | GAGAN VIHAR | JAG010 | GANDHI PARK:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 85%; Peak Loading June 2019 DT-2: 88%
373 | 1220 | KNR | GAGAN VIHAR | JAG011 | GANESH PARK:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 102%; Peak Loading June 2019 DT-2: 94%
374 | 1220 | KNR | GAGAN VIHAR | JAG012 | GOLDEN PARK:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 57%; Peak Loading June 2019 DT-2: 84%
375 | 1220 | KNR | GAGAN VIHAR | JAG013 | GOPAL PARK:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 142%; Peak Loading June 2019 DT-2: 101%
376 | 1220 | KNR | GAGAN VIHAR | JAG016 | GOVIND PURA(OLD):ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 77%; Peak Loading June 2019 DT-2: 89%
377 | 1220 | KNR | GAGAN VIHAR | JAG018 | JAGAT PURI A BLK:PL | 3 | KVA DT-1: 990; KVA DT-2: 630; KVA DT-3: 630; Peak Loading June 2019 DT-1: 88%; Peak Loading June 2019 DT-2: 74%; Peak Loading June 2019 DT-3: 131%
378 | 1220 | KNR | GAGAN VIHAR | JAG020 | JAGAT PURI F BLK:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 94%; Peak Loading June 2019 DT-2: 43%
379 | 1220 | KNR | GAGAN VIHAR | JAG022 | JITAR NAGAR:K | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 70%; Peak Loading June 2019 DT-2: 106%
380 | 1220 | KNR | GAGAN VIHAR | JAG023 | KHUREJI:ID | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 86%; Peak Loading June 2019 DT-2: 102%
381 | 1220 | KNR | GAGAN VIHAR | JAG024 | MAUSAM VIHAR:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 55%; Peak Loading June 2019 DT-2: 85%
382 | 1220 | KNR | GAGAN VIHAR | JAG025 | NEW LAYALPUR:K | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 94%; Peak Loading June 2019 DT-2: 91%; Peak Loading June 2019 DT-3: 78%
383 | 1220 | KNR | GAGAN VIHAR | JAG027 | RADHEY SHAYAM PARK:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 109%
384 | 1220 | KNR | GAGAN VIHAR | JAG028 | RAM NAGAR EXT:K | 2 | KVA DT-1: 990; KVA DT-2: 1600; Peak Loading June 2019 DT-1: 89%; Peak Loading June 2019 DT-2: 55%
385 | 1220 | KNR | GAGAN VIHAR | JAG029 | SHIV PURI:PM | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 99%
386 | 1220 | KNR | GAGAN VIHAR | JAG030 | SILVER PARK:ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 95%
387 | 1220 | KNR | GAGAN VIHAR | JAG031 | SOUTH ANARKALI:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 105%; Peak Loading June 2019 DT-2: 118%; Peak Loading June 2019 DT-3: 113%
388 | 1220 | KNR | GAGAN VIHAR | JAG032 | SOUTH ANARKALI (NALAH):PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 79%
389 | 1220 | KNR | GAGAN VIHAR | JAG034 | JAGAT PURI G BLK:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 98%; Peak Loading June 2019 DT-2: 83%
390 | 1220 | KNR | GAGAN VIHAR | JAG039 | R.S. PARK (PARKWALA) | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 102%; Peak Loading June 2019 DT-2: 93%
391 | 1220 | KNR | GANDHI NAGAR | GAN001 | AHATA KARAM CHAND:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 77%
392 | 1220 | KNR | GANDHI NAGAR | GAN002 | AJIT NAGAR GALI NO 8:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 93%
393 | 1220 | KNR | GANDHI NAGAR | GAN003 | AMAR MOHALLA:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 125%; Peak Loading June 2019 DT-2: 84%
394 | 1220 | KNR | GANDHI NAGAR | GAN005 | CHEMALI DEVI (INSIDE):PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 96%
395 | 1220 | KNR | GANDHI NAGAR | GAN007 | DUDLELA CHOWK:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 80%; Peak Loading June 2019 DT-2: 74%
396 | 1220 | KNR | GANDHI NAGAR | GAN008 | GALI GURDWARA NO. 2:ID | 4 | KVA DT-1: 990; KVA DT-2: 1600; KVA DT-3: 400; KVA DT-4: 400; Peak Loading June 2019 DT-1: 73%; Peak Loading June 2019 DT-2: 76%; Peak Loading June 2019 DT-3: 98%; Peak Loading June 2019 DT-4: 81%
397 | 1220 | KNR | GANDHI NAGAR | GAN010 | GANDHI NAGAR POLICE ST.:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 79%; Peak Loading June 2019 DT-2: 84%
398 | 1220 | KNR | GANDHI NAGAR | GAN012 | JANTA PARK NO. 1:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 107%; Peak Loading June 2019 DT-2: 82%; Peak Loading June 2019 DT-3: 81%
399 | 1220 | KNR | GANDHI NAGAR | GAN014 | KAILASH NAGAR NO. 1:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 82%; Peak Loading June 2019 DT-2: 68%; Peak Loading June 2019 DT-3: 60%
400 | 1220 | KNR | GANDHI NAGAR | GAN015 | KAILASH NAGAR NO. 15:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 85%; Peak Loading June 2019 DT-2: 75%; Peak Loading June 2019 DT-3: 80%
401 | 1220 | KNR | GANDHI NAGAR | GAN016 | KAILASH NAGAR SCHOOL:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 96%; Peak Loading June 2019 DT-2: 47%
402 | 1220 | KNR | GANDHI NAGAR | GAN023 | PEEPAL WALA SCHOOL:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 82%; Peak Loading June 2019 DT-2: 91%
403 | 1220 | KNR | GANDHI NAGAR | GAN024 | R. PURA GALI NO. 8:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 93%
404 | 1220 | KNR | GANDHI NAGAR | GAN025 | R.PURA GALI NO 6 (IN SIDE):PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 104%
405 | 1220 | KNR | GANDHI NAGAR | GAN028 | SEELAMPUR OLD PR. SCHOOL NO. 1:K | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; KVA DT-4: 990; Peak Loading June 2019 DT-1: 92%; Peak Loading June 2019 DT-2: 83%; Peak Loading June 2019 DT-3: 78%; Peak Loading June 2019 DT-4: 69%
406 | 1220 | KNR | GANDHI NAGAR | GAN029 | SEELAMPUR PHATAK:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 97%; Peak Loading June 2019 DT-2: 61%
407 | 1220 | KNR | GANDHI NAGAR | GAN032 | SHIV KUTI R.L.G. NO. 1:ID | 7 | 990 | 990 | 990 | 990 | 990 | 990 | 630 |  | 66% | 87% | 70% | 102% | 67% | 80% | 45%
408 | 1220 | KNR | GANDHI NAGAR | GAN033 | SUBHASH MOHALLA NO.1:PM | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 990; Peak Loading June 2019 DT-1: 71%; Peak Loading June 2019 DT-2: 86%; Peak Loading June 2019 DT-3: 87%; Peak Loading June 2019 DT-4: 94%
409 | 1220 | KNR | GANDHI NAGAR | GAN034 | AJIT NAGAR GALI NO 10:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 76%; Peak Loading June 2019 DT-2: 83%
410 | 1220 | KNR | GANDHI NAGAR | GAN036 | KOTHI BHAGWAN DAS OUTSIDE:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 111%
411 | 1220 | KNR | GANDHI NAGAR | GAN040 | GYAN MOHLLA | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 93%
412 | 1220 | KNR | GANDHI NAGAR | GAN045 | SJ/STN RATTEY WALA SUBHASH MOHALLA | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 85%
413 | 1220 | KNR | GEETA COLONY | GCL002 | ALOK BHARTI | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 95%
414 | 1220 | KNR | GEETA COLONY | GCL004 | B.T.S MULTANI MOHOLLA:PL | 2 | KVA DT-1: 990; KVA DT-2: 400; Peak Loading June 2019 DT-1: 65%; Peak Loading June 2019 DT-2: 81%
415 | 1220 | KNR | GEETA COLONY | GCL005 | JHEEL (BHOOSA MANDI):PL | 2 | KVA DT-1: 990; KVA DT-2: 400; Peak Loading June 2019 DT-1: 89%; Peak Loading June 2019 DT-2: 111%
416 | 1220 | KNR | GEETA COLONY | GCL011 | GEETA COLONY, 14 BLK:ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 96%
417 | 1220 | KNR | GEETA COLONY | GCL014 | GEETA COLONY,11, BLK:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 101%
418 | 1220 | KNR | GEETA COLONY | GCL015 | GEETA COLONY,12, BLK:K | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 76%; Peak Loading June 2019 DT-2: 88%
419 | 1220 | KNR | GEETA COLONY | GCL016 | GEETA COLONY,13, BLK:ID | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 630; Peak Loading June 2019 DT-1: 82%; Peak Loading June 2019 DT-2: 115%; Peak Loading June 2019 DT-3: 80%; Peak Loading June 2019 DT-4: 79%
420 | 1220 | KNR | GEETA COLONY | GCL017 | GEETA COLONY,15, BLK:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 53%; Peak Loading June 2019 DT-2: 106%
421 | 1220 | KNR | GEETA COLONY | GCL018 | GEETA COLONY,17, BLK COM CENTRE:PL | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 94%; Peak Loading June 2019 DT-2: 100%
422 | 1220 | KNR | GEETA COLONY | GCL019 | GEETA COLONY,17,BLK:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 121%; Peak Loading June 2019 DT-2: 99%
423 | 1220 | KNR | GEETA COLONY | GCL022 | GEETA COLONY,3, BLK:K | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 80%; Peak Loading June 2019 DT-2: 75%
424 | 1220 | KNR | GEETA COLONY | GCL024 | GEETA COLONY,6, BLK:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 81%; Peak Loading June 2019 DT-2: 93%
425 | 1220 | KNR | GEETA COLONY | GCL025 | GEETA COLONY,7, BLK:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 103%
426 | 1220 | KNR | GEETA COLONY | GCL026 | GEETA COLONY,8,BLK;PL | 2 | KVA DT-1: 990; KVA DT-2: 400; Peak Loading June 2019 DT-1: 102%; Peak Loading June 2019 DT-2: 89%
427 | 1220 | KNR | GEETA COLONY | GCL027 | GEETA COLONY,8-A,BLK:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 93%; Peak Loading June 2019 DT-2: 41%
428 | 1220 | KNR | GEETA COLONY | GCL028 | GEETA COLONY,POL.STATION | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 87%; Peak Loading June 2019 DT-2: 107%
429 | 1220 | KNR | GEETA COLONY | GCL030 | NEW LAHORE (MUNSHI COLONY):PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 111%
430 | 1220 | KNR | GEETA COLONY | GCL031 | NEW LAHORE EXTENSION:PL | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 110%; Peak Loading June 2019 DT-2: 109%
431 | 1220 | KNR | GEETA COLONY | GCL032 | RANI GARDEN NO.2,PARK WALA:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 85%; Peak Loading June 2019 DT-2: 106%
432 | 1220 | KNR | GEETA COLONY | GCL034 | RANI GARDEN SWITCHING S/STN:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 95%
433 | 1220 | KNR | GEETA COLONY | GCL035 | SARASWATI BHANDAR:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 92%
434 | 1220 | KNR | GEETA COLONY | GCL036 | SAROJINI PARK:PKG | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 83%
435 | 1220 | KNR | GEETA COLONY | GCL038 | SHASTRI PARK NAGAR, NO-2:K | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 92%
436 | 1220 | KNR | GEETA COLONY | GCL041 | SUBASH ROAD, TIKONA PARK:K | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 990; Peak Loading June 2019 DT-1: 95%; Peak Loading June 2019 DT-2: 95%; Peak Loading June 2019 DT-3: 72%; Peak Loading June 2019 DT-4: 79%
437 | 1220 | KNR | KANTI NAGAR | GAN017 | KAUSHIK PURI KIOSK:K | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 82%
438 | 1220 | KNR | KANTI NAGAR | GAN018 | KAUSHIK PURI PARK:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 54%; Peak Loading June 2019 DT-2: 78%
439 | 1220 | KNR | KANTI NAGAR | GAN026 | SATSANG MARG:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 86%; Peak Loading June 2019 DT-2: 106%
440 | 1220 | KNR | KANTI NAGAR | GAN027 | SEELAMPUR DOUBLE STORY:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 119%; Peak Loading June 2019 DT-2: 55%
441 | 1220 | KNR | KANTI NAGAR | GAN035 | CHAMELI DEVI OUTSIDE:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 82%
442 | 1220 | KNR | KANTI NAGAR | KRI002 | AZAD NAGAR WATER TANK:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 90%
443 | 1220 | KNR | KANTI NAGAR | KRI006 | BHAGAT SINGH PARK NO 1:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 114%; Peak Loading June 2019 DT-2: 115%
444 | 1220 | KNR | KANTI NAGAR | KRI023 | JHEEL NO. 4 NO 1:ID | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 23%; Peak Loading June 2019 DT-2: 79%
445 | 1220 | KNR | KANTI NAGAR | KRI026 | KANTI NAGAR EXT. GALI NO. 5:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 93%
446 | 1220 | KNR | KANTI NAGAR | KRI027 | KANTI NAGAR EXT. GALI NO. 9:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 53%; Peak Loading June 2019 DT-2: 90%
447 | 1220 | KNR | KANTI NAGAR | KRI039 | RAJGARH EXTN.(MINI STADIUM):ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 80%; Peak Loading June 2019 DT-2: 102%
448 | 1220 | KNR | KANTI NAGAR | KRI040 | RAJGARH MOTHER DAIRY GALI NO 6:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 97%; Peak Loading June 2019 DT-2: 84%
449 | 1220 | KNR | KANTI NAGAR | KRI045 | SHANKAR NAGAR MAIN ROAD SCHOOL NO 1:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 75%; Peak Loading June 2019 DT-2: 103%
450 | 1220 | KNR | KANTI NAGAR | KRI052 | WEST AZAD NAGAR (RASGULLA):PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 89%
451 | 1220 | KNR | KANTI NAGAR | KRI053 | WEST AZAD NAGAR SHD ROAD B&D BL NO. 1:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 84%; Peak Loading June 2019 DT-2: 96%; Peak Loading June 2019 DT-3: 122%
452 | 1220 | KNR | KANTI NAGAR | KRI055 | WEST AZAD NAGAR(KEHAR SINGH)RLG NO 1:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 90%; Peak Loading June 2019 DT-2: 79%
453 | 1220 | KNR | KANTI NAGAR | KRI057 | WEST KANTI NAGAR:ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 87%
454 | 1220 | KNR | KANTI NAGAR | KRI066 | East Azad Nagar Primary School | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 88%
455 | 1220 | KNR | KRISHNA NAGAR | KRI001 | A-BLOCK KRN:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 91%; Peak Loading June 2019 DT-2: 44%
456 | 1220 | KNR | KRISHNA NAGAR | KRI003 | B-BLOCK KRISHNA NAGAR 8/24:PM | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 93%
457 | 1220 | KNR | KRISHNA NAGAR | KRI004 | K-BLK KRN GHONOLI CHOWK:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 96%; Peak Loading June 2019 DT-2: 76%
458 | 1220 | KNR | KRISHNA NAGAR | KRI008 | C-BLOCK KRISHNA NAGAR NO 1:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 88%; Peak Loading June 2019 DT-2: 120%
459 | 1220 | KNR | KRISHNA NAGAR | KRI011 | D-BLOCK KRISHNA NAGAR:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 121%
460 | 1220 | KNR | KRISHNA NAGAR | KRI013 | F-BLOCK KRISHNA NAGAR:K | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 107%; Peak Loading June 2019 DT-2: 64%
461 | 1220 | KNR | KRISHNA NAGAR | KRI014 | E-BLOCK KRN (PARK) E 15,16:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 91%
462 | 1220 | KNR | KRISHNA NAGAR | KRI015 | E-BLOCK KRN LAJ PAT RAI CHOWK:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 77%; Peak Loading June 2019 DT-2: 85%
463 | 1220 | KNR | KRISHNA NAGAR | KRI017 | F-BLOCK KRN PLM:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 100%; Peak Loading June 2019 DT-2: 88%
464 | 1220 | KNR | KRISHNA NAGAR | KRI018 | H-BLOCK KRISHNA NAGAR (MOTHER DAIRY):K | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 74%; Peak Loading June 2019 DT-2: 100%
465 | 1220 | KNR | KRISHNA NAGAR | KRI019 | J-BLOCK KRN:PL | 2 | KVA DT-1: 1600; KVA DT-2: 990; Peak Loading June 2019 DT-1: 81%; Peak Loading June 2019 DT-2: 102%
466 | 1220 | KNR | KRISHNA NAGAR | KRI020 | JHEEL NO. 1:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 84%
467 | 1220 | KNR | KRISHNA NAGAR | KRI021 | JHEEL NO. 2:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 89%; Peak Loading June 2019 DT-2: 38%
468 | 1220 | KNR | KRISHNA NAGAR | KRI034 | OLD ANARKALI:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 72%; Peak Loading June 2019 DT-2: 117%; Peak Loading June 2019 DT-3: 85%
469 | 1220 | KNR | KRISHNA NAGAR | KRI035 | PANDIT PARK:PM | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 108%
470 | 1220 | KNR | KRISHNA NAGAR | KRI036 | RADHA PURI EXTN.(NALAH) NO. 1:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 92%; Peak Loading June 2019 DT-2: 60%
471 | 1220 | KNR | KRISHNA NAGAR | KRI038 | RADHA PURI NEW KRISHNA NAGAR:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 86%
472 | 1220 | KNR | KRISHNA NAGAR | KRI041 | RAM NAGAR L.N.MANDIR:PL | 1 | KVA DT-1: 1600; Peak Loading June 2019 DT-1: 92%
473 | 1220 | KNR | KRISHNA NAGAR | KRI042 | RAM NAGAR PARK(PLM) | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 56%; Peak Loading June 2019 DT-2: 84%
474 | 1220 | KNR | KRISHNA NAGAR | KRI047 | SHASTRI PARK:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 100%
475 | 1220 | KNR | KRISHNA NAGAR | KRI048 | ST.LIGHT OPP SWARN CINEMA ROAD NO 57:PM | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 90%
476 | 1220 | KNR | KRISHNA NAGAR | KRI051 | WEST ARJUN NAGAR:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 71%; Peak Loading June 2019 DT-2: 99%
477 | 1230 | LNR | ANAND VIHAR ISBT | MAN022 | JOSHI COLONY:ID | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 49%; Peak Loading June 2019 DT-2: 91%
478 | 1230 | LNR | ANAND VIHAR ISBT | MAN049 | MADHU VIHAR S/STN-1:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 81%; Peak Loading June 2019 DT-2: 93%
479 | 1230 | LNR | ANAND VIHAR ISBT | MAN052 | HASANPUR VILLAGE:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 86%
480 | 1230 | LNR | ANAND VIHAR ISBT | MAN053 | GAZIPUR VILLAGE NEAR TEMPEL:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 88%
481 | 1230 | LNR | ANAND VIHAR ISBT | MAN054 | GAZIPUR VILLAGE NEAR SCHOOL:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 100%; Peak Loading June 2019 DT-2: 68%
482 | 1230 | LNR | ANAND VIHAR ISBT | MAN066 | S/STN.NO-9, PPG CGHS:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 45%; Peak Loading June 2019 DT-2: 126%
483 | 1230 | LNR | ANAND VIHAR ISBT | MAN068 | S/STN.NO-13, PPG CGHS:ID | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 78%
484 | 1230 | LNR | ANAND VIHAR ISBT | MAN252 | S/STN NO-10, CGHS, PPG | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 18%; Peak Loading June 2019 DT-2: 113%
485 | 1230 | LNR | ANAND VIHAR ISBT | MAN292 | GAZIPUR PARK NEAR ASHOK DAIRY STN:OD | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 88%
486 | 1230 | LNR | ANAND VIHAR ISBT | PVR032 | S/STN. NO.7 F.I.E., PPG:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 85%; Peak Loading June 2019 DT-2: 68%
487 | 1230 | LNR | ANAND VIHAR ISBT | PVR034 | S/STN. NO.8 F.I.E., PPG:ID | 3 | KVA DT-1: 630; KVA DT-2: 630; KVA DT-3: 990; Peak Loading June 2019 DT-1: 92%; Peak Loading June 2019 DT-2: 74%; Peak Loading June 2019 DT-3: 87%
488 | 1230 | LNR | ANAND VIHAR ISBT | PVR035 | S/STN. NO.9 F.I.E., PPG:ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 81%
489 | 1230 | LNR | ANAND VIHAR ISBT | PVR039 | S/STN. NO.14 F.I.E., PPG:ID | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 86%; Peak Loading June 2019 DT-2: 49%
490 | 1230 | LNR | ANAND VIHAR ISBT | PVR040 | S/STN. NO.15 F.I.E., PPG:ID | 2 | KVA DT-1: 990; KVA DT-2: 400; Peak Loading June 2019 DT-1: 62%; Peak Loading June 2019 DT-2: 96%
491 | 1230 | LNR | ANAND VIHAR ISBT | PVR041 | S/STN. NO.16 F.I.E., PPG:ID | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 46%; Peak Loading June 2019 DT-2: 91%
492 | 1230 | LNR | ANAND VIHAR ISBT | PVR045 | S/STN. NO.20 F.I.E., PPG:ID | 3 | KVA DT-1: 400; KVA DT-2: 630; KVA DT-3: 630; Peak Loading June 2019 DT-1: 88%; Peak Loading June 2019 DT-2: 52%; Peak Loading June 2019 DT-3: 93%
493 | 1230 | LNR | ANAND VIHAR ISBT | PVR046 | S/STN. NO.21 F.I.E., PPG:ID | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 77%; Peak Loading June 2019 DT-2: 73%
494 | 1230 | LNR | ANAND VIHAR ISBT | PVR047 | S/STN. NO.22 F.I.E., PPG:ID | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 124%; Peak Loading June 2019 DT-2: 102%
495 | 1230 | LNR | ANAND VIHAR ISBT | PVR049 | S/STN. NO.24 F.I.E., PPG:ID | 2 | KVA DT-1: 400; KVA DT-2: 630; Peak Loading June 2019 DT-1: 54%; Peak Loading June 2019 DT-2: 91%
496 | 1230 | LNR | LAXMI NAGAR | LGR001 | PRIYADARSHINI VIHAR:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 97%; Peak Loading June 2019 DT-2: 91%
497 | 1230 | LNR | LAXMI NAGAR | LGR002 | PNB BANK ENCLAVE:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 63%; Peak Loading June 2019 DT-2: 66%; Peak Loading June 2019 DT-3: 106%
498 | 1230 | LNR | LAXMI NAGAR | LGR003 | LNR COMPLAINT CENTER:ID | 3 | KVA DT-1: 630; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 83%; Peak Loading June 2019 DT-2: 77%; Peak Loading June 2019 DT-3: 47%
499 | 1230 | LNR | LAXMI NAGAR | LGR004 | KISHAN KUNJ:K | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 105%; Peak Loading June 2019 DT-2: 130%; Peak Loading June 2019 DT-3: 133%
500 | 1230 | LNR | LAXMI NAGAR | LGR007 | WALIA NURSHING HOME:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 66%; Peak Loading June 2019 DT-2: 100%
501 | 1230 | LNR | LAXMI NAGAR | LGR008 | LALITA PARK:K | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 83%; Peak Loading June 2019 DT-2: 54%; Peak Loading June 2019 DT-3: 79%
502 | 1230 | LNR | LAXMI NAGAR | LGR009 | RAMESH PARK AKHARA:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 86%; Peak Loading June 2019 DT-2: 93%
503 | 1230 | LNR | LAXMI NAGAR | LGR011 | JAGAT RAM PARK:K | 5 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 630; KVA DT-5: 630; Peak Loading June 2019 DT-1: 94%; Peak Loading June 2019 DT-2: 92%; Peak Loading June 2019 DT-3: 94%; Peak Loading June 2019 DT-4: 76%; Peak Loading June 2019 DT-5: 70%
504 | 1230 | LNR | LAXMI NAGAR | LGR012 | GURU RAM DASS NAGAR:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 90%; Peak Loading June 2019 DT-2: 117%; Peak Loading June 2019 DT-3: 107%
505 | 1230 | LNR | LAXMI NAGAR | LGR014 | TIKONA PARK:ID | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; KVA DT-4: 630; Peak Loading June 2019 DT-1: 102%; Peak Loading June 2019 DT-2: 87%; Peak Loading June 2019 DT-3: 115%; Peak Loading June 2019 DT-4: 80%
506 | 1230 | LNR | LAXMI NAGAR | LGR016 | WEST GURU ANGAD NAGAR, SCHOOL WALA | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 76%
507 | 1230 | LNR | LAXMI NAGAR | LGR017 | POLICE QTR SHAKARPUR:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 23%; Peak Loading June 2019 DT-2: 79%
508 | 1230 | LNR | LAXMI NAGAR | LGR018 | D BLOCK KHATTA VIKAS MARG:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 73%; Peak Loading June 2019 DT-2: 84%; Peak Loading June 2019 DT-3: 61%
509 | 1230 | LNR | LAXMI NAGAR | LGR019 | RAMESH PARK J & K BLOCK:PL | 1 | KVA DT-1: 1600; Peak Loading June 2019 DT-1: 80%
510 | 1230 | LNR | LAXMI NAGAR | LGR020 | MASTER BLOCK SHAKARPUR:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 60%; Peak Loading June 2019 DT-2: 87%
511 | 1230 | LNR | LAXMI NAGAR | LGR021 | G-BLOCK SHAKARPUR:K | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 107%; Peak Loading June 2019 DT-2: 120%
512 | 1230 | LNR | LAXMI NAGAR | LGR022 | WB BLOCK SHAKARPUR:K | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 630; Peak Loading June 2019 DT-1: 104%; Peak Loading June 2019 DT-2: 99%; Peak Loading June 2019 DT-3: 88%; Peak Loading June 2019 DT-4: 101%
513 | 1230 | LNR | LAXMI NAGAR | LGR024 | SHAKARPUR SANJAY PARK | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 122%; Peak Loading June 2019 DT-2: 107%
514 | 1230 | LNR | LAXMI NAGAR | LGR025 | DALL MILL SHAKARPUR:PM | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 90%
515 | 1230 | LNR | LAXMI NAGAR | LGR026 | POLICE BOOTH S. PUR, V. MARG:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 85%
516 | 1230 | LNR | LAXMI NAGAR | LGR027 | U BLOCK SHAKARPUR, V. MARG:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 87%; Peak Loading June 2019 DT-2: 85%
517 | 1230 | LNR | LAXMI NAGAR | LGR030 | BODH VIHAR LAXMI NAGAR:K | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 82%; Peak Loading June 2019 DT-2: 92%
518 | 1230 | LNR | LAXMI NAGAR | LGR031 | MANGAL BAZAR LAXMI NAGAR:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 123%; Peak Loading June 2019 DT-2: 70%; Peak Loading June 2019 DT-3: 84%
519 | 1230 | LNR | LAXMI NAGAR | LGR032 | KULDEEP NURSING HOME LNG:K | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 91%; Peak Loading June 2019 DT-2: 93%; Peak Loading June 2019 DT-3: 73%
520 | 1230 | LNR | LAXMI NAGAR | LGR034 | MOHAN PARK LAXMI NAGAR:K | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 92%
521 | 1230 | LNR | LAXMI NAGAR | LGR035 | N.GANESH NAGAR SHAKARPUR:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 89%
522 | 1230 | LNR | LAXMI NAGAR | LGR036 | SHIROMANI SCHOOL, SHAKARPUR:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 104%; Peak Loading June 2019 DT-2: 60%
523 | 1230 | LNR | LAXMI NAGAR | LGR040 | J EXTN. LAXMI NAGAR:PM | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 117%
524 | 1230 | LNR | LAXMI NAGAR | LGR041 | KUNDAN NAGAR, LAXMI NAGAR:K | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 106%
525 | 1230 | LNR | LAXMI NAGAR | LGR042 | V. SAVARKAR BLOCK, SHAKARPUR:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 98%
526 | 1230 | LNR | LAXMI NAGAR | LGR043 | SUNDER BLOCK, SHAKARPUR:PL | 1 | KVA DT-1: 1600; Peak Loading June 2019 DT-1: 111%
527 | 1230 | LNR | LAXMI NAGAR | LGR049 | R BLOCK SHAKARPUR:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 45%; Peak Loading June 2019 DT-2: 86%
528 | 1230 | LNR | LAXMI NAGAR | LGR051 | H BLOCK LAXMI NAGAR:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 56%; Peak Loading June 2019 DT-2: 110%
529 | 1230 | LNR | LAXMI NAGAR | LGR052 | RAMESH PARK, G NO.12, LN:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 91%; Peak Loading June 2019 DT-2: 81%
530 | 1230 | LNR | LAXMI NAGAR | LGR054 | KISHAN KUNJ ENTN.:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 80%; Peak Loading June 2019 DT-2: 92%
531 | 1230 | LNR | LAXMI NAGAR | LGR080 | GALI MASJID ANAR WALI | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 113%
532 | 1230 | LNR | LAXMI NAGAR | LGR082 | E BLOCK ,VIKAS MARG | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 116%; Peak Loading June 2019 DT-2: 69%; Peak Loading June 2019 DT-3: 73%
533 | 1230 | LNR | LAXMI NAGAR | LGR083 | EK MINAR MASID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 136%; Peak Loading June 2019 DT-2: 62%
534 | 1230 | LNR | LAXMI NAGAR | LGR084 | WEST GURU ANGAD NAGER GALI NO-2 | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 91%
535 | 1230 | LNR | LAXMI NAGAR | LGR090 | SCHOOL BLOCK,PARK WALA S/S NEAR MANDIR | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 98%; Peak Loading June 2019 DT-2: 98%
536 | 1230 | LNR | LAXMI NAGAR | LGR093 | SURANA DHARAMSHALA S/S | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 44%; Peak Loading June 2019 DT-2: 84%
537 | 1230 | LNR | LAXMI NAGAR | LGR097 | A BLK P,D.VIHAR PARK NR. O/H WATER TANK | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 87%
538 | 1230 | LNR | LAXMI NAGAR | LGR100 | GYAN KUNJ | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 106%
539 | 1230 | LNR | LAXMI NAGAR | LGR101 | VEER SAVARKAR BLOCK VIKAS MARG | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 92%
540 | 1230 | LNR | LAXMI NAGAR | LGR103 | NEW WB BLOCK (NEAR AGGARWAL SWEETS) | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 92%
541 | 1230 | LNR | LAXMI NAGAR | LGR104 | NARAIN NAGAR (NEAR GARHWALI MOHALLA) | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 83%
542 | 1230 | LNR | LAXMI NAGAR | LGR108 | COMMUNITY CENTER SHAKARPUR | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 85%
543 | 1230 | LNR | LAXMI NAGAR | PVR008 | DDA FLAT NIRMAN VIHAR:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 81%; Peak Loading June 2019 DT-2: 87%
544 | 1230 | LNR | MANDAWALI | MAN003 | SOUTH GANESH NAGAR:PM | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 147%
545 | 1230 | LNR | MANDAWALI | MAN004 | SOUTH GANESH NAGAR EXTN.:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 54%; Peak Loading June 2019 DT-2: 113%
546 | 1230 | LNR | MANDAWALI | MAN006 | PANDAV NAGAR D PARK:K | 5 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 630; KVA DT-5: 630; Peak Loading June 2019 DT-1: 104%; Peak Loading June 2019 DT-2: 97%; Peak Loading June 2019 DT-3: 93%; Peak Loading June 2019 DT-4: 60%; Peak Loading June 2019 DT-5: 67%
547 | 1230 | LNR | MANDAWALI | MAN007 | PANDAV NAGAR S BLOCK:ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 88%
548 | 1230 | LNR | MANDAWALI | MAN008 | PANDAV NAGAR S BLOCK NEAR PETROL PUMP:PM | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 80%; Peak Loading June 2019 DT-2: 67%
549 | 1230 | LNR | MANDAWALI | MAN009 | J PARK PANDAV NAGAR:K | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 111%
550 | 1230 | LNR | MANDAWALI | MAN010 | GANESH NAGAR COM. E BLCK.:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 114%; Peak Loading June 2019 DT-2: 103%
551 | 1230 | LNR | MANDAWALI | MAN011 | GANESH NAGAR COM. C BLCK.:PL | 2 | KVA DT-1: 1600; KVA DT-2: 990; Peak Loading June 2019 DT-1: 94%; Peak Loading June 2019 DT-2: 55%
552 | 1230 | LNR | MANDAWALI | MAN013 | MANDAWALI A BLOCK SHIV MANDIR MARG:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 115%; Peak Loading June 2019 DT-2: 125%
553 | 1230 | LNR | MANDAWALI | MAN016 | MANDAWALI PRIMARY SCHOOL:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 114%; Peak Loading June 2019 DT-2: 62%; Peak Loading June 2019 DT-3: 106%
554 | 1230 | LNR | MANDAWALI | MAN017 | SCHOOL KHATTA-1, MANDAWALI:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 115%; Peak Loading June 2019 DT-2: 86%
555 | 1230 | LNR | MANDAWALI | MAN018 | SCHOOL KHATTA-II,MANDAWALI:PM | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 95%
556 | 1230 | LNR | MANDAWALI | MAN019 | MANDAWALI UNCHEPAR;PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 110%; Peak Loading June 2019 DT-2: 81%
557 | 1230 | LNR | MANDAWALI | MAN021 | MANDAWALI SUBJI MANDI:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 95%; Peak Loading June 2019 DT-2: 108%
558 | 1230 | LNR | MANDAWALI | MAN023 | UTTARY SCHOOL BLOCK:K | 3 | KVA DT-1: 990; KVA DT-2: 630; KVA DT-3: 630; Peak Loading June 2019 DT-1: 117%; Peak Loading June 2019 DT-2: 114%; Peak Loading June 2019 DT-3: 97%
559 | 1230 | LNR | MANDAWALI | MAN024 | CHANDERVIHAR SS-1:ID | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 72%; Peak Loading June 2019 DT-2: 103%
560 | 1230 | LNR | MANDAWALI | MAN025 | CHANDERVIHAR SS-II:ID | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 119%; Peak Loading June 2019 DT-2: 107%
561 | 1230 | LNR | MANDAWALI | MAN026 | WESTVINOD NAGAR NEAR MANGLAM:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 95%; Peak Loading June 2019 DT-2: 172%; Peak Loading June 2019 DT-3: 107%
562 | 1230 | LNR | MANDAWALI | MAN027 | WESTVINOD NAGAR D BLOCK:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 75%; Peak Loading June 2019 DT-2: 128%
563 | 1230 | LNR | MANDAWALI | MAN029 | A BLOCK WESTVINOD NAGAR | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 123%; Peak Loading June 2019 DT-2: 120%
564 | 1230 | LNR | MANDAWALI | MAN030 | E BLOCK WESTVINOD NAGAR:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 84%; Peak Loading June 2019 DT-2: 94%
565 | 1230 | LNR | MANDAWALI | MAN031 | MOHAN BABA MANDIR MANDAWALI:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 130%; Peak Loading June 2019 DT-2: 52%
566 | 1230 | LNR | MANDAWALI | MAN032 | SONIYA VIHAR MANDAWALI:PL | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 108%
567 | 1230 | LNR | MANDAWALI | MAN033 | B BLOCK MANDAWALI:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 112%; Peak Loading June 2019 DT-2: 64%; Peak Loading June 2019 DT-3: 33%
568 | 1230 | LNR | MANDAWALI | MAN034 | C BLOCK WESTVINOD NAGAR:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 108%; Peak Loading June 2019 DT-2: 106%
569 | 1230 | LNR | MANDAWALI | MAN037 | SHANKAR MARG MANDAWALI:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 130%
570 | 1230 | LNR | MANDAWALI | MAN038 | KRISHNA PURI MANDAWALI:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 93%
571 | 1230 | LNR | MANDAWALI | MAN039 | ALLAH COLONY MANDAWALI:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 98%
572 | 1230 | LNR | MANDAWALI | MAN059 | S/STN.NO-2, PPG CGHS:ID | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 101%
573 | 1230 | LNR | MANDAWALI | MAN212 | RAILWAY COLONY GALI NO. 2:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 107%; Peak Loading June 2019 DT-2: 79%
574 | 1230 | LNR | MANDAWALI | MAN247 | Budha marg Mandawali | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 96%
575 | 1230 | LNR | MANDAWALI | MAN273 | Ew S/S D-Blk Ramleela Ground Pandav Ngr | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 91%; Peak Loading June 2019 DT-2: 65%
576 | 1230 | LNR | MANDAWALI | MAN274 | Gnpn Complex, Rob-36 Pandav Nagar | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 103%
577 | 1230 | LNR | MANDAWALI | MAN296 | SOUTH GANESH NAGAR (NEAR RAILWAY LINE) | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 100%
578 | 1230 | LNR | PREET VIHAR | PVR001 | G-II, PREET VIHAR:ID | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 117%; Peak Loading June 2019 DT-2: 97%
579 | 1230 | LNR | PREET VIHAR | PVR006 | B BLOCK, PREET VIHAR:ID | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 33%; Peak Loading June 2019 DT-2: 77%
580 | 1230 | LNR | PREET VIHAR | PVR009 | EAST GURU ANGAD NAGAR:K | 3 | KVA DT-1: 630; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 106%; Peak Loading June 2019 DT-2: 127%; Peak Loading June 2019 DT-3: 111%
581 | 1230 | LNR | PREET VIHAR | PVR015 | G-I, PREET VIHAR:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 103%; Peak Loading June 2019 DT-2: 89%
582 | 1230 | LNR | PREET VIHAR | PVR018 | C-BLOCK, PREET VIHAR:ID | 3 | KVA DT-1: 630; KVA DT-2: 630; KVA DT-3: 630; Peak Loading June 2019 DT-1: 98%; Peak Loading June 2019 DT-2: 77%; Peak Loading June 2019 DT-3: 53%
583 | 1230 | LNR | PREET VIHAR | PVR019 | NIRMAN VIHAR (NEAR MKT.):ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 81%; Peak Loading June 2019 DT-2: 61%; Peak Loading June 2019 DT-3: 64%
584 | 1230 | LNR | PREET VIHAR | PVR021 | BHARATI ARTIST COLONY:K | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 124%
585 | 1230 | LNR | PREET VIHAR | PVR026 | B-BLOCK, PREET VIHAR, NEAR MKT.:ID | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 83%
586 | 1230 | LNR | PREET VIHAR | PVR067 | Swasthya vihar kiosk Vikas Marg | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 109%; Peak Loading June 2019 DT-2: 79%
587 | 1230 | LNR | PREET VIHAR | PVR068 | CHITRA VIHAR:ID | 3 | KVA DT-1: 630; KVA DT-2: 630; KVA DT-3: 630; Peak Loading June 2019 DT-1: 84%; Peak Loading June 2019 DT-2: 90%; Peak Loading June 2019 DT-3: 38%
588 | 1230 | LNR | PREET VIHAR | PVR082 | E-BLK PREET VIHAR(NEAR E-95 PREET VIHAR) | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 93%
589 | 1240 | MVR | S/STN 8 POCKET C | MV2002 | 15 BLCOK KALYAN PURI:K | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 53%; Peak Loading June 2019 DT-2: 89%
590 | 1240 | MVR | S/STN 8 POCKET C | MV2004 | 13 & 18 BLK,KALYANPURI | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 97%; Peak Loading June 2019 DT-2: 82%
591 | 1240 | MVR | S/STN 8 POCKET C | MV2005 | 17 BLOCK KLP:PL | 3 | KVA DT-1: 630; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 56%; Peak Loading June 2019 DT-2: 82%; Peak Loading June 2019 DT-3: 79%
592 | 1240 | MVR | S/STN 8 POCKET C | MV2007 | KHP VILLAGE MAIN ROAD:PL | 2 | KVA DT-1: 630; KVA DT-2: 400; Peak Loading June 2019 DT-1: 88%; Peak Loading June 2019 DT-2: 72%
593 | 1240 | MVR | S/STN 8 POCKET C | MV2009 | A BLOCK V. NAGAR:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 94%
594 | 1240 | MVR | S/STN 8 POCKET C | MV2010 | E BLOCK V. NAGAR:PL | 3 | KVA DT-1: 630; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 104%; Peak Loading June 2019 DT-2: 111%; Peak Loading June 2019 DT-3: 56%
595 | 1240 | MVR | S/STN 8 POCKET C | MV2018 | S/S NO. 5 PKT. B :ID | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 81%; Peak Loading June 2019 DT-2: 71%
596 | 1240 | MVR | S/STN 8 POCKET C | MV2025 | S/S NO. 4 PKT-E MVR II:ID | 2 | KVA DT-1: 400; KVA DT-2: 630; Peak Loading June 2019 DT-1: 58%; Peak Loading June 2019 DT-2: 85%
597 | 1240 | MVR | S/STN 8 POCKET C | MV2034 | D BLOCK GAZIPUR:ID | 2 | KVA DT-1: 630; KVA DT-2: 400; Peak Loading June 2019 DT-1: 47%; Peak Loading June 2019 DT-2: 83%
598 | 1240 | MVR | S/STN 8 POCKET C | MV2036 | DDA JANTA FLAT GAZIPUR:ID | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 58%; Peak Loading June 2019 DT-2: 92%
599 | 1240 | MVR | S/STN 8 POCKET C | MV2037 | S/S NO. 1 PKT A MVR-II:ID | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 96%
600 | 1240 | MVR | S/STN 8 POCKET C | MV2041 | S/S NO. 1 KHR COLONY:ID | 2 | KVA DT-1: 990; KVA DT-2: 400; Peak Loading June 2019 DT-1: 79%; Peak Loading June 2019 DT-2: 86%
601 | 1240 | MVR | S/STN 8 POCKET C | MV2043 | S/S -10 BLK KHP. COROM:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 43%; Peak Loading June 2019 DT-2: 110%
602 | 1240 | MVR | S/STN 8 POCKET C | MV2045 | S/S 8 BLK KHP COLONY:PL | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 98%; Peak Loading June 2019 DT-2: 41%
603 | 1240 | MVR | S/STN 8 POCKET C | MV2046 | S/S 10 BLK KHP COLONY (OLD):PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 88%
604 | 1240 | MVR | S/STN 8 POCKET C | MV2047 | S/S 2 BLK KHP COLONY:ID | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 119%; Peak Loading June 2019 DT-2: 68%
605 | 1240 | MVR | S/STN 8 POCKET C | MV2062 | D BLK EAST VINOD NAGAR | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 98%
606 | 1240 | MVR | S/STN 8 POCKET C | MV2064 | R BLOCK EAST VINOD NGR SPER SHINE | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 81%
607 | 1240 | MVR | SADAR APPARTMENTS | MV1007 | ACHARYA NIKETAN PL/M:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 76%
608 | 1240 | MVR | SADAR APPARTMENTS | MV1008 | ACHARYA NIKETAN:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 69%; Peak Loading June 2019 DT-2: 86%; Peak Loading June 2019 DT-3: 100%
609 | 1240 | MVR | SADAR APPARTMENTS | MV1009 | SHASHI GARDEN PLM:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 131%; Peak Loading June 2019 DT-2: 61%
610 | 1240 | MVR | SADAR APPARTMENTS | MV1018 | S/S-2 PKT-I MVR PH-I:ID | 3 | KVA DT-1: 630; KVA DT-2: 630; KVA DT-3: 630; Peak Loading June 2019 DT-1: 86%; Peak Loading June 2019 DT-2: 68%; Peak Loading June 2019 DT-3: 35%
611 | 1240 | MVR | SADAR APPARTMENTS | MV1023 | S/S-B PKT-2 MVR PH-I:ID | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 85%; Peak Loading June 2019 DT-2: 52%
612 | 1240 | MVR | SADAR APPARTMENTS | MV1024 | PARTAP NAGAR PLM:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 106%
613 | 1240 | MVR | SADAR APPARTMENTS | MV1028 | S/S-2 PKT IV MVR PH-1:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 55%; Peak Loading June 2019 DT-2: 90%
614 | 1240 | MVR | SADAR APPARTMENTS | MV1046 | STN-8 PKT-1 MVR-1(SWITCHING STN) | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 93%; Peak Loading June 2019 DT-2: 22%
615 | 1240 | MVR | SADAR APPARTMENTS | MV1058 | CHILLA VILLAGE (OLD):PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 88%
616 | 1240 | MVR | SADAR APPARTMENTS | MV1074 | ADRESH MOHALLA:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 84%; Peak Loading June 2019 DT-2: 96%
617 | 1240 | MVR | SADAR APPARTMENTS | MV1075 | SAMASPUR VILLAGE:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 63%; Peak Loading June 2019 DT-2: 84%; Peak Loading June 2019 DT-3: 42%
618 | 1240 | MVR | SADAR APPARTMENTS | MV1077 | PATPAR GANJ VILLAGE:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 98%; Peak Loading June 2019 DT-2: 58%
619 | 1240 | MVR | SADAR APPARTMENTS | MV1092 | S.S 1 CGHS MVR PH 1:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 101%; Peak Loading June 2019 DT-2: 62%; Peak Loading June 2019 DT-3: 118%
620 | 1240 | MVR | SADAR APPARTMENTS | MV1106 | S/S-4 PKT-5 PH-1:ID | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 96%
621 | 1240 | MVR | SADAR APPARTMENTS | MV1107 | NEW S/S SHASHIGARDEN:PLM | 3 | KVA DT-1: 630; KVA DT-2: 630; KVA DT-3: 630; Peak Loading June 2019 DT-1: 71%; Peak Loading June 2019 DT-2: 109%; Peak Loading June 2019 DT-3: 90%
622 | 1240 | MVR | SADAR APPARTMENTS | MV1117 | STN-4 CHILLA VIL NR DDA FLAT | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 84%
623 | 1240 | MVR | TRILOKPURI | TKP003 | 7 BLOCK TKP:K | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 88%; Peak Loading June 2019 DT-2: 85%
624 | 1240 | MVR | TRILOKPURI | TKP005 | 10 BLOCK TKP:PL | 2 | KVA DT-1: 400; KVA DT-2: 630; Peak Loading June 2019 DT-1: 90%; Peak Loading June 2019 DT-2: 69%
625 | 1240 | MVR | TRILOKPURI | TKP006 | 18 BLOCK TKP:PL:ID | 2 | KVA DT-1: 630; KVA DT-2: 100; Peak Loading June 2019 DT-1: 90%; Peak Loading June 2019 DT-2: 126%
626 | 1240 | MVR | TRILOKPURI | TKP007 | 13 BLOCK TKP:ID | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 103%; Peak Loading June 2019 DT-2: 93%
627 | 1240 | MVR | TRILOKPURI | TKP008 | 23 BLOCK TKP:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 95%; Peak Loading June 2019 DT-2: 113%
628 | 1240 | MVR | TRILOKPURI | TKP012 | 26 BLOCK TKP:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 90%; Peak Loading June 2019 DT-2: 88%
629 | 1240 | MVR | TRILOKPURI | TKP013 | 134 WORK CENTER:ID | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 85%; Peak Loading June 2019 DT-2: 58%
630 | 1240 | MVR | TRILOKPURI | TKP014 | 320 EWS CHILLA DDA FLAT,TKP | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 82%
631 | 1240 | MVR | TRILOKPURI | TKP016 | 31 BLOCK TKP:K | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 124%; Peak Loading June 2019 DT-2: 70%
632 | 1240 | MVR | TRILOKPURI | TKP018 | 28 BLOCK TKP:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 85%; Peak Loading June 2019 DT-2: 72%
633 | 1240 | MVR | TRILOKPURI | TKP020 | KOTLA VILLAGE:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 70%; Peak Loading June 2019 DT-2: 103%
634 | 1240 | MVR | TRILOKPURI | TKP023 | 17 BLOCK TKP:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 109%; Peak Loading June 2019 DT-2: 115%
635 | 1240 | MVR | TRILOKPURI | TKP024 | 2 BLOCK TKP:PL | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 121%; Peak Loading June 2019 DT-2: 74%
636 | 1240 | MVR | TRILOKPURI | TKP025 | 15 BLOCK TKP:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 89%
637 | 1240 | MVR | TRILOKPURI | TKP027 | 11&12 BLOCK TRILOK TRILOK PURI | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 95%; Peak Loading June 2019 DT-2: 90%
638 | 1240 | MVR | TRILOKPURI | TKP030 | KOTLA VILLAGE NEW | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 107%
639 | 1240 | MVR | TRILOKPURI | TKP032 | NEW 28 BLOCK TRILOKPURI | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 103%
640 | 1241 | MV3 | MVR-III | VSE004 | S/STN 5 A2 PKT MVR-III:ID | 2 | KVA DT-1: 400; KVA DT-2: 400; Peak Loading June 2019 DT-1: 57%; Peak Loading June 2019 DT-2: 110%
641 | 1241 | MV3 | MVR-III | VSE008 | S/STN 9 A2 PKT MVR - III:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 35%; Peak Loading June 2019 DT-2: 87%
642 | 1241 | MV3 | MVR-III | VSE011 | S/STN B5 DDA JANTA FLATE:ID | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 92%
643 | 1241 | MV3 | MVR-III | VSE012 | S/STN 3 B-7 DDA JANTA FLAT:ID | 2 | KVA DT-1: 400; KVA DT-2: 400; Peak Loading June 2019 DT-1: 119%; Peak Loading June 2019 DT-2: 71%
644 | 1241 | MV3 | MVR-III | VSE014 | S/STN C-1 PKT DDA JANTA FLAT:ID | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 84%
645 | 1241 | MV3 | MVR-III | VSE015 | S/STN C-2 PKT DDA JANTA FLAT:ID | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 105%
646 | 1241 | MV3 | MVR-III | VSE036 | SUBJI MANDI HARIJAN BASTI KNODLI:K | 2 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 122%
647 | 1241 | MV3 | MVR-III | VSE037 | KNODLI VILL. PANCHYAT GHAR:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 80%
648 | 1241 | MV3 | MVR-III | VSE039 | KNODLI INDAL PUBLIC SCHOOL:PM | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 108%
649 | 1241 | MV3 | MVR-III | VSE042 | B-BLK RAJBIR COLONY:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 77%; Peak Loading June 2019 DT-2: 73%
650 | 1241 | MV3 | MVR-III | VSE045 | GHARAOLI VILL. OLD:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 80%
651 | 1241 | MV3 | MVR-III | VSE046 | GHARAOLI VILL. NEW:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 79%
652 | 1241 | MV3 | MVR-III | VSE142 | STN 3 GHAROLI DAIRY CL MVR PH-3:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 106%; Peak Loading June 2019 DT-2: 83%
653 | 1241 | MV3 | MVR-III | VSE143 | STN 4 GHAROLI DAIRY CL MVR PH-3:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 101%; Peak Loading June 2019 DT-2: 106%
654 | 1241 | MV3 | MVR-III | VSE163 | S/S-2 C-BLK HARIZAN BASTI,MULLA CLY:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 114%
655 | 1241 | MV3 | NEW ASHOK NAGAR | VSE103 | ABLK NEW ASHOK NAGAR:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 103%; Peak Loading June 2019 DT-2: 80%
656 | 1241 | MV3 | NEW ASHOK NAGAR | VSE104 | ABLK (LOOP) NEW ASHOK NAGAR:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 115%; Peak Loading June 2019 DT-2: 66%
657 | 1241 | MV3 | NEW ASHOK NAGAR | VSE105 | B BLK NEW ASHOK NAGAR:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 96%; Peak Loading June 2019 DT-2: 77%
658 | 1241 | MV3 | NEW ASHOK NAGAR | VSE106 | B1 BLK NEW ASHOK NAGAR:ID | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 64%; Peak Loading June 2019 DT-2: 91%
659 | 1241 | MV3 | NEW ASHOK NAGAR | VSE107 | B2 BLK NEW ASHOK NAGAR:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 124%; Peak Loading June 2019 DT-2: 102%
660 | 1241 | MV3 | NEW ASHOK NAGAR | VSE108 | C2 BLK NEW ASHOK NAGAR:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 86%; Peak Loading June 2019 DT-2: 112%
661 | 1241 | MV3 | NEW ASHOK NAGAR | VSE109 | C3 BLK NEW ASHOK NAGAR:ID | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 145%; Peak Loading June 2019 DT-2: 85%
662 | 1241 | MV3 | NEW ASHOK NAGAR | VSE110 | C4 BLK NEW ASHOK NAGAR:ID | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 116%; Peak Loading June 2019 DT-2: 67%
663 | 1241 | MV3 | NEW ASHOK NAGAR | VSE111 | C5 BLK NEW ASHOK NAGAR:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 94%; Peak Loading June 2019 DT-2: 109%
664 | 1241 | MV3 | NEW ASHOK NAGAR | VSE112 | D BLK NEW ASHOK NAGAR:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 64%; Peak Loading June 2019 DT-2: 95%
665 | 1241 | MV3 | NEW ASHOK NAGAR | VSE113 | E1 BLK NEW ASHOK NAGAR:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 78%; Peak Loading June 2019 DT-2: 58%
666 | 1241 | MV3 | NEW ASHOK NAGAR | VSE114 | E2 BLK NEW ASHOK NAGAR:ID | 2 | KVA DT-1: 630; KVA DT-2: 400; Peak Loading June 2019 DT-1: 164%; Peak Loading June 2019 DT-2: 128%
667 | 1241 | MV3 | VASUNDHARA ENCLAVE | VSE031 | S/STN 9 MIXED HOUSING MVR III:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 74%; Peak Loading June 2019 DT-2: 100%
668 | 1241 | MV3 | VASUNDHARA ENCLAVE | VSE035 | S/STN D-BLK NEW KNODLI:ID | 2 | KVA DT-1: 400; KVA DT-2: 400; Peak Loading June 2019 DT-1: 47%; Peak Loading June 2019 DT-2: 94%
669 | 1241 | MV3 | VASUNDHARA ENCLAVE | VSE048 | DALLUPURA VILL. DURGA PARK:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 81%; Peak Loading June 2019 DT-2: 136%
670 | 1241 | MV3 | VASUNDHARA ENCLAVE | VSE172 | DALLUPURA HARIZAN BASTI SUB STN. | 3 | KVA DT-1: 630; KVA DT-2: 630; KVA DT-3: 630; Peak Loading June 2019 DT-1: 98%; Peak Loading June 2019 DT-2: 90%; Peak Loading June 2019 DT-3: 70%
671 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM001 | C-4 YAMUNA VIHAR:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 102%
672 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM003 | C-6, YAMUNA VIHAR:PG | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 110%; Peak Loading June 2019 DT-2: 98%
673 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM005 | C-7, YAMUNA VIHAR:ID | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 61%; Peak Loading June 2019 DT-2: 103%
674 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM006 | C-7/2, YAMUNA VIHAR:ID | 2 | KVA DT-1: 400; KVA DT-2: 630; Peak Loading June 2019 DT-1: 26%; Peak Loading June 2019 DT-2: 88%
675 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM007 | C-8 YAMUNA VIHAR:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 97%; Peak Loading June 2019 DT-2: 75%; Peak Loading June 2019 DT-3: 70%
676 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM008 | C-11 YAMUNA VIHAR:ID | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 83%; Peak Loading June 2019 DT-2: 78%
677 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM009 | C-12, YAMUNA VIHAR:ID | 2 | KVA DT-1: 990; KVA DT-2: 400; Peak Loading June 2019 DT-1: 49%; Peak Loading June 2019 DT-2: 92%
678 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM011 | B-2 YAMUNA VIHAR:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 93%
679 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM012 | B-4 YAMUNA VIHAR:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 60%; Peak Loading June 2019 DT-2: 105%
680 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM015 | PUMPING STATION BHAJAN PURA :ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 118%
681 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM017 | C-BLOCK GALI NO7 BHAJAN PURA:PL | 1 | KVA DT-1: 1600; Peak Loading June 2019 DT-1: 101%
682 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM018 | K-BLOCK GHONDA:ID | 3 | KVA DT-1: 990; KVA DT-2: 630; KVA DT-3: 630; Peak Loading June 2019 DT-1: 36%; Peak Loading June 2019 DT-2: 96%; Peak Loading June 2019 DT-3: 182%
683 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM019 | DISPENSERY BHAJAN PURA:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 148%; Peak Loading June 2019 DT-2: 117%
684 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM020 | D-BLOCK, SANJAY MOHALLA:K | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 92%; Peak Loading June 2019 DT-2: 121%
685 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM021 | NOOR-E-ILLAHI:K | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 72%; Peak Loading June 2019 DT-2: 136%; Peak Loading June 2019 DT-3: 90%
686 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM025 | GHONDA CHOWK:K | 4 | KVA DT-1: 630; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 630; Peak Loading June 2019 DT-1: 85%; Peak Loading June 2019 DT-2: 87%; Peak Loading June 2019 DT-3: 99%; Peak Loading June 2019 DT-4: 61%
687 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM027 | CHET RAM MAUJ PUR:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 135%; Peak Loading June 2019 DT-2: 135%; Peak Loading June 2019 DT-3: 107%
688 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM028 | SUBJI MANDI-1 MAUJ PUR | 1 | KVA DT-1: 1600; Peak Loading June 2019 DT-1: 107%
689 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM030 | BABU RAM CHOWK MAUJ PUR:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 76%; Peak Loading June 2019 DT-2: 77%
690 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM031 | SANDHYA PUBLIC SCHOOL:PL | 2 | KVA DT-1: 990; KVA DT-2: 400; Peak Loading June 2019 DT-1: 105%; Peak Loading June 2019 DT-2: 94%
691 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM033 | SUBHASH MOHALLA NO-1:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 123%
692 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM034 | SUBHASH MOHALLA NO.-2:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 400; Peak Loading June 2019 DT-1: 95%; Peak Loading June 2019 DT-2: 105%; Peak Loading June 2019 DT-3: 93%
693 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM036 | VIJAY PARK KIOSK:K | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 106%; Peak Loading June 2019 DT-2: 129%
694 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM038 | VIJAY PARK SHIV SADHAN MANDIR:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 108%
695 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM039 | VIJAY PARK NEAR NURSARY:PL | 2 | KVA DT-1: 630; KVA DT-2: 400; Peak Loading June 2019 DT-1: 128%; Peak Loading June 2019 DT-2: 115%
696 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM041 | NALA NO.4 MAUJPUR:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 118%; Peak Loading June 2019 DT-2: 114%
697 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM042 | SETH BHAGWAN DAS MAUJ PUR:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 95%
698 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM043 | CRESENT PUBLIC SCHOOL MAUJ PUR:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 104%; Peak Loading June 2019 DT-2: 112%
699 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM044 | ZAMALO KA BAGH MAUJ PUR:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 29%; Peak Loading June 2019 DT-2: 100%
700 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM045 | VIJAY MOHALLA GALI NO 11:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 107%
701 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM048 | C- 9 YAMUNA VIHAR:PG | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 119%
702 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM053 | MOHANPURI NO-2 OUTSIDE SCHOOL | 2 | KVA DT-1: 630; KVA DT-2: 400; Peak Loading June 2019 DT-1: 123%; Peak Loading June 2019 DT-2: 93%
703 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM054 | SUBHASH MOHALLA NO.-3:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 88%; Peak Loading June 2019 DT-2: 75%
704 | 1250 | YVR | C-12 YAMUNA VIHAR | YAM060 | C-1, YVR NEAR ANAND SAGAR | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 113%
705 | 1250 | YVR | GHONDA | GHO001 | A BLOCK BHAJANPURA GALI NO. -3:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 91%
706 | 1250 | YVR | GHONDA | GHO002 | B BLOCK BHAJANPURA:K | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 111%; Peak Loading June 2019 DT-2: 128%; Peak Loading June 2019 DT-3: 126%
707 | 1250 | YVR | GHONDA | GHO003 | D BLOCK BHAJANPURA:K | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 103%; Peak Loading June 2019 DT-2: 103%; Peak Loading June 2019 DT-3: 103%
708 | 1250 | YVR | GHONDA | GHO006 | SOUTH GAMRI KIOSK:K | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 55%; Peak Loading June 2019 DT-2: 91%
709 | 1250 | YVR | GHONDA | GHO007 | GAMRHI VILLAGE:PL | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 95%; Peak Loading June 2019 DT-2: 93%
710 | 1250 | YVR | GHONDA | GHO008 | GAMRI KIOSK:K | 1 | KVA DT-1: 1600; Peak Loading June 2019 DT-1: 76%
711 | 1250 | YVR | GHONDA | GHO009 | ARVIND NAGAR PRIMARY SCHOOL GAUTAM VIHAR:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 98%; Peak Loading June 2019 DT-2: 69%; Peak Loading June 2019 DT-3: 47%
712 | 1250 | YVR | GHONDA | GHO010 | GAUTAM VIHAR KIOSK:K | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 108%; Peak Loading June 2019 DT-2: 88%
713 | 1250 | YVR | GHONDA | GHO011 | JAI PRAKASH NO-1:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 97%
714 | 1250 | YVR | GHONDA | GHO012 | JAI PRAKASH NO-2:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 105%
715 | 1250 | YVR | GHONDA | GHO013 | KARTAR NAGAR HOTEL WALA:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 113%
716 | 1250 | YVR | GHONDA | GHO014 | 3.5 PUSTA KARTAR NAGAR:K | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 111%; Peak Loading June 2019 DT-2: 88%
717 | 1250 | YVR | GHONDA | GHO015 | JAGJEET NAGAR KIOSK:K | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 103%; Peak Loading June 2019 DT-2: 125%; Peak Loading June 2019 DT-3: 94%
718 | 1250 | YVR | GHONDA | GHO016 | 3 RD JAGJEET NAGAR :PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 91%
719 | 1250 | YVR | GHONDA | GHO017 | VIJAY COLONY:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 141%
720 | 1250 | YVR | GHONDA | GHO018 | USMANPUR PUSTA NO-2:PL | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 86%; Peak Loading June 2019 DT-2: 87%
721 | 1250 | YVR | GHONDA | GHO019 | KHADDEY WALI MASJID:PM | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 148%
722 | 1250 | YVR | GHONDA | GHO020 | MONI BABA MANDIR:K | 3 | KVA DT-1: 990; KVA DT-2: 630; KVA DT-3: 990; Peak Loading June 2019 DT-1: 110%; Peak Loading June 2019 DT-2: 133%; Peak Loading June 2019 DT-3: 103%
723 | 1250 | YVR | GHONDA | GHO021 | R BLOCK BRAHAMPURI:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 87%
724 | 1250 | YVR | GHONDA | GHO023 | BRAMPURI NO-6 NEAR MANDIR:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 95%
725 | 1250 | YVR | GHONDA | GHO024 | X BL BRAHAMPURI RAMNIWAS WALA:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 95%; Peak Loading June 2019 DT-2: 44%; Peak Loading June 2019 DT-3: 72%
726 | 1250 | YVR | GHONDA | GHO025 | X BL BRAHAMPURI KHATTEY WALA:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 91%; Peak Loading June 2019 DT-2: 77%
727 | 1250 | YVR | GHONDA | GHO026 | X BL BRAHAMPURI BHISHAM WALA:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 97%
728 | 1250 | YVR | GHONDA | GHO035 | BALLU KA TUBEWELL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 88%
729 | 1250 | YVR | GHONDA | GHO038 | MAIN BRAHMPURI RD GALI NO.7:PM | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 94%
730 | 1250 | YVR | GHONDA | GHO040 | MAIN BRAHMPURI RD GALI NO.19:PM | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 123%
731 | 1250 | YVR | GHONDA | GHO041 | MAIN BRAHMPURI RD GALI NO. 24 | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 79%
732 | 1250 | YVR | GHONDA | GHO042 | MAIN BRAHMPURI RD GALI NO. 23:PM | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 108%
733 | 1250 | YVR | GHONDA | GHO054 | D-BLOCK GAMRI EXTR S/ST | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 64%; Peak Loading June 2019 DT-2: 102%
734 | 1250 | YVR | GHONDA | GHO056 | A BLOCK BHAJANPURA GALI NO. -2:P/M | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 105%
735 | 1250 | YVR | GHONDA | YAM032 | GAMRI ROAD PUMP HOUSE:PL | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 70%; Peak Loading June 2019 DT-2: 96%
736 | 1250 | YVR | NEW SEELAMPUR | SLM010 | RISHI KARDOM MARG:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 79%
737 | 1250 | YVR | NEW SEELAMPUR | SLM011 | BRAHMPURI NO-I:PL | 2 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 89%
738 | 1250 | YVR | NEW SEELAMPUR | SLM013 | OUTSIDE KOTHI ZAFRABAD:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 83%; Peak Loading June 2019 DT-2: 53%
739 | 1250 | YVR | NEW SEELAMPUR | SLM014 | INSIDE KOTHI ZAFRABAD:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 54%; Peak Loading June 2019 DT-2: 89%
740 | 1250 | YVR | NEW SEELAMPUR | SLM015 | KHATTA ROAD NO 66 ZAFRABAD:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 86%; Peak Loading June 2019 DT-2: 99%
741 | 1250 | YVR | NEW SEELAMPUR | SLM016 | OUTSIDE SCHOOL ZAFRABAD:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 78%; Peak Loading June 2019 DT-2: 65%
742 | 1250 | YVR | NEW SEELAMPUR | SLM017 | NALA NO 1 SEELAMPUR:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 64%; Peak Loading June 2019 DT-2: 79%; Peak Loading June 2019 DT-3: 78%
743 | 1250 | YVR | NEW SEELAMPUR | SLM018 | SBI WELCOME:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 93%; Peak Loading June 2019 DT-2: 83%; Peak Loading June 2019 DT-3: 56%
744 | 1250 | YVR | NEW SEELAMPUR | SLM019 | PHOTO CHOCK WELCOME:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 125%; Peak Loading June 2019 DT-2: 102%; Peak Loading June 2019 DT-3: 67%
745 | 1250 | YVR | NEW SEELAMPUR | SLM020 | Z-2 BLOCK WELCOME:PL | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 71%; Peak Loading June 2019 DT-2: 93%
746 | 1250 | YVR | NEW SEELAMPUR | SLM021 | KABOOTER MARKET WELCOME:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 61%; Peak Loading June 2019 DT-2: 109%; Peak Loading June 2019 DT-3: 74%
747 | 1250 | YVR | NEW SEELAMPUR | SLM044 | CHAUHAN BANGAR GALI NO 10:PL | 5 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 990; KVA DT-5: 990; Peak Loading June 2019 DT-1: 52%; Peak Loading June 2019 DT-2: 66%; Peak Loading June 2019 DT-3: 87%; Peak Loading June 2019 DT-4: 82%; Peak Loading June 2019 DT-5: 80%
748 | 1250 | YVR | NEW SEELAMPUR | SLM056 | OPP MAZAR BRAHMPURI ROAD:PM | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 102%
749 | 1250 | YVR | NEW SEELAMPUR | SLM057 | CHAUHAN BANGAR GALI NO 5:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 98%; Peak Loading June 2019 DT-2: 67%
750 | 1250 | YVR | NEW SEELAMPUR | SLM060 | JANTA COLONY NO-2 | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 86%
751 | 1250 | YVR | NEW SEELAMPUR | SLM061 | JANTA COLONY NO-3 | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 94%
752 | 1250 | YVR | NEW SEELAMPUR | SLM073 | ARORA BLDG GALI-24 CHAUHAN | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 85%
753 | 1250 | YVR | SHASTRI PARK | SLM001 | USMAN PUR KIOSK:K | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 94%; Peak Loading June 2019 DT-2: 119%
754 | 1250 | YVR | SHASTRI PARK | SLM005 | GAUTAM PURI NO.1:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 103%
755 | 1250 | YVR | SHASTRI PARK | SLM007 | BHAGAT SINGH MOHALLA:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 87%
756 | 1250 | YVR | SHASTRI PARK | SLM027 | H BLOCK SEELAMPUR:PL | 2 | KVA DT-1: 990; KVA DT-2: 400; Peak Loading June 2019 DT-1: 77%; Peak Loading June 2019 DT-2: 52%
757 | 1250 | YVR | SHASTRI PARK | SLM034 | RAJU WALA SHASTRI PARK:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 81%
758 | 1250 | YVR | SHASTRI PARK | SLM086 | ENGG COLL GAUTAM PUR NO-3:PL | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 66%; Peak Loading June 2019 DT-2: 77%
759 | 1251 | KWR | GOKUL PURI | KWL001 | RAJEEV GANDHI NAGAR GALI NO.-3:ID | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 105%; Peak Loading June 2019 DT-2: 79%
760 | 1251 | KWR | GOKUL PURI | KWL003 | RAJEEV GANDHI NAGAR GALI NO.-15:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 84%; Peak Loading June 2019 DT-2: 89%
761 | 1251 | KWR | GOKUL PURI | KWL004 | RAJEEV GANDHI NAGAR GALI NO.-21:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 79%; Peak Loading June 2019 DT-2: 70%
762 | 1251 | KWR | GOKUL PURI | KWL005 | D BLOCK BHAGRATHI VIHAR:PL | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 87%; Peak Loading June 2019 DT-2: 48%
763 | 1251 | KWR | GOKUL PURI | KWL014 | D BL BRIJPURI GALI NO. 10:ID | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 84%
764 | 1251 | KWR | GOKUL PURI | KWL019 | A BLK G N 2 BHAGIRATHI VIHAR NO-II :ID | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 82%; Peak Loading June 2019 DT-2: 89%
765 | 1251 | KWR | GOKUL PURI | KWL027 | A BLOCK BRIJ PURI:ID | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 102%; Peak Loading June 2019 DT-2: 60%
766 | 1251 | KWR | GOKUL PURI | KWL028 | B BLOCK BRIJ PURI:ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 93%
767 | 1251 | KWR | GOKUL PURI | KWL039 | GANGA VIHAR NO-1:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 75%; Peak Loading June 2019 DT-2: 97%
768 | 1251 | KWR | GOKUL PURI | KWL040 | GANGA VIHAR NO-2:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 114%; Peak Loading June 2019 DT-2: 116%
769 | 1251 | KWR | GOKUL PURI | KWL044 | GALI NO.3 OLD MUSTAFABAD:ID | 2 | KVA DT-1: 990; KVA DT-2: 400; Peak Loading June 2019 DT-1: 87%; Peak Loading June 2019 DT-2: 93%
770 | 1251 | KWR | GOKUL PURI | KWL052 | B BLOCK GOKUL PURI:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 85%
771 | 1251 | KWR | GOKUL PURI | KWL053 | JAWHAR NAGAR NO.-1:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 90%; Peak Loading June 2019 DT-2: 105%
772 | 1251 | KWR | GOKUL PURI | KWL077 | SAMPAT NAGAR 1:ID | 2 | KVA DT-1: 630; KVA DT-2: 400; Peak Loading June 2019 DT-1: 54%; Peak Loading June 2019 DT-2: 103%
773 | 1251 | KWR | GOKUL PURI | KWL101 | MANSINGH NAGAR GALI NO. 16:ID | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 79%; Peak Loading June 2019 DT-2: 81%
774 | 1251 | KWR | GOKUL PURI | KWL103 | MAJOR MALHOTRA FARM HOUSE:PM | 1 | KVA DT-1: 100; Peak Loading June 2019 DT-1: 85%
775 | 1251 | KWR | GOKUL PURI | KWL107 | JOHRIPUR GUJARMAL MOHALLA:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 94%
776 | 1251 | KWR | GOKUL PURI | KWL162 | JAIN COMPLEX JOHIRIPUR:PM | 1 | KVA DT-1: 100; Peak Loading June 2019 DT-1: 87%
777 | 1251 | KWR | GOKUL PURI | KWL237 | SHANI BAZAR ROAD JOHRI PUR :PM | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 144%
778 | 1251 | KWR | GOKUL PURI | KWL243 | G & H BLK MUSTAFABAD GALI NO. 18:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 111%; Peak Loading June 2019 DT-2: 90%
779 | 1251 | KWR | GOKUL PURI | KWL246 | C BLOCK BRIJ PURI:ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 99%
780 | 1251 | KWR | GOKUL PURI | KWL331 | GALI NO.5 JAWAHAR NAGAR P/M | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 94%
781 | 1251 | KWR | GOKUL PURI | KWL344 | MAIN ROAD MCD SCHOOL JOHRI PUR | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 118%
782 | 1251 | KWR | GOKUL PURI | KWL349 | G BLK GANGA VIHAR(SHAMSHAAN GHAT) | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 90%; Peak Loading June 2019 DT-2: 37%
783 | 1251 | KWR | KARAWAL NAGAR | KWL010 | MUKUND VIHAR "A" BLK:ID | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 95%
784 | 1251 | KWR | KARAWAL NAGAR | KWL013 | C BLK MUKUND VIHAR GALI NO. 9:ID | 1 | KVA DT-1: 1600; Peak Loading June 2019 DT-1: 122%
785 | 1251 | KWR | KARAWAL NAGAR | KWL031 | PREM NAGAR S/STN :ID | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 101%; Peak Loading June 2019 DT-2: 53%
786 | 1251 | KWR | KARAWAL NAGAR | KWL033 | MAHALAXMI ENCLAVE:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 89%; Peak Loading June 2019 DT-2: 90%
787 | 1251 | KWR | KARAWAL NAGAR | KWL046 | C C KARAWAL NAGAR S/STN. NO. 2:I/D | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 94%; Peak Loading June 2019 DT-2: 78%
788 | 1251 | KWR | KARAWAL NAGAR | KWL056 | KARWAL NAGAR NO.-1 DAL MILL:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 88%; Peak Loading June 2019 DT-2: 94%
789 | 1251 | KWR | KARAWAL NAGAR | KWL058 | KARWAL NAGAR NO.-4:PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 78%; Peak Loading June 2019 DT-2: 86%
790 | 1251 | KWR | KARAWAL NAGAR | KWL059 | KARWAL NAGAR NO.-5 SBI KWR:PL | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 110%; Peak Loading June 2019 DT-2: 83%; Peak Loading June 2019 DT-3: 83%
791 | 1251 | KWR | KARAWAL NAGAR | KWL100 | SAHID BHAGAT SINGH CLY GALI NO 16:ID | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 98%
792 | 1251 | KWR | KARAWAL NAGAR | KWL264 | WEST KAMAL VIHAR (HVDS) INDUT. AREA:PM | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 98%
793 | 1251 | KWR | KARAWAL NAGAR | KWL287 | BABU NAGAR 1 GALI NO. 5:ID | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 91%
794 | 1251 | KWR | KARAWAL NAGAR | KWL296 | SAHID BHAGAT SINGH CLY GALI NO 6:ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 87%
795 | 1251 | KWR | SONIA VIHAR | KWL016 | CHANDU NAGAR:ID | 2 | KVA DT-1: 990; KVA DT-2: 400; Peak Loading June 2019 DT-1: 60%; Peak Loading June 2019 DT-2: 106%
796 | 1251 | KWR | SONIA VIHAR | KWL017 | E BLOCK KHAJOORI GALI NO. 3:ID | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 74%; Peak Loading June 2019 DT-2: 90%
797 | 1251 | KWR | SONIA VIHAR | KWL018 | F BLOCK KHAJOORI GALI NO. 11&13:ID | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 98%; Peak Loading June 2019 DT-2: 86%
798 | 1251 | KWR | SONIA VIHAR | KWL022 | B-II BLOCK NEHRU VIHAR GALI NO. 6:ID | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 148%
799 | 1251 | KWR | SONIA VIHAR | KWL026 | E-1, NEHRU VIHAR:ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 90%
800 | 1251 | KWR | SONIA VIHAR | KWL060 | C BLOCK KHAJORI MAIN MARKET | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 88%; Peak Loading June 2019 DT-2: 79%; Peak Loading June 2019 DT-3: 103%
801 | 1251 | KWR | SONIA VIHAR | KWL061 | FATMA NURSARY CHAND BAGH MRD WZB ROAD:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 88%
802 | 1251 | KWR | SONIA VIHAR | KWL063 | VILLAGE SABHAPUR:PM | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 120%
803 | 1251 | KWR | SONIA VIHAR | KWL064 | SHERPUR CHOWK:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 79%; Peak Loading June 2019 DT-2: 99%
804 | 1251 | KWR | SONIA VIHAR | KWL069 | DAYAL PUR 1 TANKI MAIN ROAD DAYAL PUR:PL | 3 | KVA DT-1: 630; KVA DT-2: 630; KVA DT-3: 630; Peak Loading June 2019 DT-1: 69%; Peak Loading June 2019 DT-2: 90%; Peak Loading June 2019 DT-3: 61%
805 | 1251 | KWR | SONIA VIHAR | KWL070 | B BLK GALI NO. 9, CHAND BAGH:ID | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 93%; Peak Loading June 2019 DT-2: 89%
806 | 1251 | KWR | SONIA VIHAR | KWL072 | VILLAGE KHAJOORI NR.SCHOOL:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 95%
807 | 1251 | KWR | SONIA VIHAR | KWL076 | A BL MAIN ROAD DAYALPUR:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 100%
808 | 1251 | KWR | SONIA VIHAR | KWL079 | B BLK SADAT PUR GALI NO. 8:ID | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 92%
809 | 1251 | KWR | SONIA VIHAR | KWL080 | BIHARI PUR VILLNR. NLA KHJURI PUST RD:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 85%
810 | 1251 | KWR | SONIA VIHAR | KWL083 | L BLK SADAT PUR:ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 90%
811 | 1251 | KWR | SONIA VIHAR | KWL085 | B BLK PUSTA 1 SONIA VIHAR GALI NO 1 | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 93%
812 | 1251 | KWR | SONIA VIHAR | KWL093 | CHAUHAN PATTI PUSTA VILL SONIA VIHAR:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 113%
813 | 1251 | KWR | SONIA VIHAR | KWL096 | B-I, NEHRU VIHAR:ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 118%
814 | 1251 | KWR | SONIA VIHAR | KWL113 | SONIA VIHAR "B" BLK GALI NO-27 | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 131%
815 | 1251 | KWR | SONIA VIHAR | KWL115 | C 1 KHAJOORI GALI NO. 24:PM | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 110%
816 | 1251 | KWR | SONIA VIHAR | KWL119 | F BLK DAYAL PUR : ID | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 79%
817 | 1251 | KWR | SONIA VIHAR | KWL121 | JEEVAN JYOTI SCHOOL SADAT PUR : ID | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 44%; Peak Loading June 2019 DT-2: 117%
818 | 1251 | KWR | SONIA VIHAR | KWL127 | NIKKA PLASTIC TUKMEERPUR VILLAGE:PM | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 125%
819 | 1251 | KWR | SONIA VIHAR | KWL145 | SHRI RAM COLONY B BLK RAMLILA GROUND | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 122%
820 | 1251 | KWR | SONIA VIHAR | KWL146 | C BLK SHRI RAM COLONY :PLM | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 111%
821 | 1251 | KWR | SONIA VIHAR | KWL147 | SHRI RAM COLONY D BLK:PLM | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 125%
822 | 1251 | KWR | SONIA VIHAR | KWL154 | SHRI RAM CLY E BLK GN 3 NR MASJID :PM | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 97%
823 | 1251 | KWR | SONIA VIHAR | KWL157 | D BLOCK GALI NO 2 DAYAL PUR | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 98%; Peak Loading June 2019 DT-2: 101%
824 | 1251 | KWR | SONIA VIHAR | KWL158 | D-3 NEHRU VIHAR : ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 88%; Peak Loading June 2019 DT-2: 82%
825 | 1251 | KWR | SONIA VIHAR | KWL234 | B BLK SHRI RAM COLONY :PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 117%
826 | 1251 | KWR | SONIA VIHAR | KWL235 | A BLK SHRI RAM CLY NEAR GALI 26:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 120%
827 | 1251 | KWR | SONIA VIHAR | KWL249 | A BLOCK SHRI RAM CLY. NEAR SERVICE RD:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 117%
828 | 1251 | KWR | SONIA VIHAR | KWL251 | A BLK KHAJOORI:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 119%
829 | 1251 | KWR | SONIA VIHAR | KWL292 | E BLOCK CHAND BAGH:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 129%
830 | 1251 | KWR | SONIA VIHAR | KWL295 | K BLK SADAT PUR EXT. GALI NO. 51:ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 88%
831 | 1251 | KWR | SONIA VIHAR | KWL297 | B BLK SHRI RAM COLONY SAITAN CHOWK:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 123%
832 | 1251 | KWR | SONIA VIHAR | KWL298 | Delhi Police Training Center:PM | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 115%
833 | 1260 | NNG | C-4 NANDNAGRI | NGR006 | JANTA FLAT S/S NO.1 GTB ENCLAVE:ID | 3 | KVA DT-1: 990; KVA DT-2: 630; KVA DT-3: 630; Peak Loading June 2019 DT-1: 97%; Peak Loading June 2019 DT-2: 117%; Peak Loading June 2019 DT-3: 61%
834 | 1260 | NNG | C-4 NANDNAGRI | NGR007 | JANTA FLAT S/S NO.2 GTB ENCLAVE:ID | 3 | KVA DT-1: 630; KVA DT-2: 630; KVA DT-3: 630; Peak Loading June 2019 DT-1: 83%; Peak Loading June 2019 DT-2: 94%; Peak Loading June 2019 DT-3: 82%
835 | 1260 | NNG | C-4 NANDNAGRI | NGR008 | JANTA FLAT S/S NO.3 GTB ENCLAVE:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 76%; Peak Loading June 2019 DT-2: 94%
836 | 1260 | NNG | C-4 NANDNAGRI | NGR014 | I.J K BLOCK SUNDER NAGARI:K | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 88%; Peak Loading June 2019 DT-2: 73%
837 | 1260 | NNG | C-4 NANDNAGRI | NGR015 | MN BLOCK SUNDER NAGARI:K | 3 | KVA DT-1: 630; KVA DT-2: 630; KVA DT-3: 630; Peak Loading June 2019 DT-1: 46%; Peak Loading June 2019 DT-2: 88%; Peak Loading June 2019 DT-3: 53%
838 | 1260 | NNG | C-4 NANDNAGRI | NGR016 | E-1 NAND NAGARI PK WALA GAGAN CINEMA:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 88%
839 | 1260 | NNG | C-4 NANDNAGRI | NGR018 | E-4 NAND NAGARI:ID | 3 | KVA DT-1: 630; KVA DT-2: 630; KVA DT-3: 630; Peak Loading June 2019 DT-1: 101%; Peak Loading June 2019 DT-2: 100%; Peak Loading June 2019 DT-3: 100%
840 | 1260 | NNG | C-4 NANDNAGRI | NGR019 | JAGAT PURI EXT.NO.1:ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 89%
841 | 1260 | NNG | C-4 NANDNAGRI | NGR020 | JAGAT PURI EXT.NO.2:ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 76%
842 | 1260 | NNG | C-4 NANDNAGRI | NGR021 | A-4 NAND NAGARI:ID | 3 | KVA DT-1: 630; KVA DT-2: 990; KVA DT-3: 990; Peak Loading June 2019 DT-1: 73%; Peak Loading June 2019 DT-2: 80%; Peak Loading June 2019 DT-3: 81%
843 | 1260 | NNG | C-4 NANDNAGRI | NGR022 | B-4 NAND NAGARI AKHADA WALA :ID | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; KVA DT-4: 630; Peak Loading June 2019 DT-1: 60%; Peak Loading June 2019 DT-2: 69%; Peak Loading June 2019 DT-3: 83%; Peak Loading June 2019 DT-4: 80%
844 | 1260 | NNG | C-4 NANDNAGRI | NGR023 | C BLOCK COMPLAINT CENTRE NNG:ID | 4 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; KVA DT-4: 630; Peak Loading June 2019 DT-1: 62%; Peak Loading June 2019 DT-2: 88%; Peak Loading June 2019 DT-3: 93%; Peak Loading June 2019 DT-4: 68%
845 | 1260 | NNG | C-4 NANDNAGRI | NGR030 | MANDOLI S/S-4 (PANI KI TANKI) :PL | 2 | KVA DT-1: 990; KVA DT-2: 400; Peak Loading June 2019 DT-1: 85%; Peak Loading June 2019 DT-2: 59%
846 | 1260 | NNG | C-4 NANDNAGRI | NGR035 | MANDOLI EXTN.NO.1,GALI NO.-9:ID | 2 | KVA DT-1: 400; KVA DT-2: 990; Peak Loading June 2019 DT-1: 97%; Peak Loading June 2019 DT-2: 88%
847 | 1260 | NNG | C-4 NANDNAGRI | NGR044 | SAFAI KARAMCHARI NAND NAGARI-E BLK:ID | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 84%
848 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1002 | B-BLOCK MEET NAGAR:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 98%; Peak Loading June 2019 DT-2: 76%
849 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1009 | GOKUL PUR VILL NO.KAPOOR WALA PETROL:PL | 3 | KVA DT-1: 990; KVA DT-2: 630; KVA DT-3: 630; Peak Loading June 2019 DT-1: 78%; Peak Loading June 2019 DT-2: 49%; Peak Loading June 2019 DT-3: 37%
850 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1017 | E JYOTI NAGAR BEHAIND JOYATI NURSING:ID | 4 | KVA DT-1: 630; KVA DT-2: 990; KVA DT-3: 990; KVA DT-4: 630; Peak Loading June 2019 DT-1: 92%; Peak Loading June 2019 DT-2: 124%; Peak Loading June 2019 DT-3: 101%; Peak Loading June 2019 DT-4: 93%
851 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1024 | EAST OF LONI ROAD,MIG,S/STN-7:ID | 2 | KVA DT-1: 400; KVA DT-2: 400; Peak Loading June 2019 DT-1: 91%; Peak Loading June 2019 DT-2: 84%
852 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1028 | D-BLOCK ASHOK NAGAR GALI NO-3:ID | 3 | KVA DT-1: 990; KVA DT-2: 630; KVA DT-3: 990; Peak Loading June 2019 DT-1: 96%; Peak Loading June 2019 DT-2: 87%; Peak Loading June 2019 DT-3: 95%
853 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1029 | B-BLOCK ASHOK NAGAR SCHOOL WALA:K | 3 | KVA DT-1: 990; KVA DT-2: 630; KVA DT-3: 990; Peak Loading June 2019 DT-1: 114%; Peak Loading June 2019 DT-2: 94%; Peak Loading June 2019 DT-3: 116%
854 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1031 | HARDEV PURI NO.1:ID | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 81%
855 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1032 | HARDEVPURI NO.2 ( JOSHI WALA):PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 116%
856 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1033 | E-1 BLK ASHOK NAGAR.KANCH WALA NR S BHAWAN:K | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 93%; Peak Loading June 2019 DT-2: 78%
857 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1034 | ASHOK NAGAR NO EXTN NO 1 KACHCHI CLY:PL | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 69%; Peak Loading June 2019 DT-2: 113%
858 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1035 | NATHU COLONY:K | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 92%; Peak Loading June 2019 DT-2: 70%
859 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1043 | LALITA MANDIR ASHOK NAGAR D BLK:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 92%
860 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1045 | HARIJAN BASTI, AKHADA EAST GOKAL PUR:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 89%; Peak Loading June 2019 DT-2: 76%
861 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1047 | D-1 ASHOK NAGAR WAZIRA BAD ROAD:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 115%
862 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1053 | D 1/1 BLK ASHOK NAGAR DP :PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 94%
863 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1055 | LONI BORDER S/S NO-1 | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 104%
864 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1056 | LONI BORDER S/S NO-2 | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 139%
865 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1060 | DURGA PURI MAIN GALI - 10:ID | 3 | KVA DT-1: 630; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 142%; Peak Loading June 2019 DT-2: 130%; Peak Loading June 2019 DT-3: 78%
866 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1061 | JAGAT PURI MAIN:PL | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 96%; Peak Loading June 2019 DT-2: 149%
867 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1063 | JAG JIVAN NAGAR:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 109%
868 | 1260 | NNG | MIG EAST OF LONI ROAD | LO1066 | CHANDER LOK:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 119%
869 | 1260 | NNG | SUDAMA PURI | LO2004 | JYOTI COLONY NO.1:K | 2 | KVA DT-1: 630; KVA DT-2: 400; Peak Loading June 2019 DT-1: 139%; Peak Loading June 2019 DT-2: 101%
870 | 1260 | NNG | SUDAMA PURI | LO2006 | JYOTI COLONY NO.3:K | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 65%; Peak Loading June 2019 DT-2: 109%
871 | 1260 | NNG | SUDAMA PURI | LO2007 | AMBEDKAR PARK:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 98%; Peak Loading June 2019 DT-2: 123%
872 | 1260 | NNG | SUDAMA PURI | LO2009 | SHIV MANDIR 100 FT. RD:PL | 2 | KVA DT-1: 990; KVA DT-2: 400; Peak Loading June 2019 DT-1: 75%; Peak Loading June 2019 DT-2: 101%
873 | 1260 | NNG | SUDAMA PURI | LO2012 | BABAR PUR VILLAGE:PL | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 83%; Peak Loading June 2019 DT-2: 66%
874 | 1260 | NNG | SUDAMA PURI | LO2013 | MAHA DEVI SCHOOL:PL | 2 | KVA DT-1: 630; KVA DT-2: 630; Peak Loading June 2019 DT-1: 114%; Peak Loading June 2019 DT-2: 87%
875 | 1260 | NNG | SUDAMA PURI | LO2016 | SUDAMA PURI NO.3:PL | 1 | KVA DT-1: 990; Peak Loading June 2019 DT-1: 100%
876 | 1260 | NNG | SUDAMA PURI | LO2018 | SUDAMAPURI NO. 4:PL | 1 | KVA DT-1: 400; Peak Loading June 2019 DT-1: 120%
877 | 1260 | NNG | SUDAMA PURI | LO2020 | BALBIR NAGAR EXT.:PL | 2 | KVA DT-1: 990; KVA DT-2: 630; Peak Loading June 2019 DT-1: 149%; Peak Loading June 2019 DT-2: 75%
878 | 1260 | NNG | SUDAMA PURI | LO2021 | D BLOCK KABIR NAGAR(SHAMSHAN GHAT) | 3 | KVA DT-1: 990; KVA DT-2: 630; KVA DT-3: 630; Peak Loading June 2019 DT-1: 98%; Peak Loading June 2019 DT-2: 81%; Peak Loading June 2019 DT-3: 43%
879 | 1260 | NNG | SUDAMA PURI | LO2023 | A BLOCK KABIR NAGAR:ID | 3 | KVA DT-1: 990; KVA DT-2: 990; KVA DT-3: 630; Peak Loading June 2019 DT-1: 98%; Peak Loading June 2019 DT-2: 56%; Peak Loading June 2019 DT-3: 52%
880 | 1260 | NNG | SUDAMA PURI | LO2025 | B-BLOCK KABIR NAGAR:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 82%; Peak Loading June 2019 DT-2: 77%
881 | 1260 | NNG | SUDAMA PURI | LO2026 | C BLOCK KABIR NAGAR | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 97%; Peak Loading June 2019 DT-2: 69%
882 | 1260 | NNG | SUDAMA PURI | LO2028 | HARIJAN BASTI WEST JYOTI NARAR:ID | 2 | KVA DT-1: 630; KVA DT-2: 400; Peak Loading June 2019 DT-1: 99%; Peak Loading June 2019 DT-2: 117%
883 | 1260 | NNG | SUDAMA PURI | LO2029 | KARDAM MARG KHET WALA:-PL | 2 | KVA DT-1: 630; KVA DT-2: 990; Peak Loading June 2019 DT-1: 70%; Peak Loading June 2019 DT-2: 103%
884 | 1260 | NNG | SUDAMA PURI | LO2030 | KARDAM PURI AZAD CHOWK:-ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 90%; Peak Loading June 2019 DT-2: 70%
885 | 1260 | NNG | SUDAMA PURI | LO2031 | NEW KARDAMPURI NO 1 GALI NO -4:PL | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 96%
886 | 1260 | NNG | SUDAMA PURI | LO2032 | NORTH CHAJJUPUR:ID | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 104%; Peak Loading June 2019 DT-2: 76%
887 | 1260 | NNG | SUDAMA PURI | LO2041 | West Jyoti Ngr(Beh. Gopal Nur Home):-PL | 2 | KVA DT-1: 990; KVA DT-2: 990; Peak Loading June 2019 DT-1: 91%; Peak Loading June 2019 DT-2: 67%
888 | 1260 | NNG | SUDAMA PURI | LO2044 | CNG STATION LONI ROAD:PM | 2 | KVA DT-1: 400; KVA DT-2: 400; Peak Loading June 2019 DT-1: 4%; Peak Loading June 2019 DT-2: 89%
889 | 1260 | NNG | SUDAMA PURI | LO2046 | SUDAMAPURI S/S- 5 Nr. BABARPUR BUS TERM. | 1 | KVA DT-1: 630; Peak Loading June 2019 DT-1: 141%

## Chronic Overloaded DTs >6 Month
Chronic Overloaded DTs (>70% Overloaded From Last 6 Months ) -January2019 To June2019
Month Wise Total Overloaded Hrs.
Sr.No. | SDO | DIVISION | ZONE | SSTN SAP CODE | DT CODE | SSTN NAME | NO OF DTs | DT KVA | DT Meter No. | 2019-01-01 | 2019-02-01 | 2019-03-01 | 2019-04-01 | 2019-05-01 | 2019-06-01 | Loss Band
1 | 1141 | PNR | SARAI ROHILLA | PNR101 | TG-PNR101A-1 | S/STN NO.15 GALI NO.8 KALA PAHAR | 2 | 990 | 19506290 | 113.5 | 170.5 | 468 | 250 | 243 | 61 | Loss 5-10%
2 | 1141 | PNR | SARAI ROHILLA | PNR101 | TG-PNR101A-2 | S/STN NO.15 GALI NO.8 KALA PAHAR | 2 | 990 | 19505749 | 242.5 | 168 | 430 | 152.5 | 78 | 241 | Loss 5-10%
3 | 1141 | PNR | SARAI ROHILLA | PNR104 | TG-PNR104A-2 | ZONAL OFF. K. PAHAR:PL | 2 | 990 | 19506080 | 44 | 90 | 179 | 189 | 182.5 | 138.5 | Loss 0-5%
4 | 1141 | PNR | SARAI ROHILLA | PNR106 | TG-PNR106A-2 | TIN MKT. K. PAHAR:PL | 2 | 630 | 19505104 | 181 | 143.5 | 129 | 274.5 | 303.5 | 282 | Loss 0-5%
5 | 1141 | PNR | SARAI ROHILLA | PNR120 | TG-PNR120A-1 | SOHAN SINGH K.PAHAR:PL | 3 | 630 | 19506568 | 112.5 | 122 | 261 | 199 | 223.5 | 177.5 | Loss 5-10%
6 | 1141 | PNR | SARAI ROHILLA | PNR138 | TG-PNR138A-1 | RIWA GALI NO-4 | 1 | 990 | 19502594 | 65 | 69.5 | 46 | 91.5 | 137 | 72 | Loss 5-10%
7 | 1141 | PNR | SARAI ROHILLA | PNR149 | TG-PNR149A-1 | HR. ROAD ANAND PARVAT | 2 | 630 | 19504684 | 178 | 231 | 236 | 205 | 249 | 239.5 | Loss 0-5%
8 | 1211 | GTR | E&F DILSHAD GARDEN | DGN069 | TG-DGN069A-2 | A-BLOCK JHILMIL INDILSHAD AREA:ID | 4 | 990 | 19501371 | 283.5 | 265 | 279.5 | 247.5 | 190.5 | 80 | Loss 5-10%
9 | 1211 | GTR | E&F DILSHAD GARDEN | DGN071 | TG-DGN071A-1 | B-BLK COMPLAINT CENTER JLM IND AREA:ID | 3 | 990 | 19506356 | 101 | 141 | 218 | 175 | 152.5 | 166 | Loss 0-5%
10 | 1211 | GTR | E&F DILSHAD GARDEN | DGN073 | TG-DGN073A-1 | SARDAR ALUMINIUM:ID | 1 | 990 | 19501448 | 89.5 | 69 | 64.5 | 121.5 | 165.5 | 194 | Loss 0-5%
11 | 1211 | GTR | E&F DILSHAD GARDEN | DGN077 | TG-DGN077A-2 | SANSAR:K | 3 | 990 | 19505904 | 138 | 102.5 | 128 | 87.5 | 60.5 | 84.5 | Loss 0-5%
12 | 1211 | GTR | E&F DILSHAD GARDEN | DGN077 | TG-DGN077A-3 | SANSAR:K | 3 | 990 | 19506621 | 102.5 | 175.5 | 386 | 243.5 | 254 | 263 | Loss 0-5%
13 | 1211 | GTR | E&F DILSHAD GARDEN | DGN081 | TG-DGN081A-3 | DILSHAD GDN S/STN-4:ID | 4 | 630 | 19504435 | 231 | 97.5 | 165 | 213 | 348.5 | 231 | Loss 5-10%
14 | 1211 | GTR | E&F DILSHAD GARDEN | DGN101 | TG-DGN101A-2 | B-BLK DSIDC SHED JLM IA NO-3:ID | 2 | 630 | 19501353 | 192.5 | 218 | 209.5 | 225 | 196 | 216 | Loss 0-5%
15 | 1211 | GTR | E&F DILSHAD GARDEN | DGN103 | TG-DGN103A-2 | A BLK TAHIRPUR(JLM IND AREA) S/STN-1:ID | 3 | 630 | 19501356 | 133 | 107 | 82.5 | 123.5 | 143.5 | 191 | Loss 0-5%
16 | 1211 | GTR | E&F DILSHAD GARDEN | DGN104 | TG-DGN104A-1 | A BLK TAHIRPUR(JLM IND AREA) S/STN-3:ID | 4 | 630 | 19505489 | 164 | 188 | 350 | 147.5 | 119.5 | 151.5 | Loss 0-5%
17 | 1211 | GTR | E&F DILSHAD GARDEN | DGN109 | TG-DGN109A-1 | B-34 JLM INDUSTRIAL AREA | 1 | 990 | 19501836 | 206 | 210.5 | 167.5 | 136 | 217.5 | 239 | Loss 0-5%
18 | 1211 | GTR | E&F DILSHAD GARDEN | DGN112 | TG-DGN112A-1 | DAMODAR PARK,DILSHAD GARDEN:PL | 4 | 990 | 19506505 | 350.5 | 306.5 | 604 | 285 | 270 | 284 | Loss 0-5%
19 | 1211 | GTR | E&F DILSHAD GARDEN | DGN112 | TG-DGN112A-2 | DAMODAR PARK,DILSHAD GARDEN:PL | 4 | 990 | 19502279 | 426.5 | 359.5 | 352.5 | 194 | 193 | 237.5 | Loss 0-5%
20 | 1211 | GTR | E&F DILSHAD GARDEN | DGN112 | TG-DGN112A-3 | DAMODAR PARK,DILSHAD GARDEN:PL | 4 | 990 | 19505439 | 259.5 | 196.5 | 92.5 | 355 | 338.5 | 336.5 | Loss 0-5%
21 | 1211 | GTR | E&F DILSHAD GARDEN | DGN114 | TG-DGN114A-1 | JHULFE BENGAL S/S NO. 2:PL | 3 | 630 | 19506419 | 184.5 | 174.5 | 343 | 264.5 | 290 | 384.5 | Loss 0-5%
22 | 1211 | GTR | E&F DILSHAD GARDEN | DGN114 | TG-DGN114A-3 | JHULFE BENGAL S/S NO. 2:PL | 3 | 990 | 19500063 | 131 | 145.5 | 73.5 | 157 | 224 | 271 | Loss 0-5%
23 | 1211 | GTR | E&F DILSHAD GARDEN | DGN128 | TG-DGN128A-1 | JULFE BENGAL S/S NO.I | 3 | 990 | 19505545 | 302.5 | 277 | 542 | 230 | 165.5 | 58 | Loss 0-5%
24 | 1211 | GTR | E&F DILSHAD GARDEN | DGN128 | TG-DGN128A-3 | JULFE BENGAL S/S NO.I | 3 | 630 | 19506329 | 173 | 263.5 | 420 | 300.5 | 149 | 253 | Loss 0-5%
25 | 1211 | GTR | E&F DILSHAD GARDEN | DGN147 | TG-DGN147A-1 | SATISH STEEL ROLLING MILL:ID | 2 | 630 | 19506363 | 142 | 108 | 226 | 92.5 | 61.5 | 73.5 | Loss 5-10%
26 | 1211 | GTR | E&F DILSHAD GARDEN | DGN232 | TG-DGN232A-2 | DSIDC SUBSTATION NO-2 | 4 | 990 | 19501354 | 163 | 161 | 157 | 172 | 182.5 | 167 | Loss 0-5%
27 | 1211 | GTR | E&F DILSHAD GARDEN | DGN232 | TG-DGN232A-3 | DSIDC SUBSTATION NO-2 | 4 | 990 | 19505129 | 389 | 346.5 | 354.5 | 367.5 | 346 | 373.5 | Loss 0-5%
28 | 1211 | GTR | E&F DILSHAD GARDEN | DGN237 | TG-DGN237A-2 | B-42 JHILMIL IND AREA NEARRAILWAY LINE | 2 | 990 | 19505961 | 118.5 | 55.5 | 55 | 43 | 75 | 70 | Loss 0-5%
29 | 1211 | GTR | E&F DILSHAD GARDEN | DGN252 | TG-DGN252A-1 | RAILWAY LINE IN FRONT OF B-43 JHILMIL | 1 | 990 | 19506619 | 117.5 | 138 | 254 | 167 | 188.5 | 253 | Loss 5-10%
30 | 1211 | GTR | GT ROAD SHAHDRA | DGN074 | TG-DGN074A-1 | RAJ ENGG.COMPOUND | 2 | 990 | 19501787 | 163.5 | 173 | 150 | 197.5 | 191.5 | 219.5 | Loss 0-5%
31 | 1211 | GTR | GT ROAD SHAHDRA | DGN075 | TG-DGN075A-1 | PAPER PRODUCT | 2 | 990 | 19505761 | 70 | 66 | 150 | 81.5 | 90.5 | 150 | Loss 0-5%
32 | 1211 | GTR | GT ROAD SHAHDRA | DGN105 | TG-DGN105A-1 | SHAMBU NATH COMP.(F.COL):ID | 5 | 990 | 19505392 | 266.5 | 276 | 270 | 274 | 299 | 294 | Loss 0-5%
33 | 1211 | GTR | GT ROAD SHAHDRA | DGN105 | TG-DGN105A-3 | SHAMBU NATH COMP.(F.COL):ID | 5 | 990 | 19505434 | 139.5 | 122 | 88.5 | 53 | 40.5 | 72 | Loss 0-5%
34 | 1211 | GTR | GT ROAD SHAHDRA | DGN105 | TG-DGN105A-4 | SHAMBU NATH COMP.(F.COL):ID | 5 | 990 | 19505076 | 240.5 | 191.5 | 145.5 | 185 | 145 | 120 | Loss 0-5%
35 | 1211 | GTR | GT ROAD SHAHDRA | DGN110 | TG-DGN110A-1 | VERMA CASTLE:PL | 6 | 990 | 19503035 | 237.5 | 188 | 162.5 | 225.5 | 172 | 105.5 | Loss 0-5%
36 | 1211 | GTR | GT ROAD SHAHDRA | DGN110 | TG-DGN110A-3 | VERMA CASTLE:PL | 6 | 630 | 19505004 | 140.5 | 75 | 94.5 | 67 | 140.5 | 63.5 | Loss 0-5%
37 | 1211 | GTR | GT ROAD SHAHDRA | DGN110 | TG-DGN110A-5 | VERMA CASTLE:PL | 6 | 990 | 19506053 | 42.5 | 106.5 | 213 | 149.5 | 144 | 214.5 | Loss 0-5%
38 | 1211 | GTR | GT ROAD SHAHDRA | DGN111 | TG-DGN111A-1 | FRIENDS COLONY GALI NO.1 | 3 | 990 | 19500654 | 139 | 97 | 106 | 150 | 116 | 142 | Loss 5-10%
39 | 1211 | GTR | GT ROAD SHAHDRA | DGN127 | TG-DGN127A-2 | GALI NO.1B FRIENDS COLONY:PL | 4 | 990 | 19504119 | 181.5 | 154.5 | 152.5 | 147 | 77 | 98 | Loss 0-5%
40 | 1211 | GTR | GT ROAD SHAHDRA | DGN129 | TG-DGN129A-2 | FRIENDS COLONY GALI NO-5-6 NEAR RLY.LINE:PM | 6 | 990 | 19506017 | 210.5 | 206 | 279 | 104 | 175.5 | 237 | Loss 0-5%
41 | 1211 | GTR | GT ROAD SHAHDRA | DGN129 | TG-DGN129A-4 | FRIENDS COLONY GALI NO-5-6 NEAR RLY.LINE:PM | 6 | 990 | 19505079 | 78 | 71 | 184.5 | 186 | 228 | 248.5 | Loss 0-5%
42 | 1211 | GTR | GT ROAD SHAHDRA | DGN178 | TG-DGN178A-1 | HANSRAJ COMPOUND S/STN | 4 | 990 | 19505895 | 176.5 | 180.5 | 312 | 142 | 196 | 150.5 | Loss 0-5%
43 | 1211 | GTR | GT ROAD SHAHDRA | DGN198 | TG-DGN198A-1 | GALI NO-1 METRO PARKING SS-2 | 3 | 990 | 19506421 | 163 | 197 | 606 | 294 | 291.5 | 271 | Loss 5-10%
44 | 1211 | GTR | GT ROAD SHAHDRA | DGN231 | TG-DGN231A-1 | GALI NO-1 RAILWAY LINE FRIENDS COLONY | 2 | 990 | 19504996 | 185.5 | 75 | 128.5 | 217 | 205.5 | 193 | Loss 5-10%
45 | 1211 | GTR | GT ROAD SHAHDRA | DGN231 | TG-DGN231A-2 | GALI NO-1 RAILWAY LINE FRIENDS COLONY | 2 | 630 | 19506054 | 195 | 218 | 430 | 227.5 | 185 | 227.5 | Loss 5-10%
46 | 1211 | GTR | GT ROAD SHAHDRA | DGN236 | TG-DGN236A-1 | 1B Friends colony near railway line. | 1 | 990 | 19505054 | 254.5 | 48 | 96 | 141 | 99 | 117.5 | Loss 5-10%
47 | 1220 | KNR | GANDHI NAGAR | GAN025 | TG-GAN025A-1 | R.PURA GALI NO 6 (IN SIDE):PL | 1 | 990 | 19506600 | 41.5 | 148 | 242 | 255.5 | 285.5 | 252 | Loss 5-10%
48 | 1220 | KNR | GANDHI NAGAR | GAN029 | TG-GAN029A-1 | SEELAMPUR PHATAK:PL | 2 | 990 | 19506480 | 311 | 321.5 | 521 | 474 | 335.5 | 151 | Loss >30%
49 | 1220 | KNR | KRISHNA NAGAR | KRI035 | TG-KRI035A-1 | PANDIT PARK:PM | 1 | 990 | 19500865 | 27.5 | 103 | 85.5 | 178.5 | 258 | 296 | Loss >30%
50 | 1230 | LNR | ANAND VIHAR ISBT | PVR034 | TG-PVR034A-1 | S/STN. NO.8 F.I.E., PPG:ID | 3 | 630 | 19505921 | 64.5 | 38.5 | 170 | 161 | 119.5 | 124 | Loss 5-10%
51 | 1230 | LNR | ANAND VIHAR ISBT | PVR040 | TG-PVR040A-2 | S/STN. NO.15 F.I.E., PPG:ID | 2 | 400 | 19504783 | 108 | 81 | 74.5 | 160.5 | 202.5 | 122 | Loss 0-5%
52 | 1230 | LNR | MANDAWALI | MAN026 | TG-MAN026A-2 | WESTVINOD NAGAR NEAR MANGLAM:PL | 3 | 990 | 19506134 | 146.5 | 121.5 | 177 | 244.5 | 512.5 | 543.5 | Loss 5-10%
53 | 1240 | MVR | S/STN 8 POCKET C | MV2010 | TG-MV2010A-2 | E BLOCK V. NAGAR:PL | 3 | 990 | 19502553 | 104 | 82 | 41.5 | 86.5 | 81.5 | 128 | Loss 5-10%
54 | 1250 | YVR | GHONDA | GHO019 | TG-GHO019A-1 | KHADDEY WALI MASJID:PM | 1 | 630 | 19506336 | 119 | 84.5 | 66 | 333.5 | 710 | 698 | Loss 10-20%
55 | 1250 | YVR | GHONDA | GHO040 | TG-GHO040A-1 | MAIN BRAHMPURI RD GALI NO.19:PM | 1 | 630 | 19506050 | 87.5 | 28.5 | 47 | 249.5 | 425 | 568 | Loss 5-10%
56 | 1251 | KWR | GOKUL PURI | KWL053 | TG-KWL053A-2 | JAWHAR NAGAR NO.-1:PL | 2 | 990 | 19504953 | 137 | 126.5 | 151.5 | 181 | 173 | 184 | Loss 5-10%
57 | 1251 | KWR | GOKUL PURI | KWL237 | TG-KWL237A-1 | SHANI BAZAR ROAD JOHRI PUR :PM | 1 | 630 | 19505924 | 144.5 | 175.5 | 388 | 213.5 | 174 | 166 | Loss 5-10%
58 | 1251 | KWR | GOKUL PURI | KWL331 | TG-KWL331A-1 | GALI NO.5 JAWAHAR NAGAR P/M | 1 | 990 | 19504775 | 138 | 65.5 | 29 | 133 | 124.5 | 131 | Loss 10-20%
59 | 1251 | KWR | GOKUL PURI | KWL344 | TG-KWL344A-1 | MAIN ROAD MCD SCHOOL JOHRI PUR | 1 | 990 | 19505304 | 69.5 | 203 | 76.5 | 222 | 261.5 | 208 | Loss 10-20%
60 | 1251 | KWR | KARAWAL NAGAR | KWL010 | TG-KWL010A-1 | MUKUND VIHAR "A" BLK:ID | 1 | 630 | 19500537 | 64.5 | 54.5 | 26.5 | 69 | 117 | 201.5 | Loss 5-10%
61 | 1251 | KWR | KARAWAL NAGAR | KWL056 | TG-KWL056A-2 | KARWAL NAGAR NO.-1 DAL MILL:PL | 2 | 990 | 19506728 | 189.5 | 188 | 319 | 213 | 235.5 | 134 | Loss 10-20%
62 | 1251 | KWR | KARAWAL NAGAR | KWL058 | TG-KWL058A-2 | KARWAL NAGAR NO.-4:PL | 2 | 990 | 19503507 | 130.5 | 36 | 47 | 86.5 | 125.5 | 102.5 | Loss 10-20%
63 | 1251 | KWR | KARAWAL NAGAR | KWL059 | TG-KWL059A-1 | KARWAL NAGAR NO.-5 SBI KWR:PL | 3 | 990 | 19500596 | 161.5 | 183.5 | 177 | 193 | 186 | 147.5 | Loss 10-20%
64 | 1251 | KWR | KARAWAL NAGAR | KWL059 | TG-KWL059A-2 | KARWAL NAGAR NO.-5 SBI KWR:PL | 3 | 990 | 19502963 | 160 | 96 | 162.5 | 198 | 35 | 93.5 | Loss 10-20%
65 | 1251 | KWR | KARAWAL NAGAR | KWL264 | TG-KWL264A-1 | WEST KAMAL VIHAR (HVDS) INDUT. AREA:PM | 1 | 400 | 19505888 | 89 | 72.5 | 79 | 60 | 58 | 77 | Loss 0-5%
66 | 1251 | KWR | SONIA VIHAR | KWL064 | TG-KWL064A-2 | SHERPUR CHOWK:PL | 2 | 630 | 19506395 | 98.5 | 136.5 | 195 | 146 | 171 | 137 | Loss 10-20%